## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_392_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_392_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_392_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_392_0_node_179 | 20 | n |  | TRUE
4 | bus_MV_392_0_node_123 | 20 | n |  | TRUE
5 | bus_MV_392_0_node_10 | 20 | n |  | TRUE
6 | bus_MV_392_0_node_3 | 20 | n |  | TRUE
7 | bus_MV_392_0_node_4 | 20 | n |  | TRUE
8 | bus_MV_392_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_392_0_node_12 | 20 | n |  | TRUE
10 | bus_MV_392_0_node_13 | 20 | n |  | TRUE
11 | bus_MV_392_0_node_11 | 20 | n |  | TRUE
12 | bus_MV_392_0_node_6 | 20 | n |  | TRUE
13 | bus_MV_392_0_node_16 | 20 | n |  | TRUE
14 | bus_MV_392_0_node_14 | 20 | n |  | TRUE
15 | bus_MV_392_0_node_15 | 20 | n |  | TRUE
16 | bus_MV_392_0_node_140 | 20 | n |  | TRUE
17 | bus_MV_392_0_node_92 | 20 | n |  | TRUE
18 | bus_MV_392_0_node_141 | 20 | n |  | TRUE
19 | bus_MV_392_0_node_142 | 20 | n |  | TRUE
20 | bus_MV_392_0_node_144 | 20 | n |  | TRUE
21 | bus_MV_392_0_node_146 | 20 | n |  | TRUE
22 | bus_MV_392_0_node_78 | 20 | n |  | TRUE
23 | bus_MV_392_0_node_74 | 20 | n |  | TRUE
24 | bus_MV_392_0_node_133 | 20 | n |  | TRUE
25 | bus_MV_392_0_node_134 | 20 | n |  | TRUE
26 | bus_MV_392_0_node_58 | 20 | n |  | TRUE
27 | bus_MV_392_0_node_135 | 20 | n |  | TRUE
28 | bus_MV_392_0_node_48 | 20 | n |  | TRUE
29 | bus_MV_392_0_node_55 | 20 | n |  | TRUE
30 | bus_MV_392_0_node_45 | 20 | n |  | TRUE
31 | bus_MV_392_0_node_46 | 20 | n |  | TRUE
32 | bus_MV_392_0_node_47 | 20 | n |  | TRUE
33 | bus_MV_392_0_node_56 | 20 | n |  | TRUE
34 | bus_MV_392_0_node_49 | 20 | n |  | TRUE
35 | bus_MV_392_0_node_50 | 20 | n |  | TRUE
36 | bus_MV_392_0_node_52 | 20 | n |  | TRUE
37 | bus_MV_392_0_node_53 | 20 | n |  | TRUE
38 | bus_MV_392_0_node_51 | 20 | n |  | TRUE
39 | bus_MV_392_0_node_59 | 20 | n |  | TRUE
40 | bus_MV_392_0_node_54 | 20 | n |  | TRUE
41 | bus_MV_392_0_node_57 | 20 | n |  | TRUE
42 | bus_MV_392_0_node_86 | 20 | n |  | TRUE
43 | bus_MV_392_0_node_181 | 20 | n |  | TRUE
44 | bus_MV_392_0_node_182 | 20 | n |  | TRUE
45 | bus_MV_392_0_node_69 | 20 | n |  | TRUE
46 | bus_MV_392_0_node_64 | 20 | n |  | TRUE
47 | bus_MV_392_0_node_65 | 20 | n |  | TRUE
48 | bus_MV_392_0_node_66 | 20 | n |  | TRUE
49 | bus_MV_392_0_node_93 | 20 | n |  | TRUE
50 | bus_MV_392_0_node_176 | 20 | n |  | TRUE
51 | bus_MV_392_0_node_67 | 20 | n |  | TRUE
52 | bus_MV_392_0_node_68 | 20 | n |  | TRUE
53 | bus_MV_392_0_node_82 | 20 | n |  | TRUE
54 | bus_MV_392_0_node_72 | 20 | n |  | TRUE
55 | bus_MV_392_0_node_70 | 20 | n |  | TRUE
56 | bus_MV_392_0_node_177 | 20 | n |  | TRUE
57 | bus_MV_392_0_node_71 | 20 | n |  | TRUE
58 | bus_MV_392_0_node_95 | 20 | n |  | TRUE
59 | bus_MV_392_0_node_91 | 20 | n |  | TRUE
60 | bus_MV_392_0_node_79 | 20 | n |  | TRUE
61 | bus_MV_392_0_node_94 | 20 | n |  | TRUE
62 | bus_MV_392_0_node_81 | 20 | n |  | TRUE
63 | bus_MV_392_0_node_83 | 20 | n |  | TRUE
64 | bus_MV_392_0_node_84 | 20 | n |  | TRUE
65 | bus_MV_392_0_node_85 | 20 | n |  | TRUE
66 | bus_MV_392_0_node_87 | 20 | n |  | TRUE
67 | bus_HV_392_0_node_95 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_392_0_load_0 | 0 | 0.26136 | 0.12658 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_392_0_load_179 | 3 | 0.14188 | 0.068715 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_392_0_load_123 | 4 | 0.18496 | 0.089582 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_392_0_load_10 | 5 | 0.19083 | 0.092424 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_392_0_load_3 | 6 | 0.36853 | 0.17849 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_392_0_load_11 | 11 | 0.30113 | 0.14584 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_392_0_load_6 | 12 | 0.17667 | 0.085566 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_392_0_load_16 | 13 | 0.15974 | 0.077363 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_392_0_load_15 | 15 | 0.22068 | 0.10688 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_392_0_load_140 | 16 | 0.10812 | 0.052365 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_392_0_load_142 | 19 | 0.28518 | 0.13812 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_392_0_load_144 | 20 | 0.099942 | 0.048404 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_392_0_load_146 | 21 | 0.12658 | 0.061305 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_392_0_load_74 | 23 | 0.3523 | 0.17063 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_392_0_load_133 | 24 | 0.28247 | 0.13681 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_392_0_load_134 | 25 | 0.12611 | 0.061076 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_392_0_load_135 | 27 | 0.079039 | 0.038281 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_392_0_load_45 | 30 | 0.32834 | 0.15902 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_392_0_load_56 | 33 | 0.21168 | 0.10252 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_392_0_load_49 | 34 | 0.30163 | 0.14608 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_392_0_load_59 | 39 | 0.16111 | 0.078028 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_392_0_load_54 | 40 | 0.31849 | 0.15425 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_392_0_load_181 | 43 | 0.086356 | 0.041824 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_392_0_load_182 | 44 | 0.31478 | 0.15246 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_392_0_load_64 | 46 | 0.20338 | 0.098501 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_392_0_load_93 | 49 | 0.26218 | 0.12698 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_392_0_load_176 | 50 | 0.24577 | 0.11903 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_392_0_load_67 | 51 | 0.33838 | 0.16388 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_392_0_load_177 | 56 | 0.12628 | 0.061161 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_392_0_load_95 | 58 | 0.18737 | 0.090746 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_392_0_load_91 | 59 | 0.19694 | 0.095381 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_392_0_load_94 | 61 | 0.37345 | 0.18087 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_392_0_load_81 | 62 | 0.19716 | 0.095489 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_392_0_load_84 | 64 | 0.19549 | 0.094679 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 58 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_392_0_line_0 |  | 0 | 1 | 0.082936 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_392_0_line_1 |  | 1 | 2 | 0.97959 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
2 | MV_392_0_line_2 |  | 1 | 3 | 1.9913 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
3 | MV_392_0_line_3 |  | 2 | 4 | 0.084091 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
4 | MV_392_0_line_4 |  | 2 | 5 | 0.41061 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_392_0_line_5 |  | 3 | 36 | 0.070304 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
6 | MV_392_0_line_6 |  | 4 | 9 | 0.050794 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
7 | MV_392_0_line_7 |  | 6 | 7 | 0.010597 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_392_0_line_8 |  | 7 | 8 | 0.5276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_392_0_line_9 |  | 8 | 9 | 0.18341 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
10 | MV_392_0_line_10 |  | 8 | 10 | 0.33937 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
11 | MV_392_0_line_11 |  | 8 | 11 | 0.010497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_392_0_line_12 |  | 10 | 14 | 0.40519 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
13 | MV_392_0_line_13 |  | 10 | 15 | 0.055853 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_392_0_line_14 |  | 12 | 13 | 0.63819 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
15 | MV_392_0_line_15 |  | 13 | 14 | 0.055925 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
16 | MV_392_0_line_16 |  | 16 | 17 | 0.055125 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_392_0_line_17 |  | 16 | 18 | 0.07522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_392_0_line_18 |  | 17 | 57 | 0.63828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_392_0_line_19 |  | 18 | 19 | 0.089166 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_392_0_line_20 |  | 19 | 20 | 0.14273 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_392_0_line_21 |  | 21 | 22 | 0.063337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_392_0_line_22 |  | 21 | 23 | 0.05759 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_392_0_line_23 |  | 22 | 60 | 0.71362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_392_0_line_24 |  | 22 | 45 | 0.13904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_392_0_line_25 |  | 24 | 25 | 0.0044713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_392_0_line_26 |  | 25 | 26 | 0.083193 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_392_0_line_27 |  | 26 | 42 | 0.67313 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
28 | MV_392_0_line_28 |  | 26 | 41 | 0.38921 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
29 | MV_392_0_line_29 |  | 27 | 28 | 0.094685 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
30 | MV_392_0_line_30 |  | 27 | 29 | 0.022104 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
31 | MV_392_0_line_31 |  | 28 | 31 | 0.97313 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
32 | MV_392_0_line_32 |  | 29 | 37 | 0.015884 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
33 | MV_392_0_line_33 |  | 30 | 31 | 0.046514 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_392_0_line_34 |  | 31 | 32 | 0.083279 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
35 | MV_392_0_line_35 |  | 32 | 33 | 0.05111 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
36 | MV_392_0_line_36 |  | 33 | 41 | 0.042099 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
37 | MV_392_0_line_37 |  | 34 | 35 | 0.12087 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_392_0_line_38 |  | 35 | 36 | 0.5523 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
39 | MV_392_0_line_39 |  | 35 | 37 | 0.27387 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
40 | MV_392_0_line_40 |  | 36 | 38 | 0.39376 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_392_0_line_41 |  | 37 | 40 | 0.037844 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_392_0_line_42 |  | 38 | 39 | 0.050251 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_392_0_line_43 |  | 42 | 66 | 0.66486 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
44 | MV_392_0_line_44 |  | 42 | 43 | 0.023428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_392_0_line_45 |  | 44 | 45 | 0.037851 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_392_0_line_46 |  | 45 | 48 | 0.50279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_392_0_line_47 |  | 46 | 47 | 0.028031 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_392_0_line_48 |  | 47 | 48 | 0.31992 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_392_0_line_49 |  | 47 | 49 | 0.22088 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_392_0_line_50 |  | 48 | 50 | 0.036157 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_392_0_line_51 |  | 49 | 66 | 0.051215 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_392_0_line_52 |  | 51 | 52 | 0.01191 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
53 | MV_392_0_line_53 |  | 51 | 53 | 0.3014 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
54 | MV_392_0_line_54 |  | 52 | 54 | 0.88522 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
55 | MV_392_0_line_55 |  | 53 | 63 | 0.32473 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
56 | MV_392_0_line_56 |  | 53 | 62 | 0.065909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_392_0_line_57 |  | 54 | 59 | 0.041237 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_392_0_line_58 |  | 54 | 55 | 0.20736 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_392_0_line_59 |  | 54 | 57 | 0.42393 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
60 | MV_392_0_line_60 |  | 55 | 56 | 0.006668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_392_0_line_61 |  | 57 | 58 | 0.1086 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
62 | MV_392_0_line_62 |  | 60 | 61 | 0.061556 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_392_0_line_63 |  | 63 | 64 | 0.023703 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
64 | MV_392_0_line_64 |  | 64 | 65 | 0.10446 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
65 | MV_392_0_line_65 |  | 65 | 66 | 0.14887 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_392_0_trafo_95 | 25 MVA 110/20 kV | 67 | 58 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2613453.5063 | 1230377.4979
1 | 2613482.0161 | 1230299.6156
2 | 2613616.9745 | 1229503.6798
3 | 2611609.9628 | 1229620.7474
4 | 2613700.4542 | 1229513.804
5 | 2613493.2807 | 1229112.1438
6 | 2613638.2751 | 1229719.3793
7 | 2613641.6915 | 1229709.3478
8 | 2613894.6141 | 1229575.0728
9 | 2613750.8784 | 1229519.9185
10 | 2613879.0789 | 1229297.6936
11 | 2613896.1959 | 1229585.4494
12 | 2613513.5018 | 1228689.3936
13 | 2614030.7491 | 1229063.2082
14 | 2614024.6565 | 1229118.7937
15 | 2613829.6271 | 1229271.7301
16 | 2612210.5957 | 1227395.6891
17 | 2612211.7036 | 1227450.8029
18 | 2612204.5644 | 1227321.4452
19 | 2612116.7042 | 1227338.0652
20 | 2611976.5401 | 1227365.0284
21 | 2611271.7812 | 1227174.1421
22 | 2611315.885 | 1227218.8819
23 | 2611245.7503 | 1227122.7707
24 | 2610940.144 | 1228859.678
25 | 2610938.0751 | 1228863.6418
26 | 2610877.0257 | 1228872.7248
27 | 2611223.8316 | 1229473.4066
28 | 2611162.3885 | 1229401.3647
29 | 2611244.7707 | 1229480.4883
30 | 2611052.576 | 1229149.2553
31 | 2611020.9509 | 1229115.0655
32 | 2610956.7235 | 1229062.6274
33 | 2610911.6095 | 1229038.6085
34 | 2611250.9834 | 1229709.2584
35 | 2611141.4571 | 1229658.1341
36 | 2611539.8153 | 1229615.1972
37 | 2611259.2416 | 1229487.1306
38 | 2611635.1283 | 1229421.3553
39 | 2611620.3998 | 1229469.3997
40 | 2611279.6557 | 1229455.2945
41 | 2610874.1685 | 1229019.151
42 | 2610623.2226 | 1228249.2769
43 | 2610621.8246 | 1228225.8939
44 | 2611264.2163 | 1227296.6303
45 | 2611287.7636 | 1227266.946
46 | 2610944.6716 | 1227596.8035
47 | 2610923.4139 | 1227615.0754
48 | 2611038.1043 | 1227369.3407
49 | 2610810.4176 | 1227804.8602
50 | 2611052.9721 | 1227336.382
51 | 2611258.6032 | 1227754.3457
52 | 2611270.4194 | 1227752.6003
53 | 2611225.2239 | 1228053.8936
54 | 2611603.8463 | 1227640.1157
55 | 2611540.0119 | 1227500.1539
56 | 2611540.4992 | 1227506.8032
57 | 2611808.5807 | 1227735.3393
58 | 2611911.5151 | 1227770.8311
59 | 2611645.0187 | 1227637.8054
60 | 2611115.599 | 1226897.806
61 | 2611089.6004 | 1226953.6018
62 | 2611162.4932 | 1228067.1285
63 | 2610984.9997 | 1227988.0976
64 | 2610961.3032 | 1227989.9997
65 | 2610856.9224 | 1227998.9481
66 | 2610817.987 | 1227855.2592
67 | 2611911.5151 | 1227770.8311

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98182 | -0.49358 | 0.26136 | 0.12658
1 | 0.98186 | -0.49331 | 0 | 0
2 | 0.98118 | -0.50689 | 0 | 0
3 | 0.98554 | -0.36127 | 0.14188 | 0.068715
4 | 0.98113 | -0.5079 | 0.18496 | 0.089582
5 | 0.98102 | -0.50788 | 0.19083 | 0.092424
6 | 0.98072 | -0.50777 | 0.36853 | 0.17849
7 | 0.98073 | -0.50772 | 0 | 0
8 | 0.98098 | -0.50993 | 0 | 0
9 | 0.9811 | -0.50843 | 0 | 0
10 | 0.98087 | -0.5112 | 0 | 0
11 | 0.98097 | -0.50989 | 0.30113 | 0.14584
12 | 0.98065 | -0.51559 | 0.17667 | 0.085566
13 | 0.98079 | -0.51219 | 0.15974 | 0.077363
14 | 0.9808 | -0.51208 | 0 | 0
15 | 0.98085 | -0.51136 | 0.22068 | 0.10688
16 | 0.99922 | -0.0031597 | 0.10812 | 0.052365
17 | 0.99926 | -0.0034688 | 0 | 0
18 | 0.99919 | -0.0028279 | 0 | 0
19 | 0.99914 | -0.0024234 | 0.28518 | 0.13812
20 | 0.99912 | -0.0025971 | 0.099942 | 0.048404
21 | 0.99017 | -0.16677 | 0.12658 | 0.061305
22 | 0.99021 | -0.16713 | 0 | 0
23 | 0.99013 | -0.16702 | 0.3523 | 0.17063
24 | 0.9888 | -0.28762 | 0.28247 | 0.13681
25 | 0.9888 | -0.28763 | 0.12611 | 0.061076
26 | 0.98885 | -0.28804 | 0 | 0
27 | 0.98646 | -0.34285 | 0.079039 | 0.038281
28 | 0.98673 | -0.33325 | 0 | 0
29 | 0.98643 | -0.34338 | 0 | 0
30 | 0.98792 | -0.30876 | 0.32834 | 0.15902
31 | 0.98794 | -0.30895 | 0 | 0
32 | 0.98805 | -0.30663 | 0 | 0
33 | 0.98821 | -0.30083 | 0.21168 | 0.10252
34 | 0.98605 | -0.3501 | 0.30163 | 0.14608
35 | 0.98612 | -0.34964 | 0 | 0
36 | 0.9856 | -0.36006 | 0 | 0
37 | 0.98641 | -0.34376 | 0 | 0
38 | 0.98552 | -0.3594 | 0 | 0
39 | 0.9855 | -0.3595 | 0.16111 | 0.078028
40 | 0.9864 | -0.34361 | 0.31849 | 0.15425
41 | 0.98827 | -0.29958 | 0 | 0
42 | 0.99137 | -0.19751 | 0 | 0
43 | 0.99137 | -0.19749 | 0.086356 | 0.041824
44 | 0.99034 | -0.16825 | 0.31478 | 0.15246
45 | 0.99036 | -0.1684 | 0 | 0
46 | 0.99167 | -0.17941 | 0.20338 | 0.098501
47 | 0.99169 | -0.17934 | 0 | 0
48 | 0.99111 | -0.17462 | 0 | 0
49 | 0.99237 | -0.17414 | 0.26218 | 0.12698
50 | 0.99109 | -0.17473 | 0.24577 | 0.11903
51 | 0.99587 | -0.080305 | 0.33838 | 0.16388
52 | 0.9959 | -0.079654 | 0 | 0
53 | 0.99404 | -0.14506 | 0 | 0
54 | 0.9984 | -0.031126 | 0 | 0
55 | 0.99837 | -0.030847 | 0 | 0
56 | 0.99837 | -0.030837 | 0.12628 | 0.061161
57 | 0.99966 | -0.0067096 | 0 | 0
58 | 1 | 0 | -7.41 | -3.2639
59 | 0.99839 | -0.031225 | 0.19694 | 0.095381
60 | 0.98987 | -0.16427 | 0 | 0
61 | 0.98982 | -0.16455 | 0.37345 | 0.18087
62 | 0.99402 | -0.1449 | 0.19716 | 0.095489
63 | 0.99319 | -0.16153 | 0 | 0
64 | 0.99313 | -0.16273 | 0.19549 | 0.094679
65 | 0.99287 | -0.16786 | 0 | 0
66 | 0.9925 | -0.17517 | 0 | 0
67 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.26136 | -0.12658 | 0.26137 | 0.12649 | 1.0771e-05 | -8.8701e-05 | 0.0085382 | 0.008537 | 0.0085382 | 0.98182 | -0.49358 | 0.98186 | -0.49331 | 4.0658
1 | 1.604 | 0.69017 | -1.603 | -0.72535 | 0.00095276 | -0.035177 | 0.051338 | 0.051766 | 0.051766 | 0.98186 | -0.49331 | 0.98118 | -0.50689 | 12.296
2 | -1.8653 | -0.81666 | 1.8704 | 0.82153 | 0.005085 | 0.0048679 | 0.059868 | 0.059838 | 0.059868 | 0.98186 | -0.49331 | 0.98554 | -0.36127 | 14.6019
3 | 1.4122 | 0.63338 | -1.4121 | -0.63641 | 6.3867e-05 | -0.0030339 | 0.045535 | 0.045572 | 0.045572 | 0.98118 | -0.50689 | 0.98113 | -0.5079 | 10.8248
4 | 0.19086 | 0.09197 | -0.19083 | -0.092424 | 2.8452e-05 | -0.00045401 | 0.0062333 | 0.0062393 | 0.0062393 | 0.98118 | -0.50689 | 0.98102 | -0.50788 | 2.9711
5 | -2.0123 | -0.89025 | 2.0124 | 0.88774 | 0.00010684 | -0.0025107 | 0.064453 | 0.064422 | 0.064453 | 0.98554 | -0.36127 | 0.9856 | -0.36006 | 15.3095
6 | 1.2271 | 0.54683 | -1.2271 | -0.54867 | 2.9063e-05 | -0.0018411 | 0.039528 | 0.03955 | 0.03955 | 0.98113 | -0.5079 | 0.9811 | -0.50843 | 9.3944
7 | -0.36853 | -0.17849 | 0.36853 | 0.17848 | 2.7429e-06 | -1.045e-05 | 0.012053 | 0.012053 | 0.012053 | 0.98072 | -0.50777 | 0.98073 | -0.50772 | 5.7395
8 | -0.36853 | -0.17848 | 0.36863 | 0.16639 | 0.00010102 | -0.012089 | 0.012053 | 0.011902 | 0.012053 | 0.98073 | -0.50772 | 0.98098 | -0.50993 | 5.4786
9 | -1.227 | -0.55463 | 1.2271 | 0.54867 | 0.00013883 | -0.0059549 | 0.039624 | 0.03955 | 0.039624 | 0.98098 | -0.50993 | 0.9811 | -0.50843 | 10.9457
10 | 0.55719 | 0.24264 | -0.55714 | -0.2538 | 5.2815e-05 | -0.011164 | 0.017884 | 0.018018 | 0.018018 | 0.98098 | -0.50993 | 0.98087 | -0.5112 | 4.9773
11 | 0.30113 | 0.1456 | -0.30113 | -0.14584 | 1.3581e-06 | -0.00024078 | 0.009843 | 0.0098461 | 0.0098461 | 0.98098 | -0.50993 | 0.98097 | -0.50989 | 4.4755
12 | 0.33645 | 0.14698 | -0.33643 | -0.16034 | 2.3192e-05 | -0.013356 | 0.010806 | 0.010969 | 0.010969 | 0.98087 | -0.5112 | 0.9808 | -0.51208 | 3.0301
13 | 0.22068 | 0.10682 | -0.22068 | -0.10688 | 5.1818e-06 | -6.0904e-05 | 0.0072157 | 0.0072165 | 0.0072165 | 0.98087 | -0.5112 | 0.98085 | -0.51136 | 3.4364
14 | -0.17667 | -0.085566 | 0.17669 | 0.084817 | 1.9529e-05 | -0.00074901 | 0.0057785 | 0.0057687 | 0.0057785 | 0.98065 | -0.51559 | 0.98079 | -0.51219 | 1.651
15 | -0.33643 | -0.16218 | 0.33643 | 0.16034 | 3.257e-06 | -0.0018432 | 0.010993 | 0.010969 | 0.010993 | 0.98079 | -0.51219 | 0.9808 | -0.51208 | 3.0366
16 | -0.49328 | -0.23481 | 0.4933 | 0.2335 | 1.8313e-05 | -0.0013087 | 0.015783 | 0.015767 | 0.015783 | 0.99922 | -0.0031597 | 0.99926 | -0.0034688 | 7.1741
17 | 0.38516 | 0.18245 | -0.38514 | -0.18423 | 1.5251e-05 | -0.0017886 | 0.012312 | 0.012335 | 0.012335 | 0.99922 | -0.0031597 | 0.99919 | -0.0028279 | 5.6067
18 | -0.4933 | -0.2335 | 0.4935 | 0.21834 | 0.00020934 | -0.015161 | 0.015767 | 0.015584 | 0.015767 | 0.99926 | -0.0034688 | 0.99966 | -0.0067096 | 7.1667
19 | 0.38514 | 0.18423 | -0.38512 | -0.18635 | 1.815e-05 | -0.00212 | 0.012335 | 0.012361 | 0.012361 | 0.99919 | -0.0028279 | 0.99914 | -0.0024234 | 5.6188
20 | 0.099944 | 0.048236 | -0.099942 | -0.048404 | 2.6162e-06 | -0.00016846 | 0.0032063 | 0.0032085 | 0.0032085 | 0.99914 | -0.0024234 | 0.99912 | -0.0025971 | 1.5278
21 | -0.4789 | -0.23187 | 0.47892 | 0.2304 | 2.0322e-05 | -0.0014767 | 0.015512 | 0.015493 | 0.015512 | 0.99017 | -0.16677 | 0.99021 | -0.16713 | 7.051
22 | 0.35232 | 0.17057 | -0.3523 | -0.17063 | 1.3364e-05 | -5.9033e-05 | 0.011412 | 0.011413 | 0.011413 | 0.99017 | -0.16677 | 0.99013 | -0.16702 | 5.4347
23 | 0.37361 | 0.16415 | -0.37347 | -0.18081 | 0.00013711 | -0.01666 | 0.011897 | 0.012101 | 0.012101 | 0.99021 | -0.16713 | 0.98987 | -0.16427 | 5.5004
24 | -0.85252 | -0.39455 | 0.85266 | 0.39133 | 0.00013901 | -0.0032143 | 0.027386 | 0.027346 | 0.027386 | 0.99021 | -0.16713 | 0.99036 | -0.1684 | 12.4483
25 | -0.28247 | -0.13681 | 0.28247 | 0.1367 | 5.0109e-07 | -0.00010423 | 0.0091628 | 0.0091615 | 0.0091628 | 0.9888 | -0.28762 | 0.9888 | -0.28763 | 4.1649
26 | -0.40858 | -0.19778 | 0.4086 | 0.19584 | 1.9469e-05 | -0.0019364 | 0.013252 | 0.013228 | 0.013252 | 0.9888 | -0.28763 | 0.98885 | -0.28804 | 6.0237
27 | -3.8292 | -1.6705 | 3.8363 | 1.68 | 0.0071362 | 0.0094777 | 0.12196 | 0.12195 | 0.12196 | 0.98885 | -0.28804 | 0.99137 | -0.19751 | 29.7463
28 | 3.4206 | 1.4746 | -3.4189 | -1.4876 | 0.0016871 | -0.012982 | 0.10874 | 0.10891 | 0.10891 | 0.98885 | -0.28804 | 0.98827 | -0.29958 | 25.8695
29 | -2.8744 | -1.2637 | 2.875 | 1.2644 | 0.00056983 | 0.00070572 | 0.091886 | 0.091885 | 0.091886 | 0.98646 | -0.34285 | 0.98673 | -0.33325 | 22.4113
30 | 2.7954 | 1.2254 | -2.7953 | -1.2262 | 6.4548e-05 | -0.00076242 | 0.089318 | 0.089328 | 0.089328 | 0.98646 | -0.34285 | 0.98643 | -0.34338 | 21.218
31 | -2.875 | -1.2644 | 2.878 | 1.2309 | 0.0029932 | -0.033491 | 0.091885 | 0.091463 | 0.091885 | 0.98673 | -0.33325 | 0.98794 | -0.30895 | 21.8254
32 | 2.7953 | 1.2262 | -2.7953 | -1.2267 | 4.6393e-05 | -0.00054784 | 0.089328 | 0.089335 | 0.089335 | 0.98643 | -0.34338 | 0.98641 | -0.34376 | 21.2196
33 | -0.32834 | -0.15902 | 0.32835 | 0.15794 | 7.0478e-06 | -0.0010818 | 0.01066 | 0.010647 | 0.01066 | 0.98792 | -0.30876 | 0.98794 | -0.30895 | 4.8457
34 | -3.2063 | -1.3888 | 3.2067 | 1.386 | 0.00031763 | -0.0028139 | 0.1021 | 0.10206 | 0.1021 | 0.98794 | -0.30895 | 0.98805 | -0.30663 | 24.2519
35 | -3.2067 | -1.386 | 3.207 | 1.3865 | 0.0003795 | 0.00048486 | 0.10206 | 0.10206 | 0.10206 | 0.98805 | -0.30663 | 0.98821 | -0.30083 | 24.8938
36 | -3.4187 | -1.489 | 3.4189 | 1.4876 | 0.0001828 | -0.0014028 | 0.10893 | 0.10891 | 0.10893 | 0.98821 | -0.30083 | 0.98827 | -0.29958 | 25.8738
37 | -0.30163 | -0.14608 | 0.30165 | 0.14596 | 2.0728e-05 | -0.00012732 | 0.0098116 | 0.0098098 | 0.0098116 | 0.98605 | -0.3501 | 0.98612 | -0.34964 | 4.6722
38 | 2.1745 | 0.93697 | -2.1735 | -0.95658 | 0.00097453 | -0.019612 | 0.069314 | 0.069554 | 0.069554 | 0.98612 | -0.34964 | 0.9856 | -0.36006 | 16.5211
39 | -2.4762 | -1.0829 | 2.4768 | 1.0733 | 0.00062646 | -0.0096018 | 0.079116 | 0.078997 | 0.079116 | 0.98612 | -0.34964 | 0.98641 | -0.34376 | 18.7923
40 | 0.16112 | 0.068844 | -0.16111 | -0.077972 | 1.4137e-05 | -0.0091276 | 0.005132 | 0.0052428 | 0.0052428 | 0.9856 | -0.36006 | 0.98552 | -0.3594 | 2.3831
41 | 0.3185 | 0.15337 | -0.31849 | -0.15425 | 5.4129e-06 | -0.00087756 | 0.010345 | 0.010356 | 0.010356 | 0.98641 | -0.34376 | 0.9864 | -0.34361 | 4.7075
42 | 0.16111 | 0.077972 | -0.16111 | -0.078028 | 2.4614e-06 | -5.6723e-05 | 0.0052428 | 0.0052436 | 0.0052436 | 0.98552 | -0.3594 | 0.9855 | -0.3595 | 2.4969
43 | -3.9227 | -1.7212 | 3.9265 | 1.6997 | 0.0037773 | -0.021523 | 0.12474 | 0.12444 | 0.12474 | 0.99137 | -0.19751 | 0.9925 | -0.17517 | 29.6284
44 | 0.086356 | 0.041275 | -0.086356 | -0.041824 | 2.4355e-07 | -0.00054969 | 0.002787 | 0.002794 | 0.002794 | 0.99137 | -0.19751 | 0.99137 | -0.19749 | 1.27
45 | -0.31478 | -0.15246 | 0.31479 | 0.15157 | 5.2464e-06 | -0.00088482 | 0.010195 | 0.010184 | 0.010195 | 0.99034 | -0.16825 | 0.99036 | -0.1684 | 4.6341
46 | -1.1675 | -0.54291 | 1.1684 | 0.5314 | 0.00094174 | -0.011504 | 0.037529 | 0.037386 | 0.037529 | 0.99036 | -0.1684 | 0.99111 | -0.17462 | 17.0587
47 | -0.20338 | -0.098501 | 0.20338 | 0.098469 | 2.161e-06 | -3.1556e-05 | 0.0065781 | 0.0065777 | 0.0065781 | 0.99167 | -0.17941 | 0.99169 | -0.17934 | 3.1324
48 | 1.415 | 0.64314 | -1.4142 | -0.65039 | 0.00087611 | -0.0072477 | 0.045246 | 0.045337 | 0.045337 | 0.99169 | -0.17934 | 0.99111 | -0.17462 | 20.6077
49 | -1.6184 | -0.74161 | 1.6195 | 0.74202 | 0.0010568 | 0.00040244 | 0.051822 | 0.051819 | 0.051822 | 0.99169 | -0.17934 | 0.99237 | -0.17414 | 24.6772
50 | 0.24577 | 0.11899 | -0.24577 | -0.11903 | 4.0752e-06 | -3.9847e-05 | 0.0079533 | 0.0079539 | 0.0079539 | 0.99111 | -0.17462 | 0.99109 | -0.17473 | 3.7876
51 | -1.8817 | -0.869 | 1.8819 | 0.86787 | 0.00024848 | -0.0011307 | 0.060291 | 0.060277 | 0.060291 | 0.99237 | -0.17414 | 0.9925 | -0.17517 | 27.4052
52 | -6.5555 | -2.9163 | 6.5557 | 2.916 | 0.00018855 | -0.00027815 | 0.20798 | 0.20798 | 0.20798 | 0.99587 | -0.080305 | 0.9959 | -0.079654 | 49.4018
53 | 6.2172 | 2.7524 | -6.2088 | -2.7407 | 0.0083454 | 0.011696 | 0.19709 | 0.19709 | 0.19709 | 0.99587 | -0.080305 | 0.99404 | -0.14506 | 48.0716
54 | -6.5557 | -2.916 | 6.5697 | 2.8952 | 0.013987 | -0.020784 | 0.20798 | 0.20758 | 0.20798 | 0.9959 | -0.079654 | 0.9984 | -0.031126 | 49.4006
55 | 6.0117 | 2.6467 | -6.0073 | -2.655 | 0.0043278 | -0.0082741 | 0.19075 | 0.1909 | 0.1909 | 0.99404 | -0.14506 | 0.99319 | -0.16153 | 45.3439
56 | 0.19716 | 0.093936 | -0.19716 | -0.095489 | 3.5504e-06 | -0.0015539 | 0.0063424 | 0.006362 | 0.006362 | 0.99404 | -0.14506 | 0.99402 | -0.1449 | 2.8918
57 | 0.19694 | 0.095333 | -0.19694 | -0.095381 | 2.9408e-06 | -4.7229e-05 | 0.0063263 | 0.0063269 | 0.0063269 | 0.9984 | -0.031126 | 0.99839 | -0.031225 | 3.0128
58 | 0.12629 | 0.056069 | -0.12628 | -0.061003 | 4.4838e-06 | -0.0049335 | 0.0039951 | 0.0040551 | 0.0040551 | 0.9984 | -0.031126 | 0.99837 | -0.030847 | 1.8432
59 | -6.8929 | -3.0466 | 6.9003 | 3.0372 | 0.0073606 | -0.0094062 | 0.2179 | 0.21771 | 0.2179 | 0.9984 | -0.031126 | 0.99966 | -0.0067096 | 51.7577
60 | 0.12628 | 0.061003 | -0.12628 | -0.061161 | 1.4646e-07 | -0.00015864 | 0.0040551 | 0.0040571 | 0.0040571 | 0.99837 | -0.030847 | 0.99837 | -0.030837 | 1.8441
61 | -7.3938 | -3.2555 | 7.396 | 3.2534 | 0.0021628 | -0.0021616 | 0.23329 | 0.23325 | 0.23329 | 0.99966 | -0.0067096 | 1 | 0 | 55.4145
62 | 0.37347 | 0.18081 | -0.37345 | -0.18087 | 1.6061e-05 | -6.1941e-05 | 0.012101 | 0.012102 | 0.012102 | 0.98987 | -0.16427 | 0.98982 | -0.16455 | 5.7627
63 | 6.0073 | 2.655 | -6.007 | -2.6556 | 0.00031616 | -0.00060291 | 0.1909 | 0.19091 | 0.19091 | 0.99319 | -0.16153 | 0.99313 | -0.16273 | 45.3464
64 | 5.8115 | 2.5609 | -5.8102 | -2.5637 | 0.0013031 | -0.0027385 | 0.1846 | 0.18464 | 0.18464 | 0.99313 | -0.16273 | 0.99287 | -0.16786 | 43.8586
65 | 5.8102 | 2.5637 | -5.8084 | -2.5676 | 0.0018583 | -0.0038982 | 0.18464 | 0.18471 | 0.18471 | 0.99287 | -0.16786 | 0.9925 | -0.17517 | 43.8742

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 7.5973 | 3.3546

## res_load
| p_mw | q_mvar
0 | 0.26136 | 0.12658
1 | 0.14188 | 0.068715
2 | 0.18496 | 0.089582
3 | 0.19083 | 0.092424
4 | 0.36853 | 0.17849
5 | 0.30113 | 0.14584
6 | 0.17667 | 0.085566
7 | 0.15974 | 0.077363
8 | 0.22068 | 0.10688
9 | 0.10812 | 0.052365
10 | 0.28518 | 0.13812
11 | 0.099942 | 0.048404
12 | 0.12658 | 0.061305
13 | 0.3523 | 0.17063
14 | 0.28247 | 0.13681
15 | 0.12611 | 0.061076
16 | 0.079039 | 0.038281
17 | 0.32834 | 0.15902
18 | 0.21168 | 0.10252
19 | 0.30163 | 0.14608
20 | 0.16111 | 0.078028
21 | 0.31849 | 0.15425
22 | 0.086356 | 0.041824
23 | 0.31478 | 0.15246
24 | 0.20338 | 0.098501
25 | 0.26218 | 0.12698
26 | 0.24577 | 0.11903
27 | 0.33838 | 0.16388
28 | 0.12628 | 0.061161
29 | 0.18737 | 0.090746
30 | 0.19694 | 0.095381
31 | 0.37345 | 0.18087
32 | 0.19716 | 0.095489
33 | 0.19549 | 0.094679

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1