## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_392_1_node_122 | 20 | n |  | TRUE
1 | bus_MV_392_1_node_121 | 20 | n |  | TRUE
2 | bus_MV_392_1_node_119 | 20 | n |  | TRUE
3 | bus_MV_392_1_node_120 | 20 | n |  | TRUE
4 | bus_MV_392_1_node_118 | 20 | n |  | TRUE
5 | bus_MV_392_1_node_17 | 20 | n |  | TRUE
6 | bus_MV_392_1_node_18 | 20 | n |  | TRUE
7 | bus_MV_392_1_node_19 | 20 | n |  | TRUE
8 | bus_MV_392_1_node_27 | 20 | n |  | TRUE
9 | bus_MV_392_1_node_28 | 20 | n |  | TRUE
10 | bus_MV_392_1_node_127 | 20 | n |  | TRUE
11 | bus_MV_392_1_node_180 | 20 | n |  | TRUE
12 | bus_MV_392_1_node_165 | 20 | n |  | TRUE
13 | bus_MV_392_1_node_20 | 20 | n |  | TRUE
14 | bus_MV_392_1_node_129 | 20 | n |  | TRUE
15 | bus_MV_392_1_node_21 | 20 | n |  | TRUE
16 | bus_MV_392_1_node_22 | 20 | n |  | TRUE
17 | bus_MV_392_1_node_23 | 20 | n |  | TRUE
18 | bus_MV_392_1_node_128 | 20 | n |  | TRUE
19 | bus_MV_392_1_node_125 | 20 | n |  | TRUE
20 | bus_MV_392_1_node_126 | 20 | n |  | TRUE
21 | bus_MV_392_1_node_124 | 20 | n |  | TRUE
22 | bus_MV_392_1_node_24 | 20 | n |  | TRUE
23 | bus_MV_392_1_node_173 | 20 | n |  | TRUE
24 | bus_MV_392_1_node_62 | 20 | n |  | TRUE
25 | bus_MV_392_1_node_171 | 20 | n |  | TRUE
26 | bus_MV_392_1_node_167 | 20 | n |  | TRUE
27 | bus_MV_392_1_node_30 | 20 | n |  | TRUE
28 | bus_MV_392_1_node_131 | 20 | n |  | TRUE
29 | bus_MV_392_1_node_132 | 20 | n |  | TRUE
30 | bus_MV_392_1_node_130 | 20 | n |  | TRUE
31 | bus_MV_392_1_node_31 | 20 | n |  | TRUE
32 | bus_MV_392_1_node_43 | 20 | n |  | TRUE
33 | bus_MV_392_1_node_174 | 20 | n |  | TRUE
34 | bus_MV_392_1_node_172 | 20 | n |  | TRUE
35 | bus_MV_392_1_node_42 | 20 | n |  | TRUE
36 | bus_MV_392_1_node_109 | 20 | n |  | TRUE
37 | bus_MV_392_1_node_110 | 20 | n |  | TRUE
38 | bus_MV_392_1_node_117 | 20 | n |  | TRUE
39 | bus_MV_392_1_node_32 | 20 | n |  | TRUE
40 | bus_MV_392_1_node_33 | 20 | n |  | TRUE
41 | bus_MV_392_1_node_35 | 20 | n |  | TRUE
42 | bus_MV_392_1_node_36 | 20 | n |  | TRUE
43 | bus_MV_392_1_node_39 | 20 | n |  | TRUE
44 | bus_MV_392_1_node_34 | 20 | n |  | TRUE
45 | bus_MV_392_1_node_99 | 20 | n |  | TRUE
46 | bus_MV_392_1_node_61 | 20 | n |  | TRUE
47 | bus_MV_392_1_node_60 | 20 | n |  | TRUE
48 | bus_MV_392_1_node_170 | 20 | n |  | TRUE
49 | bus_MV_392_1_node_38 | 20 | n |  | TRUE
50 | bus_MV_392_1_node_37 | 20 | n |  | TRUE
51 | bus_MV_392_1_node_136 | 20 | n |  | TRUE
52 | bus_MV_392_1_node_40 | 20 | n |  | TRUE
53 | bus_MV_392_1_node_44 | 20 | n |  | TRUE
54 | bus_MV_392_1_node_96 | 20 | n |  | TRUE
55 | bus_MV_392_1_node_41 | 20 | n |  | TRUE
56 | bus_MV_392_1_node_139 | 20 | n |  | TRUE
57 | bus_MV_392_1_node_175 | 20 | n |  | TRUE
58 | bus_MV_392_1_node_97 | 20 | n |  | TRUE
59 | bus_MV_392_1_node_76 | 20 | n |  | TRUE
60 | bus_MV_392_1_node_77 | 20 | n |  | TRUE
61 | bus_MV_392_1_node_80 | 20 | n |  | TRUE
62 | bus_MV_392_1_node_75 | 20 | n |  | TRUE
63 | bus_MV_392_1_node_178 | 20 | n |  | TRUE
64 | bus_MV_392_1_node_145 | 20 | n |  | TRUE
65 | bus_MV_392_1_node_88 | 20 | n |  | TRUE
66 | bus_MV_392_1_node_89 | 20 | n |  | TRUE
67 | bus_MV_392_1_node_90 | 20 | n |  | TRUE
68 | bus_MV_392_1_node_138 | 20 | n |  | TRUE
69 | bus_MV_392_1_node_137 | 20 | n |  | TRUE
70 | bus_MV_392_1_node_98 | 20 | n |  | TRUE
71 | bus_MV_392_1_node_147 | 20 | n |  | TRUE
72 | bus_MV_392_1_node_100 | 20 | n |  | TRUE
73 | bus_MV_392_1_node_101 | 20 | n |  | TRUE
74 | bus_MV_392_1_node_102 | 20 | n |  | TRUE
75 | bus_MV_392_1_node_107 | 20 | n |  | TRUE
76 | bus_MV_392_1_node_108 | 20 | n |  | TRUE
77 | bus_MV_392_1_node_164 | 20 | n |  | TRUE
78 | bus_MV_392_1_node_149 | 20 | n |  | TRUE
79 | bus_MV_392_1_node_157 | 20 | n |  | TRUE
80 | bus_MV_392_1_node_103 | 20 | n |  | TRUE
81 | bus_MV_392_1_node_104 | 20 | n |  | TRUE
82 | bus_MV_392_1_node_105 | 20 | n |  | TRUE
83 | bus_MV_392_1_node_106 | 20 | n |  | TRUE
84 | bus_MV_392_1_node_113 | 20 | n |  | TRUE
85 | bus_MV_392_1_node_148 | 20 | n |  | TRUE
86 | bus_MV_392_1_node_112 | 20 | n |  | TRUE
87 | bus_MV_392_1_node_169 | 20 | n |  | TRUE
88 | bus_MV_392_1_node_111 | 20 | n |  | TRUE
89 | bus_MV_392_1_node_152 | 20 | n |  | TRUE
90 | bus_MV_392_1_node_158 | 20 | n |  | TRUE
91 | bus_MV_392_1_node_115 | 20 | n |  | TRUE
92 | bus_MV_392_1_node_156 | 20 | n |  | TRUE
93 | bus_MV_392_1_node_168 | 20 | n |  | TRUE
94 | bus_MV_392_1_node_151 | 20 | n |  | TRUE
95 | bus_MV_392_1_node_159 | 20 | n |  | TRUE
96 | bus_MV_392_1_node_116 | 20 | n |  | TRUE
97 | bus_MV_392_1_node_114 | 20 | n |  | TRUE
98 | bus_MV_392_1_node_161 | 20 | n |  | TRUE
99 | bus_MV_392_1_node_160 | 20 | n |  | TRUE
100 | bus_MV_392_1_node_143 | 20 | n |  | TRUE
101 | bus_MV_392_1_node_153 | 20 | n |  | TRUE
102 | bus_MV_392_1_node_150 | 20 | n |  | TRUE
103 | bus_MV_392_1_node_154 | 20 | n |  | TRUE
104 | bus_MV_392_1_node_155 | 20 | n |  | TRUE
105 | bus_MV_392_1_node_162 | 20 | n |  | TRUE
106 | bus_MV_392_1_node_163 | 20 | n |  | TRUE
107 | bus_HV_392_1_node_114 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_392_1_load_122 | 0 | 0.11567 | 0.056022 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_392_1_load_118 | 4 | 0.18409 | 0.089159 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_392_1_load_17 | 5 | 0.33167 | 0.16064 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_392_1_load_27 | 8 | 0.20212 | 0.09789 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_392_1_load_127 | 10 | 0.17006 | 0.082366 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_392_1_load_180 | 11 | 0.15769 | 0.076375 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_392_1_load_129 | 14 | 0.15494 | 0.075039 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_392_1_load_21 | 15 | 0.20738 | 0.10044 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_392_1_load_128 | 18 | 0.076528 | 0.037064 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_392_1_load_124 | 21 | 0.10577 | 0.051227 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_392_1_load_24 | 22 | 0.29166 | 0.14126 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_392_1_load_173 | 23 | 0.21314 | 0.10323 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_392_1_load_62 | 24 | 0.11716 | 0.056741 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_392_1_load_167 | 26 | 0.24887 | 0.12053 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_392_1_load_131 | 28 | 0.16756 | 0.081153 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_392_1_load_130 | 30 | 0.071419 | 0.03459 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_392_1_load_31 | 31 | 0.16326 | 0.079068 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_392_1_load_174 | 33 | 0.20672 | 0.10012 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_392_1_load_109 | 36 | 0.20328 | 0.098452 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_392_1_load_32 | 39 | 0.15093 | 0.073098 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_392_1_load_99 | 45 | 0.27675 | 0.13404 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_392_1_load_60 | 47 | 0.17022 | 0.082441 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_392_1_load_170 | 48 | 0.14324 | 0.069374 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_392_1_load_136 | 51 | 0.10248 | 0.049631 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_392_1_load_40 | 52 | 0.15006 | 0.072677 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_392_1_load_44 | 53 | 0.18008 | 0.087218 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_392_1_load_96 | 54 | 0.19797 | 0.095883 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_392_1_load_41 | 55 | 0.22172 | 0.10738 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_392_1_load_175 | 57 | 0.25993 | 0.12589 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_392_1_load_75 | 62 | 0.30594 | 0.14817 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_392_1_load_178 | 63 | 0.40319 | 0.19527 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_392_1_load_145 | 64 | 0.077483 | 0.037527 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_392_1_load_88 | 65 | 0.37934 | 0.18372 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_392_1_load_138 | 68 | 0.074186 | 0.03593 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_392_1_load_137 | 69 | 0.097167 | 0.04706 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_392_1_load_147 | 71 | 0.098552 | 0.047731 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_392_1_load_100 | 72 | 0.18185 | 0.088075 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_392_1_load_164 | 77 | 0.1119 | 0.054196 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_392_1_load_149 | 78 | 0.11273 | 0.054599 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_392_1_load_104 | 81 | 0.092399 | 0.044751 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_392_1_load_113 | 84 | 0.34779 | 0.16844 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_392_1_load_148 | 85 | 0.12938 | 0.062662 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_392_1_load_169 | 87 | 0.27392 | 0.13267 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_392_1_load_158 | 90 | 0.41924 | 0.20305 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_392_1_load_156 | 92 | 0.16245 | 0.078676 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_392_1_load_168 | 93 | 0.13372 | 0.064763 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_392_1_load_151 | 94 | 0.11372 | 0.055077 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_392_1_load_159 | 95 | 0.15111 | 0.073188 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_392_1_load_114 | 97 | 0.33342 | 0.16148 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_392_1_load_161 | 98 | 0.25769 | 0.12481 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_392_1_load_153 | 101 | 0.09458 | 0.045807 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_392_1_load_150 | 102 | 0.30675 | 0.14857 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_392_1_load_154 | 103 | 0.070081 | 0.033942 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_392_1_load_155 | 104 | 0.086651 | 0.041967 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_392_1_load_162 | 105 | 0.14045 | 0.068021 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_392_1_load_163 | 106 | 0.61511 | 0.29791 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 97 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_392_1_line_0 |  | 0 | 1 | 0.14752 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_392_1_line_1 |  | 1 | 2 | 0.31182 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_392_1_line_2 |  | 2 | 3 | 0.31192 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_392_1_line_3 |  | 2 | 4 | 0.044739 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_392_1_line_4 |  | 3 | 12 | 0.21962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_392_1_line_5 |  | 3 | 98 | 0.024735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_392_1_line_6 |  | 5 | 6 | 0.047685 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_392_1_line_7 |  | 6 | 7 | 1.1279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_392_1_line_8 |  | 7 | 13 | 0.15763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_392_1_line_9 |  | 7 | 14 | 0.038754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_392_1_line_10 |  | 8 | 9 | 0.019336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_392_1_line_11 |  | 8 | 10 | 1.166 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_392_1_line_12 |  | 9 | 27 | 0.41056 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_392_1_line_13 |  | 10 | 20 | 0.064455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_392_1_line_14 |  | 11 | 12 | 0.071403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_392_1_line_15 |  | 13 | 15 | 0.0413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_392_1_line_16 |  | 15 | 16 | 0.046301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_392_1_line_17 |  | 16 | 17 | 0.004025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_392_1_line_18 |  | 17 | 18 | 0.036152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_392_1_line_19 |  | 17 | 19 | 0.0549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_392_1_line_20 |  | 19 | 20 | 0.054142 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_392_1_line_21 |  | 19 | 21 | 0.061767 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_392_1_line_22 |  | 22 | 23 | 0.59642 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
23 | MV_392_1_line_23 |  | 22 | 24 | 1.9263 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
24 | MV_392_1_line_24 |  | 23 | 25 | 0.028286 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
25 | MV_392_1_line_25 |  | 24 | 26 | 0.95032 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_392_1_line_26 |  | 25 | 42 | 0.46989 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
27 | MV_392_1_line_27 |  | 27 | 31 | 0.041628 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_392_1_line_28 |  | 28 | 29 | 0.029794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_392_1_line_29 |  | 28 | 30 | 0.041451 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_392_1_line_30 |  | 28 | 31 | 0.4321 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_392_1_line_31 |  | 29 | 38 | 0.92548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_392_1_line_32 |  | 32 | 33 | 0.016465 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_392_1_line_33 |  | 32 | 34 | 0.37822 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_392_1_line_34 |  | 32 | 35 | 0.78849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_392_1_line_35 |  | 34 | 57 | 0.058372 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_392_1_line_36 |  | 35 | 55 | 0.064563 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_392_1_line_37 |  | 35 | 56 | 0.67651 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
38 | MV_392_1_line_38 |  | 35 | 43 | 0.50768 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
39 | MV_392_1_line_39 |  | 36 | 37 | 0.006969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_392_1_line_40 |  | 36 | 38 | 0.72634 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_392_1_line_41 |  | 37 | 86 | 1.0001 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
42 | MV_392_1_line_42 |  | 37 | 88 | 0.14253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_392_1_line_43 |  | 38 | 93 | 0.03985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_392_1_line_44 |  | 39 | 40 | 0.031283 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_392_1_line_45 |  | 40 | 41 | 1.0364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_392_1_line_46 |  | 40 | 42 | 0.19993 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
47 | MV_392_1_line_47 |  | 40 | 43 | 0.34704 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
48 | MV_392_1_line_48 |  | 41 | 46 | 0.77235 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_392_1_line_49 |  | 41 | 47 | 0.011691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_392_1_line_50 |  | 41 | 44 | 0.39357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_392_1_line_51 |  | 42 | 48 | 0.084554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_392_1_line_52 |  | 42 | 49 | 0.31752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_392_1_line_53 |  | 43 | 53 | 0.016882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_392_1_line_54 |  | 43 | 50 | 0.55786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_392_1_line_55 |  | 44 | 45 | 0.024361 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_392_1_line_56 |  | 46 | 54 | 0.046986 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_392_1_line_57 |  | 49 | 52 | 0.048702 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_392_1_line_58 |  | 50 | 51 | 0.041546 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_392_1_line_59 |  | 54 | 58 | 0.039275 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_392_1_line_60 |  | 56 | 69 | 0.050875 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
61 | MV_392_1_line_61 |  | 58 | 70 | 0.19245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_392_1_line_62 |  | 59 | 60 | 0.21057 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
63 | MV_392_1_line_63 |  | 59 | 61 | 0.90295 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
64 | MV_392_1_line_64 |  | 59 | 62 | 0.056186 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_392_1_line_65 |  | 60 | 65 | 0.028092 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
66 | MV_392_1_line_66 |  | 61 | 63 | 0.026331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_392_1_line_67 |  | 61 | 64 | 0.89615 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
68 | MV_392_1_line_68 |  | 64 | 100 | 0.019908 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
69 | MV_392_1_line_69 |  | 65 | 66 | 0.14578 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
70 | MV_392_1_line_70 |  | 66 | 67 | 0.25202 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
71 | MV_392_1_line_71 |  | 67 | 68 | 0.050914 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
72 | MV_392_1_line_72 |  | 68 | 69 | 0.0065511 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
73 | MV_392_1_line_73 |  | 70 | 71 | 0.10027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_392_1_line_74 |  | 72 | 73 | 0.02789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_392_1_line_75 |  | 72 | 74 | 0.036708 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_392_1_line_76 |  | 73 | 75 | 0.061365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_392_1_line_77 |  | 74 | 76 | 0.11043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_392_1_line_78 |  | 75 | 77 | 0.078503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_392_1_line_79 |  | 76 | 78 | 0.15875 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
80 | MV_392_1_line_80 |  | 76 | 79 | 0.004094 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
81 | MV_392_1_line_81 |  | 78 | 83 | 0.15823 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
82 | MV_392_1_line_82 |  | 79 | 92 | 0.09885 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
83 | MV_392_1_line_83 |  | 80 | 81 | 0.021981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_392_1_line_84 |  | 80 | 82 | 0.14742 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_392_1_line_85 |  | 80 | 83 | 0.2762 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_392_1_line_86 |  | 82 | 84 | 0.057638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_392_1_line_87 |  | 83 | 85 | 0.099994 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_392_1_line_88 |  | 85 | 91 | 0.27086 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
89 | MV_392_1_line_89 |  | 86 | 87 | 0.019066 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
90 | MV_392_1_line_90 |  | 87 | 96 | 0.033563 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
91 | MV_392_1_line_91 |  | 88 | 89 | 0.005614 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_392_1_line_92 |  | 88 | 90 | 0.016823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_392_1_line_93 |  | 89 | 94 | 0.042457 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_392_1_line_94 |  | 90 | 95 | 0.039816 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_392_1_line_95 |  | 91 | 96 | 0.29569 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
96 | MV_392_1_line_96 |  | 91 | 97 | 0.083875 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
97 | MV_392_1_line_97 |  | 92 | 104 | 0.041545 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
98 | MV_392_1_line_98 |  | 94 | 102 | 0.00071591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_392_1_line_99 |  | 95 | 99 | 0.026213 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_392_1_line_100 |  | 98 | 99 | 0.020344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_392_1_line_101 |  | 99 | 105 | 0.013067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_392_1_line_102 |  | 100 | 101 | 0.40772 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
103 | MV_392_1_line_103 |  | 101 | 103 | 0.035345 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
104 | MV_392_1_line_104 |  | 103 | 104 | 0.0016167 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
105 | MV_392_1_line_105 |  | 105 | 106 | 0.048763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_392_1_trafo_114 | 25 MVA 110/20 kV | 107 | 97 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2613897.6006 | 1227725.4027
1 | 2613771.0683 | 1227649.5538
2 | 2613529.6186 | 1227644.7438
3 | 2613602.0135 | 1227394.9382
4 | 2613499.6646 | 1227611.512
5 | 2615894.7348 | 1226266.4425
6 | 2615929.1242 | 1226299.4758
7 | 2615101.7998 | 1226675.8045
8 | 2614060.3017 | 1225751.2073
9 | 2614050.214 | 1225734.6961
10 | 2614928.5851 | 1226529.3939
11 | 2613835.9015 | 1227446.2054
12 | 2613765.5851 | 1227441.1734
13 | 2615068.4395 | 1226561.3527
14 | 2615069.4993 | 1226654.391
15 | 2615103.5392 | 1226539.4284
16 | 2615076.8742 | 1226501.5276
17 | 2615073.5414 | 1226503.7983
18 | 2615044.999 | 1226482.1154
19 | 2615028.036 | 1226534.7019
20 | 2614982.6176 | 1226564.372
21 | 2614979.273 | 1226497.9926
22 | 2612983.0054 | 1224154.3354
23 | 2612439.3031 | 1224399.5011
24 | 2614885.7423 | 1223854.1551
25 | 2612442.4971 | 1224427.6019
26 | 2614969.3619 | 1222907.518
27 | 2613780.0836 | 1225623.3685
28 | 2613681.7171 | 1226064.1906
29 | 2613668.0817 | 1226090.6973
30 | 2613690.6268 | 1226023.7086
31 | 2613740.449 | 1225636.0959
32 | 2612547.5548 | 1225503.3179
33 | 2612531.4771 | 1225507.0753
34 | 2612617.5742 | 1225164.8
35 | 2612081.9063 | 1225504.7601
36 | 2613496.2891 | 1227177.0919
37 | 2613502.7852 | 1227179.6637
38 | 2613642.8198 | 1226465.6826
39 | 2612010.6063 | 1224913.0254
40 | 2612005.0432 | 1224882.2407
41 | 2611088.1513 | 1224676.8516
42 | 2612164.4 | 1224789.6194
43 | 2612047.7796 | 1225106.5468
44 | 2610946.875 | 1224777.2058
45 | 2610971.1085 | 1224774.7154
46 | 2610594.6819 | 1224838.0745
47 | 2611086.1713 | 1224665.33
48 | 2612226.7585 | 1224846.6244
49 | 2612028.0609 | 1224628.6385
50 | 2612466.6306 | 1225023.0561
51 | 2612505.5785 | 1225009.5143
52 | 2611997.6933 | 1224593.2902
53 | 2612043.0242 | 1225122.7467
54 | 2610571.9877 | 1224879.214
55 | 2612125.9874 | 1225551.9325
56 | 2611583.8863 | 1225962.6328
57 | 2612600.355 | 1225220.5742
58 | 2610562.7929 | 1224917.3979
59 | 2611083.1284 | 1226262.5051
60 | 2611283.9007 | 1226201.6001
61 | 2611362.2646 | 1226710.8703
62 | 2611034.6747 | 1226233.9321
63 | 2611375.0329 | 1226687.8254
64 | 2612118.9641 | 1227190.9677
65 | 2611311.1313 | 1226194.3917
66 | 2611438.516 | 1226265.2866
67 | 2611545.1703 | 1226041.0819
68 | 2611585.2663 | 1226012.053
69 | 2611587.7373 | 1226005.9859
70 | 2610594.403 | 1225098.4041
71 | 2610687.6984 | 1225071.9825
72 | 2612739.7687 | 1227374.4484
73 | 2612748.7071 | 1227400.872
74 | 2612706.1751 | 1227389.4636
75 | 2612717.1162 | 1227443.3743
76 | 2612653.3062 | 1227292.5053
77 | 2612638.8255 | 1227443.9188
78 | 2612790.7273 | 1227212.3392
79 | 2612649.9367 | 1227294.844
80 | 2613010.7824 | 1227275.0956
81 | 2612999.7202 | 1227256.1008
82 | 2613107.7469 | 1227303.4464
83 | 2612927.6969 | 1227132.4311
84 | 2613126.5946 | 1227357.8644
85 | 2612942.1123 | 1227062.7807
86 | 2613184.7027 | 1227106.3103
87 | 2613176.7006 | 1227089.0046
88 | 2613549.9839 | 1227278.5178
89 | 2613547.1001 | 1227273.6973
90 | 2613558.9492 | 1227292.7524
91 | 2613084.7187 | 1226832.5068
92 | 2612563.9782 | 1227343.6543
93 | 2613604.1832 | 1226455.4885
94 | 2613508.0058 | 1227290.2565
95 | 2613575.9193 | 1227328.5924
96 | 2613175.1508 | 1227059.8284
97 | 2613025.1451 | 1226773.2973
98 | 2613592.9601 | 1227371.9197
99 | 2613585.5137 | 1227352.9869
100 | 2612138.6286 | 1227187.8654
101 | 2612496.3384 | 1227383.5067
102 | 2613507.3466 | 1227290.5358
103 | 2612526.791 | 1227365.5644
104 | 2612528.1839 | 1227364.7437
105 | 2613573.0733 | 1227356.9843
106 | 2613531.437 | 1227378.0295
107 | 2613025.1451 | 1226773.2973

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99586 | -0.027855 | 0.11567 | 0.056022
1 | 0.99589 | -0.027646 | 0 | 0
2 | 0.99594 | -0.028004 | 0 | 0
3 | 0.99606 | -0.028905 | 0 | 0
4 | 0.99592 | -0.028104 | 0.18409 | 0.089159
5 | 0.98703 | -0.057931 | 0.33167 | 0.16064
6 | 0.98706 | -0.057735 | 0 | 0
7 | 0.98754 | -0.061355 | 0 | 0
8 | 0.99024 | -0.044714 | 0.20212 | 0.09789
9 | 0.99027 | -0.044958 | 0 | 0
10 | 0.98789 | -0.063856 | 0.17006 | 0.082366
11 | 0.996 | -0.028416 | 0.15769 | 0.076375
12 | 0.99601 | -0.028548 | 0 | 0
13 | 0.98764 | -0.061997 | 0 | 0
14 | 0.98753 | -0.061283 | 0.15494 | 0.075039
15 | 0.98766 | -0.062159 | 0.20738 | 0.10044
16 | 0.9877 | -0.062455 | 0 | 0
17 | 0.98771 | -0.062481 | 0 | 0
18 | 0.9877 | -0.062448 | 0.076528 | 0.037064
19 | 0.98776 | -0.062876 | 0 | 0
20 | 0.98782 | -0.063326 | 0 | 0
21 | 0.98775 | -0.062798 | 0.10577 | 0.051227
22 | 0.98725 | -0.41441 | 0.29166 | 0.14126
23 | 0.98772 | -0.40268 | 0.21314 | 0.10323
24 | 0.98641 | -0.43554 | 0.11716 | 0.056741
25 | 0.98774 | -0.40253 | 0 | 0
26 | 0.98594 | -0.43852 | 0.24887 | 0.12053
27 | 0.99093 | -0.050002 | 0 | 0
28 | 0.9922 | -0.039755 | 0.16756 | 0.081153
29 | 0.99226 | -0.040256 | 0 | 0
30 | 0.99219 | -0.039792 | 0.071419 | 0.03459
31 | 0.99103 | -0.049178 | 0.16326 | 0.079068
32 | 0.98864 | -0.38168 | 0 | 0
33 | 0.98863 | -0.38164 | 0.20672 | 0.10012
34 | 0.98851 | -0.38059 | 0 | 0
35 | 0.98911 | -0.38523 | 0 | 0
36 | 0.99669 | -0.034499 | 0.20328 | 0.098452
37 | 0.99671 | -0.034634 | 0 | 0
38 | 0.99421 | -0.055098 | 0 | 0
39 | 0.98808 | -0.39861 | 0.15093 | 0.073098
40 | 0.98809 | -0.39855 | 0 | 0
41 | 0.98711 | -0.39231 | 0 | 0
42 | 0.98796 | -0.40005 | 0 | 0
43 | 0.98847 | -0.39361 | 0 | 0
44 | 0.98697 | -0.39109 | 0 | 0
45 | 0.98696 | -0.39117 | 0.27675 | 0.13404
46 | 0.98682 | -0.39035 | 0 | 0
47 | 0.98711 | -0.39229 | 0.17022 | 0.082441
48 | 0.98795 | -0.3999 | 0.14324 | 0.069374
49 | 0.9879 | -0.39956 | 0 | 0
50 | 0.9884 | -0.39318 | 0 | 0
51 | 0.98839 | -0.39313 | 0.10248 | 0.049631
52 | 0.98789 | -0.39947 | 0.15006 | 0.072677
53 | 0.98847 | -0.39358 | 0.18008 | 0.087218
54 | 0.9868 | -0.3902 | 0.19797 | 0.095883
55 | 0.98908 | -0.38541 | 0.22172 | 0.10738
56 | 0.99147 | -0.31966 | 0 | 0
57 | 0.98848 | -0.38077 | 0.25993 | 0.12589
58 | 0.98679 | -0.39027 | 0 | 0
59 | 0.99292 | -0.29464 | 0 | 0
60 | 0.99268 | -0.29611 | 0 | 0
61 | 0.99405 | -0.28754 | 0 | 0
62 | 0.9929 | -0.29443 | 0.30594 | 0.14817
63 | 0.99404 | -0.28741 | 0.40319 | 0.19527
64 | 0.99654 | -0.13726 | 0.077483 | 0.037527
65 | 0.99262 | -0.2968 | 0.37934 | 0.18372
66 | 0.99208 | -0.31169 | 0 | 0
67 | 0.99165 | -0.31731 | 0 | 0
68 | 0.99157 | -0.31844 | 0.074186 | 0.03593
69 | 0.99155 | -0.31858 | 0.097167 | 0.04706
70 | 0.98677 | -0.3901 | 0 | 0
71 | 0.98676 | -0.38999 | 0.098552 | 0.047731
72 | 0.99794 | -0.065666 | 0.18185 | 0.088075
73 | 0.99794 | -0.065635 | 0 | 0
74 | 0.99795 | -0.065785 | 0 | 0
75 | 0.99793 | -0.065563 | 0 | 0
76 | 0.998 | -0.066131 | 0 | 0
77 | 0.99792 | -0.065462 | 0.1119 | 0.054196
78 | 0.99826 | -0.064587 | 0.11273 | 0.054599
79 | 0.99799 | -0.066169 | 0 | 0
80 | 0.99837 | -0.061699 | 0 | 0
81 | 0.99836 | -0.061675 | 0.092399 | 0.044751
82 | 0.9983 | -0.061113 | 0 | 0
83 | 0.99852 | -0.063005 | 0 | 0
84 | 0.99828 | -0.060875 | 0.34779 | 0.16844
85 | 0.9987 | -0.061924 | 0.12938 | 0.062662
86 | 0.99911 | -0.006704 | 0 | 0
87 | 0.99921 | -0.0041182 | 0.27392 | 0.13267
88 | 0.99626 | -0.030674 | 0 | 0
89 | 0.99626 | -0.030646 | 0 | 0
90 | 0.99622 | -0.030288 | 0.41924 | 0.20305
91 | 0.99972 | -0.0015757 | 0 | 0
92 | 0.99784 | -0.067074 | 0.16245 | 0.078676
93 | 0.9942 | -0.055034 | 0.13372 | 0.064763
94 | 0.99624 | -0.030432 | 0.11372 | 0.055077
95 | 0.99614 | -0.029575 | 0.15111 | 0.073188
96 | 0.99926 | -0.0038635 | 0 | 0
97 | 1 | 0 | -10.5593 | -4.673
98 | 0.99607 | -0.029006 | 0.25769 | 0.12481
99 | 0.99609 | -0.029152 | 0 | 0
100 | 0.99657 | -0.13709 | 0 | 0
101 | 0.99772 | -0.067765 | 0.09458 | 0.045807
102 | 0.99624 | -0.03043 | 0.30675 | 0.14857
103 | 0.99777 | -0.067458 | 0.070081 | 0.033942
104 | 0.99777 | -0.067443 | 0.086651 | 0.041967
105 | 0.99608 | -0.029034 | 0.14045 | 0.068021
106 | 0.99604 | -0.028674 | 0.61511 | 0.29791
107 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.11567 | -0.056022 | 0.11567 | 0.055849 | 3.6461e-06 | -0.00017238 | 0.0037256 | 0.0037233 | 0.0037256 | 0.99586 | -0.027855 | 0.99589 | -0.027646 | 1.7741
1 | -0.11567 | -0.055849 | 0.11568 | 0.048467 | 5.6315e-06 | -0.0073825 | 0.0037233 | 0.0036354 | 0.0037233 | 0.99589 | -0.027646 | 0.99594 | -0.028004 | 1.6924
2 | -0.29977 | -0.13757 | 0.29981 | 0.1302 | 3.771e-05 | -0.0073768 | 0.0095603 | 0.009473 | 0.0095603 | 0.99594 | -0.028004 | 0.99606 | -0.028905 | 4.3456
3 | 0.18409 | 0.089108 | -0.18409 | -0.089159 | 2.8017e-06 | -5.1221e-05 | 0.0059282 | 0.0059289 | 0.0059289 | 0.99594 | -0.028004 | 0.99592 | -0.028104 | 2.8233
4 | 0.1577 | 0.069484 | -0.1577 | -0.074684 | 7.4046e-06 | -0.0052001 | 0.0049945 | 0.0050572 | 0.0050572 | 0.99606 | -0.028905 | 0.99601 | -0.028548 | 2.2987
5 | -0.45751 | -0.19968 | 0.45752 | 0.1991 | 6.9083e-06 | -0.00058388 | 0.014467 | 0.014461 | 0.014467 | 0.99606 | -0.028905 | 0.99607 | -0.029006 | 6.5761
6 | -0.33167 | -0.16064 | 0.33168 | 0.16059 | 9.8691e-06 | -4.9279e-05 | 0.010778 | 0.010777 | 0.010778 | 0.98703 | -0.057931 | 0.98706 | -0.057735 | 5.1325
7 | -0.33168 | -0.16059 | 0.33185 | 0.13439 | 0.00016969 | -0.0262 | 0.010777 | 0.010466 | 0.010777 | 0.98706 | -0.057735 | 0.98754 | -0.061355 | 4.8989
8 | -0.48679 | -0.20852 | 0.48684 | 0.20487 | 5.0292e-05 | -0.0036559 | 0.01548 | 0.015438 | 0.01548 | 0.98754 | -0.061355 | 0.98764 | -0.061997 | 7.0365
9 | 0.15494 | 0.074137 | -0.15494 | -0.075039 | 1.3072e-06 | -0.00090198 | 0.0050209 | 0.0050323 | 0.0050323 | 0.98754 | -0.061355 | 0.98753 | -0.061283 | 2.2874
10 | -1.2512 | -0.56556 | 1.2513 | 0.56512 | 4.1357e-05 | -0.00044045 | 0.040029 | 0.040024 | 0.040029 | 0.99024 | -0.044714 | 0.99027 | -0.044958 | 18.1952
11 | 1.0491 | 0.46767 | -1.0468 | -0.46757 | 0.0023305 | 9.8051e-05 | 0.033485 | 0.033502 | 0.033502 | 0.99024 | -0.044714 | 0.98789 | -0.063856 | 15.9531
12 | -1.2513 | -0.56512 | 1.2522 | 0.55576 | 0.0008755 | -0.0093595 | 0.040024 | 0.039909 | 0.040024 | 0.99027 | -0.044958 | 0.99093 | -0.050002 | 18.1927
13 | 0.87673 | 0.38521 | -0.87667 | -0.38669 | 6.7422e-05 | -0.0014818 | 0.027983 | 0.028001 | 0.028001 | 0.98789 | -0.063856 | 0.98782 | -0.063326 | 12.7276
14 | -0.15769 | -0.076375 | 0.1577 | 0.074684 | 2.4481e-06 | -0.0016905 | 0.0050784 | 0.0050572 | 0.0050784 | 0.996 | -0.028416 | 0.99601 | -0.028548 | 2.3084
15 | -0.48684 | -0.20487 | 0.48685 | 0.20391 | 1.3132e-05 | -0.00095798 | 0.015438 | 0.015427 | 0.015438 | 0.98764 | -0.061997 | 0.98766 | -0.062159 | 7.0174
16 | -0.69423 | -0.30435 | 0.69426 | 0.30328 | 3.0324e-05 | -0.0010694 | 0.022155 | 0.022143 | 0.022155 | 0.98766 | -0.062159 | 0.9877 | -0.062455 | 10.0706
17 | -0.69426 | -0.30328 | 0.69427 | 0.30319 | 2.6344e-06 | -9.2971e-05 | 0.022143 | 0.022142 | 0.022143 | 0.9877 | -0.062455 | 0.98771 | -0.062481 | 10.0649
18 | 0.076529 | 0.036222 | -0.076528 | -0.037064 | 2.9681e-07 | -0.00084199 | 0.0024746 | 0.0024852 | 0.0024852 | 0.98771 | -0.062481 | 0.9877 | -0.062448 | 1.1296
19 | -0.77079 | -0.33941 | 0.77084 | 0.33814 | 4.4381e-05 | -0.0012657 | 0.024615 | 0.0246 | 0.024615 | 0.98771 | -0.062481 | 0.98776 | -0.062876 | 11.1887
20 | -0.87661 | -0.38793 | 0.87667 | 0.38669 | 5.67e-05 | -0.0012445 | 0.028016 | 0.028001 | 0.028016 | 0.98776 | -0.062876 | 0.98782 | -0.063326 | 12.7344
21 | 0.10577 | 0.049789 | -0.10577 | -0.051227 | 9.6761e-07 | -0.0014386 | 0.0034165 | 0.0034347 | 0.0034347 | 0.98776 | -0.062876 | 0.98775 | -0.062798 | 1.5612
22 | -0.65805 | -0.31543 | 0.6583 | 0.31498 | 0.00024918 | -0.00044584 | 0.021338 | 0.021329 | 0.021338 | 0.98725 | -0.41441 | 0.98772 | -0.40268 | 6.0965
23 | 0.36639 | 0.17417 | -0.36614 | -0.17624 | 0.00024944 | -0.002072 | 0.011862 | 0.011892 | 0.011892 | 0.98725 | -0.41441 | 0.98641 | -0.43554 | 3.3977
24 | -0.87144 | -0.41821 | 0.87145 | 0.41727 | 1.0899e-05 | -0.0009388 | 0.02825 | 0.028238 | 0.02825 | 0.98772 | -0.40268 | 0.98774 | -0.40253 | 7.8038
25 | 0.24898 | 0.1195 | -0.24887 | -0.12053 | 0.0001108 | -0.0010339 | 0.0080823 | 0.0080963 | 0.0080963 | 0.98641 | -0.43554 | 0.98594 | -0.43852 | 3.8554
26 | -0.87145 | -0.41727 | 0.87163 | 0.40167 | 0.00017971 | -0.0156 | 0.028238 | 0.028042 | 0.028238 | 0.98774 | -0.40253 | 0.98796 | -0.40005 | 7.8005
27 | -1.2522 | -0.55576 | 1.2523 | 0.55579 | 0.00011813 | 2.5191e-05 | 0.039909 | 0.039909 | 0.039909 | 0.99093 | -0.050002 | 0.99103 | -0.049178 | 19.0045
28 | -1.6561 | -0.75103 | 1.6562 | 0.75036 | 0.00011131 | -0.00066733 | 0.052906 | 0.052898 | 0.052906 | 0.9922 | -0.039755 | 0.99226 | -0.040256 | 24.0483
29 | 0.07142 | 0.034542 | -0.071419 | -0.03459 | 3.9358e-07 | -4.8468e-05 | 0.0023082 | 0.0023088 | 0.0023088 | 0.9922 | -0.039755 | 0.99219 | -0.039792 | 1.0994
30 | 1.4171 | 0.63533 | -1.4155 | -0.63485 | 0.001572 | 0.00047742 | 0.045184 | 0.04519 | 0.04519 | 0.9922 | -0.039755 | 0.99103 | -0.049178 | 21.5191
31 | -1.6562 | -0.75036 | 1.6596 | 0.72958 | 0.0034402 | -0.020778 | 0.052898 | 0.05264 | 0.052898 | 0.99226 | -0.040256 | 0.99421 | -0.055098 | 24.0444
32 | 0.20672 | 0.099735 | -0.20672 | -0.10012 | 9.88e-07 | -0.00038394 | 0.0067019 | 0.0067068 | 0.0067068 | 0.98864 | -0.38168 | 0.98863 | -0.38164 | 3.0485
33 | 0.25998 | 0.11701 | -0.25994 | -0.12583 | 3.5444e-05 | -0.0088148 | 0.0083246 | 0.0084337 | 0.0084337 | 0.98864 | -0.38168 | 0.98851 | -0.38059 | 3.8335
34 | -0.4667 | -0.21675 | 0.46693 | 0.19841 | 0.00023414 | -0.01834 | 0.015025 | 0.014807 | 0.015025 | 0.98864 | -0.38168 | 0.98911 | -0.38523 | 6.8296
35 | 0.25994 | 0.12583 | -0.25993 | -0.12589 | 7.3981e-06 | -6.3457e-05 | 0.0084337 | 0.0084346 | 0.0084346 | 0.98851 | -0.38059 | 0.98848 | -0.38077 | 4.0165
36 | 0.22173 | 0.10731 | -0.22172 | -0.10738 | 5.9462e-06 | -7.1679e-05 | 0.0071892 | 0.0071902 | 0.0071902 | 0.98911 | -0.38523 | 0.98908 | -0.38541 | 3.4239
37 | -3.0337 | -1.3016 | 3.0395 | 1.3074 | 0.0057642 | 0.0057594 | 0.096346 | 0.096336 | 0.096346 | 0.98911 | -0.38523 | 0.99147 | -0.31966 | 27.5274
38 | 2.3451 | 0.99588 | -2.3437 | -1.0119 | 0.0013593 | -0.01604 | 0.074358 | 0.074553 | 0.074553 | 0.98911 | -0.38523 | 0.98847 | -0.39361 | 20.5949
39 | -2.0008 | -0.89362 | 2.0009 | 0.89347 | 3.7476e-05 | -0.00015418 | 0.063468 | 0.063466 | 0.063468 | 0.99669 | -0.034499 | 0.99671 | -0.034634 | 28.8491
40 | 1.7976 | 0.79517 | -1.7934 | -0.7934 | 0.004195 | 0.0017684 | 0.05693 | 0.05694 | 0.05694 | 0.99669 | -0.034499 | 0.99421 | -0.055098 | 27.1142
41 | -4.464 | -2.0552 | 4.4738 | 2.0281 | 0.0097582 | -0.027076 | 0.14234 | 0.14192 | 0.14234 | 0.99671 | -0.034634 | 0.99911 | -0.006704 | 39.3191
42 | 2.4632 | 1.1617 | -2.462 | -1.1648 | 0.0011845 | -0.0030279 | 0.078877 | 0.078918 | 0.078918 | 0.99671 | -0.034634 | 0.99626 | -0.030674 | 35.872
43 | 0.13372 | 0.063822 | -0.13372 | -0.064763 | 9.8737e-07 | -0.00094017 | 0.0043022 | 0.004314 | 0.004314 | 0.99421 | -0.055098 | 0.9942 | -0.055034 | 1.9609
44 | -0.15093 | -0.073098 | 0.15093 | 0.073062 | 1.3378e-06 | -3.5623e-05 | 0.0048994 | 0.004899 | 0.0048994 | 0.98808 | -0.39861 | 0.98809 | -0.39855 | 2.3331
45 | 0.74441 | 0.30087 | -0.74364 | -0.32477 | 0.0007701 | -0.023907 | 0.023457 | 0.023731 | 0.023731 | 0.98809 | -0.39855 | 0.98711 | -0.39231 | 10.7868
46 | 1.1651 | 0.52662 | -1.1649 | -0.53322 | 0.00013503 | -0.0065975 | 0.037354 | 0.037435 | 0.037435 | 0.98809 | -0.39855 | 0.98796 | -0.40005 | 10.3412
47 | -2.0604 | -0.90055 | 2.0611 | 0.88945 | 0.00072192 | -0.011103 | 0.065695 | 0.065559 | 0.065695 | 0.98809 | -0.39855 | 0.98847 | -0.39361 | 18.1477
48 | 0.29663 | 0.11774 | -0.29654 | -0.13567 | 9.1751e-05 | -0.017936 | 0.0093331 | 0.0095394 | 0.0095394 | 0.98711 | -0.39231 | 0.98682 | -0.39035 | 4.3361
49 | 0.17022 | 0.082169 | -0.17022 | -0.082441 | 4.7716e-07 | -0.00027184 | 0.0055276 | 0.0055311 | 0.0055311 | 0.98711 | -0.39231 | 0.98711 | -0.39229 | 2.5141
50 | 0.27679 | 0.12487 | -0.27675 | -0.13401 | 4.1957e-05 | -0.0091426 | 0.0088802 | 0.0089936 | 0.0089936 | 0.98711 | -0.39231 | 0.98697 | -0.39109 | 4.088
51 | 0.14324 | 0.067404 | -0.14324 | -0.069374 | 2.4282e-06 | -0.0019698 | 0.0046257 | 0.0046505 | 0.0046505 | 0.98796 | -0.40005 | 0.98795 | -0.3999 | 2.1139
52 | 0.15007 | 0.064146 | -0.15006 | -0.071542 | 9.8161e-06 | -0.0073963 | 0.0047687 | 0.0048578 | 0.0048578 | 0.98796 | -0.40005 | 0.9879 | -0.39956 | 2.2081
53 | 0.18008 | 0.086825 | -0.18008 | -0.087218 | 7.6894e-07 | -0.00039361 | 0.0058386 | 0.0058436 | 0.0058436 | 0.98847 | -0.39361 | 0.98847 | -0.39358 | 2.6562
54 | 0.10248 | 0.035652 | -0.10248 | -0.048663 | 7.8004e-06 | -0.013011 | 0.0031689 | 0.0033133 | 0.0033133 | 0.98847 | -0.39361 | 0.9884 | -0.39318 | 1.506
55 | 0.27675 | 0.13401 | -0.27675 | -0.13404 | 3.5109e-06 | -2.613e-05 | 0.0089936 | 0.008994 | 0.008994 | 0.98697 | -0.39109 | 0.98696 | -0.39117 | 4.2829
56 | 0.29654 | 0.13567 | -0.29653 | -0.13676 | 5.7161e-06 | -0.0010907 | 0.0095394 | 0.0095528 | 0.0095528 | 0.98682 | -0.39035 | 0.9868 | -0.3902 | 4.3422
57 | 0.15006 | 0.071542 | -0.15006 | -0.072677 | 1.5388e-06 | -0.0011344 | 0.0048578 | 0.0048721 | 0.0048721 | 0.9879 | -0.39956 | 0.98789 | -0.39947 | 2.2146
58 | 0.10248 | 0.048663 | -0.10248 | -0.049631 | 6.1111e-07 | -0.00096888 | 0.0033133 | 0.0033255 | 0.0033255 | 0.9884 | -0.39318 | 0.98839 | -0.39313 | 1.5116
59 | 0.098556 | 0.040881 | -0.098556 | -0.040927 | 6.8187e-07 | -4.523e-05 | 0.0031213 | 0.0031218 | 0.0031218 | 0.9868 | -0.3902 | 0.98679 | -0.39027 | 1.4866
60 | -3.0395 | -1.3074 | 3.0397 | 1.3058 | 0.000228 | -0.0015501 | 0.096336 | 0.096316 | 0.096336 | 0.99147 | -0.31966 | 0.99155 | -0.31858 | 26.6122
61 | 0.098556 | 0.040927 | -0.098553 | -0.0454 | 2.5452e-06 | -0.0044734 | 0.0031218 | 0.0031743 | 0.0031743 | 0.98679 | -0.39027 | 0.98677 | -0.3901 | 1.4429
62 | 3.5944 | 1.5512 | -3.5935 | -1.5638 | 0.00084398 | -0.012565 | 0.11382 | 0.11397 | 0.11397 | 0.99292 | -0.29464 | 0.99268 | -0.29611 | 17.8632
63 | -3.9003 | -1.6981 | 3.9045 | 1.6445 | 0.0042454 | -0.053607 | 0.12368 | 0.12303 | 0.12368 | 0.99292 | -0.29464 | 0.99405 | -0.28754 | 19.3849
64 | 0.30594 | 0.14685 | -0.30594 | -0.14817 | 7.3141e-06 | -0.0013204 | 0.0098664 | 0.0098831 | 0.0098831 | 0.99292 | -0.29464 | 0.9929 | -0.29443 | 4.4923
65 | 3.5935 | 1.5638 | -3.5933 | -1.5646 | 0.00017625 | -0.00082153 | 0.11397 | 0.11398 | 0.11398 | 0.99268 | -0.29611 | 0.99262 | -0.2968 | 31.4857
66 | 0.4032 | 0.19465 | -0.40319 | -0.19527 | 5.9461e-06 | -0.00061946 | 0.013002 | 0.01301 | 0.01301 | 0.99405 | -0.28754 | 0.99404 | -0.28741 | 5.9136
67 | -4.3077 | -1.8391 | 4.3137 | 1.8538 | 0.0059186 | 0.014688 | 0.13602 | 0.13601 | 0.13602 | 0.99405 | -0.28754 | 0.99654 | -0.13726 | 21.0886
68 | -4.3911 | -1.8913 | 4.3913 | 1.8902 | 0.00011799 | -0.0011758 | 0.1385 | 0.13848 | 0.1385 | 0.99654 | -0.13726 | 0.99657 | -0.13709 | 21.7083
69 | 3.214 | 1.3809 | -3.2126 | -1.3795 | 0.0013851 | 0.0014038 | 0.10173 | 0.10173 | 0.10173 | 0.99262 | -0.2968 | 0.99208 | -0.31169 | 29.0668
70 | 3.2126 | 1.3795 | -3.2114 | -1.3871 | 0.0012611 | -0.0075896 | 0.10173 | 0.10183 | 0.10183 | 0.99208 | -0.31169 | 0.99165 | -0.31731 | 28.1303
71 | 3.2114 | 1.3871 | -3.2111 | -1.3886 | 0.00025506 | -0.0015321 | 0.10183 | 0.10185 | 0.10185 | 0.99165 | -0.31731 | 0.99157 | -0.31844 | 28.1358
72 | 3.1369 | 1.3527 | -3.1369 | -1.3529 | 3.1298e-05 | -0.00019822 | 0.099454 | 0.099457 | 0.099457 | 0.99157 | -0.31844 | 0.99155 | -0.31858 | 27.4742
73 | 0.098553 | 0.0454 | -0.098552 | -0.047731 | 1.3611e-06 | -0.0023306 | 0.0031743 | 0.0032035 | 0.0032035 | 0.98677 | -0.3901 | 0.98676 | -0.38999 | 1.4561
74 | 0.1119 | 0.050208 | -0.1119 | -0.050871 | 4.6973e-07 | -0.00066302 | 0.003548 | 0.0035559 | 0.0035559 | 0.99794 | -0.065666 | 0.99794 | -0.065635 | 1.6163
75 | -0.29376 | -0.13828 | 0.29376 | 0.13741 | 4.3178e-06 | -0.00087157 | 0.009392 | 0.0093812 | 0.009392 | 0.99794 | -0.065666 | 0.99795 | -0.065785 | 4.2691
76 | 0.1119 | 0.050871 | -0.1119 | -0.05233 | 1.041e-06 | -0.0014588 | 0.0035559 | 0.0035735 | 0.0035735 | 0.99794 | -0.065635 | 0.99793 | -0.065563 | 1.6243
77 | -0.29376 | -0.13741 | 0.29377 | 0.13479 | 1.2931e-05 | -0.0026222 | 0.0093812 | 0.0093493 | 0.0093812 | 0.99795 | -0.065785 | 0.998 | -0.066131 | 4.2642
78 | 0.1119 | 0.05233 | -0.1119 | -0.054196 | 1.347e-06 | -0.0018662 | 0.0035735 | 0.0035967 | 0.0035967 | 0.99793 | -0.065563 | 0.99792 | -0.065462 | 1.6349
79 | -5.1028 | -2.2216 | 5.1041 | 2.2124 | 0.0012704 | -0.0092221 | 0.16098 | 0.16087 | 0.16098 | 0.998 | -0.066131 | 0.99826 | -0.064587 | 25.2326
80 | 4.809 | 2.0868 | -4.809 | -2.0871 | 2.9089e-05 | -0.00023982 | 0.15164 | 0.15164 | 0.15164 | 0.998 | -0.066131 | 0.99799 | -0.066169 | 23.7679
81 | -5.2168 | -2.267 | 5.2181 | 2.2578 | 0.001322 | -0.0091657 | 0.16449 | 0.16437 | 0.16449 | 0.99826 | -0.064587 | 0.99852 | -0.063005 | 25.7819
82 | 4.809 | 2.0871 | -4.8083 | -2.0929 | 0.00070269 | -0.0057893 | 0.15164 | 0.15171 | 0.15171 | 0.99799 | -0.066169 | 0.99784 | -0.067074 | 23.7791
83 | 0.0924 | 0.044228 | -0.092399 | -0.044751 | 2.5803e-07 | -0.00052303 | 0.002962 | 0.0029686 | 0.0029686 | 0.99837 | -0.061699 | 0.99836 | -0.061675 | 1.3493
84 | 0.34783 | 0.16357 | -0.3478 | -0.16708 | 2.4405e-05 | -0.003501 | 0.011114 | 0.011158 | 0.011158 | 0.99837 | -0.061699 | 0.9983 | -0.061113 | 5.0716
85 | -0.44023 | -0.2078 | 0.4403 | 0.20125 | 7.2639e-05 | -0.0065526 | 0.014076 | 0.013996 | 0.014076 | 0.99837 | -0.061699 | 0.99852 | -0.063005 | 6.3981
86 | 0.3478 | 0.16708 | -0.34779 | -0.16844 | 9.5939e-06 | -0.0013686 | 0.011158 | 0.011175 | 0.011175 | 0.9983 | -0.061113 | 0.99828 | -0.060875 | 5.0794
87 | -5.6584 | -2.4591 | 5.6594 | 2.4534 | 0.00098263 | -0.005712 | 0.17837 | 0.1783 | 0.17837 | 0.99852 | -0.063005 | 0.9987 | -0.061924 | 27.9573
88 | -5.7888 | -2.516 | 5.792 | 2.5243 | 0.0032186 | 0.0082813 | 0.18245 | 0.18244 | 0.18245 | 0.9987 | -0.061924 | 0.99972 | -0.0015757 | 28.2864
89 | -4.4738 | -2.0281 | 4.4741 | 2.0285 | 0.00035255 | 0.00037932 | 0.14192 | 0.14192 | 0.14192 | 0.99911 | -0.006704 | 0.99921 | -0.0041182 | 40.5498
90 | -4.7481 | -2.1612 | 4.7483 | 2.1592 | 0.00023554 | -0.001973 | 0.15071 | 0.15069 | 0.15071 | 0.99921 | -0.0041182 | 0.99926 | -0.0038635 | 23.6229
91 | 0.42048 | 0.20249 | -0.42048 | -0.20262 | 1.3707e-06 | -0.00013263 | 0.013523 | 0.013525 | 0.013525 | 0.99626 | -0.030674 | 0.99626 | -0.030646 | 6.1476
92 | 2.0415 | 0.96227 | -2.0414 | -0.96264 | 9.6052e-05 | -0.00037015 | 0.065396 | 0.065401 | 0.065401 | 0.99626 | -0.030674 | 0.99622 | -0.030288 | 29.7276
93 | 0.42048 | 0.20262 | -0.42047 | -0.20363 | 1.0377e-05 | -0.001003 | 0.013525 | 0.013537 | 0.013537 | 0.99626 | -0.030646 | 0.99624 | -0.030432 | 6.1534
94 | 1.6222 | 0.75959 | -1.622 | -0.76049 | 0.00014323 | -0.0009009 | 0.051903 | 0.051915 | 0.051915 | 0.99622 | -0.030288 | 0.99614 | -0.029575 | 23.5978
95 | 4.7504 | 2.1418 | -4.7483 | -2.1592 | 0.0020717 | -0.017393 | 0.15047 | 0.15069 | 0.15069 | 0.99972 | -0.0015757 | 0.99926 | -0.0038635 | 23.619
96 | -10.5424 | -4.6661 | 10.5453 | 4.6625 | 0.0028718 | -0.0036514 | 0.3329 | 0.33284 | 0.3329 | 0.99972 | -0.0015757 | 1 | 0 | 52.1794
97 | 4.6459 | 2.0142 | -4.6456 | -2.0166 | 0.00027555 | -0.0024437 | 0.14649 | 0.14652 | 0.14652 | 0.99784 | -0.067074 | 0.99777 | -0.067443 | 22.9661
98 | 0.30675 | 0.14855 | -0.30675 | -0.14857 | 9.3257e-08 | -1.6937e-05 | 0.009876 | 0.0098762 | 0.0098762 | 0.99624 | -0.030432 | 0.99624 | -0.03043 | 4.4892
99 | 1.4709 | 0.68731 | -1.4708 | -0.6879 | 7.748e-05 | -0.00059803 | 0.04705 | 0.047057 | 0.047057 | 0.99614 | -0.029575 | 0.99609 | -0.029152 | 21.3897
100 | -0.71521 | -0.3239 | 0.71523 | 0.32343 | 1.4059e-05 | -0.00047777 | 0.022754 | 0.022749 | 0.022754 | 0.99607 | -0.029006 | 0.99609 | -0.029152 | 10.3429
101 | 0.75559 | 0.36448 | -0.75558 | -0.36478 | 1.0313e-05 | -0.00030649 | 0.024312 | 0.024316 | 0.024316 | 0.99609 | -0.029152 | 0.99608 | -0.029034 | 11.0528
102 | -4.3913 | -1.8902 | 4.3941 | 1.8971 | 0.0027913 | 0.0069457 | 0.13848 | 0.13848 | 0.13848 | 0.99657 | -0.13709 | 0.99772 | -0.067765 | 21.4705
103 | -4.4886 | -1.9429 | 4.4889 | 1.9408 | 0.00021869 | -0.0020877 | 0.14152 | 0.14149 | 0.14152 | 0.99772 | -0.067765 | 0.99777 | -0.067458 | 22.1812
104 | -4.5589 | -1.9748 | 4.5589 | 1.9747 | 1.0322e-05 | -9.5318e-05 | 0.14374 | 0.14374 | 0.14374 | 0.99777 | -0.067458 | 0.99777 | -0.067443 | 22.53
105 | 0.61514 | 0.29676 | -0.61511 | -0.29791 | 2.5523e-05 | -0.0011475 | 0.019794 | 0.019808 | 0.019808 | 0.99608 | -0.029034 | 0.99604 | -0.028674 | 9.0037

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 10.8927 | 4.8345

## res_load
| p_mw | q_mvar
0 | 0.11567 | 0.056022
1 | 0.18409 | 0.089159
2 | 0.33167 | 0.16064
3 | 0.20212 | 0.09789
4 | 0.17006 | 0.082366
5 | 0.15769 | 0.076375
6 | 0.15494 | 0.075039
7 | 0.20738 | 0.10044
8 | 0.076528 | 0.037064
9 | 0.10577 | 0.051227
10 | 0.29166 | 0.14126
11 | 0.21314 | 0.10323
12 | 0.11716 | 0.056741
13 | 0.24887 | 0.12053
14 | 0.16756 | 0.081153
15 | 0.071419 | 0.03459
16 | 0.16326 | 0.079068
17 | 0.20672 | 0.10012
18 | 0.20328 | 0.098452
19 | 0.15093 | 0.073098
20 | 0.27675 | 0.13404
21 | 0.17022 | 0.082441
22 | 0.14324 | 0.069374
23 | 0.10248 | 0.049631
24 | 0.15006 | 0.072677
25 | 0.18008 | 0.087218
26 | 0.19797 | 0.095883
27 | 0.22172 | 0.10738
28 | 0.25993 | 0.12589
29 | 0.30594 | 0.14817
30 | 0.40319 | 0.19527
31 | 0.077483 | 0.037527
32 | 0.37934 | 0.18372
33 | 0.074186 | 0.03593
34 | 0.097167 | 0.04706
35 | 0.098552 | 0.047731
36 | 0.18185 | 0.088075
37 | 0.1119 | 0.054196
38 | 0.11273 | 0.054599
39 | 0.092399 | 0.044751
40 | 0.34779 | 0.16844
41 | 0.12938 | 0.062662
42 | 0.27392 | 0.13267
43 | 0.41924 | 0.20305
44 | 0.16245 | 0.078676
45 | 0.13372 | 0.064763
46 | 0.11372 | 0.055077
47 | 0.15111 | 0.073188
48 | 0.33342 | 0.16148
49 | 0.25769 | 0.12481
50 | 0.09458 | 0.045807
51 | 0.30675 | 0.14857
52 | 0.070081 | 0.033942
53 | 0.086651 | 0.041967
54 | 0.14045 | 0.068021
55 | 0.61511 | 0.29791

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1