## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_3_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_3_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_3_0_node_97 | 20 | n |  | TRUE
3 | bus_MV_3_0_node_96 | 20 | n |  | TRUE
4 | bus_MV_3_0_node_2 | 20 | n |  | TRUE
5 | bus_MV_3_0_node_100 | 20 | n |  | TRUE
6 | bus_MV_3_0_node_43 | 20 | n |  | TRUE
7 | bus_MV_3_0_node_99 | 20 | n |  | TRUE
8 | bus_MV_3_0_node_42 | 20 | n |  | TRUE
9 | bus_MV_3_0_node_3 | 20 | n |  | TRUE
10 | bus_MV_3_0_node_4 | 20 | n |  | TRUE
11 | bus_MV_3_0_node_5 | 20 | n |  | TRUE
12 | bus_MV_3_0_node_8 | 20 | n |  | TRUE
13 | bus_MV_3_0_node_113 | 20 | n |  | TRUE
14 | bus_MV_3_0_node_106 | 20 | n |  | TRUE
15 | bus_MV_3_0_node_7 | 20 | n |  | TRUE
16 | bus_MV_3_0_node_28 | 20 | n |  | TRUE
17 | bus_MV_3_0_node_35 | 20 | n |  | TRUE
18 | bus_MV_3_0_node_36 | 20 | n |  | TRUE
19 | bus_MV_3_0_node_25 | 20 | n |  | TRUE
20 | bus_MV_3_0_node_26 | 20 | n |  | TRUE
21 | bus_MV_3_0_node_114 | 20 | n |  | TRUE
22 | bus_MV_3_0_node_37 | 20 | n |  | TRUE
23 | bus_MV_3_0_node_33 | 20 | n |  | TRUE
24 | bus_MV_3_0_node_31 | 20 | n |  | TRUE
25 | bus_MV_3_0_node_30 | 20 | n |  | TRUE
26 | bus_MV_3_0_node_32 | 20 | n |  | TRUE
27 | bus_MV_3_0_node_34 | 20 | n |  | TRUE
28 | bus_MV_3_0_node_38 | 20 | n |  | TRUE
29 | bus_MV_3_0_node_27 | 20 | n |  | TRUE
30 | bus_MV_3_0_node_41 | 20 | n |  | TRUE
31 | bus_MV_3_0_node_40 | 20 | n |  | TRUE
32 | bus_MV_3_0_node_13 | 20 | n |  | TRUE
33 | bus_MV_3_0_node_29 | 20 | n |  | TRUE
34 | bus_MV_3_0_node_39 | 20 | n |  | TRUE
35 | bus_MV_3_0_node_21 | 20 | n |  | TRUE
36 | bus_MV_3_0_node_89 | 20 | n |  | TRUE
37 | bus_MV_3_0_node_87 | 20 | n |  | TRUE
38 | bus_MV_3_0_node_14 | 20 | n |  | TRUE
39 | bus_MV_3_0_node_24 | 20 | n |  | TRUE
40 | bus_MV_3_0_node_11 | 20 | n |  | TRUE
41 | bus_MV_3_0_node_9 | 20 | n |  | TRUE
42 | bus_MV_3_0_node_10 | 20 | n |  | TRUE
43 | bus_MV_3_0_node_12 | 20 | n |  | TRUE
44 | bus_MV_3_0_node_16 | 20 | n |  | TRUE
45 | bus_MV_3_0_node_112 | 20 | n |  | TRUE
46 | bus_MV_3_0_node_45 | 20 | n |  | TRUE
47 | bus_MV_3_0_node_15 | 20 | n |  | TRUE
48 | bus_MV_3_0_node_19 | 20 | n |  | TRUE
49 | bus_MV_3_0_node_47 | 20 | n |  | TRUE
50 | bus_MV_3_0_node_111 | 20 | n |  | TRUE
51 | bus_MV_3_0_node_17 | 20 | n |  | TRUE
52 | bus_MV_3_0_node_20 | 20 | n |  | TRUE
53 | bus_MV_3_0_node_108 | 20 | n |  | TRUE
54 | bus_MV_3_0_node_18 | 20 | n |  | TRUE
55 | bus_MV_3_0_node_46 | 20 | n |  | TRUE
56 | bus_MV_3_0_node_44 | 20 | n |  | TRUE
57 | bus_MV_3_0_node_83 | 20 | n |  | TRUE
58 | bus_MV_3_0_node_86 | 20 | n |  | TRUE
59 | bus_MV_3_0_node_81 | 20 | n |  | TRUE
60 | bus_MV_3_0_node_72 | 20 | n |  | TRUE
61 | bus_MV_3_0_node_73 | 20 | n |  | TRUE
62 | bus_MV_3_0_node_101 | 20 | n |  | TRUE
63 | bus_MV_3_0_node_74 | 20 | n |  | TRUE
64 | bus_MV_3_0_node_75 | 20 | n |  | TRUE
65 | bus_MV_3_0_node_103 | 20 | n |  | TRUE
66 | bus_MV_3_0_node_76 | 20 | n |  | TRUE
67 | bus_MV_3_0_node_104 | 20 | n |  | TRUE
68 | bus_MV_3_0_node_98 | 20 | n |  | TRUE
69 | bus_MV_3_0_node_95 | 20 | n |  | TRUE
70 | bus_MV_3_0_node_91 | 20 | n |  | TRUE
71 | bus_MV_3_0_node_90 | 20 | n |  | TRUE
72 | bus_MV_3_0_node_88 | 20 | n |  | TRUE
73 | bus_MV_3_0_node_94 | 20 | n |  | TRUE
74 | bus_MV_3_0_node_80 | 20 | n |  | TRUE
75 | bus_MV_3_0_node_82 | 20 | n |  | TRUE
76 | bus_MV_3_0_node_122 | 20 | n |  | TRUE
77 | bus_MV_3_0_node_109 | 20 | n |  | TRUE
78 | bus_MV_3_0_node_53 | 20 | n |  | TRUE
79 | bus_MV_3_0_node_110 | 20 | n |  | TRUE
80 | bus_MV_3_0_node_71 | 20 | n |  | TRUE
81 | bus_MV_3_0_node_64 | 20 | n |  | TRUE
82 | bus_MV_3_0_node_70 | 20 | n |  | TRUE
83 | bus_MV_3_0_node_77 | 20 | n |  | TRUE
84 | bus_MV_3_0_node_78 | 20 | n |  | TRUE
85 | bus_MV_3_0_node_48 | 20 | n |  | TRUE
86 | bus_MV_3_0_node_49 | 20 | n |  | TRUE
87 | bus_MV_3_0_node_51 | 20 | n |  | TRUE
88 | bus_MV_3_0_node_50 | 20 | n |  | TRUE
89 | bus_MV_3_0_node_58 | 20 | n |  | TRUE
90 | bus_MV_3_0_node_107 | 20 | n |  | TRUE
91 | bus_MV_3_0_node_69 | 20 | n |  | TRUE
92 | bus_MV_3_0_node_67 | 20 | n |  | TRUE
93 | bus_MV_3_0_node_68 | 20 | n |  | TRUE
94 | bus_MV_3_0_node_119 | 20 | n |  | TRUE
95 | bus_MV_3_0_node_115 | 20 | n |  | TRUE
96 | bus_MV_3_0_node_116 | 20 | n |  | TRUE
97 | bus_MV_3_0_node_66 | 20 | n |  | TRUE
98 | bus_MV_3_0_node_52 | 20 | n |  | TRUE
99 | bus_MV_3_0_node_54 | 20 | n |  | TRUE
100 | bus_MV_3_0_node_118 | 20 | n |  | TRUE
101 | bus_MV_3_0_node_117 | 20 | n |  | TRUE
102 | bus_MV_3_0_node_63 | 20 | n |  | TRUE
103 | bus_MV_3_0_node_55 | 20 | n |  | TRUE
104 | bus_MV_3_0_node_56 | 20 | n |  | TRUE
105 | bus_MV_3_0_node_57 | 20 | n |  | TRUE
106 | bus_MV_3_0_node_120 | 20 | n |  | TRUE
107 | bus_MV_3_0_node_62 | 20 | n |  | TRUE
108 | bus_MV_3_0_node_59 | 20 | n |  | TRUE
109 | bus_MV_3_0_node_60 | 20 | n |  | TRUE
110 | bus_MV_3_0_node_61 | 20 | n |  | TRUE
111 | bus_MV_3_0_node_121 | 20 | n |  | TRUE
112 | bus_MV_3_0_node_84 | 20 | n |  | TRUE
113 | bus_MV_3_0_node_85 | 20 | n |  | TRUE
114 | bus_MV_3_0_node_92 | 20 | n |  | TRUE
115 | bus_MV_3_0_node_93 | 20 | n |  | TRUE
116 | bus_HV_3_0_node_18 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_3_0_load_0 | 0 | 0.051734 | 0.025056 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_3_0_load_97 | 2 | 0.32049 | 0.15522 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_3_0_load_100 | 5 | 0.30004 | 0.14531 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_3_0_load_99 | 7 | 0.076321 | 0.036964 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_3_0_load_3 | 9 | 0.37289 | 0.1806 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_3_0_load_113 | 13 | 0.2997 | 0.14515 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_3_0_load_106 | 14 | 0.20462 | 0.099101 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_3_0_load_35 | 17 | 0.35521 | 0.17204 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_3_0_load_36 | 18 | 0.3486 | 0.16883 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_3_0_load_114 | 21 | 0.21856 | 0.10585 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_3_0_load_37 | 22 | 0.40019 | 0.19382 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_3_0_load_30 | 25 | 0.21916 | 0.10614 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_3_0_load_38 | 28 | 0.34788 | 0.16849 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_3_0_load_40 | 31 | 0.27452 | 0.13296 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_3_0_load_39 | 34 | 0.15134 | 0.073298 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_3_0_load_21 | 35 | 0.27806 | 0.13467 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_3_0_load_87 | 37 | 0.32171 | 0.15581 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_3_0_load_24 | 39 | 0.27831 | 0.13479 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_3_0_load_9 | 41 | 0.32239 | 0.15614 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_3_0_load_112 | 45 | 0.98675 | 0.47791 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_3_0_load_45 | 46 | 0.41407 | 0.20054 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_3_0_load_47 | 49 | 0.34747 | 0.16829 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_3_0_load_111 | 50 | 0.36028 | 0.17449 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_3_0_load_108 | 53 | 0.37314 | 0.18072 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_3_0_load_46 | 55 | 0.17038 | 0.082518 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_3_0_load_44 | 56 | 0.28189 | 0.13653 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_3_0_load_83 | 57 | 0.10221 | 0.049504 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_3_0_load_72 | 60 | 0.25619 | 0.12408 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_3_0_load_101 | 62 | 0.085051 | 0.041192 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_3_0_load_103 | 65 | 0.11927 | 0.057767 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_3_0_load_104 | 67 | 0.080229 | 0.038856 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_3_0_load_98 | 68 | 0.069343 | 0.033584 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_3_0_load_95 | 69 | 0.69832 | 0.33821 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_3_0_load_91 | 70 | 0.13641 | 0.066065 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_3_0_load_90 | 71 | 0.11023 | 0.053387 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_3_0_load_88 | 72 | 0.10329 | 0.050027 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_3_0_load_94 | 73 | 0.11851 | 0.057397 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_3_0_load_80 | 74 | 0.094529 | 0.045782 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_3_0_load_82 | 75 | 0.21304 | 0.10318 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_3_0_load_110 | 79 | 0.11357 | 0.055003 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_3_0_load_64 | 81 | 0.24628 | 0.11928 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_3_0_load_70 | 82 | 0.073252 | 0.035478 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_3_0_load_77 | 83 | 0.17783 | 0.086126 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_3_0_load_78 | 84 | 0.23207 | 0.1124 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_3_0_load_48 | 85 | 0.18803 | 0.091067 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_3_0_load_58 | 89 | 0.26822 | 0.1299 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_3_0_load_107 | 90 | 0.22723 | 0.11005 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_3_0_load_119 | 94 | 0.35182 | 0.17039 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_3_0_load_115 | 95 | 0.27883 | 0.13504 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_3_0_load_66 | 97 | 0.13799 | 0.06683 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_3_0_load_52 | 98 | 0.18618 | 0.090169 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_3_0_load_117 | 101 | 0.20947 | 0.10145 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_3_0_load_63 | 102 | 0.28356 | 0.13733 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_3_0_load_55 | 103 | 0.073013 | 0.035362 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_3_0_load_120 | 106 | 0.090474 | 0.043819 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_3_0_load_59 | 108 | 0.3097 | 0.14999 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_3_0_load_121 | 111 | 0.1046 | 0.05066 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_3_0_load_84 | 112 | 0.11753 | 0.056921 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_3_0_load_93 | 115 | 0.27249 | 0.13197 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 54 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_3_0_line_0 |  | 0 | 1 | 0.10807 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_3_0_line_1 |  | 1 | 2 | 0.62459 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_3_0_line_2 |  | 2 | 3 | 0.12146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_3_0_line_3 |  | 3 | 73 | 0.075514 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_3_0_line_4 |  | 4 | 5 | 0.014845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_3_0_line_5 |  | 4 | 6 | 0.061521 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_3_0_line_6 |  | 6 | 7 | 0.061054 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_3_0_line_7 |  | 6 | 8 | 0.029023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_3_0_line_8 |  | 8 | 69 | 0.093311 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_3_0_line_9 |  | 8 | 30 | 0.12357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_3_0_line_10 |  | 9 | 10 | 0.092083 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_3_0_line_11 |  | 10 | 11 | 0.45926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_3_0_line_12 |  | 11 | 12 | 0.77949 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_3_0_line_13 |  | 11 | 13 | 0.041258 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_3_0_line_14 |  | 11 | 14 | 0.22786 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_3_0_line_15 |  | 12 | 18 | 0.01444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_3_0_line_16 |  | 12 | 15 | 0.40534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_3_0_line_17 |  | 14 | 23 | 0.086626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_3_0_line_18 |  | 15 | 16 | 0.42026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_3_0_line_19 |  | 15 | 17 | 0.017724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_3_0_line_20 |  | 16 | 22 | 0.029254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_3_0_line_21 |  | 16 | 19 | 0.36077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_3_0_line_22 |  | 19 | 20 | 0.46307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_3_0_line_23 |  | 19 | 21 | 0.065997 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_3_0_line_24 |  | 20 | 33 | 0.54498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_3_0_line_25 |  | 20 | 34 | 0.031374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_3_0_line_26 |  | 20 | 32 | 0.34396 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
27 | MV_3_0_line_27 |  | 20 | 35 | 0.1992 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_3_0_line_28 |  | 23 | 24 | 0.058257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_3_0_line_29 |  | 24 | 25 | 0.003935 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_3_0_line_30 |  | 25 | 26 | 0.037574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_3_0_line_31 |  | 26 | 27 | 0.076526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_3_0_line_32 |  | 27 | 28 | 0.035258 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_3_0_line_33 |  | 29 | 30 | 0.039565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_3_0_line_34 |  | 29 | 31 | 0.041038 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_3_0_line_35 |  | 29 | 32 | 0.29739 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_3_0_line_36 |  | 30 | 68 | 0.02287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_3_0_line_37 |  | 32 | 38 | 0.2214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_3_0_line_38 |  | 32 | 39 | 0.019541 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_3_0_line_39 |  | 32 | 40 | 0.44045 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
40 | MV_3_0_line_40 |  | 33 | 36 | 0.02164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_3_0_line_41 |  | 33 | 37 | 0.042939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_3_0_line_42 |  | 36 | 70 | 0.032159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_3_0_line_43 |  | 36 | 71 | 0.0056951 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_3_0_line_44 |  | 37 | 72 | 0.046027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_3_0_line_45 |  | 38 | 46 | 0.003782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_3_0_line_46 |  | 40 | 44 | 0.60765 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
47 | MV_3_0_line_47 |  | 40 | 41 | 0.031324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_3_0_line_48 |  | 41 | 42 | 0.007332 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_3_0_line_49 |  | 42 | 43 | 0.4244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_3_0_line_50 |  | 43 | 45 | 0.036349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_3_0_line_51 |  | 44 | 50 | 0.00755 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_3_0_line_52 |  | 44 | 51 | 0.30214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_3_0_line_53 |  | 44 | 52 | 0.52919 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
54 | MV_3_0_line_54 |  | 47 | 48 | 0.16401 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_3_0_line_55 |  | 47 | 49 | 0.067953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_3_0_line_56 |  | 48 | 52 | 0.26141 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
57 | MV_3_0_line_57 |  | 48 | 56 | 0.033522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_3_0_line_58 |  | 48 | 54 | 0.56257 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
59 | MV_3_0_line_59 |  | 51 | 53 | 0.004503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_3_0_line_60 |  | 52 | 57 | 0.058118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_3_0_line_61 |  | 53 | 58 | 0.049588 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_3_0_line_62 |  | 54 | 55 | 0.078815 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
63 | MV_3_0_line_63 |  | 55 | 59 | 1.2897 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
64 | MV_3_0_line_64 |  | 58 | 113 | 0.041692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_3_0_line_65 |  | 59 | 76 | 1.6705 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_3_0_line_66 |  | 59 | 74 | 0.14798 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
67 | MV_3_0_line_67 |  | 60 | 61 | 0.17394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_3_0_line_68 |  | 60 | 62 | 0.22214 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
69 | MV_3_0_line_69 |  | 61 | 63 | 0.23141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_3_0_line_70 |  | 61 | 64 | 0.24283 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_3_0_line_71 |  | 62 | 80 | 1.445 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
72 | MV_3_0_line_72 |  | 63 | 65 | 0.082507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_3_0_line_73 |  | 64 | 66 | 0.37882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_3_0_line_74 |  | 64 | 67 | 0.22814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_3_0_line_75 |  | 66 | 83 | 0.077117 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_3_0_line_76 |  | 69 | 73 | 0.069606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_3_0_line_77 |  | 70 | 114 | 0.030981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_3_0_line_78 |  | 74 | 75 | 0.2057 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
79 | MV_3_0_line_79 |  | 75 | 77 | 0.043447 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
80 | MV_3_0_line_80 |  | 76 | 111 | 0.011758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_3_0_line_81 |  | 77 | 78 | 3.4172 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
82 | MV_3_0_line_82 |  | 78 | 99 | 0.83994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_3_0_line_83 |  | 78 | 100 | 2.6473 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
84 | MV_3_0_line_84 |  | 78 | 98 | 0.028256 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_3_0_line_85 |  | 79 | 80 | 1.6834 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
86 | MV_3_0_line_86 |  | 79 | 81 | 1.784 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
87 | MV_3_0_line_87 |  | 80 | 82 | 0.25918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_3_0_line_88 |  | 81 | 96 | 1.0783 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
89 | MV_3_0_line_89 |  | 83 | 84 | 0.066113 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_3_0_line_90 |  | 85 | 86 | 0.097525 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_3_0_line_91 |  | 86 | 87 | 0.3882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_3_0_line_92 |  | 87 | 90 | 0.006506 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_3_0_line_93 |  | 87 | 91 | 0.21815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_3_0_line_94 |  | 87 | 92 | 0.88147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_3_0_line_95 |  | 87 | 88 | 0.46284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_3_0_line_96 |  | 88 | 89 | 0.003539 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_3_0_line_97 |  | 91 | 95 | 0.003169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_3_0_line_98 |  | 91 | 96 | 0.36787 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_3_0_line_99 |  | 92 | 97 | 0.026823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_3_0_line_100 |  | 92 | 93 | 0.47376 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_3_0_line_101 |  | 93 | 94 | 0.058962 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_3_0_line_102 |  | 96 | 101 | 0.076231 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
103 | MV_3_0_line_103 |  | 97 | 110 | 0.06052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_3_0_line_104 |  | 99 | 102 | 0.011275 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_3_0_line_105 |  | 100 | 101 | 0.066761 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
106 | MV_3_0_line_106 |  | 103 | 104 | 0.094611 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_3_0_line_107 |  | 104 | 105 | 0.71638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_3_0_line_108 |  | 105 | 106 | 0.05083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_3_0_line_109 |  | 106 | 107 | 0.004303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_3_0_line_110 |  | 107 | 109 | 0.74187 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_3_0_line_111 |  | 108 | 109 | 0.020144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_3_0_line_112 |  | 109 | 110 | 0.23491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_3_0_line_113 |  | 112 | 113 | 0.020216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_3_0_line_114 |  | 114 | 115 | 0.027225 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_3_0_trafo_18 | 25 MVA 110/20 kV | 116 | 54 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2663428.7129 | 1210691.2614
1 | 2663383.2189 | 1210659.2141
2 | 2662998.2438 | 1211151.0605
3 | 2663036.7805 | 1211230.7717
4 | 2662841.4356 | 1211049.9234
5 | 2662831.7969 | 1211058.1158
6 | 2662876.7124 | 1211100.3257
7 | 2662935.8877 | 1211115.3537
8 | 2662873.9807 | 1211125.8903
9 | 2664271.6446 | 1211962.9703
10 | 2664180.8354 | 1211947.7057
11 | 2663914.8659 | 1211818.7606
12 | 2663718.4216 | 1211553.0636
13 | 2663880.7513 | 1211841.9651
14 | 2663992.2757 | 1211604.4477
15 | 2663520.5836 | 1211375.1788
16 | 2663291.6353 | 1211367.2637
17 | 2663538.3545 | 1211374.7567
18 | 2663732.902 | 1211553.3184
19 | 2663050.8036 | 1211411.6526
20 | 2662805.0581 | 1211514.6019
21 | 2662990.9288 | 1211383.8922
22 | 2663320.5742 | 1211372.0847
23 | 2664074.732 | 1211631.7381
24 | 2664118.5329 | 1211645.6505
25 | 2664117.3982 | 1211649.4184
26 | 2664152.9945 | 1211661.7307
27 | 2664216.5628 | 1211685.8737
28 | 2664247.0302 | 1211703.7682
29 | 2662832.1929 | 1211258.5756
30 | 2662845.8176 | 1211238.429
31 | 2662792.3162 | 1211248.8833
32 | 2662692.7236 | 1211355.0455
33 | 2662983.8228 | 1211279.6535
34 | 2662780.2828 | 1211533.6862
35 | 2662930.3996 | 1211669.4281
36 | 2662990.5511 | 1211261.3689
37 | 2662942.2887 | 1211268.7587
38 | 2662538.9706 | 1211409.7212
39 | 2662688.8823 | 1211374.2058
40 | 2662424.9233 | 1211190.7825
41 | 2662432.1045 | 1211160.2946
42 | 2662424.9723 | 1211158.5078
43 | 2662670.894 | 1211066.2845
44 | 2662256.0365 | 1211313.3931
45 | 2662635.3374 | 1211058.2619
46 | 2662536.4777 | 1211406.8711
47 | 2662169.5493 | 1211726.2766
48 | 2662118.0421 | 1211609.28
49 | 2662181.3815 | 1211793.1852
50 | 2662248.4985 | 1211314.1038
51 | 2662257.8649 | 1211107.6534
52 | 2662278.6971 | 1211683.7443
53 | 2662260.2152 | 1211103.8089
54 | 2661782.8092 | 1211712.4516
55 | 2661706.3777 | 1211693.2158
56 | 2662098.0496 | 1211582.3332
57 | 2662247.7322 | 1211651.1427
58 | 2662286.1294 | 1211061.5313
59 | 2660517.8428 | 1211192.5294
60 | 2660925.3712 | 1216311.3087
61 | 2660942.6879 | 1216139.9911
62 | 2661143.4323 | 1216353.6855
63 | 2660782.1129 | 1216147.668
64 | 2661063.8532 | 1215944.4211
65 | 2660784.7782 | 1216230.1319
66 | 2661190.0377 | 1215832.4566
67 | 2660852.6918 | 1215883.4733
68 | 2662851.2072 | 1211216.2031
69 | 2662896.8116 | 1211192.4892
70 | 2663021.6772 | 1211269.4558
71 | 2662991.8838 | 1211255.8319
72 | 2662897.7681 | 1211257.0804
73 | 2662963.8083 | 1211211.3708
74 | 2660378.1364 | 1211143.7325
75 | 2660378.5663 | 1211349.4361
76 | 2661109.1748 | 1209630.1413
77 | 2660350.5499 | 1211382.406
78 | 2657993.9588 | 1213856.9715
79 | 2659968.4355 | 1218202.0979
80 | 2661584.1872 | 1217729.7997
81 | 2659340.4467 | 1216532.3286
82 | 2661683.0983 | 1217962.6448
83 | 2661249.558 | 1215783.2262
84 | 2661208.0349 | 1215731.7792
85 | 2657941.8452 | 1216599.06
86 | 2657858.0297 | 1216648.9212
87 | 2657928.7536 | 1216771.9499
88 | 2657519.8662 | 1216836.6423
89 | 2657522.8695 | 1216838.528
90 | 2657926.3489 | 1216777.9969
91 | 2658125.7824 | 1216821.442
92 | 2657826.9477 | 1217334.2399
93 | 2657880.0124 | 1217116.7436
94 | 2657909.5835 | 1217065.7327
95 | 2658125.836 | 1216818.2739
96 | 2658265.04 | 1216611.0054
97 | 2657810.2339 | 1217355.2132
98 | 2657968.89 | 1213844.0447
99 | 2657593.095 | 1213556.9952
100 | 2658192.9446 | 1216496.7647
101 | 2658207.3098 | 1216561.2222
102 | 2657592.9102 | 1213568.2669
103 | 2656677.9725 | 1217728.8045
104 | 2656729.6755 | 1217649.5699
105 | 2657200.4568 | 1217861.3535
106 | 2657241.7604 | 1217832.5322
107 | 2657245.1711 | 1217829.8967
108 | 2657576.4062 | 1217365.8236
109 | 2657595.2387 | 1217373.0099
110 | 2657769.1525 | 1217399.5754
111 | 2661105.6564 | 1209618.9208
112 | 2662325.8427 | 1211035.3182
113 | 2662307.9235 | 1211025.9594
114 | 2663051.6622 | 1211277.2462
115 | 2663065.7324 | 1211300.5535
116 | 2661782.8092 | 1211712.4516

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99161 | -0.039799 | 0.051734 | 0.025056
1 | 0.99162 | -0.039858 | 0 | 0
2 | 0.99168 | -0.039304 | 0.32049 | 0.15522
3 | 0.99174 | -0.039817 | 0 | 0
4 | 0.99191 | -0.041886 | 0 | 0
5 | 0.99191 | -0.041832 | 0.30004 | 0.14531
6 | 0.99195 | -0.041657 | 0 | 0
7 | 0.99194 | -0.041603 | 0.076321 | 0.036964
8 | 0.99196 | -0.041786 | 0 | 0
9 | 0.9856 | -0.005444 | 0.37289 | 0.1806
10 | 0.98567 | -0.0050164 | 0 | 0
11 | 0.98589 | -0.0069614 | 0 | 0
12 | 0.98734 | -0.019423 | 0 | 0
13 | 0.98587 | -0.0071152 | 0.2997 | 0.14515
14 | 0.98555 | -0.0092894 | 0.20462 | 0.099101
15 | 0.98827 | -0.027246 | 0 | 0
16 | 0.98943 | -0.036891 | 0 | 0
17 | 0.98826 | -0.027169 | 0.35521 | 0.17204
18 | 0.98733 | -0.019361 | 0.3486 | 0.16883
19 | 0.9906 | -0.046684 | 0 | 0
20 | 0.99224 | -0.060157 | 0 | 0
21 | 0.99058 | -0.046862 | 0.21856 | 0.10585
22 | 0.98941 | -0.036749 | 0.40019 | 0.19382
23 | 0.98548 | -0.0087179 | 0 | 0
24 | 0.98544 | -0.0083271 | 0 | 0
25 | 0.98544 | -0.0083005 | 0.21916 | 0.10614
26 | 0.98542 | -0.0081469 | 0 | 0
27 | 0.98539 | -0.0078275 | 0 | 0
28 | 0.98537 | -0.0076773 | 0.34788 | 0.16849
29 | 0.99229 | -0.044751 | 0 | 0
30 | 0.99221 | -0.044011 | 0 | 0
31 | 0.99227 | -0.044889 | 0.27452 | 0.13296
32 | 0.99302 | -0.051218 | 0 | 0
33 | 0.99159 | -0.054276 | 0 | 0
34 | 0.99224 | -0.0601 | 0.15134 | 0.073298
35 | 0.99214 | -0.060839 | 0.27806 | 0.13467
36 | 0.99157 | -0.054142 | 0 | 0
37 | 0.99156 | -0.054059 | 0.32171 | 0.15581
38 | 0.9929 | -0.050144 | 0 | 0
39 | 0.99301 | -0.051285 | 0.27831 | 0.13479
40 | 0.99432 | -0.0272 | 0 | 0
41 | 0.99427 | -0.026726 | 0.32239 | 0.15614
42 | 0.99426 | -0.026644 | 0 | 0
43 | 0.99372 | -0.021733 | 0 | 0
44 | 0.99592 | -0.019774 | 0 | 0
45 | 0.99368 | -0.0213 | 0.98675 | 0.47791
46 | 0.9929 | -0.050125 | 0.41407 | 0.20054
47 | 0.99816 | -0.0080632 | 0 | 0
48 | 0.99823 | -0.00871 | 0 | 0
49 | 0.99813 | -0.0077832 | 0.34747 | 0.16829
50 | 0.99592 | -0.019741 | 0.36028 | 0.17449
51 | 0.99573 | -0.018086 | 0 | 0
52 | 0.99746 | -0.012451 | 0 | 0
53 | 0.99573 | -0.01806 | 0.37314 | 0.18072
54 | 1 | 0 | -14.3487 | -6.4734
55 | 0.99982 | -0.0062148 | 0.17038 | 0.082518
56 | 0.99822 | -0.0085974 | 0.28189 | 0.13653
57 | 0.99746 | -0.012382 | 0.10221 | 0.049504
58 | 0.99572 | -0.018138 | 0 | 0
59 | 0.99702 | -0.10456 | 0 | 0
60 | 0.9814 | -0.65493 | 0.25619 | 0.12408
61 | 0.98126 | -0.65396 | 0 | 0
62 | 0.98163 | -0.64883 | 0.085051 | 0.041192
63 | 0.98123 | -0.65369 | 0 | 0
64 | 0.98111 | -0.65278 | 0 | 0
65 | 0.98122 | -0.65357 | 0.11927 | 0.057767
66 | 0.98091 | -0.65101 | 0 | 0
67 | 0.98109 | -0.6526 | 0.080229 | 0.038856
68 | 0.99221 | -0.043992 | 0.069343 | 0.033584
69 | 0.99182 | -0.040501 | 0.69832 | 0.33821
70 | 0.99155 | -0.053985 | 0.13641 | 0.066065
71 | 0.99157 | -0.054135 | 0.11023 | 0.053387
72 | 0.99156 | -0.054003 | 0.10329 | 0.050027
73 | 0.99178 | -0.040124 | 0.11851 | 0.057397
74 | 0.99688 | -0.10724 | 0.094529 | 0.045782
75 | 0.99646 | -0.12225 | 0.21304 | 0.10318
76 | 0.99668 | -0.10687 | 0 | 0
77 | 0.99642 | -0.12298 | 0 | 0
78 | 0.98969 | -0.36157 | 0 | 0
79 | 0.98317 | -0.59398 | 0.11357 | 0.055003
80 | 0.98231 | -0.62458 | 0 | 0
81 | 0.98417 | -0.55805 | 0.24628 | 0.11928
82 | 0.98229 | -0.62439 | 0.073252 | 0.035478
83 | 0.98087 | -0.65062 | 0.17783 | 0.086126
84 | 0.98084 | -0.65081 | 0.23207 | 0.1124
85 | 0.98343 | -0.52197 | 0.18803 | 0.091067
86 | 0.98346 | -0.52174 | 0 | 0
87 | 0.98356 | -0.52253 | 0 | 0
88 | 0.9834 | -0.52116 | 0 | 0
89 | 0.9834 | -0.52115 | 0.26822 | 0.1299
90 | 0.98355 | -0.52251 | 0.22723 | 0.11005
91 | 0.98401 | -0.52558 | 0 | 0
92 | 0.98248 | -0.51574 | 0 | 0
93 | 0.98226 | -0.51385 | 0 | 0
94 | 0.98222 | -0.51411 | 0.35182 | 0.17039
95 | 0.98401 | -0.52557 | 0.27883 | 0.13504
96 | 0.98492 | -0.53182 | 0 | 0
97 | 0.98245 | -0.51561 | 0.13799 | 0.06683
98 | 0.98968 | -0.36151 | 0.18618 | 0.090169
99 | 0.98939 | -0.35922 | 0 | 0
100 | 0.98509 | -0.52631 | 0 | 0
101 | 0.98504 | -0.52733 | 0.20947 | 0.10145
102 | 0.98938 | -0.35918 | 0.28356 | 0.13733
103 | 0.98204 | -0.51427 | 0.073013 | 0.035362
104 | 0.98206 | -0.51418 | 0 | 0
105 | 0.98212 | -0.51443 | 0 | 0
106 | 0.98213 | -0.51442 | 0.090474 | 0.043819
107 | 0.98213 | -0.51443 | 0 | 0
108 | 0.98227 | -0.51456 | 0.3097 | 0.14999
109 | 0.98228 | -0.51464 | 0 | 0
110 | 0.98242 | -0.51542 | 0 | 0
111 | 0.99668 | -0.10685 | 0.1046 | 0.05066
112 | 0.99571 | -0.018053 | 0.11753 | 0.056921
113 | 0.99571 | -0.018081 | 0 | 0
114 | 0.99154 | -0.053883 | 0 | 0
115 | 0.99153 | -0.053974 | 0.27249 | 0.13197
116 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.051734 | -0.025056 | 0.051734 | 0.022519 | 3.9642e-07 | -0.0025371 | 0.0016734 | 0.0016425 | 0.0016734 | 0.99161 | -0.039799 | 0.99162 | -0.039858 | 0.76063
1 | -0.051734 | -0.022519 | 0.051737 | 0.021787 | 2.9869e-06 | -0.00073138 | 0.0016425 | 0.0016341 | 0.0016425 | 0.99162 | -0.039858 | 0.99168 | -0.039304 | 0.78216
2 | -0.37222 | -0.17701 | 0.37225 | 0.17416 | 2.3274e-05 | -0.0028453 | 0.011998 | 0.011963 | 0.011998 | 0.99168 | -0.039304 | 0.99174 | -0.039817 | 5.4537
3 | -0.37225 | -0.17416 | 0.37226 | 0.17239 | 1.44e-05 | -0.0017691 | 0.011963 | 0.011941 | 0.011963 | 0.99174 | -0.039817 | 0.99178 | -0.040124 | 5.4376
4 | 0.30004 | 0.14497 | -0.30004 | -0.14531 | 1.8647e-06 | -0.00034818 | 0.0096978 | 0.0097022 | 0.0097022 | 0.99191 | -0.041886 | 0.99191 | -0.041832 | 4.4101
5 | -0.30004 | -0.14497 | 0.30005 | 0.1449 | 1.0308e-05 | -6.5807e-05 | 0.0096978 | 0.0096968 | 0.0096978 | 0.99191 | -0.041886 | 0.99195 | -0.041657 | 4.618
6 | 0.076322 | 0.03553 | -0.076321 | -0.036964 | 4.9279e-07 | -0.0014342 | 0.00245 | 0.0024679 | 0.0024679 | 0.99195 | -0.041657 | 0.99194 | -0.041603 | 1.1218
7 | -0.37637 | -0.18043 | 0.37638 | 0.17975 | 5.7125e-06 | -0.00068015 | 0.012147 | 0.012138 | 0.012147 | 0.99195 | -0.041657 | 0.99196 | -0.041786 | 5.5212
8 | 1.1893 | 0.56424 | -1.1891 | -0.56637 | 0.00018294 | -0.0021377 | 0.038308 | 0.038335 | 0.038335 | 0.99196 | -0.041786 | 0.99182 | -0.040501 | 17.4251
9 | -1.5657 | -0.74399 | 1.5661 | 0.74121 | 0.0004195 | -0.0027794 | 0.050446 | 0.05041 | 0.050446 | 0.99196 | -0.041786 | 0.99221 | -0.044011 | 22.93
10 | -0.37289 | -0.1806 | 0.37292 | 0.18051 | 2.4158e-05 | -9.1662e-05 | 0.012135 | 0.012134 | 0.012135 | 0.9856 | -0.005444 | 0.98567 | -0.0050164 | 5.7787
11 | -0.37292 | -0.18051 | 0.37301 | 0.16988 | 8.9274e-05 | -0.010629 | 0.012134 | 0.012001 | 0.012134 | 0.98567 | -0.0050164 | 0.98589 | -0.0069614 | 5.5154
12 | -1.4447 | -0.68173 | 1.447 | 0.66429 | 0.0022659 | -0.017444 | 0.046776 | 0.046552 | 0.046776 | 0.98589 | -0.0069614 | 0.98734 | -0.019423 | 21.2617
13 | 0.29971 | 0.14511 | -0.2997 | -0.14515 | 6.9888e-06 | -4.3496e-05 | 0.0097502 | 0.0097508 | 0.0097508 | 0.98589 | -0.0069614 | 0.98587 | -0.0071152 | 4.6432
14 | 0.77201 | 0.36674 | -0.77176 | -0.36685 | 0.0002543 | -0.00010502 | 0.025026 | 0.025029 | 0.025029 | 0.98589 | -0.0069614 | 0.98555 | -0.0092894 | 11.9187
15 | 0.3486 | 0.1685 | -0.3486 | -0.16883 | 2.4714e-06 | -0.00033536 | 0.011321 | 0.011325 | 0.011325 | 0.98734 | -0.019423 | 0.98733 | -0.019361 | 5.1476
16 | -1.7956 | -0.83279 | 1.7974 | 0.82388 | 0.0018086 | -0.0089067 | 0.057871 | 0.057755 | 0.057871 | 0.98734 | -0.019423 | 0.98827 | -0.027246 | 26.3049
17 | 0.56714 | 0.26775 | -0.5671 | -0.26974 | 3.9079e-05 | -0.0019972 | 0.01837 | 0.018395 | 0.018395 | 0.98555 | -0.0092894 | 0.98548 | -0.0087179 | 8.3615
18 | -2.1526 | -0.99551 | 2.1553 | 0.98649 | 0.002688 | -0.0090142 | 0.069277 | 0.069157 | 0.069277 | 0.98827 | -0.027246 | 0.98943 | -0.036891 | 31.4895
19 | 0.35522 | 0.17163 | -0.35521 | -0.17204 | 3.1435e-06 | -0.00041237 | 0.011524 | 0.011529 | 0.011529 | 0.98827 | -0.027246 | 0.98826 | -0.027169 | 5.2404
20 | 0.4002 | 0.19314 | -0.40019 | -0.19382 | 6.5688e-06 | -0.00068182 | 0.012965 | 0.012973 | 0.012973 | 0.98943 | -0.036891 | 0.98941 | -0.036749 | 5.897
21 | -2.5555 | -1.1796 | 2.5587 | 1.1721 | 0.0032439 | -0.0074804 | 0.08212 | 0.082017 | 0.08212 | 0.98943 | -0.036891 | 0.9906 | -0.046684 | 37.3271
22 | -2.7773 | -1.2779 | 2.7822 | 1.2685 | 0.0048995 | -0.009414 | 0.089091 | 0.08896 | 0.089091 | 0.9906 | -0.046684 | 0.99224 | -0.060157 | 40.4961
23 | 0.21856 | 0.10578 | -0.21856 | -0.10585 | 5.8884e-06 | -7.3624e-05 | 0.007076 | 0.007077 | 0.007077 | 0.9906 | -0.046684 | 0.99058 | -0.046862 | 3.37
24 | 0.94484 | 0.44043 | -0.94416 | -0.45303 | 0.00067269 | -0.012603 | 0.030328 | 0.030487 | 0.030487 | 0.99224 | -0.060157 | 0.99159 | -0.054276 | 13.8579
25 | 0.15134 | 0.072561 | -0.15134 | -0.073298 | 1.0006e-06 | -0.00073721 | 0.004883 | 0.0048923 | 0.0048923 | 0.99224 | -0.060157 | 0.99224 | -0.0601 | 2.2238
26 | -4.1565 | -1.916 | 4.1594 | 1.9065 | 0.0029424 | -0.0094884 | 0.13315 | 0.13301 | 0.13315 | 0.99224 | -0.060157 | 0.99302 | -0.051218 | 36.7828
27 | 0.27809 | 0.13445 | -0.27806 | -0.13467 | 2.8671e-05 | -0.00021615 | 0.0089865 | 0.0089894 | 0.0089894 | 0.99224 | -0.060157 | 0.99214 | -0.060839 | 4.2807
28 | 0.5671 | 0.26974 | -0.56707 | -0.27109 | 2.6342e-05 | -0.001343 | 0.018395 | 0.018412 | 0.018412 | 0.98548 | -0.0087179 | 0.98544 | -0.0083271 | 8.3693
29 | 0.56707 | 0.27109 | -0.56707 | -0.27118 | 1.781e-06 | -9.0708e-05 | 0.018412 | 0.018414 | 0.018414 | 0.98544 | -0.0083271 | 0.98544 | -0.0083005 | 8.3698
30 | 0.34791 | 0.16503 | -0.3479 | -0.1659 | 6.3888e-06 | -0.00086927 | 0.01128 | 0.011291 | 0.011291 | 0.98544 | -0.0083005 | 0.98542 | -0.0081469 | 5.1323
31 | 0.3479 | 0.1659 | -0.34789 | -0.16767 | 1.305e-05 | -0.0017703 | 0.011291 | 0.011314 | 0.011314 | 0.98542 | -0.0081469 | 0.98539 | -0.0078275 | 5.1425
32 | 0.34789 | 0.16767 | -0.34788 | -0.16849 | 6.0303e-06 | -0.0008156 | 0.011314 | 0.011324 | 0.011324 | 0.98539 | -0.0078275 | 0.98537 | -0.0076773 | 5.1473
33 | 1.6356 | 0.77337 | -1.6354 | -0.77425 | 0.00014636 | -0.00088667 | 0.052633 | 0.052645 | 0.052645 | 0.99229 | -0.044751 | 0.99221 | -0.044011 | 23.9294
34 | 0.27453 | 0.13291 | -0.27452 | -0.13296 | 5.7574e-06 | -4.4631e-05 | 0.0088734 | 0.008874 | 0.008874 | 0.99229 | -0.044751 | 0.99227 | -0.044889 | 4.2257
35 | -1.9101 | -0.90628 | 1.9116 | 0.89973 | 0.0014998 | -0.0065517 | 0.061506 | 0.061419 | 0.061506 | 0.99229 | -0.044751 | 0.99302 | -0.051218 | 27.9573
36 | 0.069343 | 0.033047 | -0.069343 | -0.033584 | 1.5296e-07 | -0.00053752 | 0.0022349 | 0.0022417 | 0.0022417 | 0.99221 | -0.044011 | 0.99221 | -0.043992 | 1.0189
37 | 0.41412 | 0.19526 | -0.41407 | -0.20045 | 5.2615e-05 | -0.0051963 | 0.01331 | 0.013375 | 0.013375 | 0.99302 | -0.051218 | 0.9929 | -0.050144 | 6.0795
38 | 0.27831 | 0.13477 | -0.27831 | -0.13479 | 2.8135e-06 | -2.1242e-05 | 0.0089892 | 0.0089895 | 0.0089895 | 0.99302 | -0.051218 | 0.99301 | -0.051285 | 4.2807
39 | -6.7635 | -3.1362 | 6.771 | 3.1266 | 0.0075648 | -0.0096689 | 0.21673 | 0.21652 | 0.21673 | 0.99302 | -0.051218 | 0.99432 | -0.0272 | 51.4791
40 | 0.51915 | 0.24928 | -0.51914 | -0.24978 | 8.1237e-06 | -0.00050561 | 0.016766 | 0.016772 | 0.016772 | 0.99159 | -0.054276 | 0.99157 | -0.054142 | 7.6237
41 | 0.42501 | 0.20375 | -0.425 | -0.20476 | 1.0803e-05 | -0.0010048 | 0.013721 | 0.013734 | 0.013734 | 0.99159 | -0.054276 | 0.99156 | -0.054059 | 6.2428
42 | 0.40891 | 0.19653 | -0.40891 | -0.19728 | 7.4954e-06 | -0.00075272 | 0.013208 | 0.013218 | 0.013218 | 0.99157 | -0.054142 | 0.99155 | -0.053985 | 6.0081
43 | 0.11023 | 0.053253 | -0.11023 | -0.053387 | 9.6634e-08 | -0.00013367 | 0.003564 | 0.0035657 | 0.0035657 | 0.99157 | -0.054142 | 0.99157 | -0.054135 | 1.6208
44 | 0.10329 | 0.048947 | -0.10329 | -0.050027 | 6.8322e-07 | -0.0010803 | 0.0033278 | 0.0033414 | 0.0033414 | 0.99156 | -0.054059 | 0.99156 | -0.054003 | 1.5188
45 | 0.41407 | 0.20045 | -0.41407 | -0.20054 | 9.033e-07 | -8.8754e-05 | 0.013375 | 0.013376 | 0.013376 | 0.9929 | -0.050144 | 0.9929 | -0.050125 | 6.0801
46 | -8.0809 | -3.749 | 8.0934 | 3.7183 | 0.012537 | -0.030749 | 0.25863 | 0.25817 | 0.25863 | 0.99432 | -0.0272 | 0.99592 | -0.019774 | 40.537
47 | 1.3099 | 0.62248 | -1.3098 | -0.62319 | 7.4147e-05 | -0.00071739 | 0.042104 | 0.042113 | 0.042113 | 0.99432 | -0.0272 | 0.99427 | -0.026726 | 19.1423
48 | 0.98739 | 0.46705 | -0.98738 | -0.46722 | 9.8448e-06 | -0.00017014 | 0.031713 | 0.031715 | 0.031715 | 0.99427 | -0.026726 | 0.99426 | -0.026644 | 14.416
49 | 0.98738 | 0.46722 | -0.9868 | -0.47706 | 0.00057214 | -0.009842 | 0.031715 | 0.031841 | 0.031841 | 0.99426 | -0.026644 | 0.99372 | -0.021733 | 14.473
50 | 0.9868 | 0.47706 | -0.98675 | -0.47791 | 4.9214e-05 | -0.00084238 | 0.031841 | 0.031851 | 0.031851 | 0.99372 | -0.021733 | 0.99368 | -0.0213 | 14.478
51 | 0.36028 | 0.17431 | -0.36028 | -0.17449 | 1.3568e-06 | -0.00017839 | 0.011601 | 0.011603 | 0.011603 | 0.99592 | -0.019774 | 0.99592 | -0.019741 | 5.2743
52 | 0.49077 | 0.22889 | -0.49067 | -0.23601 | 9.9936e-05 | -0.0071243 | 0.015696 | 0.015785 | 0.015785 | 0.99592 | -0.019774 | 0.99573 | -0.018086 | 7.175
53 | -8.9445 | -4.1215 | 8.9578 | 4.0959 | 0.013306 | -0.025538 | 0.28546 | 0.28506 | 0.28546 | 0.99592 | -0.019774 | 0.99746 | -0.012451 | 44.7431
54 | -0.34748 | -0.16668 | 0.34751 | 0.16278 | 2.7082e-05 | -0.0038938 | 0.011146 | 0.011097 | 0.011146 | 0.99816 | -0.0080632 | 0.99823 | -0.00871 | 5.0663
55 | 0.34748 | 0.16668 | -0.34747 | -0.16829 | 1.129e-05 | -0.0016131 | 0.011146 | 0.011166 | 0.011166 | 0.99816 | -0.0080632 | 0.99813 | -0.0077832 | 5.0755
56 | 9.0667 | 4.1315 | -9.06 | -4.1441 | 0.0067108 | -0.012576 | 0.28813 | 0.28833 | 0.28833 | 0.99823 | -0.00871 | 0.99746 | -0.012451 | 45.193
57 | 0.2819 | 0.13573 | -0.28189 | -0.13653 | 3.6676e-06 | -0.00079645 | 0.0090478 | 0.0090579 | 0.0090579 | 0.99823 | -0.00871 | 0.99822 | -0.0085974 | 4.1172
58 | -9.6961 | -4.43 | 9.7126 | 4.404 | 0.016498 | -0.025995 | 0.30828 | 0.30786 | 0.30828 | 0.99823 | -0.00871 | 1 | 0 | 48.3194
59 | 0.49067 | 0.23601 | -0.49067 | -0.23612 | 1.498e-06 | -0.00010615 | 0.015785 | 0.015786 | 0.015786 | 0.99573 | -0.018086 | 0.99573 | -0.01806 | 7.1756
60 | 0.10221 | 0.048124 | -0.10221 | -0.049504 | 8.3381e-07 | -0.0013804 | 0.0032696 | 0.0032869 | 0.0032869 | 0.99746 | -0.012451 | 0.99746 | -0.012382 | 1.494
61 | 0.11753 | 0.055398 | -0.11753 | -0.055456 | 1.2539e-06 | -5.7908e-05 | 0.0037669 | 0.0037676 | 0.0037676 | 0.99573 | -0.01806 | 0.99572 | -0.018138 | 1.7941
62 | 4.6221 | 2.0589 | -4.6215 | -2.0582 | 0.00059933 | 0.00066373 | 0.14607 | 0.14607 | 0.14607 | 1 | 0 | 0.99982 | -0.0062148 | 17.8135
63 | 4.4512 | 1.9757 | -4.4421 | -1.9659 | 0.00909 | 0.0098325 | 0.14061 | 0.14065 | 0.14065 | 0.99982 | -0.0062148 | 0.99702 | -0.10456 | 17.1521
64 | 0.11753 | 0.055456 | -0.11753 | -0.056443 | 7.9264e-07 | -0.0009867 | 0.0037676 | 0.0037799 | 0.0037799 | 0.99572 | -0.018138 | 0.99571 | -0.018081 | 1.7181
65 | 0.10463 | 0.04842 | -0.1046 | -0.050381 | 3.3409e-05 | -0.0019608 | 0.0033382 | 0.0033627 | 0.0033627 | 0.99702 | -0.10456 | 0.99668 | -0.10687 | 1.6013
66 | 4.3374 | 1.9174 | -4.3369 | -1.9282 | 0.00051107 | -0.010768 | 0.13731 | 0.13744 | 0.13744 | 0.99702 | -0.10456 | 0.99688 | -0.10724 | 16.3232
67 | 0.6097 | 0.26264 | -0.60961 | -0.26662 | 8.8755e-05 | -0.003973 | 0.019527 | 0.019574 | 0.019574 | 0.9814 | -0.65493 | 0.98126 | -0.65396 | 8.8973
68 | -0.86589 | -0.38672 | 0.86604 | 0.38663 | 0.00015866 | -8.7455e-05 | 0.027894 | 0.027891 | 0.027894 | 0.9814 | -0.65493 | 0.98163 | -0.64883 | 7.9699
69 | 0.11928 | 0.050552 | -0.11927 | -0.05587 | 4.5611e-06 | -0.0053186 | 0.0038112 | 0.0038749 | 0.0038749 | 0.98126 | -0.65396 | 0.98123 | -0.65369 | 1.7613
70 | 0.49033 | 0.21606 | -0.49025 | -0.22162 | 8.0892e-05 | -0.0055578 | 0.015763 | 0.01583 | 0.01583 | 0.98126 | -0.65396 | 0.98111 | -0.65278 | 7.1955
71 | -0.9511 | -0.42783 | 0.95158 | 0.42492 | 0.00048371 | -0.0029066 | 0.030669 | 0.030626 | 0.030669 | 0.98163 | -0.64883 | 0.98231 | -0.62458 | 3.7401
72 | 0.11927 | 0.05587 | -0.11927 | -0.057767 | 1.664e-06 | -0.0018962 | 0.0038749 | 0.0038989 | 0.0038989 | 0.98123 | -0.65369 | 0.98122 | -0.65357 | 1.7722
73 | 0.41002 | 0.18801 | -0.40993 | -0.19669 | 8.9805e-05 | -0.0086779 | 0.013272 | 0.013381 | 0.013381 | 0.98111 | -0.65278 | 0.98091 | -0.65101 | 6.0821
74 | 0.080231 | 0.033614 | -0.080229 | -0.038856 | 2.0434e-06 | -0.0052424 | 0.0025595 | 0.0026229 | 0.0026229 | 0.98111 | -0.65278 | 0.98109 | -0.6526 | 1.1922
75 | 0.40993 | 0.19669 | -0.40991 | -0.19845 | 1.8464e-05 | -0.0017661 | 0.013381 | 0.013403 | 0.013403 | 0.98091 | -0.65101 | 0.98087 | -0.65062 | 6.0924
76 | 0.49079 | 0.22816 | -0.49077 | -0.22979 | 2.3089e-05 | -0.0016279 | 0.015753 | 0.015773 | 0.015773 | 0.99182 | -0.040501 | 0.99178 | -0.040124 | 7.1696
77 | 0.2725 | 0.13122 | -0.2725 | -0.13194 | 3.21e-06 | -0.00072629 | 0.0088053 | 0.0088145 | 0.0088145 | 0.99155 | -0.053985 | 0.99154 | -0.053883 | 4.0066
78 | 4.2424 | 1.8824 | -4.2411 | -1.881 | 0.0013244 | 0.0013885 | 0.1344 | 0.13441 | 0.13441 | 0.99688 | -0.10724 | 0.99646 | -0.12225 | 16.3911
79 | 4.028 | 1.7779 | -4.0279 | -1.781 | 0.0001294 | -0.0031771 | 0.12755 | 0.12759 | 0.12759 | 0.99646 | -0.12225 | 0.99642 | -0.12298 | 15.1535
80 | 0.1046 | 0.050381 | -0.1046 | -0.05066 | 1.7769e-07 | -0.00027882 | 0.0033627 | 0.0033662 | 0.0033662 | 0.99668 | -0.10687 | 0.99668 | -0.10685 | 1.5301
81 | 4.0279 | 1.781 | -4.0081 | -1.761 | 0.019843 | 0.020005 | 0.12759 | 0.12769 | 0.12769 | 0.99642 | -0.12298 | 0.98969 | -0.36157 | 15.5725
82 | 0.28365 | 0.11746 | -0.28356 | -0.13707 | 9.2211e-05 | -0.01961 | 0.0089549 | 0.0091893 | 0.0091893 | 0.98969 | -0.36157 | 0.98939 | -0.35922 | 4.177
83 | 3.5382 | 1.5541 | -3.5262 | -1.5434 | 0.011996 | 0.010687 | 0.11272 | 0.1128 | 0.1128 | 0.98969 | -0.36157 | 0.98509 | -0.52631 | 13.7559
84 | 0.18618 | 0.089508 | -0.18618 | -0.090169 | 1.3714e-06 | -0.00066039 | 0.0060254 | 0.0060338 | 0.0060338 | 0.98969 | -0.36157 | 0.98968 | -0.36151 | 2.7426
85 | 1.0255 | 0.45116 | -1.0248 | -0.45443 | 0.00065019 | -0.0032672 | 0.032895 | 0.032945 | 0.032945 | 0.98317 | -0.59398 | 0.98231 | -0.62458 | 4.0177
86 | -1.139 | -0.50616 | 1.1399 | 0.50293 | 0.00085036 | -0.0032373 | 0.036598 | 0.036545 | 0.036598 | 0.98317 | -0.59398 | 0.98417 | -0.55805 | 4.4632
87 | 0.073254 | 0.029507 | -0.073252 | -0.035478 | 1.919e-06 | -0.0059705 | 0.0023208 | 0.0023919 | 0.0023919 | 0.98231 | -0.62458 | 0.98229 | -0.62439 | 1.0872
88 | -1.3862 | -0.6222 | 1.3869 | 0.6206 | 0.00076275 | -0.0016014 | 0.044567 | 0.044535 | 0.044567 | 0.98417 | -0.55805 | 0.98492 | -0.53182 | 5.435
89 | 0.23208 | 0.11233 | -0.23207 | -0.1124 | 6.7835e-06 | -7.1684e-05 | 0.0075882 | 0.0075891 | 0.0075891 | 0.98087 | -0.65062 | 0.98084 | -0.65081 | 3.6139
90 | -0.18803 | -0.091067 | 0.18804 | 0.090958 | 6.5336e-06 | -0.00010851 | 0.0061327 | 0.0061313 | 0.0061327 | 0.98343 | -0.52197 | 0.98346 | -0.52174 | 2.9203
91 | -0.18804 | -0.090958 | 0.18806 | 0.081999 | 1.9127e-05 | -0.0089599 | 0.0061313 | 0.0060213 | 0.0061313 | 0.98346 | -0.52174 | 0.98356 | -0.52253 | 2.7869
92 | 0.22723 | 0.1099 | -0.22723 | -0.11005 | 4.7682e-07 | -0.00015013 | 0.0074084 | 0.0074103 | 0.0074103 | 0.98356 | -0.52253 | 0.98355 | -0.52251 | 3.3683
93 | -1.6479 | -0.70367 | 1.6487 | 0.69887 | 0.0008046 | -0.0048024 | 0.05259 | 0.052533 | 0.05259 | 0.98356 | -0.52253 | 0.98401 | -0.52558 | 23.9048
94 | 0.96433 | 0.39262 | -0.96322 | -0.41263 | 0.0011071 | -0.020009 | 0.030559 | 0.030789 | 0.030789 | 0.98356 | -0.52253 | 0.98248 | -0.51574 | 13.9952
95 | 0.26826 | 0.11915 | -0.26822 | -0.12982 | 4.6555e-05 | -0.010675 | 0.0086152 | 0.0087473 | 0.0087473 | 0.98356 | -0.52253 | 0.9834 | -0.52116 | 3.976
96 | 0.26822 | 0.12982 | -0.26822 | -0.1299 | 3.6154e-07 | -8.1608e-05 | 0.0087473 | 0.0087483 | 0.0087483 | 0.9834 | -0.52116 | 0.9834 | -0.52115 | 3.9765
97 | 0.27883 | 0.13497 | -0.27883 | -0.13504 | 3.4942e-07 | -7.316e-05 | 0.0090877 | 0.0090886 | 0.0090886 | 0.98401 | -0.52558 | 0.98401 | -0.52557 | 4.1312
98 | -1.9275 | -0.83384 | 1.9294 | 0.82588 | 0.0018612 | -0.0079605 | 0.061611 | 0.061512 | 0.061611 | 0.98401 | -0.52558 | 0.98492 | -0.53182 | 28.0048
99 | 0.61131 | 0.25319 | -0.61129 | -0.2538 | 1.3539e-05 | -0.00061414 | 0.019441 | 0.019448 | 0.019448 | 0.98248 | -0.51574 | 0.98245 | -0.51561 | 8.8401
100 | 0.35192 | 0.15944 | -0.35183 | -0.17033 | 8.247e-05 | -0.010892 | 0.011352 | 0.011488 | 0.011488 | 0.98248 | -0.51574 | 0.98226 | -0.51385 | 5.2218
101 | 0.35183 | 0.17033 | -0.35182 | -0.17039 | 1.3865e-05 | -5.9227e-05 | 0.011488 | 0.011489 | 0.011489 | 0.98226 | -0.51385 | 0.98222 | -0.51411 | 5.4709
102 | -3.3163 | -1.4465 | 3.3166 | 1.4467 | 0.00030551 | 0.00025087 | 0.10604 | 0.10604 | 0.10604 | 0.98492 | -0.53182 | 0.98504 | -0.52733 | 12.9321
103 | 0.47331 | 0.18697 | -0.47329 | -0.18836 | 1.8083e-05 | -0.0013893 | 0.014953 | 0.014968 | 0.014968 | 0.98245 | -0.51561 | 0.98242 | -0.51542 | 6.8037
104 | 0.28356 | 0.13707 | -0.28356 | -0.13733 | 1.2715e-06 | -0.00026314 | 0.0091893 | 0.0091927 | 0.0091927 | 0.98939 | -0.35922 | 0.98938 | -0.35918 | 4.1785
105 | 3.5262 | 1.5434 | -3.5261 | -1.5482 | 0.00015553 | -0.0048068 | 0.1128 | 0.11286 | 0.11286 | 0.98509 | -0.52631 | 0.98504 | -0.52733 | 13.4034
106 | -0.073013 | -0.035362 | 0.073014 | 0.035253 | 9.5806e-07 | -0.00010833 | 0.0023847 | 0.0023833 | 0.0023847 | 0.98204 | -0.51427 | 0.98206 | -0.51418 | 1.1356
107 | -0.073014 | -0.035253 | 0.073019 | 0.018758 | 5.008e-06 | -0.016496 | 0.0023833 | 0.0022159 | 0.0023833 | 0.98206 | -0.51418 | 0.98212 | -0.51443 | 1.0833
108 | -0.073019 | -0.018758 | 0.073019 | 0.017587 | 3.3194e-07 | -0.0011705 | 0.0022159 | 0.0022076 | 0.0022159 | 0.98212 | -0.51443 | 0.98213 | -0.51442 | 1.0072
109 | -0.16349 | -0.061406 | 0.16349 | 0.061307 | 1.5132e-07 | -9.9054e-05 | 0.0051333 | 0.0051323 | 0.0051333 | 0.98213 | -0.51442 | 0.98213 | -0.51443 | 2.3333
110 | -0.16349 | -0.061307 | 0.16352 | 0.044226 | 2.5253e-05 | -0.017081 | 0.0051323 | 0.0049782 | 0.0051323 | 0.98213 | -0.51443 | 0.98228 | -0.51464 | 2.3329
111 | -0.3097 | -0.14999 | 0.3097 | 0.14953 | 2.7486e-06 | -0.00046324 | 0.010113 | 0.010107 | 0.010113 | 0.98227 | -0.51456 | 0.98228 | -0.51464 | 4.5967
112 | -0.47322 | -0.19376 | 0.47329 | 0.18836 | 7.054e-05 | -0.0053916 | 0.015028 | 0.014968 | 0.015028 | 0.98228 | -0.51464 | 0.98242 | -0.51542 | 6.8307
113 | -0.11753 | -0.056921 | 0.11753 | 0.056443 | 3.8621e-07 | -0.00047843 | 0.0037859 | 0.0037799 | 0.0037859 | 0.99571 | -0.018053 | 0.99571 | -0.018081 | 1.7209
114 | 0.2725 | 0.13194 | -0.27249 | -0.13197 | 3.7689e-06 | -2.9593e-05 | 0.0088145 | 0.0088149 | 0.0088149 | 0.99154 | -0.053883 | 0.99153 | -0.053974 | 4.1976

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 14.3487 | 6.4734

## res_load
| p_mw | q_mvar
0 | 0.051734 | 0.025056
1 | 0.32049 | 0.15522
2 | 0.30004 | 0.14531
3 | 0.076321 | 0.036964
4 | 0.37289 | 0.1806
5 | 0.2997 | 0.14515
6 | 0.20462 | 0.099101
7 | 0.35521 | 0.17204
8 | 0.3486 | 0.16883
9 | 0.21856 | 0.10585
10 | 0.40019 | 0.19382
11 | 0.21916 | 0.10614
12 | 0.34788 | 0.16849
13 | 0.27452 | 0.13296
14 | 0.15134 | 0.073298
15 | 0.27806 | 0.13467
16 | 0.32171 | 0.15581
17 | 0.27831 | 0.13479
18 | 0.32239 | 0.15614
19 | 0.98675 | 0.47791
20 | 0.41407 | 0.20054
21 | 0.34747 | 0.16829
22 | 0.36028 | 0.17449
23 | 0.37314 | 0.18072
24 | 0.17038 | 0.082518
25 | 0.28189 | 0.13653
26 | 0.10221 | 0.049504
27 | 0.25619 | 0.12408
28 | 0.085051 | 0.041192
29 | 0.11927 | 0.057767
30 | 0.080229 | 0.038856
31 | 0.069343 | 0.033584
32 | 0.69832 | 0.33821
33 | 0.13641 | 0.066065
34 | 0.11023 | 0.053387
35 | 0.10329 | 0.050027
36 | 0.11851 | 0.057397
37 | 0.094529 | 0.045782
38 | 0.21304 | 0.10318
39 | 0.11357 | 0.055003
40 | 0.24628 | 0.11928
41 | 0.073252 | 0.035478
42 | 0.17783 | 0.086126
43 | 0.23207 | 0.1124
44 | 0.18803 | 0.091067
45 | 0.26822 | 0.1299
46 | 0.22723 | 0.11005
47 | 0.35182 | 0.17039
48 | 0.27883 | 0.13504
49 | 0.13799 | 0.06683
50 | 0.18618 | 0.090169
51 | 0.20947 | 0.10145
52 | 0.28356 | 0.13733
53 | 0.073013 | 0.035362
54 | 0.090474 | 0.043819
55 | 0.3097 | 0.14999
56 | 0.1046 | 0.05066
57 | 0.11753 | 0.056921
58 | 0.27249 | 0.13197

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1