## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_402_1_node_14 | 20 | n |  | TRUE
1 | bus_MV_402_1_node_15 | 20 | n |  | TRUE
2 | bus_MV_402_1_node_91 | 20 | n |  | TRUE
3 | bus_MV_402_1_node_17 | 20 | n |  | TRUE
4 | bus_MV_402_1_node_18 | 20 | n |  | TRUE
5 | bus_MV_402_1_node_19 | 20 | n |  | TRUE
6 | bus_MV_402_1_node_316 | 20 | n |  | TRUE
7 | bus_MV_402_1_node_266 | 20 | n |  | TRUE
8 | bus_MV_402_1_node_47 | 20 | n |  | TRUE
9 | bus_MV_402_1_node_48 | 20 | n |  | TRUE
10 | bus_MV_402_1_node_54 | 20 | n |  | TRUE
11 | bus_MV_402_1_node_49 | 20 | n |  | TRUE
12 | bus_MV_402_1_node_82 | 20 | n |  | TRUE
13 | bus_MV_402_1_node_52 | 20 | n |  | TRUE
14 | bus_MV_402_1_node_102 | 20 | n |  | TRUE
15 | bus_MV_402_1_node_100 | 20 | n |  | TRUE
16 | bus_MV_402_1_node_93 | 20 | n |  | TRUE
17 | bus_MV_402_1_node_101 | 20 | n |  | TRUE
18 | bus_MV_402_1_node_94 | 20 | n |  | TRUE
19 | bus_MV_402_1_node_92 | 20 | n |  | TRUE
20 | bus_MV_402_1_node_308 | 20 | n |  | TRUE
21 | bus_MV_402_1_node_50 | 20 | n |  | TRUE
22 | bus_MV_402_1_node_288 | 20 | n |  | TRUE
23 | bus_MV_402_1_node_289 | 20 | n |  | TRUE
24 | bus_MV_402_1_node_87 | 20 | n |  | TRUE
25 | bus_MV_402_1_node_88 | 20 | n |  | TRUE
26 | bus_MV_402_1_node_89 | 20 | n |  | TRUE
27 | bus_MV_402_1_node_313 | 20 | n |  | TRUE
28 | bus_MV_402_1_node_53 | 20 | n |  | TRUE
29 | bus_MV_402_1_node_83 | 20 | n |  | TRUE
30 | bus_MV_402_1_node_55 | 20 | n |  | TRUE
31 | bus_MV_402_1_node_56 | 20 | n |  | TRUE
32 | bus_MV_402_1_node_57 | 20 | n |  | TRUE
33 | bus_MV_402_1_node_58 | 20 | n |  | TRUE
34 | bus_MV_402_1_node_62 | 20 | n |  | TRUE
35 | bus_MV_402_1_node_64 | 20 | n |  | TRUE
36 | bus_MV_402_1_node_60 | 20 | n |  | TRUE
37 | bus_MV_402_1_node_61 | 20 | n |  | TRUE
38 | bus_MV_402_1_node_99 | 20 | n |  | TRUE
39 | bus_MV_402_1_node_103 | 20 | n |  | TRUE
40 | bus_MV_402_1_node_59 | 20 | n |  | TRUE
41 | bus_MV_402_1_node_66 | 20 | n |  | TRUE
42 | bus_MV_402_1_node_65 | 20 | n |  | TRUE
43 | bus_MV_402_1_node_270 | 20 | n |  | TRUE
44 | bus_MV_402_1_node_310 | 20 | n |  | TRUE
45 | bus_MV_402_1_node_63 | 20 | n |  | TRUE
46 | bus_MV_402_1_node_86 | 20 | n |  | TRUE
47 | bus_MV_402_1_node_224 | 20 | n |  | TRUE
48 | bus_MV_402_1_node_222 | 20 | n |  | TRUE
49 | bus_MV_402_1_node_72 | 20 | n |  | TRUE
50 | bus_MV_402_1_node_85 | 20 | n |  | TRUE
51 | bus_MV_402_1_node_98 | 20 | n |  | TRUE
52 | bus_MV_402_1_node_263 | 20 | n |  | TRUE
53 | bus_MV_402_1_node_273 | 20 | n |  | TRUE
54 | bus_MV_402_1_node_268 | 20 | n |  | TRUE
55 | bus_MV_402_1_node_274 | 20 | n |  | TRUE
56 | bus_MV_402_1_node_275 | 20 | n |  | TRUE
57 | bus_MV_402_1_node_267 | 20 | n |  | TRUE
58 | bus_MV_402_1_node_269 | 20 | n |  | TRUE
59 | bus_MV_402_1_node_225 | 20 | n |  | TRUE
60 | bus_MV_402_1_node_223 | 20 | n |  | TRUE
61 | bus_MV_402_1_node_282 | 20 | n |  | TRUE
62 | bus_MV_402_1_node_71 | 20 | n |  | TRUE
63 | bus_MV_402_1_node_262 | 20 | n |  | TRUE
64 | bus_MV_402_1_node_67 | 20 | n |  | TRUE
65 | bus_MV_402_1_node_68 | 20 | n |  | TRUE
66 | bus_MV_402_1_node_69 | 20 | n |  | TRUE
67 | bus_MV_402_1_node_70 | 20 | n |  | TRUE
68 | bus_MV_402_1_node_73 | 20 | n |  | TRUE
69 | bus_MV_402_1_node_284 | 20 | n |  | TRUE
70 | bus_MV_402_1_node_281 | 20 | n |  | TRUE
71 | bus_MV_402_1_node_285 | 20 | n |  | TRUE
72 | bus_MV_402_1_node_74 | 20 | n |  | TRUE
73 | bus_MV_402_1_node_75 | 20 | n |  | TRUE
74 | bus_MV_402_1_node_76 | 20 | n |  | TRUE
75 | bus_MV_402_1_node_79 | 20 | n |  | TRUE
76 | bus_MV_402_1_node_283 | 20 | n |  | TRUE
77 | bus_MV_402_1_node_279 | 20 | n |  | TRUE
78 | bus_MV_402_1_node_280 | 20 | n |  | TRUE
79 | bus_MV_402_1_node_78 | 20 | n |  | TRUE
80 | bus_MV_402_1_node_311 | 20 | n |  | TRUE
81 | bus_MV_402_1_node_290 | 20 | n |  | TRUE
82 | bus_MV_402_1_node_81 | 20 | n |  | TRUE
83 | bus_MV_402_1_node_287 | 20 | n |  | TRUE
84 | bus_MV_402_1_node_307 | 20 | n |  | TRUE
85 | bus_MV_402_1_node_325 | 20 | n |  | TRUE
86 | bus_MV_402_1_node_84 | 20 | n |  | TRUE
87 | bus_MV_402_1_node_314 | 20 | n |  | TRUE
88 | bus_MV_402_1_node_97 | 20 | n |  | TRUE
89 | bus_MV_402_1_node_96 | 20 | n |  | TRUE
90 | bus_MV_402_1_node_90 | 20 | n |  | TRUE
91 | bus_MV_402_1_node_276 | 20 | n |  | TRUE
92 | bus_MV_402_1_node_95 | 20 | n |  | TRUE
93 | bus_MV_402_1_node_315 | 20 | n |  | TRUE
94 | bus_MV_402_1_node_208 | 20 | n |  | TRUE
95 | bus_MV_402_1_node_209 | 20 | n |  | TRUE
96 | bus_MV_402_1_node_210 | 20 | n |  | TRUE
97 | bus_MV_402_1_node_211 | 20 | n |  | TRUE
98 | bus_MV_402_1_node_221 | 20 | n |  | TRUE
99 | bus_MV_402_1_node_213 | 20 | n |  | TRUE
100 | bus_MV_402_1_node_217 | 20 | n |  | TRUE
101 | bus_MV_402_1_node_215 | 20 | n |  | TRUE
102 | bus_MV_402_1_node_216 | 20 | n |  | TRUE
103 | bus_MV_402_1_node_232 | 20 | n |  | TRUE
104 | bus_MV_402_1_node_214 | 20 | n |  | TRUE
105 | bus_MV_402_1_node_302 | 20 | n |  | TRUE
106 | bus_MV_402_1_node_230 | 20 | n |  | TRUE
107 | bus_MV_402_1_node_231 | 20 | n |  | TRUE
108 | bus_MV_402_1_node_212 | 20 | n |  | TRUE
109 | bus_MV_402_1_node_218 | 20 | n |  | TRUE
110 | bus_MV_402_1_node_219 | 20 | n |  | TRUE
111 | bus_MV_402_1_node_220 | 20 | n |  | TRUE
112 | bus_MV_402_1_node_295 | 20 | n |  | TRUE
113 | bus_MV_402_1_node_256 | 20 | n |  | TRUE
114 | bus_MV_402_1_node_229 | 20 | n |  | TRUE
115 | bus_MV_402_1_node_241 | 20 | n |  | TRUE
116 | bus_MV_402_1_node_242 | 20 | n |  | TRUE
117 | bus_MV_402_1_node_243 | 20 | n |  | TRUE
118 | bus_MV_402_1_node_245 | 20 | n |  | TRUE
119 | bus_MV_402_1_node_246 | 20 | n |  | TRUE
120 | bus_MV_402_1_node_244 | 20 | n |  | TRUE
121 | bus_MV_402_1_node_322 | 20 | n |  | TRUE
122 | bus_MV_402_1_node_319 | 20 | n |  | TRUE
123 | bus_MV_402_1_node_226 | 20 | n |  | TRUE
124 | bus_MV_402_1_node_227 | 20 | n |  | TRUE
125 | bus_MV_402_1_node_228 | 20 | n |  | TRUE
126 | bus_MV_402_1_node_233 | 20 | n |  | TRUE
127 | bus_MV_402_1_node_240 | 20 | n |  | TRUE
128 | bus_MV_402_1_node_234 | 20 | n |  | TRUE
129 | bus_MV_402_1_node_251 | 20 | n |  | TRUE
130 | bus_MV_402_1_node_320 | 20 | n |  | TRUE
131 | bus_MV_402_1_node_252 | 20 | n |  | TRUE
132 | bus_MV_402_1_node_237 | 20 | n |  | TRUE
133 | bus_MV_402_1_node_236 | 20 | n |  | TRUE
134 | bus_MV_402_1_node_249 | 20 | n |  | TRUE
135 | bus_MV_402_1_node_250 | 20 | n |  | TRUE
136 | bus_MV_402_1_node_248 | 20 | n |  | TRUE
137 | bus_MV_402_1_node_247 | 20 | n |  | TRUE
138 | bus_MV_402_1_node_260 | 20 | n |  | TRUE
139 | bus_MV_402_1_node_261 | 20 | n |  | TRUE
140 | bus_MV_402_1_node_317 | 20 | n |  | TRUE
141 | bus_MV_402_1_node_259 | 20 | n |  | TRUE
142 | bus_MV_402_1_node_253 | 20 | n |  | TRUE
143 | bus_MV_402_1_node_254 | 20 | n |  | TRUE
144 | bus_MV_402_1_node_255 | 20 | n |  | TRUE
145 | bus_MV_402_1_node_257 | 20 | n |  | TRUE
146 | bus_MV_402_1_node_299 | 20 | n |  | TRUE
147 | bus_MV_402_1_node_323 | 20 | n |  | TRUE
148 | bus_MV_402_1_node_258 | 20 | n |  | TRUE
149 | bus_MV_402_1_node_297 | 20 | n |  | TRUE
150 | bus_MV_402_1_node_321 | 20 | n |  | TRUE
151 | bus_MV_402_1_node_265 | 20 | n |  | TRUE
152 | bus_MV_402_1_node_264 | 20 | n |  | TRUE
153 | bus_MV_402_1_node_312 | 20 | n |  | TRUE
154 | bus_MV_402_1_node_286 | 20 | n |  | TRUE
155 | bus_MV_402_1_node_296 | 20 | n |  | TRUE
156 | bus_MV_402_1_node_298 | 20 | n |  | TRUE
157 | bus_MV_402_1_node_324 | 20 | n |  | TRUE
158 | bus_MV_402_1_node_330 | 20 | n |  | TRUE
159 | bus_MV_402_1_node_331 | 20 | n |  | TRUE
160 | bus_MV_402_1_node_332 | 20 | n |  | TRUE
161 | bus_HV_402_1_node_222 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_402_1_load_14 | 0 | 0.084559 | 0.040954 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_402_1_load_19 | 5 | 0.15623 | 0.075665 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_402_1_load_316 | 6 | 0.072992 | 0.035352 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_402_1_load_47 | 8 | 0.13828 | 0.066972 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_402_1_load_82 | 12 | 0.14767 | 0.071518 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_402_1_load_102 | 14 | 0.07831 | 0.037927 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_402_1_load_100 | 15 | 0.16475 | 0.079794 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_402_1_load_308 | 20 | 0.09343 | 0.04525 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_402_1_load_50 | 21 | 0.12626 | 0.061149 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_402_1_load_288 | 22 | 0.074927 | 0.036289 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_402_1_load_87 | 24 | 0.1494 | 0.07236 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_402_1_load_313 | 27 | 0.15069 | 0.072982 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_402_1_load_55 | 30 | 0.16301 | 0.078951 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_402_1_load_61 | 37 | 0.074888 | 0.03627 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_402_1_load_103 | 39 | 0.1169 | 0.056616 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_402_1_load_65 | 42 | 0.11709 | 0.056709 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_402_1_load_310 | 44 | 0.11948 | 0.057867 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_402_1_load_86 | 46 | 0.10023 | 0.048542 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_402_1_load_222 | 48 | 0.1529 | 0.074053 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_402_1_load_85 | 50 | 0.15105 | 0.073158 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_402_1_load_98 | 51 | 0.1415 | 0.068534 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_402_1_load_273 | 53 | 0.1437 | 0.069599 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_402_1_load_267 | 57 | 0.10732 | 0.051978 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_402_1_load_225 | 59 | 0.13692 | 0.066313 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_402_1_load_282 | 61 | 0.12372 | 0.05992 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_402_1_load_262 | 63 | 0.16379 | 0.079328 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_402_1_load_67 | 64 | 0.14277 | 0.069148 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_402_1_load_69 | 66 | 0.24534 | 0.11883 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_402_1_load_73 | 68 | 0.095336 | 0.046173 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_402_1_load_284 | 69 | 0.24028 | 0.11637 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_402_1_load_285 | 71 | 0.092803 | 0.044947 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_402_1_load_74 | 72 | 0.13692 | 0.066315 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_402_1_load_279 | 77 | 0.72381 | 0.35056 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_402_1_load_311 | 80 | 0.14724 | 0.071311 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_402_1_load_290 | 81 | 0.27491 | 0.13315 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_402_1_load_287 | 83 | 0.11022 | 0.053382 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_402_1_load_307 | 84 | 0.13252 | 0.064182 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_402_1_load_325 | 85 | 0.21972 | 0.10642 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_402_1_load_314 | 87 | 0.16216 | 0.078538 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_402_1_load_96 | 89 | 0.073671 | 0.03568 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_402_1_load_90 | 90 | 0.1502 | 0.072747 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_402_1_load_276 | 91 | 0.11447 | 0.055441 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_402_1_load_95 | 92 | 0.14087 | 0.068227 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_402_1_load_315 | 93 | 0.12048 | 0.058352 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_402_1_load_208 | 94 | 0.056918 | 0.027567 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_402_1_load_221 | 98 | 0.072078 | 0.034909 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_402_1_load_217 | 100 | 0.15938 | 0.07719 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_402_1_load_232 | 103 | 0.11155 | 0.054027 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_402_1_load_302 | 105 | 0.14496 | 0.07021 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_402_1_load_231 | 107 | 0.055638 | 0.026947 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_402_1_load_212 | 108 | 0.12006 | 0.058149 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_402_1_load_220 | 111 | 0.11783 | 0.057066 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_402_1_load_295 | 112 | 0.097886 | 0.047408 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_402_1_load_229 | 114 | 0.075073 | 0.036359 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_402_1_load_241 | 115 | 0.1094 | 0.052986 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_402_1_load_322 | 121 | 0.12626 | 0.06115 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_402_1_load_319 | 122 | 0.06666 | 0.032285 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_402_1_load_227 | 124 | 0.085566 | 0.041442 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_402_1_load_228 | 125 | 0.10858 | 0.052588 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_402_1_load_233 | 126 | 0.15837 | 0.0767 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_402_1_load_240 | 127 | 0.15539 | 0.07526 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_402_1_load_251 | 129 | 0.11641 | 0.056378 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_402_1_load_320 | 130 | 0.14773 | 0.071547 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_402_1_load_237 | 132 | 0.1212 | 0.0587 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_402_1_load_250 | 135 | 0.12142 | 0.058805 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_402_1_load_248 | 136 | 0.051876 | 0.025125 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_402_1_load_317 | 140 | 0.15849 | 0.07676 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_402_1_load_259 | 141 | 0.10991 | 0.05323 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_402_1_load_254 | 143 | 0.12636 | 0.061199 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_402_1_load_323 | 147 | 0.10926 | 0.052919 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_402_1_load_321 | 150 | 0.077509 | 0.037539 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_402_1_load_264 | 152 | 0.099779 | 0.048325 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_402_1_load_312 | 153 | 0.084317 | 0.040837 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_402_1_load_286 | 154 | 0.78225 | 0.37886 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_402_1_load_296 | 155 | 0.073976 | 0.035828 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_402_1_load_324 | 157 | 0.11932 | 0.057789 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_402_1_load_332 | 160 | 0.18513 | 0.08966 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_402_1_line_0 |  | 0 | 1 | 0.019249 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
1 | MV_402_1_line_1 |  | 0 | 2 | 1.4635 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
2 | MV_402_1_line_2 |  | 1 | 3 | 0.55554 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
3 | MV_402_1_line_3 |  | 2 | 19 | 0.43842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_402_1_line_4 |  | 2 | 90 | 0.005854 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
5 | MV_402_1_line_5 |  | 3 | 4 | 0.87563 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
6 | MV_402_1_line_6 |  | 3 | 5 | 0.066542 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_402_1_line_7 |  | 4 | 6 | 0.15899 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
8 | MV_402_1_line_8 |  | 6 | 7 | 2.5814 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
9 | MV_402_1_line_9 |  | 7 | 152 | 0.070092 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
10 | MV_402_1_line_10 |  | 8 | 9 | 0.044733 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_402_1_line_11 |  | 8 | 10 | 0.10666 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_402_1_line_12 |  | 9 | 11 | 0.06689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_402_1_line_13 |  | 10 | 12 | 0.020921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_402_1_line_14 |  | 10 | 13 | 0.17326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_402_1_line_15 |  | 11 | 14 | 0.039588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_402_1_line_16 |  | 11 | 15 | 0.019191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_402_1_line_17 |  | 12 | 29 | 0.004148 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_402_1_line_18 |  | 13 | 28 | 0.20726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_402_1_line_19 |  | 15 | 16 | 0.074114 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_402_1_line_20 |  | 16 | 17 | 0.017705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_402_1_line_21 |  | 16 | 18 | 0.56281 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_402_1_line_22 |  | 16 | 19 | 1.0048 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_402_1_line_23 |  | 17 | 20 | 0.071764 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_402_1_line_24 |  | 18 | 93 | 0.031248 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_402_1_line_25 |  | 19 | 92 | 0.10383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_402_1_line_26 |  | 21 | 22 | 0.21962 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_402_1_line_27 |  | 21 | 23 | 0.082516 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_402_1_line_28 |  | 22 | 26 | 0.033797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_402_1_line_29 |  | 23 | 27 | 0.06762 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_402_1_line_30 |  | 24 | 25 | 0.049387 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_402_1_line_31 |  | 25 | 26 | 0.13892 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_402_1_line_32 |  | 27 | 28 | 0.04062 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_402_1_line_33 |  | 29 | 86 | 0.46317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_402_1_line_34 |  | 30 | 31 | 0.004129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_402_1_line_35 |  | 31 | 32 | 0.14755 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_402_1_line_36 |  | 31 | 33 | 0.27601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_402_1_line_37 |  | 32 | 34 | 0.12505 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
38 | MV_402_1_line_38 |  | 32 | 35 | 0.20936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_402_1_line_39 |  | 32 | 36 | 0.32404 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
40 | MV_402_1_line_40 |  | 32 | 37 | 0.005804 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_402_1_line_41 |  | 33 | 38 | 0.034147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_402_1_line_42 |  | 33 | 39 | 0.003827 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_402_1_line_43 |  | 34 | 45 | 0.49886 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
44 | MV_402_1_line_44 |  | 34 | 46 | 0.033701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_402_1_line_45 |  | 35 | 49 | 0.12888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_402_1_line_46 |  | 35 | 50 | 0.00454 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_402_1_line_47 |  | 36 | 44 | 0.075258 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
48 | MV_402_1_line_48 |  | 38 | 51 | 0.021608 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_402_1_line_49 |  | 40 | 41 | 0.78129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_402_1_line_50 |  | 40 | 42 | 0.057978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_402_1_line_51 |  | 40 | 43 | 0.39231 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_402_1_line_52 |  | 41 | 52 | 0.004208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_402_1_line_53 |  | 43 | 53 | 0.040955 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
54 | MV_402_1_line_54 |  | 43 | 54 | 0.2677 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
55 | MV_402_1_line_55 |  | 44 | 58 | 0.081532 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
56 | MV_402_1_line_56 |  | 45 | 47 | 0.05806 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_402_1_line_57 |  | 45 | 48 | 0.075514 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
58 | MV_402_1_line_58 |  | 47 | 59 | 0.040058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_402_1_line_59 |  | 48 | 60 | 0.056207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_402_1_line_60 |  | 49 | 61 | 0.05583 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_402_1_line_61 |  | 49 | 62 | 0.046988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_402_1_line_62 |  | 52 | 63 | 0.003562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_402_1_line_63 |  | 53 | 55 | 0.019249 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
64 | MV_402_1_line_64 |  | 54 | 58 | 0.1936 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
65 | MV_402_1_line_65 |  | 54 | 57 | 0.064289 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_402_1_line_66 |  | 55 | 56 | 0.32162 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
67 | MV_402_1_line_67 |  | 56 | 91 | 0.025728 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_402_1_line_68 |  | 56 | 90 | 0.59248 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
69 | MV_402_1_line_69 |  | 60 | 123 | 0.1607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_402_1_line_70 |  | 61 | 70 | 0.023408 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_402_1_line_71 |  | 62 | 68 | 0.0085143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_402_1_line_72 |  | 62 | 67 | 0.047683 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_402_1_line_73 |  | 64 | 65 | 0.028983 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_402_1_line_74 |  | 65 | 66 | 0.0015871 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_402_1_line_75 |  | 66 | 67 | 0.03508 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_402_1_line_76 |  | 68 | 69 | 0.020051 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_402_1_line_77 |  | 69 | 71 | 0.001568 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_402_1_line_78 |  | 70 | 76 | 0.027618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_402_1_line_79 |  | 70 | 78 | 0.014642 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_402_1_line_80 |  | 71 | 154 | 0.049552 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_402_1_line_81 |  | 72 | 73 | 0.007957 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_402_1_line_82 |  | 72 | 74 | 0.047365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_402_1_line_83 |  | 73 | 75 | 0.1969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_402_1_line_84 |  | 74 | 76 | 0.17579 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_402_1_line_85 |  | 75 | 81 | 0.017497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_402_1_line_86 |  | 75 | 79 | 0.16592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_402_1_line_87 |  | 76 | 84 | 0.026887 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_402_1_line_88 |  | 76 | 85 | 0.24729 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_402_1_line_89 |  | 76 | 82 | 0.11453 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_402_1_line_90 |  | 77 | 78 | 0.065425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_402_1_line_91 |  | 79 | 80 | 0.031895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_402_1_line_92 |  | 82 | 83 | 0.085471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_402_1_line_93 |  | 86 | 87 | 0.056502 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_402_1_line_94 |  | 86 | 88 | 0.413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_402_1_line_95 |  | 88 | 89 | 0.1856 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_402_1_line_96 |  | 94 | 95 | 0.088676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_402_1_line_97 |  | 95 | 96 | 0.064251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_402_1_line_98 |  | 96 | 97 | 0.16615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_402_1_line_99 |  | 96 | 98 | 0.14958 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_402_1_line_100 |  | 97 | 99 | 0.44948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_402_1_line_101 |  | 97 | 100 | 0.057737 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_402_1_line_102 |  | 99 | 108 | 0.1101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_402_1_line_103 |  | 99 | 104 | 0.44299 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_402_1_line_104 |  | 100 | 109 | 0.052657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_402_1_line_105 |  | 101 | 102 | 0.23985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_402_1_line_106 |  | 101 | 103 | 0.005214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_402_1_line_107 |  | 101 | 104 | 0.2117 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_402_1_line_108 |  | 102 | 107 | 0.09381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_402_1_line_109 |  | 104 | 105 | 0.009911 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_402_1_line_110 |  | 104 | 106 | 0.29157 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_402_1_line_111 |  | 106 | 114 | 0.006951 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_402_1_line_112 |  | 109 | 110 | 0.0681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_402_1_line_113 |  | 109 | 111 | 0.02808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_402_1_line_114 |  | 110 | 112 | 0.13801 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_402_1_line_115 |  | 112 | 113 | 2.0954 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_402_1_line_116 |  | 113 | 143 | 0.16828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_402_1_line_117 |  | 114 | 125 | 0.32087 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_402_1_line_118 |  | 115 | 116 | 0.085788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_402_1_line_119 |  | 115 | 117 | 0.18875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_402_1_line_120 |  | 116 | 118 | 0.27743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_402_1_line_121 |  | 116 | 119 | 0.32144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_402_1_line_122 |  | 117 | 120 | 0.77526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_402_1_line_123 |  | 118 | 122 | 0.05489 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_402_1_line_124 |  | 119 | 137 | 0.33267 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_402_1_line_125 |  | 119 | 130 | 0.007683 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_402_1_line_126 |  | 120 | 121 | 0.038743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_402_1_line_127 |  | 123 | 124 | 0.10315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_402_1_line_128 |  | 124 | 125 | 0.31343 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
129 | MV_402_1_line_129 |  | 126 | 127 | 0.1032 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
130 | MV_402_1_line_130 |  | 126 | 128 | 0.10266 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
131 | MV_402_1_line_131 |  | 126 | 129 | 3.1736 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
132 | MV_402_1_line_132 |  | 128 | 130 | 0.31016 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
133 | MV_402_1_line_133 |  | 129 | 131 | 0.086067 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
134 | MV_402_1_line_134 |  | 129 | 132 | 0.24973 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
135 | MV_402_1_line_135 |  | 131 | 142 | 0.21877 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
136 | MV_402_1_line_136 |  | 133 | 134 | 0.085631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_402_1_line_137 |  | 133 | 135 | 0.089812 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
138 | MV_402_1_line_138 |  | 134 | 136 | 0.043809 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_402_1_line_139 |  | 135 | 137 | 0.01994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_402_1_line_140 |  | 138 | 139 | 0.34047 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_402_1_line_141 |  | 138 | 140 | 2.5395 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
142 | MV_402_1_line_142 |  | 138 | 141 | 0.06634 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
143 | MV_402_1_line_143 |  | 139 | 153 | 0.004143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_402_1_line_144 |  | 140 | 142 | 0.09153 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
145 | MV_402_1_line_145 |  | 141 | 151 | 1.7788 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
146 | MV_402_1_line_146 |  | 143 | 144 | 0.11567 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
147 | MV_402_1_line_147 |  | 144 | 145 | 0.47604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_402_1_line_148 |  | 145 | 146 | 0.041487 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
149 | MV_402_1_line_149 |  | 146 | 147 | 0.00713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_402_1_line_150 |  | 146 | 148 | 0.24747 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
151 | MV_402_1_line_151 |  | 146 | 149 | 0.12006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_402_1_line_152 |  | 148 | 150 | 0.076554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_402_1_line_153 |  | 149 | 156 | 0.25839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_402_1_line_154 |  | 149 | 155 | 0.0060094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_402_1_line_155 |  | 151 | 152 | 0.052907 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
156 | MV_402_1_line_156 |  | 156 | 157 | 0.044918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_402_1_line_157 |  | 157 | 158 | 0.045665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_402_1_line_158 |  | 158 | 159 | 0.03817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_402_1_line_159 |  | 159 | 160 | 0.013484 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_402_1_trafo_222 | 25 MVA 110/20 kV | 161 | 48 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2704909.2032 | 1281531.1635
1 | 2704897.0322 | 1281546.1049
2 | 2705835.623 | 1280398.2292
3 | 2704467.3374 | 1281620.2095
4 | 2704122.0107 | 1282156.4292
5 | 2704529.2035 | 1281595.7061
6 | 2703983.8534 | 1282235.5734
7 | 2703593.9115 | 1279683.7861
8 | 2706743.4576 | 1279852.8432
9 | 2706701.0648 | 1279867.1223
10 | 2706843.9991 | 1279817.2315
11 | 2706663.2647 | 1279811.9888
12 | 2706863.0244 | 1279825.8396
13 | 2706827.0601 | 1279711.3625
14 | 2706688.7433 | 1279781.6333
15 | 2706649.2325 | 1279825.1247
16 | 2706591.4384 | 1279778.7269
17 | 2706602.3154 | 1279764.7331
18 | 2706732.2556 | 1280020.8143
19 | 2706121.5807 | 1280260.0434
20 | 2706652.073 | 1279713.0194
21 | 2707074.6352 | 1279811.3867
22 | 2707269.5623 | 1279710.2127
23 | 2707088.78 | 1279730.0923
24 | 2707397.5073 | 1279746.087
25 | 2707384.9311 | 1279793.8457
26 | 2707299.791 | 1279698.0651
27 | 2707021.2683 | 1279732.7915
28 | 2706980.6972 | 1279734.7906
29 | 2706866.5456 | 1279828.0498
30 | 2706619.8937 | 1279453.8596
31 | 2706623.4703 | 1279451.7779
32 | 2706636.4027 | 1279331.2921
33 | 2706737.9909 | 1279686.3496
34 | 2706704.4373 | 1279263.8506
35 | 2706553.3641 | 1279175.1843
36 | 2706403.945 | 1279478.2374
37 | 2706636.3202 | 1279337.0958
38 | 2706767.8899 | 1279685.768
39 | 2706736.4399 | 1279689.8469
40 | 2706018.6217 | 1279288.1724
41 | 2705483.678 | 1278988.8132
42 | 2706070.3297 | 1279262.023
43 | 2705884.8371 | 1279656.9673
44 | 2706336.4065 | 1279511.4382
45 | 2706915.7951 | 1278895.791
46 | 2706731.0357 | 1279284.6506
47 | 2706959.1284 | 1278933.1992
48 | 2706968.89 | 1278842.0942
49 | 2706437.3019 | 1279118.5935
50 | 2706556.1417 | 1279171.5868
51 | 2706772.1041 | 1279706.9634
52 | 2705483.9711 | 1278993.0111
53 | 2705896.476 | 1279696.2338
54 | 2706101.0991 | 1279645.132
55 | 2705901.7331 | 1279714.756
56 | 2705621.2345 | 1279844.843
57 | 2706136.779 | 1279698.6109
58 | 2706260.8019 | 1279542.4035
59 | 2706989.4988 | 1278959.4291
60 | 2707022.3635 | 1278824.2926
61 | 2706392.3164 | 1279085.6793
62 | 2706407.6837 | 1279155.0697
63 | 2705484.2306 | 1278996.5634
64 | 2706401.0075 | 1279224.6135
65 | 2706377.8662 | 1279218.4333
66 | 2706379.1992 | 1279217.5719
67 | 2706407.4491 | 1279196.7807
68 | 2706400.7157 | 1279159.9626
69 | 2706384.3064 | 1279171.485
70 | 2706375.3461 | 1279069.5651
71 | 2706383.0232 | 1279172.3861
72 | 2706216.1405 | 1278912.0881
73 | 2706212.6096 | 1278904.9515
74 | 2706256.571 | 1278915.2524
75 | 2706242.7972 | 1278826.458
76 | 2706368.9436 | 1279050.4325
77 | 2706300.463 | 1279095.9119
78 | 2706363.3112 | 1279077.7332
79 | 2706134.2572 | 1278818.9752
80 | 2706150.4743 | 1278846.4694
81 | 2706238.4513 | 1278809.5089
82 | 2706309.149 | 1278952.7557
83 | 2706359.075 | 1278904.3257
84 | 2706368.6324 | 1279023.5471
85 | 2706528.7116 | 1278861.6794
86 | 2706878.4036 | 1280151.8461
87 | 2706934.8301 | 1280153.6372
88 | 2706691.3046 | 1280278.3393
89 | 2706510.4493 | 1280320.0523
90 | 2705840.6432 | 1280395.1943
91 | 2705597.0753 | 1279853.8852
92 | 2706221.1816 | 1280233.4903
93 | 2706747.2021 | 1280047.5979
94 | 2708039.9558 | 1277937.1429
95 | 2708120.739 | 1277900.045
96 | 2708167.4017 | 1277894.462
97 | 2708144.9934 | 1278053.1941
98 | 2708266.348 | 1277798.6573
99 | 2707848.4104 | 1278200.0081
100 | 2708202.0622 | 1278044.4326
101 | 2707976.991 | 1278425.2296
102 | 2708046.4325 | 1278594.0199
103 | 2707979.0147 | 1278430.0377
104 | 2707796.0687 | 1278486.6651
105 | 2707786.6187 | 1278489.7396
106 | 2707771.4168 | 1278725.997
107 | 2708136.9694 | 1278605.6227
108 | 2707739.9746 | 1278211.7373
109 | 2708254.4751 | 1278039.979
110 | 2708243.9877 | 1278107.2694
111 | 2708257.8731 | 1278012.1051
112 | 2708373.3679 | 1278069.2946
113 | 2710461.5228 | 1277895.2141
114 | 2707764.5833 | 1278727.3734
115 | 2708019.7875 | 1274193.8641
116 | 2707936.4551 | 1274178.1259
117 | 2708204.907 | 1274165.8628
118 | 2707839.7577 | 1274417.026
119 | 2707725.1855 | 1274233.9052
120 | 2708960.8016 | 1274295.1477
121 | 2708998.4367 | 1274300.6807
122 | 2707856.8095 | 1274467.0041
123 | 2707122.6607 | 1278836.6687
124 | 2707200.9692 | 1278903.2067
125 | 2707444.4369 | 1278705.8141
126 | 2707332.599 | 1274378.8381
127 | 2707294.0926 | 1274283.0868
128 | 2707421.6002 | 1274327.6784
129 | 2704549.9724 | 1275904.8647
130 | 2707718.3377 | 1274237.4278
131 | 2704583.6272 | 1275983.9307
132 | 2704414.0587 | 1275695.3551
133 | 2707657.0241 | 1273926.3118
134 | 2707686.655 | 1273846.4594
135 | 2707713.28 | 1273996.3221
136 | 2707660.6924 | 1273814.7467
137 | 2707714.2926 | 1274016.236
138 | 2705195.492 | 1278675.1196
139 | 2705314.2889 | 1278977.1873
140 | 2704573.8903 | 1276212.8936
141 | 2705189.7285 | 1278741.2093
142 | 2704617.6641 | 1276132.5096
143 | 2710623.1695 | 1277943.153
144 | 2710600.1034 | 1278056.5013
145 | 2711005.9876 | 1278300.0015
146 | 2711044.4596 | 1278315.5286
147 | 2711043.1851 | 1278322.5443
148 | 2711054.4469 | 1278068.2582
149 | 2711089.0956 | 1278378.0147
150 | 2711068.0644 | 1277992.9238
151 | 2703611.6564 | 1279562.0893
152 | 2703602.9849 | 1279614.2835
153 | 2705314.9406 | 1278973.0953
154 | 2706347.1888 | 1279206.199
155 | 2711090.0702 | 1278383.9445
156 | 2711254.7806 | 1278262.0314
157 | 2711231.1834 | 1278297.7968
158 | 2711231.0821 | 1278340.6005
159 | 2711197.5066 | 1278336.0523
160 | 2711186.5064 | 1278343.8966
161 | 2706968.89 | 1278842.0942

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99273 | -0.2675 | 0.084559 | 0.040954
1 | 0.99272 | -0.2676 | 0 | 0
2 | 0.99448 | -0.15418 | 0 | 0
3 | 0.99239 | -0.27021 | 0 | 0
4 | 0.99191 | -0.27358 | 0 | 0
5 | 0.99237 | -0.27033 | 0.15623 | 0.075665
6 | 0.99183 | -0.27411 | 0.072992 | 0.035352
7 | 0.98909 | -0.43951 | 0 | 0
8 | 0.99132 | -0.13557 | 0.13828 | 0.066972
9 | 0.9914 | -0.13486 | 0 | 0
10 | 0.99113 | -0.13708 | 0 | 0
11 | 0.99149 | -0.13552 | 0 | 0
12 | 0.99112 | -0.13701 | 0.14767 | 0.071518
13 | 0.99102 | -0.13617 | 0 | 0
14 | 0.99149 | -0.13549 | 0.07831 | 0.037927
15 | 0.99152 | -0.13573 | 0.16475 | 0.079794
16 | 0.9917 | -0.13432 | 0 | 0
17 | 0.9917 | -0.1343 | 0 | 0
18 | 0.99161 | -0.13376 | 0 | 0
19 | 0.99358 | -0.14802 | 0 | 0
20 | 0.99168 | -0.13438 | 0.09343 | 0.04525
21 | 0.99077 | -0.13541 | 0.12626 | 0.061149
22 | 0.99067 | -0.1361 | 0.074927 | 0.036289
23 | 0.99082 | -0.13502 | 0 | 0
24 | 0.99062 | -0.1359 | 0.1494 | 0.07236
25 | 0.99064 | -0.1358 | 0 | 0
26 | 0.99066 | -0.13604 | 0 | 0
27 | 0.99085 | -0.13529 | 0.15069 | 0.072982
28 | 0.99089 | -0.13501 | 0 | 0
29 | 0.99112 | -0.13701 | 0 | 0
30 | 0.99774 | -0.035423 | 0.16301 | 0.078951
31 | 0.99774 | -0.035431 | 0 | 0
32 | 0.99782 | -0.036085 | 0 | 0
33 | 0.99765 | -0.034656 | 0 | 0
34 | 0.99817 | -0.03406 | 0 | 0
35 | 0.99686 | -0.027368 | 0 | 0
36 | 0.99736 | -0.039493 | 0 | 0
37 | 0.99782 | -0.03608 | 0.074888 | 0.03627
38 | 0.99765 | -0.0346 | 0 | 0
39 | 0.99765 | -0.034651 | 0.1169 | 0.056616
40 | 0.99619 | -0.060165 | 0 | 0
41 | 0.99603 | -0.059096 | 0 | 0
42 | 0.99619 | -0.060086 | 0.11709 | 0.056709
43 | 0.9964 | -0.058141 | 0 | 0
44 | 0.99715 | -0.052742 | 0.11948 | 0.057867
45 | 0.99957 | -0.025787 | 0 | 0
46 | 0.99816 | -0.03402 | 0.10023 | 0.048542
47 | 0.99956 | -0.025698 | 0 | 0
48 | 1 | 0 | -10.8021 | -4.6862
49 | 0.99629 | -0.022193 | 0 | 0
50 | 0.99686 | -0.027359 | 0.15105 | 0.073158
51 | 0.99764 | -0.034564 | 0.1415 | 0.068534
52 | 0.99603 | -0.059087 | 0 | 0
53 | 0.9963 | -0.064533 | 0.1437 | 0.069599
54 | 0.99677 | -0.055529 | 0 | 0
55 | 0.99628 | -0.064704 | 0 | 0
56 | 0.99588 | -0.067495 | 0 | 0
57 | 0.99675 | -0.055613 | 0.10732 | 0.051978
58 | 0.99703 | -0.053575 | 0 | 0
59 | 0.99955 | -0.025634 | 0.13692 | 0.066313
60 | 0.99987 | 0.00091639 | 0 | 0
61 | 0.99615 | -0.020998 | 0.12372 | 0.05992
62 | 0.99619 | -0.021303 | 0 | 0
63 | 0.99603 | -0.05908 | 0.16379 | 0.079328
64 | 0.99614 | -0.020873 | 0.14277 | 0.069148
65 | 0.99615 | -0.020923 | 0 | 0
66 | 0.99615 | -0.020925 | 0.24534 | 0.11883
67 | 0.99617 | -0.021087 | 0 | 0
68 | 0.99618 | -0.02118 | 0.095336 | 0.046173
69 | 0.99615 | -0.020912 | 0.24028 | 0.11637
70 | 0.9961 | -0.020531 | 0 | 0
71 | 0.99615 | -0.020896 | 0.092803 | 0.044947
72 | 0.99584 | -0.021294 | 0.13692 | 0.066315
73 | 0.99584 | -0.021258 | 0 | 0
74 | 0.99588 | -0.021581 | 0 | 0
75 | 0.99573 | -0.020349 | 0 | 0
76 | 0.99607 | -0.020215 | 0 | 0
77 | 0.99603 | -0.019837 | 0.72381 | 0.35056
78 | 0.99609 | -0.020404 | 0 | 0
79 | 0.9957 | -0.020084 | 0 | 0
80 | 0.9957 | -0.020028 | 0.14724 | 0.071311
81 | 0.99573 | -0.020292 | 0.27491 | 0.13315
82 | 0.99604 | -0.02039 | 0 | 0
83 | 0.99603 | -0.020281 | 0.11022 | 0.053382
84 | 0.99606 | -0.020259 | 0.13252 | 0.064182
85 | 0.99596 | -0.02088 | 0.21972 | 0.10642
86 | 0.99099 | -0.13618 | 0 | 0
87 | 0.99097 | -0.13607 | 0.16216 | 0.078538
88 | 0.99095 | -0.13594 | 0 | 0
89 | 0.99092 | -0.13611 | 0.073671 | 0.03568
90 | 0.99449 | -0.15413 | 0.1502 | 0.072747
91 | 0.99588 | -0.06746 | 0.11447 | 0.055441
92 | 0.99357 | -0.14785 | 0.14087 | 0.068227
93 | 0.99161 | -0.13371 | 0.12048 | 0.058352
94 | 0.99505 | 0.00093502 | 0.056918 | 0.027567
95 | 0.99506 | 0.00088001 | 0 | 0
96 | 0.99506 | 0.00084764 | 0 | 0
97 | 0.99509 | 0.00068617 | 0 | 0
98 | 0.99505 | 0.00096088 | 0.072078 | 0.034909
99 | 0.99577 | -0.0042134 | 0 | 0
100 | 0.99497 | -0.00026094 | 0.15938 | 0.07719
101 | 0.99646 | -0.0090187 | 0 | 0
102 | 0.99645 | -0.0089359 | 0 | 0
103 | 0.99646 | -0.0090117 | 0.11155 | 0.054027
104 | 0.99651 | -0.0093018 | 0 | 0
105 | 0.99651 | -0.0092846 | 0.14496 | 0.07021
106 | 0.99711 | -0.013331 | 0 | 0
107 | 0.99644 | -0.0088797 | 0.055638 | 0.026947
108 | 0.99575 | -0.0040632 | 0.12006 | 0.058149
109 | 0.99491 | 0.00018789 | 0 | 0
110 | 0.99484 | 0.0006806 | 0 | 0
111 | 0.99491 | 0.00022728 | 0.11783 | 0.057066
112 | 0.99471 | 0.001701 | 0.097886 | 0.047408
113 | 0.99194 | -0.021696 | 0 | 0
114 | 0.99712 | -0.013425 | 0.075073 | 0.036359
115 | 0.98223 | -0.81339 | 0.1094 | 0.052986
116 | 0.98225 | -0.81351 | 0 | 0
117 | 0.9822 | -0.81336 | 0 | 0
118 | 0.98223 | -0.81336 | 0 | 0
119 | 0.98238 | -0.81394 | 0 | 0
120 | 0.98207 | -0.81265 | 0 | 0
121 | 0.98207 | -0.81259 | 0.12626 | 0.06115
122 | 0.98222 | -0.81332 | 0.06666 | 0.032285
123 | 0.99948 | 0.0035642 | 0 | 0
124 | 0.99923 | 0.0052857 | 0.085566 | 0.041442
125 | 0.99816 | -0.0041641 | 0.10858 | 0.052588
126 | 0.98287 | -0.80885 | 0.15837 | 0.0767
127 | 0.98283 | -0.80906 | 0.15539 | 0.07526
128 | 0.98275 | -0.81012 | 0 | 0
129 | 0.9848 | -0.69031 | 0.11641 | 0.056378
130 | 0.98238 | -0.81396 | 0.14773 | 0.071547
131 | 0.98483 | -0.69011 | 0 | 0
132 | 0.98474 | -0.69069 | 0.1212 | 0.0587
133 | 0.98229 | -0.81343 | 0 | 0
134 | 0.98228 | -0.81339 | 0 | 0
135 | 0.9823 | -0.81335 | 0.12142 | 0.058805
136 | 0.98228 | -0.81336 | 0.051876 | 0.025125
137 | 0.9823 | -0.81339 | 0 | 0
138 | 0.98719 | -0.55097 | 0 | 0
139 | 0.98716 | -0.5507 | 0 | 0
140 | 0.98499 | -0.6853 | 0.15849 | 0.07676
141 | 0.98725 | -0.54724 | 0.10991 | 0.05323
142 | 0.98492 | -0.68958 | 0 | 0
143 | 0.99179 | -0.020585 | 0.12636 | 0.061199
144 | 0.99167 | -0.021648 | 0 | 0
145 | 0.99132 | -0.018998 | 0 | 0
146 | 0.99128 | -0.019339 | 0 | 0
147 | 0.99128 | -0.01933 | 0.10926 | 0.052919
148 | 0.99124 | -0.019617 | 0 | 0
149 | 0.99122 | -0.018871 | 0 | 0
150 | 0.99123 | -0.019549 | 0.077509 | 0.037539
151 | 0.98903 | -0.4399 | 0 | 0
152 | 0.98905 | -0.43974 | 0.099779 | 0.048325
153 | 0.98716 | -0.5507 | 0.084317 | 0.040837
154 | 0.9961 | -0.02043 | 0.78225 | 0.37886
155 | 0.99122 | -0.018866 | 0.073976 | 0.035828
156 | 0.99112 | -0.01802 | 0 | 0
157 | 0.9911 | -0.017862 | 0.11932 | 0.057789
158 | 0.99109 | -0.017764 | 0 | 0
159 | 0.99108 | -0.01768 | 0 | 0
160 | 0.99108 | -0.01765 | 0.18513 | 0.08966
161 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 1.8653 | 0.71845 | -1.8653 | -0.71963 | 2.01e-05 | -0.0011806 | 0.058125 | 0.058138 | 0.058138 | 0.99273 | -0.2675 | 0.99272 | -0.2676 | 9.1125
1 | -1.9499 | -0.7594 | 1.9518 | 0.76261 | 0.0019338 | 0.0032028 | 0.060848 | 0.060827 | 0.060848 | 0.99273 | -0.2675 | 0.99448 | -0.15418 | 9.4338
2 | 1.8653 | 0.71963 | -1.8647 | -0.75369 | 0.00058385 | -0.034059 | 0.058138 | 0.058505 | 0.058505 | 0.99272 | -0.2676 | 0.99239 | -0.27021 | 9.1701
3 | 1.6263 | 0.69502 | -1.6247 | -0.7049 | 0.0015461 | -0.0098847 | 0.051337 | 0.051456 | 0.051456 | 0.99448 | -0.15418 | 0.99358 | -0.14802 | 23.3891
4 | -3.5781 | -1.4576 | 3.5781 | 1.4573 | 2.2751e-05 | -0.00035096 | 0.11215 | 0.11215 | 0.11215 | 0.99448 | -0.15418 | 0.99449 | -0.15413 | 17.5785
5 | 1.7085 | 0.6781 | -1.7077 | -0.73182 | 0.00078212 | -0.053717 | 0.053469 | 0.05407 | 0.05407 | 0.99239 | -0.27021 | 0.99191 | -0.27358 | 8.4749
6 | 0.15623 | 0.075588 | -0.15623 | -0.075665 | 3.0224e-06 | -7.6339e-05 | 0.0050486 | 0.0050495 | 0.0050495 | 0.99239 | -0.27021 | 0.99237 | -0.27033 | 2.4045
7 | 1.7077 | 0.73182 | -1.7075 | -0.74157 | 0.00014393 | -0.0097469 | 0.05407 | 0.054183 | 0.054183 | 0.99191 | -0.27358 | 0.99183 | -0.27411 | 8.4927
8 | 1.6346 | 0.70621 | -1.6321 | -0.70305 | 0.0024771 | 0.0031605 | 0.051825 | 0.051865 | 0.051865 | 0.99183 | -0.27411 | 0.98909 | -0.43951 | 8.0411
9 | 1.6321 | 0.70305 | -1.632 | -0.70733 | 5.8317e-05 | -0.0042754 | 0.051865 | 0.051915 | 0.051915 | 0.98909 | -0.43951 | 0.98905 | -0.43974 | 8.1372
10 | -1.0235 | -0.45786 | 1.0235 | 0.45786 | 8.4961e-05 | 7.3335e-07 | 0.03265 | 0.032649 | 0.03265 | 0.99132 | -0.13557 | 0.9914 | -0.13486 | 15.5476
11 | 0.88518 | 0.39089 | -0.88503 | -0.39092 | 0.0001509 | -3.0589e-05 | 0.028178 | 0.02818 | 0.02818 | 0.99132 | -0.13557 | 0.99113 | -0.13708 | 13.4189
12 | -1.0235 | -0.45786 | 1.0236 | 0.45632 | 9.5135e-05 | -0.0015416 | 0.032649 | 0.032631 | 0.032649 | 0.9914 | -0.13486 | 0.99149 | -0.13552 | 14.8406
13 | 0.38354 | 0.16307 | -0.38354 | -0.16356 | 4.1173e-06 | -0.00048947 | 0.012139 | 0.012144 | 0.012144 | 0.99113 | -0.13708 | 0.99112 | -0.13701 | 5.5201
14 | 0.50149 | 0.22785 | -0.50143 | -0.23189 | 5.9716e-05 | -0.0040457 | 0.016043 | 0.016092 | 0.016092 | 0.99113 | -0.13708 | 0.99102 | -0.13617 | 7.3147
15 | 0.07831 | 0.036998 | -0.07831 | -0.037927 | 3.3762e-07 | -0.00092908 | 0.0025217 | 0.0025334 | 0.0025334 | 0.99149 | -0.13552 | 0.99149 | -0.13549 | 1.1515
16 | -1.1019 | -0.49332 | 1.102 | 0.49288 | 3.1653e-05 | -0.00044106 | 0.035152 | 0.035146 | 0.035152 | 0.99149 | -0.13552 | 0.99152 | -0.13573 | 15.9781
17 | 0.23587 | 0.092046 | -0.23587 | -0.092143 | 3.012e-07 | -9.7198e-05 | 0.0073746 | 0.0073756 | 0.0073756 | 0.99112 | -0.13701 | 0.99112 | -0.13701 | 3.3526
18 | 0.50143 | 0.23189 | -0.50135 | -0.23673 | 7.1918e-05 | -0.0048381 | 0.016092 | 0.016152 | 0.016152 | 0.99102 | -0.13617 | 0.99089 | -0.13501 | 7.3419
19 | -1.2667 | -0.57267 | 1.267 | 0.57272 | 0.00021631 | 4.8491e-05 | 0.040474 | 0.040473 | 0.040474 | 0.99152 | -0.13573 | 0.9917 | -0.13432 | 19.2734
20 | 0.093432 | 0.044751 | -0.093432 | -0.045167 | 2.1531e-07 | -0.00041567 | 0.0030156 | 0.0030209 | 0.0030209 | 0.9917 | -0.13432 | 0.9917 | -0.1343 | 1.3731
21 | 0.12049 | 0.044408 | -0.12048 | -0.057619 | 1.09e-05 | -0.013211 | 0.0037381 | 0.0038879 | 0.0038879 | 0.9917 | -0.13432 | 0.99161 | -0.13376 | 1.7672
22 | -1.4809 | -0.66188 | 1.4838 | 0.63912 | 0.0029729 | -0.022757 | 0.047217 | 0.046941 | 0.047217 | 0.9917 | -0.13432 | 0.99358 | -0.14802 | 21.4622
23 | 0.093432 | 0.045167 | -0.09343 | -0.04525 | 1.1672e-06 | -8.3523e-05 | 0.0030209 | 0.0030219 | 0.0030219 | 0.9917 | -0.1343 | 0.99168 | -0.13438 | 1.439
24 | 0.12048 | 0.057619 | -0.12048 | -0.058352 | 6.3208e-07 | -0.00073343 | 0.0038879 | 0.0038972 | 0.0038972 | 0.99161 | -0.13376 | 0.99161 | -0.13371 | 1.7715
25 | 0.14087 | 0.065781 | -0.14087 | -0.068227 | 2.8474e-06 | -0.0024465 | 0.0045172 | 0.0045477 | 0.0045477 | 0.99358 | -0.14802 | 0.99357 | -0.14785 | 2.0671
26 | 0.22436 | 0.1043 | -0.22434 | -0.10455 | 2.0344e-05 | -0.0002446 | 0.007209 | 0.0072121 | 0.0072121 | 0.99077 | -0.13541 | 0.99067 | -0.1361 | 3.4343
27 | -0.35062 | -0.16545 | 0.35064 | 0.16537 | 1.8758e-05 | -8.4953e-05 | 0.011296 | 0.011295 | 0.011296 | 0.99077 | -0.13541 | 0.99082 | -0.13502 | 5.3791
28 | 0.14941 | 0.068258 | -0.14941 | -0.06905 | 1.0358e-06 | -0.00079163 | 0.0047866 | 0.0047962 | 0.0047962 | 0.99067 | -0.1361 | 0.99066 | -0.13604 | 2.1801
29 | -0.35064 | -0.16537 | 0.35065 | 0.16378 | 1.1496e-05 | -0.0015816 | 0.011295 | 0.011275 | 0.011295 | 0.99082 | -0.13502 | 0.99085 | -0.13529 | 5.134
30 | -0.1494 | -0.07236 | 0.14941 | 0.072304 | 2.0589e-06 | -5.6569e-05 | 0.0048375 | 0.0048368 | 0.0048375 | 0.99062 | -0.1359 | 0.99064 | -0.1358 | 2.3036
31 | -0.14941 | -0.072304 | 0.14941 | 0.06905 | 4.3022e-06 | -0.0032539 | 0.0048368 | 0.0047962 | 0.0048368 | 0.99064 | -0.1358 | 0.99066 | -0.13604 | 2.1985
32 | -0.50134 | -0.23677 | 0.50135 | 0.23673 | 1.8883e-05 | -3.5784e-05 | 0.016153 | 0.016152 | 0.016153 | 0.99085 | -0.13529 | 0.99089 | -0.13501 | 7.6918
33 | 0.23587 | 0.092143 | -0.23584 | -0.10299 | 3.4177e-05 | -0.010852 | 0.0073756 | 0.0074965 | 0.0074965 | 0.99112 | -0.13701 | 0.99099 | -0.13618 | 3.4075
34 | -0.16301 | -0.078951 | 0.16301 | 0.078853 | 1.5135e-07 | -9.8095e-05 | 0.0052405 | 0.0052392 | 0.0052405 | 0.99774 | -0.035423 | 0.99774 | -0.035431 | 2.382
35 | -0.42144 | -0.19603 | 0.42148 | 0.19254 | 3.5512e-05 | -0.0034969 | 0.013448 | 0.013406 | 0.013448 | 0.99774 | -0.035431 | 0.99782 | -0.036085 | 6.1128
36 | 0.25843 | 0.11718 | -0.2584 | -0.12373 | 2.5076e-05 | -0.0065524 | 0.0082098 | 0.00829 | 0.00829 | 0.99774 | -0.035431 | 0.99765 | -0.034656 | 3.7682
37 | -8.6266 | -3.7684 | 8.6295 | 3.7622 | 0.0028651 | -0.0062124 | 0.27235 | 0.27225 | 0.27235 | 0.99782 | -0.036085 | 0.99817 | -0.03406 | 42.6873
38 | 3.6258 | 1.7228 | -3.622 | -1.7266 | 0.0037716 | -0.0038534 | 0.11613 | 0.1162 | 0.1162 | 0.99782 | -0.036085 | 0.99686 | -0.027368 | 52.8162
39 | 4.5045 | 1.8169 | -4.5025 | -1.8361 | 0.0019802 | -0.019147 | 0.14052 | 0.14074 | 0.14074 | 0.99782 | -0.036085 | 0.99736 | -0.039493 | 22.0595
40 | 0.074888 | 0.036132 | -0.074888 | -0.03627 | 4.4868e-08 | -0.00013796 | 0.0024055 | 0.0024073 | 0.0024073 | 0.99782 | -0.036085 | 0.99782 | -0.03608 | 1.0942
41 | 0.14151 | 0.067209 | -0.14151 | -0.068021 | 9.3876e-07 | -0.00081119 | 0.0045329 | 0.004543 | 0.004543 | 0.99765 | -0.034656 | 0.99765 | -0.0346 | 2.065
42 | 0.1169 | 0.056525 | -0.1169 | -0.056616 | 7.2129e-08 | -9.0924e-05 | 0.0037571 | 0.0037583 | 0.0037583 | 0.99765 | -0.034656 | 0.99765 | -0.034651 | 1.7083
43 | -8.7297 | -3.8099 | 8.7414 | 3.7852 | 0.011682 | -0.024696 | 0.27546 | 0.2751 | 0.27546 | 0.99817 | -0.03406 | 0.99957 | -0.025787 | 43.1761
44 | 0.10023 | 0.047741 | -0.10023 | -0.048542 | 4.6523e-07 | -0.00080156 | 0.0032107 | 0.0032207 | 0.0032207 | 0.99817 | -0.03406 | 0.99816 | -0.03402 | 1.464
45 | 3.4709 | 1.6536 | -3.4688 | -1.656 | 0.0021335 | -0.0024232 | 0.11134 | 0.11137 | 0.11137 | 0.99686 | -0.027368 | 0.99629 | -0.022193 | 50.625
46 | 0.15105 | 0.07305 | -0.15105 | -0.073158 | 1.431e-07 | -0.00010767 | 0.0048589 | 0.0048603 | 0.0048603 | 0.99686 | -0.027368 | 0.99686 | -0.027359 | 2.2092
47 | 4.5025 | 1.8361 | -4.502 | -1.8348 | 0.00053217 | 0.0013276 | 0.14074 | 0.14074 | 0.14074 | 0.99736 | -0.039493 | 0.99715 | -0.052742 | 21.8202
48 | 0.14151 | 0.068021 | -0.1415 | -0.068534 | 5.9621e-07 | -0.00051331 | 0.004543 | 0.0045495 | 0.0045495 | 0.99765 | -0.0346 | 0.99764 | -0.034564 | 2.068
49 | 0.16382 | 0.060643 | -0.16379 | -0.079144 | 2.7784e-05 | -0.018501 | 0.005062 | 0.0052722 | 0.0052722 | 0.99619 | -0.060165 | 0.99603 | -0.059096 | 2.3965
50 | 0.11709 | 0.055336 | -0.11709 | -0.056709 | 1.0951e-06 | -0.0013734 | 0.0037529 | 0.0037701 | 0.0037701 | 0.99619 | -0.060165 | 0.99619 | -0.060086 | 1.7137
51 | -0.28091 | -0.11598 | 0.28097 | 0.11555 | 5.418e-05 | -0.00043095 | 0.0088067 | 0.0088016 | 0.0088067 | 0.99619 | -0.060165 | 0.9964 | -0.058141 | 4.1937
52 | 0.16379 | 0.079144 | -0.16379 | -0.079244 | 1.5618e-07 | -9.9629e-05 | 0.0052722 | 0.0052735 | 0.0052735 | 0.99603 | -0.059096 | 0.99603 | -0.059087 | 2.397
53 | 3.9911 | 1.6416 | -3.9909 | -1.641 | 0.00022856 | 0.00055841 | 0.12503 | 0.12503 | 0.12503 | 0.9964 | -0.058141 | 0.9963 | -0.064533 | 19.3844
54 | -4.2721 | -1.7571 | 4.2736 | 1.7413 | 0.0014795 | -0.015872 | 0.13383 | 0.13365 | 0.13383 | 0.9964 | -0.058141 | 0.99677 | -0.055529 | 20.9766
55 | 4.3825 | 1.7769 | -4.382 | -1.7817 | 0.00047239 | -0.004827 | 0.13691 | 0.13696 | 0.13696 | 0.99715 | -0.052742 | 0.99703 | -0.053575 | 21.4672
56 | 0.13692 | 0.063974 | -0.13692 | -0.065358 | 1.4823e-06 | -0.0013846 | 0.0043646 | 0.0043817 | 0.0043817 | 0.99957 | -0.025787 | 0.99956 | -0.025698 | 1.9917
57 | -8.8783 | -3.8492 | 8.8804 | 3.8547 | 0.0021055 | 0.0055575 | 0.27947 | 0.27946 | 0.27947 | 0.99957 | -0.025787 | 1 | 0 | 43.3281
58 | 0.13692 | 0.065358 | -0.13692 | -0.066313 | 1.0295e-06 | -0.00095527 | 0.0043817 | 0.0043937 | 0.0043937 | 0.99956 | -0.025698 | 0.99955 | -0.025634 | 1.9971
59 | 1.9077 | 0.82096 | -1.9074 | -0.82222 | 0.00026978 | -0.0012618 | 0.059953 | 0.059969 | 0.059969 | 1 | 0 | 0.99987 | 0.00091639 | 27.2585
60 | 1.8697 | 0.88728 | -1.8695 | -0.88852 | 0.00026809 | -0.0012434 | 0.059966 | 0.059983 | 0.059983 | 0.99629 | -0.022193 | 0.99615 | -0.020998 | 27.2649
61 | 1.5991 | 0.76872 | -1.5989 | -0.76979 | 0.00016583 | -0.0010643 | 0.051409 | 0.051423 | 0.051423 | 0.99629 | -0.022193 | 0.99619 | -0.021303 | 23.374
62 | 0.16379 | 0.079244 | -0.16379 | -0.079328 | 1.3229e-07 | -8.4334e-05 | 0.0052735 | 0.0052746 | 0.0052746 | 0.99603 | -0.059087 | 0.99603 | -0.05908 | 2.3975
63 | 3.8472 | 1.5714 | -3.8471 | -1.5726 | 8.6249e-05 | -0.0011519 | 0.12041 | 0.12043 | 0.12043 | 0.9963 | -0.064533 | 0.99628 | -0.064704 | 18.8754
64 | -4.3809 | -1.7932 | 4.382 | 1.7817 | 0.0011232 | -0.011456 | 0.13709 | 0.13696 | 0.13709 | 0.99677 | -0.055529 | 0.99703 | -0.053575 | 21.4879
65 | 0.10732 | 0.051903 | -0.10732 | -0.051978 | 1.3658e-06 | -7.5396e-05 | 0.0034526 | 0.0034535 | 0.0034535 | 0.99677 | -0.055529 | 0.99675 | -0.055613 | 1.6445
66 | 3.8471 | 1.5726 | -3.8457 | -1.5918 | 0.0014439 | -0.019237 | 0.12043 | 0.12065 | 0.12065 | 0.99628 | -0.064704 | 0.99588 | -0.067495 | 18.9101
67 | 0.11447 | 0.054832 | -0.11447 | -0.055441 | 4.6591e-07 | -0.00060909 | 0.0036792 | 0.0036869 | 0.0036869 | 0.99588 | -0.067495 | 0.99588 | -0.06746 | 1.6759
68 | 3.7312 | 1.537 | -3.7283 | -1.53 | 0.0028943 | 0.0069718 | 0.11697 | 0.11698 | 0.11698 | 0.99588 | -0.067495 | 0.99449 | -0.15413 | 18.1367
69 | 1.9074 | 0.82222 | -1.9067 | -0.82582 | 0.00077206 | -0.0036053 | 0.059969 | 0.060013 | 0.060013 | 0.99987 | 0.00091639 | 0.99948 | 0.0035642 | 27.2785
70 | 1.7457 | 0.8286 | -1.7457 | -0.82913 | 9.8009e-05 | -0.0005255 | 0.055999 | 0.056006 | 0.056006 | 0.99615 | -0.020998 | 0.9961 | -0.020531 | 25.4574
71 | 1.2108 | 0.58449 | -1.2107 | -0.58469 | 1.7254e-05 | -0.00019662 | 0.03896 | 0.038962 | 0.038962 | 0.99619 | -0.021303 | 0.99618 | -0.02118 | 17.7101
72 | 0.38813 | 0.18529 | -0.38812 | -0.18642 | 9.8992e-06 | -0.0011269 | 0.012463 | 0.012477 | 0.012477 | 0.99619 | -0.021303 | 0.99617 | -0.021087 | 5.6715
73 | -0.14277 | -0.069148 | 0.14277 | 0.068461 | 8.1619e-07 | -0.00068645 | 0.0045971 | 0.0045885 | 0.0045971 | 0.99614 | -0.020873 | 0.99615 | -0.020923 | 2.0896
74 | -0.14277 | -0.068461 | 0.14277 | 0.068424 | 4.4614e-08 | -3.7588e-05 | 0.0045885 | 0.004588 | 0.0045885 | 0.99615 | -0.020923 | 0.99615 | -0.020925 | 2.0857
75 | -0.38812 | -0.18725 | 0.38812 | 0.18642 | 7.2971e-06 | -0.00082899 | 0.012488 | 0.012477 | 0.012488 | 0.99615 | -0.020925 | 0.99617 | -0.021087 | 5.6763
76 | 1.1154 | 0.53852 | -1.1154 | -0.53898 | 3.449e-05 | -0.00046484 | 0.035893 | 0.035899 | 0.035899 | 0.99618 | -0.02118 | 0.99615 | -0.020912 | 16.3175
77 | 0.8751 | 0.42261 | -0.87509 | -0.42265 | 1.6602e-06 | -3.6658e-05 | 0.028162 | 0.028162 | 0.028162 | 0.99615 | -0.020912 | 0.99615 | -0.020896 | 12.801
78 | 1.0218 | 0.48045 | -1.0217 | -0.48109 | 3.9487e-05 | -0.00064254 | 0.032722 | 0.03273 | 0.03273 | 0.9961 | -0.020531 | 0.99607 | -0.020215 | 14.8772
79 | 0.72387 | 0.34868 | -0.72386 | -0.34902 | 1.06e-05 | -0.00034373 | 0.023285 | 0.023289 | 0.023289 | 0.9961 | -0.020531 | 0.99609 | -0.020404 | 10.5861
80 | 0.78229 | 0.3777 | -0.78225 | -0.37886 | 4.1947e-05 | -0.0011615 | 0.025174 | 0.025189 | 0.025189 | 0.99615 | -0.020896 | 0.9961 | -0.02043 | 11.4495
81 | 0.42221 | 0.19453 | -0.42221 | -0.19471 | 1.9293e-06 | -0.00018783 | 0.013476 | 0.013478 | 0.013478 | 0.99584 | -0.021294 | 0.99584 | -0.021258 | 6.1263
82 | -0.55913 | -0.26084 | 0.55915 | 0.25973 | 2.0211e-05 | -0.0011156 | 0.017885 | 0.017871 | 0.017885 | 0.99584 | -0.021294 | 0.99588 | -0.021581 | 8.1296
83 | 0.42221 | 0.19471 | -0.42216 | -0.19936 | 4.795e-05 | -0.0046474 | 0.013478 | 0.013535 | 0.013535 | 0.99584 | -0.021258 | 0.99573 | -0.020349 | 6.1523
84 | -0.55915 | -0.25973 | 0.55925 | 0.25958 | 0.00010002 | -0.00014552 | 0.017871 | 0.017869 | 0.017871 | 0.99588 | -0.021581 | 0.99607 | -0.020215 | 8.5102
85 | 0.27491 | 0.13273 | -0.27491 | -0.13315 | 1.8308e-06 | -0.00041367 | 0.0088504 | 0.0088556 | 0.0088556 | 0.99573 | -0.020349 | 0.99573 | -0.020292 | 4.0253
86 | 0.14724 | 0.06663 | -0.14724 | -0.070556 | 4.9123e-06 | -0.0039262 | 0.0046855 | 0.0047336 | 0.0047336 | 0.99573 | -0.020349 | 0.9957 | -0.020084 | 2.1516
87 | 0.13252 | 0.064151 | -0.13252 | -0.064182 | 8.7229e-07 | -3.1299e-05 | 0.004267 | 0.0042674 | 0.0042674 | 0.99607 | -0.020215 | 0.99606 | -0.020259 | 2.0321
88 | 0.21974 | 0.10614 | -0.21972 | -0.10642 | 2.205e-05 | -0.00027906 | 0.0070725 | 0.0070762 | 0.0070762 | 0.99607 | -0.020215 | 0.99596 | -0.02088 | 3.3696
89 | 0.11022 | 0.051224 | -0.11022 | -0.051358 | 2.5332e-06 | -0.00013406 | 0.0035226 | 0.0035242 | 0.0035242 | 0.99607 | -0.020215 | 0.99604 | -0.02039 | 1.6782
90 | -0.72381 | -0.35056 | 0.72386 | 0.34902 | 4.7414e-05 | -0.0015357 | 0.023309 | 0.023289 | 0.023309 | 0.99603 | -0.019837 | 0.99609 | -0.020404 | 10.595
91 | 0.14724 | 0.070556 | -0.14724 | -0.071311 | 9.5599e-07 | -0.00075471 | 0.0047336 | 0.0047431 | 0.0047431 | 0.9957 | -0.020084 | 0.9957 | -0.020028 | 2.1559
92 | 0.11022 | 0.051358 | -0.11022 | -0.053382 | 1.4273e-06 | -0.0020241 | 0.0035242 | 0.0035494 | 0.0035494 | 0.99604 | -0.02039 | 0.99603 | -0.020281 | 1.6134
93 | 0.16216 | 0.077214 | -0.16216 | -0.078538 | 2.0714e-06 | -0.0013242 | 0.005232 | 0.0052487 | 0.0052487 | 0.99099 | -0.13618 | 0.99097 | -0.13607 | 2.3858
94 | 0.073675 | 0.025781 | -0.073673 | -0.035464 | 2.9783e-06 | -0.0096826 | 0.0022738 | 0.0023819 | 0.0023819 | 0.99099 | -0.13618 | 0.99095 | -0.13594 | 1.0827
95 | 0.073673 | 0.035464 | -0.073671 | -0.03568 | 1.8783e-06 | -0.0002164 | 0.0023819 | 0.0023846 | 0.0023846 | 0.99095 | -0.13594 | 0.99092 | -0.13611 | 1.1355
96 | -0.056918 | -0.027567 | 0.056918 | 0.02547 | 3.9285e-07 | -0.0020962 | 0.0018347 | 0.001809 | 0.0018347 | 0.99505 | 0.00093502 | 0.99506 | 0.00088001 | 0.83397
97 | -0.056918 | -0.02547 | 0.056919 | 0.023952 | 2.7796e-07 | -0.0015189 | 0.001809 | 0.0017915 | 0.001809 | 0.99506 | 0.00088001 | 0.99506 | 0.00084764 | 0.82229
98 | -0.129 | -0.055325 | 0.129 | 0.051398 | 3.638e-06 | -0.003927 | 0.004072 | 0.0040284 | 0.004072 | 0.99506 | 0.00084764 | 0.99509 | 0.00068617 | 1.8509
99 | 0.07208 | 0.031373 | -0.072078 | -0.034909 | 1.0577e-06 | -0.0035358 | 0.0022806 | 0.0023234 | 0.0023234 | 0.99506 | 0.00084764 | 0.99505 | 0.00096088 | 1.0561
100 | -1.1983 | -0.53021 | 1.1991 | 0.51983 | 0.00086425 | -0.010378 | 0.038013 | 0.037889 | 0.038013 | 0.99509 | 0.00068617 | 0.99577 | -0.0042134 | 17.2786
101 | 1.0693 | 0.47881 | -1.0692 | -0.47881 | 0.00011884 | 6.1906e-06 | 0.033988 | 0.033988 | 0.033988 | 0.99509 | 0.00068617 | 0.99497 | -0.00026094 | 16.185
102 | 0.12006 | 0.055543 | -0.12006 | -0.058149 | 2.1798e-06 | -0.0026058 | 0.0038351 | 0.0038674 | 0.0038674 | 0.99577 | -0.0042134 | 0.99575 | -0.0040632 | 1.7579
103 | -1.3192 | -0.57538 | 1.3202 | 0.56519 | 0.0010265 | -0.010191 | 0.041723 | 0.041603 | 0.041723 | 0.99577 | -0.0042134 | 0.99651 | -0.0093018 | 18.9651
104 | 0.90978 | 0.40162 | -0.90972 | -0.40284 | 5.8553e-05 | -0.0012272 | 0.028853 | 0.028868 | 0.028868 | 0.99497 | -0.00026094 | 0.99491 | 0.00018789 | 13.1218
105 | 0.05564 | 0.019037 | -0.055639 | -0.024723 | 9.6057e-07 | -0.0056858 | 0.0017036 | 0.0017638 | 0.0017638 | 0.99646 | -0.0090187 | 0.99645 | -0.0089359 | 0.80175
106 | 0.11155 | 0.053904 | -0.11155 | -0.054027 | 8.9748e-08 | -0.00012358 | 0.0035892 | 0.0035907 | 0.0035907 | 0.99646 | -0.0090187 | 0.99646 | -0.0090117 | 1.6322
107 | -0.16719 | -0.072941 | 0.1672 | 0.067924 | 7.807e-06 | -0.0050169 | 0.0052844 | 0.005228 | 0.0052844 | 0.99646 | -0.0090187 | 0.99651 | -0.0093018 | 2.402
108 | 0.055639 | 0.024723 | -0.055638 | -0.026947 | 3.9554e-07 | -0.0022238 | 0.0017638 | 0.001791 | 0.001791 | 0.99645 | -0.0089359 | 0.99644 | -0.0088797 | 0.81408
109 | 0.14497 | 0.069975 | -0.14496 | -0.07021 | 2.8788e-07 | -0.0002349 | 0.0046631 | 0.0046661 | 0.0046661 | 0.99651 | -0.0093018 | 0.99651 | -0.0092846 | 2.1209
110 | -1.6324 | -0.70308 | 1.6334 | 0.69647 | 0.0010303 | -0.0066116 | 0.051488 | 0.051409 | 0.051488 | 0.99651 | -0.0093018 | 0.99711 | -0.013331 | 23.4037
111 | -1.6334 | -0.69647 | 1.6335 | 0.69631 | 2.4524e-05 | -0.00015773 | 0.051409 | 0.051407 | 0.051409 | 0.99711 | -0.013331 | 0.99712 | -0.013425 | 23.3679
112 | 0.7919 | 0.34644 | -0.79184 | -0.34803 | 5.7226e-05 | -0.0015924 | 0.02508 | 0.025098 | 0.025098 | 0.99491 | 0.00018789 | 0.99484 | 0.0006806 | 11.4083
113 | 0.11783 | 0.056402 | -0.11783 | -0.057066 | 5.3972e-07 | -0.00066347 | 0.0037903 | 0.0037986 | 0.0037986 | 0.99491 | 0.00018789 | 0.99491 | 0.00022728 | 1.7266
114 | 0.79184 | 0.34803 | -0.79172 | -0.35126 | 0.00011624 | -0.0032263 | 0.025098 | 0.025137 | 0.025137 | 0.99484 | 0.0006806 | 0.99471 | 0.001701 | 11.4257
115 | 0.69384 | 0.30385 | -0.69203 | -0.30519 | 0.0018064 | -0.0013367 | 0.021982 | 0.022011 | 0.022011 | 0.99471 | 0.001701 | 0.99194 | -0.021696 | 10.4814
116 | 0.69203 | 0.30519 | -0.69192 | -0.30911 | 0.00010907 | -0.0039205 | 0.022011 | 0.022058 | 0.022058 | 0.99194 | -0.021696 | 0.99179 | -0.020585 | 10.0262
117 | -1.7085 | -0.73267 | 1.7102 | 0.73333 | 0.0016558 | 0.0006559 | 0.05382 | 0.053815 | 0.05382 | 0.99712 | -0.013425 | 0.99816 | -0.0041641 | 25.6284
118 | -0.23568 | -0.091048 | 0.23569 | 0.089074 | 6.2972e-06 | -0.0019743 | 0.0074256 | 0.0074049 | 0.0074256 | 0.98223 | -0.81339 | 0.98225 | -0.81351 | 3.3753
119 | 0.12628 | 0.038062 | -0.12628 | -0.042409 | 3.8233e-06 | -0.0043466 | 0.0038763 | 0.0039151 | 0.0039151 | 0.98223 | -0.81339 | 0.9822 | -0.81336 | 1.7796
120 | 0.066662 | 0.02463 | -0.06666 | -0.03102 | 1.6692e-06 | -0.0063904 | 0.0020886 | 0.0021609 | 0.0021609 | 0.98225 | -0.81351 | 0.98223 | -0.81336 | 0.98221
121 | -0.30235 | -0.1137 | 0.30239 | 0.10631 | 3.8367e-05 | -0.0073943 | 0.0094934 | 0.009419 | 0.0094934 | 0.98225 | -0.81351 | 0.98238 | -0.81394 | 4.3152
122 | 0.12628 | 0.042409 | -0.12626 | -0.060259 | 1.6612e-05 | -0.01785 | 0.0039151 | 0.0041124 | 0.0041124 | 0.9822 | -0.81336 | 0.98207 | -0.81265 | 1.8693
123 | 0.06666 | 0.03102 | -0.06666 | -0.032285 | 3.4467e-07 | -0.0012643 | 0.0021609 | 0.0021768 | 0.0021768 | 0.98223 | -0.81336 | 0.98222 | -0.81332 | 0.98946
124 | 0.17331 | 0.072725 | -0.17329 | -0.080385 | 1.3766e-05 | -0.0076606 | 0.0055229 | 0.0056139 | 0.0056139 | 0.98238 | -0.81394 | 0.9823 | -0.81339 | 2.5518
125 | -0.4757 | -0.17903 | 0.4757 | 0.17886 | 2.2878e-06 | -0.00017635 | 0.014936 | 0.014934 | 0.014936 | 0.98238 | -0.81394 | 0.98238 | -0.81396 | 6.789
126 | 0.12626 | 0.060259 | -0.12626 | -0.06115 | 8.7711e-07 | -0.0008919 | 0.0041124 | 0.0041237 | 0.0041237 | 0.98207 | -0.81265 | 0.98207 | -0.81259 | 1.8744
127 | 1.9067 | 0.82582 | -1.9062 | -0.82813 | 0.0004962 | -0.0023125 | 0.060013 | 0.060041 | 0.060041 | 0.99948 | 0.0035642 | 0.99923 | 0.0052857 | 27.2913
128 | 1.8206 | 0.78669 | -1.8188 | -0.78592 | 0.0018335 | 0.00077522 | 0.057297 | 0.057301 | 0.057301 | 0.99923 | 0.0052857 | 0.99816 | -0.0041641 | 27.2862
129 | 0.1554 | 0.075144 | -0.15539 | -0.07526 | 4.7276e-06 | -0.00011605 | 0.0050698 | 0.0050713 | 0.0050713 | 0.98287 | -0.80885 | 0.98283 | -0.80906 | 2.4149
130 | 0.62371 | 0.25011 | -0.62364 | -0.25018 | 7.1254e-05 | -7.3743e-05 | 0.019737 | 0.019738 | 0.019738 | 0.98287 | -0.80885 | 0.98275 | -0.81012 | 9.3991
131 | -0.93748 | -0.40195 | 0.93849 | 0.40044 | 0.0010152 | -0.0015162 | 0.029959 | 0.02991 | 0.029959 | 0.98287 | -0.80885 | 0.9848 | -0.69031 | 4.6447
132 | 0.62364 | 0.25018 | -0.62343 | -0.2504 | 0.00021534 | -0.00022259 | 0.019738 | 0.019742 | 0.019742 | 0.98275 | -0.81012 | 0.98238 | -0.81396 | 9.401
133 | -1.1761 | -0.51523 | 1.1761 | 0.51001 | 3.7613e-05 | -0.0052236 | 0.037638 | 0.037577 | 0.037638 | 0.9848 | -0.69031 | 0.98483 | -0.69011 | 5.8994
134 | 0.12121 | 0.058415 | -0.1212 | -0.0587 | 6.9279e-06 | -0.00028478 | 0.0039441 | 0.0039478 | 0.0039478 | 0.9848 | -0.69031 | 0.98474 | -0.69069 | 1.8799
135 | -1.1761 | -0.51001 | 1.1762 | 0.49673 | 9.5062e-05 | -0.01328 | 0.037577 | 0.037423 | 0.037577 | 0.98483 | -0.69011 | 0.98492 | -0.68958 | 5.8898
136 | 0.051877 | 0.022143 | -0.051876 | -0.024116 | 3.1852e-07 | -0.0019726 | 0.0016576 | 0.0016812 | 0.0016812 | 0.98229 | -0.81343 | 0.98228 | -0.81339 | 0.7642
137 | -0.051877 | -0.022143 | 0.051877 | 0.02204 | 4.3937e-07 | -0.00010318 | 0.0016576 | 0.0016564 | 0.0016576 | 0.98229 | -0.81343 | 0.9823 | -0.81335 | 0.78934
138 | 0.051876 | 0.024116 | -0.051876 | -0.025125 | 1.6655e-07 | -0.0010092 | 0.0016812 | 0.0016939 | 0.0016939 | 0.98228 | -0.81339 | 0.98228 | -0.81336 | 0.76998
139 | -0.17329 | -0.080844 | 0.17329 | 0.080385 | 8.3981e-07 | -0.00045913 | 0.0056196 | 0.0056139 | 0.0056196 | 0.9823 | -0.81335 | 0.9823 | -0.81339 | 2.5544
140 | 0.08432 | 0.032819 | -0.084317 | -0.04074 | 3.2892e-06 | -0.0079211 | 0.0026459 | 0.0027384 | 0.0027384 | 0.98719 | -0.55097 | 0.98716 | -0.5507 | 1.2447
141 | 1.3364 | 0.57449 | -1.3348 | -0.57349 | 0.0016419 | 0.0010019 | 0.042537 | 0.042577 | 0.042577 | 0.98719 | -0.55097 | 0.98499 | -0.6853 | 6.601
142 | -1.4207 | -0.60731 | 1.4208 | 0.60735 | 4.8346e-05 | 4.0632e-05 | 0.045182 | 0.045181 | 0.045182 | 0.98719 | -0.55097 | 0.98725 | -0.54724 | 7.0049
143 | 0.084317 | 0.04074 | -0.084317 | -0.040837 | 4.1496e-08 | -9.6382e-05 | 0.0027384 | 0.0027397 | 0.0027397 | 0.98716 | -0.5507 | 0.98716 | -0.5507 | 1.2453
144 | 1.1763 | 0.49673 | -1.1762 | -0.49673 | 4.5761e-05 | 3.1134e-07 | 0.037422 | 0.037423 | 0.037423 | 0.98499 | -0.6853 | 0.98492 | -0.68958 | 5.802
145 | -1.5307 | -0.66058 | 1.5322 | 0.66223 | 0.0015082 | 0.0016548 | 0.048748 | 0.04872 | 0.048748 | 0.98725 | -0.54724 | 0.98903 | -0.4399 | 7.5578
146 | 0.56556 | 0.24791 | -0.56549 | -0.248 | 6.6583e-05 | -9.4108e-05 | 0.017974 | 0.017975 | 0.017975 | 0.99179 | -0.020585 | 0.99167 | -0.021648 | 8.5596
147 | 0.56549 | 0.248 | -0.56529 | -0.25912 | 0.00020685 | -0.011112 | 0.017975 | 0.018108 | 0.018108 | 0.99167 | -0.021648 | 0.99132 | -0.018998 | 8.231
148 | 0.56529 | 0.25912 | -0.56526 | -0.25915 | 2.4239e-05 | -3.3487e-05 | 0.018108 | 0.018109 | 0.018109 | 0.99132 | -0.018998 | 0.99128 | -0.019339 | 8.6233
149 | 0.10926 | 0.052751 | -0.10926 | -0.052919 | 1.189e-07 | -0.00016724 | 0.0035333 | 0.0035355 | 0.0035355 | 0.99128 | -0.019339 | 0.99128 | -0.01933 | 1.607
150 | 0.077512 | 0.035455 | -0.077509 | -0.035743 | 2.7205e-06 | -0.00028859 | 0.0024822 | 0.0024857 | 0.0024857 | 0.99128 | -0.019339 | 0.99124 | -0.019617 | 1.1837
151 | 0.37849 | 0.17094 | -0.37846 | -0.17375 | 2.351e-05 | -0.0028097 | 0.012094 | 0.012128 | 0.012128 | 0.99128 | -0.019339 | 0.99122 | -0.018871 | 5.5128
152 | 0.077509 | 0.035743 | -0.077509 | -0.037539 | 6.3711e-07 | -0.0017957 | 0.0024857 | 0.0025081 | 0.0025081 | 0.99124 | -0.019617 | 0.99123 | -0.019549 | 1.14
153 | 0.30449 | 0.13807 | -0.30446 | -0.14412 | 3.2949e-05 | -0.006051 | 0.0097367 | 0.0098109 | 0.0098109 | 0.99122 | -0.018871 | 0.99112 | -0.01802 | 4.4595
154 | 0.073977 | 0.035687 | -0.073976 | -0.035828 | 4.59e-08 | -0.00014096 | 0.002392 | 0.0023938 | 0.0023938 | 0.99122 | -0.018871 | 0.99122 | -0.018866 | 1.0881
155 | -1.5322 | -0.66223 | 1.5322 | 0.659 | 3.8775e-05 | -0.0032299 | 0.04872 | 0.048682 | 0.04872 | 0.98903 | -0.4399 | 0.98905 | -0.43974 | 7.6363
156 | 0.30446 | 0.14412 | -0.30445 | -0.14517 | 5.7797e-06 | -0.0010518 | 0.0098109 | 0.0098241 | 0.0098241 | 0.99112 | -0.01802 | 0.9911 | -0.017862 | 4.4655
157 | 0.18513 | 0.087379 | -0.18513 | -0.08845 | 2.1723e-06 | -0.0010703 | 0.0059627 | 0.0059761 | 0.0059761 | 0.9911 | -0.017862 | 0.99109 | -0.017764 | 2.7164
158 | 0.18513 | 0.08845 | -0.18513 | -0.089344 | 1.8233e-06 | -0.00089464 | 0.0059761 | 0.0059874 | 0.0059874 | 0.99109 | -0.017764 | 0.99108 | -0.01768 | 2.7215
159 | 0.18513 | 0.089344 | -0.18513 | -0.08966 | 6.4574e-07 | -0.00031604 | 0.0059874 | 0.0059914 | 0.0059914 | 0.99108 | -0.01768 | 0.99108 | -0.01765 | 2.7233

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 10.955 | 4.7603

## res_load
| p_mw | q_mvar
0 | 0.084559 | 0.040954
1 | 0.15623 | 0.075665
2 | 0.072992 | 0.035352
3 | 0.13828 | 0.066972
4 | 0.14767 | 0.071518
5 | 0.07831 | 0.037927
6 | 0.16475 | 0.079794
7 | 0.09343 | 0.04525
8 | 0.12626 | 0.061149
9 | 0.074927 | 0.036289
10 | 0.1494 | 0.07236
11 | 0.15069 | 0.072982
12 | 0.16301 | 0.078951
13 | 0.074888 | 0.03627
14 | 0.1169 | 0.056616
15 | 0.11709 | 0.056709
16 | 0.11948 | 0.057867
17 | 0.10023 | 0.048542
18 | 0.1529 | 0.074053
19 | 0.15105 | 0.073158
20 | 0.1415 | 0.068534
21 | 0.1437 | 0.069599
22 | 0.10732 | 0.051978
23 | 0.13692 | 0.066313
24 | 0.12372 | 0.05992
25 | 0.16379 | 0.079328
26 | 0.14277 | 0.069148
27 | 0.24534 | 0.11883
28 | 0.095336 | 0.046173
29 | 0.24028 | 0.11637
30 | 0.092803 | 0.044947
31 | 0.13692 | 0.066315
32 | 0.72381 | 0.35056
33 | 0.14724 | 0.071311
34 | 0.27491 | 0.13315
35 | 0.11022 | 0.053382
36 | 0.13252 | 0.064182
37 | 0.21972 | 0.10642
38 | 0.16216 | 0.078538
39 | 0.073671 | 0.03568
40 | 0.1502 | 0.072747
41 | 0.11447 | 0.055441
42 | 0.14087 | 0.068227
43 | 0.12048 | 0.058352
44 | 0.056918 | 0.027567
45 | 0.072078 | 0.034909
46 | 0.15938 | 0.07719
47 | 0.11155 | 0.054027
48 | 0.14496 | 0.07021
49 | 0.055638 | 0.026947
50 | 0.12006 | 0.058149
51 | 0.11783 | 0.057066
52 | 0.097886 | 0.047408
53 | 0.075073 | 0.036359
54 | 0.1094 | 0.052986
55 | 0.12626 | 0.06115
56 | 0.06666 | 0.032285
57 | 0.085566 | 0.041442
58 | 0.10858 | 0.052588
59 | 0.15837 | 0.0767
60 | 0.15539 | 0.07526
61 | 0.11641 | 0.056378
62 | 0.14773 | 0.071547
63 | 0.1212 | 0.0587
64 | 0.12142 | 0.058805
65 | 0.051876 | 0.025125
66 | 0.15849 | 0.07676
67 | 0.10991 | 0.05323
68 | 0.12636 | 0.061199
69 | 0.10926 | 0.052919
70 | 0.077509 | 0.037539
71 | 0.099779 | 0.048325
72 | 0.084317 | 0.040837
73 | 0.78225 | 0.37886
74 | 0.073976 | 0.035828
75 | 0.11932 | 0.057789
76 | 0.18513 | 0.08966

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1