## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_403_1_node_149 | 20 | n |  | TRUE
1 | bus_MV_403_1_node_95 | 20 | n |  | TRUE
2 | bus_MV_403_1_node_150 | 20 | n |  | TRUE
3 | bus_MV_403_1_node_151 | 20 | n |  | TRUE
4 | bus_MV_403_1_node_152 | 20 | n |  | TRUE
5 | bus_MV_403_1_node_107 | 20 | n |  | TRUE
6 | bus_MV_403_1_node_153 | 20 | n |  | TRUE
7 | bus_MV_403_1_node_90 | 20 | n |  | TRUE
8 | bus_MV_403_1_node_160 | 20 | n |  | TRUE
9 | bus_MV_403_1_node_62 | 20 | n |  | TRUE
10 | bus_MV_403_1_node_161 | 20 | n |  | TRUE
11 | bus_MV_403_1_node_162 | 20 | n |  | TRUE
12 | bus_MV_403_1_node_105 | 20 | n |  | TRUE
13 | bus_MV_403_1_node_163 | 20 | n |  | TRUE
14 | bus_MV_403_1_node_87 | 20 | n |  | TRUE
15 | bus_MV_403_1_node_169 | 20 | n |  | TRUE
16 | bus_MV_403_1_node_93 | 20 | n |  | TRUE
17 | bus_MV_403_1_node_171 | 20 | n |  | TRUE
18 | bus_MV_403_1_node_170 | 20 | n |  | TRUE
19 | bus_MV_403_1_node_92 | 20 | n |  | TRUE
20 | bus_MV_403_1_node_98 | 20 | n |  | TRUE
21 | bus_MV_403_1_node_61 | 20 | n |  | TRUE
22 | bus_MV_403_1_node_96 | 20 | n |  | TRUE
23 | bus_MV_403_1_node_82 | 20 | n |  | TRUE
24 | bus_MV_403_1_node_83 | 20 | n |  | TRUE
25 | bus_MV_403_1_node_84 | 20 | n |  | TRUE
26 | bus_MV_403_1_node_85 | 20 | n |  | TRUE
27 | bus_MV_403_1_node_106 | 20 | n |  | TRUE
28 | bus_MV_403_1_node_86 | 20 | n |  | TRUE
29 | bus_MV_403_1_node_102 | 20 | n |  | TRUE
30 | bus_MV_403_1_node_88 | 20 | n |  | TRUE
31 | bus_MV_403_1_node_89 | 20 | n |  | TRUE
32 | bus_MV_403_1_node_91 | 20 | n |  | TRUE
33 | bus_MV_403_1_node_94 | 20 | n |  | TRUE
34 | bus_MV_403_1_node_97 | 20 | n |  | TRUE
35 | bus_MV_403_1_node_99 | 20 | n |  | TRUE
36 | bus_MV_403_1_node_100 | 20 | n |  | TRUE
37 | bus_MV_403_1_node_101 | 20 | n |  | TRUE
38 | bus_MV_403_1_node_103 | 20 | n |  | TRUE
39 | bus_MV_403_1_node_104 | 20 | n |  | TRUE
40 | bus_HV_403_1_node_153 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_403_1_load_149 | 0 | 0.93131 | 0.45105 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_403_1_load_150 | 2 | 0.094287 | 0.045665 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_403_1_load_151 | 3 | 0.17109 | 0.082865 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_403_1_load_152 | 4 | 0.34821 | 0.16865 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_403_1_load_153 | 6 | 0.16228 | 0.078598 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_403_1_load_160 | 8 | 0.12865 | 0.062307 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_403_1_load_161 | 10 | 0.091323 | 0.04423 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_403_1_load_163 | 13 | 0.095283 | 0.046148 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_403_1_load_169 | 15 | 0.08995 | 0.043565 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_403_1_load_170 | 18 | 0.13189 | 0.063878 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_403_1_load_61 | 21 | 0.37628 | 0.18224 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_403_1_load_96 | 22 | 0.082344 | 0.039881 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_403_1_load_82 | 23 | 0.12717 | 0.061591 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_403_1_load_106 | 27 | 0.13196 | 0.063913 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_403_1_load_102 | 29 | 0.13345 | 0.064632 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_403_1_load_88 | 30 | 0.084935 | 0.041136 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_403_1_load_94 | 33 | 0.14732 | 0.071348 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_403_1_load_97 | 34 | 0.067519 | 0.032701 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_403_1_load_99 | 35 | 0.13475 | 0.065261 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_403_1_load_103 | 38 | 0.094546 | 0.045791 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_403_1_line_0 |  | 0 | 1 | 0.038557 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_403_1_line_1 |  | 0 | 2 | 0.0073026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_403_1_line_2 |  | 1 | 5 | 0.19674 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_403_1_line_3 |  | 1 | 26 | 0.84149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_403_1_line_4 |  | 2 | 3 | 0.05395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_403_1_line_5 |  | 4 | 5 | 0.02547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_403_1_line_6 |  | 6 | 7 | 0.04732 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_403_1_line_7 |  | 7 | 19 | 0.28921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_403_1_line_8 |  | 7 | 26 | 0.1806 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_403_1_line_9 |  | 8 | 9 | 1.1632 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_403_1_line_10 |  | 9 | 21 | 0.012231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_403_1_line_11 |  | 10 | 11 | 0.008989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_403_1_line_12 |  | 11 | 12 | 0.053679 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_403_1_line_13 |  | 12 | 13 | 0.12591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_403_1_line_14 |  | 12 | 39 | 0.29492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_403_1_line_15 |  | 13 | 14 | 0.005613 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_403_1_line_16 |  | 14 | 25 | 0.26017 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_403_1_line_17 |  | 14 | 28 | 0.24275 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_403_1_line_18 |  | 15 | 16 | 0.046681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_403_1_line_19 |  | 15 | 17 | 0.065432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_403_1_line_20 |  | 16 | 31 | 0.86286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_403_1_line_21 |  | 17 | 20 | 0.69785 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_403_1_line_22 |  | 18 | 19 | 0.073683 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_403_1_line_23 |  | 19 | 31 | 0.77278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_403_1_line_24 |  | 19 | 32 | 0.52256 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_403_1_line_25 |  | 20 | 34 | 0.084323 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_403_1_line_26 |  | 21 | 22 | 2.0218 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_403_1_line_27 |  | 22 | 34 | 0.41515 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_403_1_line_28 |  | 23 | 24 | 0.019395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_403_1_line_29 |  | 23 | 25 | 0.079111 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_403_1_line_30 |  | 24 | 26 | 0.17202 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_403_1_line_31 |  | 26 | 27 | 0.039035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_403_1_line_32 |  | 28 | 29 | 0.04832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_403_1_line_33 |  | 29 | 37 | 0.024902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_403_1_line_34 |  | 30 | 31 | 0.055466 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_403_1_line_35 |  | 32 | 33 | 0.060232 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_403_1_line_36 |  | 35 | 36 | 0.024989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_403_1_line_37 |  | 36 | 37 | 0.21968 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_403_1_line_38 |  | 38 | 39 | 0.076574 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_403_1_trafo_153 | 25 MVA 110/20 kV | 40 | 6 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2583974.4361 | 1207827.2459
1 | 2583996.4509 | 1207795.5913
2 | 2583970.2666 | 1207833.2411
3 | 2583975.6674 | 1207878.0708
4 | 2583806.6633 | 1207870.3376
5 | 2583826.6683 | 1207854.5729
6 | 2584593.8643 | 1207622.9044
7 | 2584546.7763 | 1207627.5849
8 | 2588312.5407 | 1204950.735
9 | 2587380.9262 | 1205647.303
10 | 2584715.5884 | 1208048.3249
11 | 2584719.7522 | 1208056.2964
12 | 2584744.6052 | 1208103.9033
13 | 2584646.1716 | 1208180.7218
14 | 2584641.5639 | 1208177.4986
15 | 2585003.9902 | 1207551.2367
16 | 2584981.3484 | 1207515.1852
17 | 2585066.1671 | 1207572.1582
18 | 2584326.9513 | 1207560.702
19 | 2584370.9992 | 1207619.8519
20 | 2585461.9765 | 1206997.414
21 | 2587368.8148 | 1205649.2409
22 | 2585546.2518 | 1206524.3921
23 | 2584554.7037 | 1207978.9039
24 | 2584572.0589 | 1207970.7533
25 | 2584495.6081 | 1208025.9386
26 | 2584564.1642 | 1207802.8921
27 | 2584586.7875 | 1207834.6149
28 | 2584476.8137 | 1208272.4353
29 | 2584435.4559 | 1208297.602
30 | 2584856.9663 | 1207719.3028
31 | 2584823.0941 | 1207763.2247
32 | 2584240.5073 | 1207318.1969
33 | 2584215.043 | 1207263.6122
34 | 2585522.8383 | 1206938.8774
35 | 2584251.5738 | 1208230.4609
36 | 2584266.5575 | 1208250.4878
37 | 2584415.25 | 1208312.2186
38 | 2584924.7759 | 1208428.3558
39 | 2584881.8384 | 1208364.9522
40 | 2584593.8643 | 1207622.9044

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99744 | 0.016951 | 0.93131 | 0.45105
1 | 0.9975 | 0.016401 | 0 | 0
2 | 0.99744 | 0.016974 | 0.094287 | 0.045665
3 | 0.99742 | 0.017083 | 0.17109 | 0.082865
4 | 0.9974 | 0.017294 | 0.34821 | 0.16865
5 | 0.99741 | 0.017188 | 0 | 0
6 | 1 | 0 | -3.4856 | -1.5501
7 | 0.99969 | -0.0025563 | 0 | 0
8 | 0.99386 | -0.0099665 | 0.12865 | 0.062307
9 | 0.99415 | -0.0080676 | 0 | 0
10 | 0.99871 | 0.0047472 | 0.091323 | 0.04423
11 | 0.99872 | 0.0047374 | 0 | 0
12 | 0.99872 | 0.0046815 | 0 | 0
13 | 0.99875 | 0.0044821 | 0.095283 | 0.046148
14 | 0.99875 | 0.0044674 | 0 | 0
15 | 0.99762 | 0.012837 | 0.08995 | 0.043565
16 | 0.99766 | 0.012445 | 0 | 0
17 | 0.99756 | 0.01332 | 0 | 0
18 | 0.99927 | 0.00017562 | 0.13189 | 0.063878
19 | 0.99929 | 6.3316e-05 | 0 | 0
20 | 0.99668 | 0.0073499 | 0 | 0
21 | 0.99415 | -0.0080855 | 0.37628 | 0.18224
22 | 0.99613 | 0.0048668 | 0.082344 | 0.039881
23 | 0.99899 | 0.0028639 | 0.12717 | 0.061591
24 | 0.999 | 0.002748 | 0 | 0
25 | 0.99893 | 0.0032221 | 0 | 0
26 | 0.99915 | 0.0017451 | 0 | 0
27 | 0.99914 | 0.0018057 | 0.13196 | 0.063913
28 | 0.99867 | 0.005086 | 0 | 0
29 | 0.99866 | 0.0052199 | 0.13345 | 0.064632
30 | 0.99847 | 0.0057574 | 0.084935 | 0.041136
31 | 0.99848 | 0.0058147 | 0 | 0
32 | 0.99919 | 0.00077557 | 0 | 0
33 | 0.99917 | 0.00066799 | 0.14732 | 0.071348
34 | 0.99661 | 0.0079872 | 0.067519 | 0.032701
35 | 0.99861 | 0.0056004 | 0.13475 | 0.065261
36 | 0.99861 | 0.0055604 | 0 | 0
37 | 0.99865 | 0.0052504 | 0 | 0
38 | 0.99867 | 0.0048601 | 0.094546 | 0.045791
39 | 0.99869 | 0.0049481 | 0 | 0
40 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -1.1967 | -0.57813 | 1.1968 | 0.57724 | 7.6132e-05 | -0.00089336 | 0.038464 | 0.038453 | 0.038464 | 0.99744 | 0.016951 | 0.9975 | 0.016401 | 17.4837
1 | 0.26538 | 0.12708 | -0.26538 | -0.12725 | 7.0718e-07 | -0.00017326 | 0.0085158 | 0.008518 | 0.008518 | 0.99744 | 0.016951 | 0.99744 | 0.016974 | 3.8718
2 | 0.34825 | 0.16338 | -0.34822 | -0.16804 | 3.2718e-05 | -0.0046637 | 0.011132 | 0.01119 | 0.01119 | 0.9975 | 0.016401 | 0.99741 | 0.017188 | 5.0865
3 | -1.545 | -0.74062 | 1.5478 | 0.72141 | 0.0027482 | -0.019209 | 0.049584 | 0.049337 | 0.049584 | 0.9975 | 0.016401 | 0.99915 | 0.0017451 | 22.5384
4 | 0.1711 | 0.081584 | -0.17109 | -0.082865 | 2.1739e-06 | -0.0012809 | 0.005486 | 0.005502 | 0.005502 | 0.99744 | 0.016974 | 0.99742 | 0.017083 | 2.5009
5 | -0.34821 | -0.16865 | 0.34822 | 0.16804 | 4.2609e-06 | -0.00060371 | 0.011198 | 0.01119 | 0.011198 | 0.9974 | 0.017294 | 0.99741 | 0.017188 | 5.09
6 | 3.4716 | 1.5396 | -3.4706 | -1.539 | 0.0010133 | 0.00057822 | 0.10963 | 0.10963 | 0.10963 | 1 | 0 | 0.99969 | -0.0025563 | 52.2046
7 | 1.1127 | 0.46855 | -1.1122 | -0.47531 | 0.0004703 | -0.0067586 | 0.034862 | 0.03494 | 0.03494 | 0.99969 | -0.0025563 | 0.99929 | 6.3316e-05 | 15.8819
8 | 2.3579 | 1.0705 | -2.3565 | -1.0744 | 0.001349 | -0.0039068 | 0.074776 | 0.074828 | 0.074828 | 0.99969 | -0.0025563 | 0.99915 | 0.0017451 | 34.0127
9 | -0.12865 | -0.062307 | 0.12868 | 0.060957 | 3.5578e-05 | -0.0013498 | 0.0041519 | 0.0041347 | 0.0041519 | 0.99386 | -0.0099665 | 0.99415 | -0.0080676 | 1.9771
10 | -0.12868 | -0.060957 | 0.12868 | 0.060669 | 2.7888e-07 | -0.00028854 | 0.0041347 | 0.0041311 | 0.0041347 | 0.99415 | -0.0080676 | 0.99415 | -0.0080855 | 1.8794
11 | -0.091323 | -0.04423 | 0.091323 | 0.044016 | 1.0314e-07 | -0.00021404 | 0.002933 | 0.0029303 | 0.002933 | 0.99871 | 0.0047472 | 0.99872 | 0.0047374 | 1.3332
12 | -0.091323 | -0.044016 | 0.091324 | 0.042737 | 6.1197e-07 | -0.0012782 | 0.0029303 | 0.0029144 | 0.0029303 | 0.99872 | 0.0047374 | 0.99872 | 0.0046815 | 1.3319
13 | -0.18587 | -0.081416 | 0.18588 | 0.078419 | 5.7487e-06 | -0.0029969 | 0.0058654 | 0.0058312 | 0.0058654 | 0.99872 | 0.0046815 | 0.99875 | 0.0044821 | 2.6661
14 | 0.094551 | 0.038678 | -0.094547 | -0.0457 | 3.5262e-06 | -0.0070223 | 0.0029528 | 0.0030355 | 0.0030355 | 0.99872 | 0.0046815 | 0.99869 | 0.0049481 | 1.3798
15 | -0.28116 | -0.12457 | 0.28116 | 0.12443 | 5.9192e-07 | -0.00013351 | 0.0088885 | 0.0088869 | 0.0088885 | 0.99875 | 0.0044821 | 0.99875 | 0.0044674 | 4.0402
16 | -0.54939 | -0.24099 | 0.5495 | 0.23482 | 0.000104 | -0.0061666 | 0.01734 | 0.017269 | 0.01734 | 0.99875 | 0.0044674 | 0.99893 | 0.0032221 | 7.8818
17 | 0.26823 | 0.11655 | -0.26821 | -0.12233 | 2.3341e-05 | -0.005774 | 0.0084531 | 0.0085211 | 0.0085211 | 0.99875 | 0.0044674 | 0.99867 | 0.005086 | 3.8732
18 | -0.74663 | -0.35292 | 0.74667 | 0.35183 | 3.5568e-05 | -0.0010988 | 0.023897 | 0.023883 | 0.023897 | 0.99762 | 0.012837 | 0.99766 | 0.012445 | 10.8623
19 | 0.65668 | 0.30936 | -0.65664 | -0.3109 | 3.8576e-05 | -0.0015433 | 0.021005 | 0.021024 | 0.021024 | 0.99762 | 0.012837 | 0.99756 | 0.01332 | 9.5565
20 | -0.74667 | -0.35183 | 0.74732 | 0.3315 | 0.00065021 | -0.020329 | 0.023883 | 0.023636 | 0.023883 | 0.99766 | 0.012445 | 0.99848 | 0.0058147 | 10.856
21 | 0.65664 | 0.3109 | -0.65609 | -0.31139 | 0.00054986 | -0.00048389 | 0.021024 | 0.021035 | 0.021035 | 0.99756 | 0.01332 | 0.99668 | 0.0073499 | 10.0165
22 | -0.13189 | -0.063878 | 0.13189 | 0.062122 | 1.7538e-06 | -0.0017562 | 0.0042335 | 0.0042116 | 0.0042335 | 0.99927 | 0.00017562 | 0.99929 | 6.3316e-05 | 1.9243
23 | 0.83296 | 0.35437 | -0.83225 | -0.37257 | 0.00071116 | -0.018199 | 0.02615 | 0.026363 | 0.026363 | 0.99929 | 6.3316e-05 | 0.99848 | 0.0058147 | 11.9831
24 | 0.14733 | 0.058824 | -0.14732 | -0.071278 | 1.5101e-05 | -0.012453 | 0.0045829 | 0.0047281 | 0.0047281 | 0.99929 | 6.3316e-05 | 0.99919 | 0.00077557 | 2.1492
25 | 0.65609 | 0.31139 | -0.65604 | -0.31337 | 4.9866e-05 | -0.001985 | 0.021035 | 0.021059 | 0.021059 | 0.99668 | 0.0073499 | 0.99661 | 0.0079872 | 9.5725
26 | -0.50496 | -0.24291 | 0.50592 | 0.24112 | 0.00095193 | -0.001794 | 0.016271 | 0.016241 | 0.016271 | 0.99415 | -0.0080855 | 0.99613 | 0.0048668 | 7.7482
27 | -0.58826 | -0.281 | 0.58852 | 0.28067 | 0.00026392 | -0.0003267 | 0.018893 | 0.018886 | 0.018893 | 0.99613 | 0.0048668 | 0.99661 | 0.0079872 | 8.9965
28 | -0.6767 | -0.29453 | 0.67671 | 0.29408 | 1.1773e-05 | -0.00045866 | 0.021326 | 0.021321 | 0.021326 | 0.99899 | 0.0028639 | 0.999 | 0.002748 | 9.6938
29 | 0.54953 | 0.23294 | -0.5495 | -0.23482 | 3.1456e-05 | -0.0018756 | 0.017247 | 0.017269 | 0.017269 | 0.99899 | 0.0028639 | 0.99893 | 0.0032221 | 7.8494
30 | -0.67671 | -0.29408 | 0.67681 | 0.29001 | 0.00010416 | -0.0040686 | 0.021321 | 0.021274 | 0.021321 | 0.999 | 0.002748 | 0.99915 | 0.0017451 | 9.6914
31 | 0.13197 | 0.062983 | -0.13196 | -0.063913 | 9.3266e-07 | -0.00093014 | 0.0042247 | 0.0042364 | 0.0042364 | 0.99915 | 0.0017451 | 0.99914 | 0.0018057 | 1.9256
32 | 0.26821 | 0.12233 | -0.2682 | -0.12348 | 4.6914e-06 | -0.0011492 | 0.0085211 | 0.0085349 | 0.0085349 | 0.99867 | 0.005086 | 0.99866 | 0.0052199 | 3.8795
33 | 0.13475 | 0.058844 | -0.13475 | -0.059437 | 6.0157e-07 | -0.00059278 | 0.0042504 | 0.0042573 | 0.0042573 | 0.99866 | 0.0052199 | 0.99865 | 0.0052504 | 1.9351
34 | -0.084935 | -0.041136 | 0.084935 | 0.04107 | 7.3547e-07 | -6.5552e-05 | 0.0027285 | 0.0027276 | 0.0027285 | 0.99847 | 0.0057574 | 0.99848 | 0.0058147 | 1.2993
35 | 0.14732 | 0.071278 | -0.14732 | -0.071348 | 2.3995e-06 | -7.0285e-05 | 0.0047281 | 0.0047291 | 0.0047291 | 0.99919 | 0.00077557 | 0.99917 | 0.00066799 | 2.2519
36 | -0.13475 | -0.065261 | 0.13475 | 0.064666 | 6.2382e-07 | -0.0005948 | 0.004328 | 0.0043206 | 0.004328 | 0.99861 | 0.0056004 | 0.99861 | 0.0055604 | 1.9673
37 | -0.13475 | -0.064666 | 0.13475 | 0.059437 | 5.3933e-06 | -0.0052291 | 0.0043206 | 0.0042573 | 0.0043206 | 0.99861 | 0.0055604 | 0.99865 | 0.0052504 | 1.9639
38 | -0.094546 | -0.045791 | 0.094547 | 0.0457 | 1.2576e-06 | -9.0386e-05 | 0.0030366 | 0.0030355 | 0.0030366 | 0.99867 | 0.0048601 | 0.99869 | 0.0049481 | 1.446

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 3.6479 | 1.6287

## res_load
| p_mw | q_mvar
0 | 0.93131 | 0.45105
1 | 0.094287 | 0.045665
2 | 0.17109 | 0.082865
3 | 0.34821 | 0.16865
4 | 0.16228 | 0.078598
5 | 0.12865 | 0.062307
6 | 0.091323 | 0.04423
7 | 0.095283 | 0.046148
8 | 0.08995 | 0.043565
9 | 0.13189 | 0.063878
10 | 0.37628 | 0.18224
11 | 0.082344 | 0.039881
12 | 0.12717 | 0.061591
13 | 0.13196 | 0.063913
14 | 0.13345 | 0.064632
15 | 0.084935 | 0.041136
16 | 0.14732 | 0.071348
17 | 0.067519 | 0.032701
18 | 0.13475 | 0.065261
19 | 0.094546 | 0.045791

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1