## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_415_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_415_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_415_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_415_0_node_76 | 20 | n |  | TRUE
4 | bus_MV_415_0_node_145 | 20 | n |  | TRUE
5 | bus_MV_415_0_node_77 | 20 | n |  | TRUE
6 | bus_MV_415_0_node_157 | 20 | n |  | TRUE
7 | bus_MV_415_0_node_158 | 20 | n |  | TRUE
8 | bus_MV_415_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_415_0_node_162 | 20 | n |  | TRUE
10 | bus_MV_415_0_node_4 | 20 | n |  | TRUE
11 | bus_MV_415_0_node_6 | 20 | n |  | TRUE
12 | bus_MV_415_0_node_8 | 20 | n |  | TRUE
13 | bus_MV_415_0_node_9 | 20 | n |  | TRUE
14 | bus_MV_415_0_node_7 | 20 | n |  | TRUE
15 | bus_MV_415_0_node_12 | 20 | n |  | TRUE
16 | bus_MV_415_0_node_10 | 20 | n |  | TRUE
17 | bus_MV_415_0_node_11 | 20 | n |  | TRUE
18 | bus_MV_415_0_node_115 | 20 | n |  | TRUE
19 | bus_MV_415_0_node_27 | 20 | n |  | TRUE
20 | bus_MV_415_0_node_28 | 20 | n |  | TRUE
21 | bus_MV_415_0_node_29 | 20 | n |  | TRUE
22 | bus_MV_415_0_node_16 | 20 | n |  | TRUE
23 | bus_MV_415_0_node_17 | 20 | n |  | TRUE
24 | bus_MV_415_0_node_109 | 20 | n |  | TRUE
25 | bus_MV_415_0_node_18 | 20 | n |  | TRUE
26 | bus_MV_415_0_node_108 | 20 | n |  | TRUE
27 | bus_MV_415_0_node_14 | 20 | n |  | TRUE
28 | bus_MV_415_0_node_143 | 20 | n |  | TRUE
29 | bus_MV_415_0_node_142 | 20 | n |  | TRUE
30 | bus_MV_415_0_node_13 | 20 | n |  | TRUE
31 | bus_MV_415_0_node_15 | 20 | n |  | TRUE
32 | bus_MV_415_0_node_26 | 20 | n |  | TRUE
33 | bus_MV_415_0_node_19 | 20 | n |  | TRUE
34 | bus_MV_415_0_node_21 | 20 | n |  | TRUE
35 | bus_MV_415_0_node_102 | 20 | n |  | TRUE
36 | bus_MV_415_0_node_130 | 20 | n |  | TRUE
37 | bus_MV_415_0_node_20 | 20 | n |  | TRUE
38 | bus_MV_415_0_node_23 | 20 | n |  | TRUE
39 | bus_MV_415_0_node_40 | 20 | n |  | TRUE
40 | bus_MV_415_0_node_140 | 20 | n |  | TRUE
41 | bus_MV_415_0_node_22 | 20 | n |  | TRUE
42 | bus_MV_415_0_node_24 | 20 | n |  | TRUE
43 | bus_MV_415_0_node_101 | 20 | n |  | TRUE
44 | bus_MV_415_0_node_38 | 20 | n |  | TRUE
45 | bus_MV_415_0_node_160 | 20 | n |  | TRUE
46 | bus_MV_415_0_node_25 | 20 | n |  | TRUE
47 | bus_MV_415_0_node_134 | 20 | n |  | TRUE
48 | bus_MV_415_0_node_103 | 20 | n |  | TRUE
49 | bus_MV_415_0_node_110 | 20 | n |  | TRUE
50 | bus_MV_415_0_node_107 | 20 | n |  | TRUE
51 | bus_MV_415_0_node_42 | 20 | n |  | TRUE
52 | bus_MV_415_0_node_44 | 20 | n |  | TRUE
53 | bus_MV_415_0_node_43 | 20 | n |  | TRUE
54 | bus_MV_415_0_node_82 | 20 | n |  | TRUE
55 | bus_MV_415_0_node_129 | 20 | n |  | TRUE
56 | bus_MV_415_0_node_131 | 20 | n |  | TRUE
57 | bus_MV_415_0_node_132 | 20 | n |  | TRUE
58 | bus_MV_415_0_node_78 | 20 | n |  | TRUE
59 | bus_MV_415_0_node_79 | 20 | n |  | TRUE
60 | bus_MV_415_0_node_71 | 20 | n |  | TRUE
61 | bus_MV_415_0_node_133 | 20 | n |  | TRUE
62 | bus_MV_415_0_node_33 | 20 | n |  | TRUE
63 | bus_MV_415_0_node_41 | 20 | n |  | TRUE
64 | bus_MV_415_0_node_83 | 20 | n |  | TRUE
65 | bus_MV_415_0_node_36 | 20 | n |  | TRUE
66 | bus_MV_415_0_node_135 | 20 | n |  | TRUE
67 | bus_MV_415_0_node_30 | 20 | n |  | TRUE
68 | bus_MV_415_0_node_32 | 20 | n |  | TRUE
69 | bus_MV_415_0_node_34 | 20 | n |  | TRUE
70 | bus_MV_415_0_node_113 | 20 | n |  | TRUE
71 | bus_MV_415_0_node_116 | 20 | n |  | TRUE
72 | bus_MV_415_0_node_111 | 20 | n |  | TRUE
73 | bus_MV_415_0_node_35 | 20 | n |  | TRUE
74 | bus_MV_415_0_node_37 | 20 | n |  | TRUE
75 | bus_MV_415_0_node_39 | 20 | n |  | TRUE
76 | bus_MV_415_0_node_161 | 20 | n |  | TRUE
77 | bus_MV_415_0_node_69 | 20 | n |  | TRUE
78 | bus_MV_415_0_node_153 | 20 | n |  | TRUE
79 | bus_MV_415_0_node_68 | 20 | n |  | TRUE
80 | bus_MV_415_0_node_45 | 20 | n |  | TRUE
81 | bus_MV_415_0_node_46 | 20 | n |  | TRUE
82 | bus_MV_415_0_node_106 | 20 | n |  | TRUE
83 | bus_MV_415_0_node_105 | 20 | n |  | TRUE
84 | bus_MV_415_0_node_70 | 20 | n |  | TRUE
85 | bus_MV_415_0_node_80 | 20 | n |  | TRUE
86 | bus_MV_415_0_node_98 | 20 | n |  | TRUE
87 | bus_MV_415_0_node_156 | 20 | n |  | TRUE
88 | bus_MV_415_0_node_81 | 20 | n |  | TRUE
89 | bus_MV_415_0_node_90 | 20 | n |  | TRUE
90 | bus_MV_415_0_node_141 | 20 | n |  | TRUE
91 | bus_MV_415_0_node_136 | 20 | n |  | TRUE
92 | bus_MV_415_0_node_47 | 20 | n |  | TRUE
93 | bus_MV_415_0_node_48 | 20 | n |  | TRUE
94 | bus_MV_415_0_node_49 | 20 | n |  | TRUE
95 | bus_MV_415_0_node_50 | 20 | n |  | TRUE
96 | bus_MV_415_0_node_51 | 20 | n |  | TRUE
97 | bus_MV_415_0_node_53 | 20 | n |  | TRUE
98 | bus_MV_415_0_node_54 | 20 | n |  | TRUE
99 | bus_MV_415_0_node_52 | 20 | n |  | TRUE
100 | bus_MV_415_0_node_58 | 20 | n |  | TRUE
101 | bus_MV_415_0_node_59 | 20 | n |  | TRUE
102 | bus_MV_415_0_node_57 | 20 | n |  | TRUE
103 | bus_MV_415_0_node_104 | 20 | n |  | TRUE
104 | bus_MV_415_0_node_86 | 20 | n |  | TRUE
105 | bus_MV_415_0_node_67 | 20 | n |  | TRUE
106 | bus_MV_415_0_node_64 | 20 | n |  | TRUE
107 | bus_MV_415_0_node_63 | 20 | n |  | TRUE
108 | bus_MV_415_0_node_60 | 20 | n |  | TRUE
109 | bus_MV_415_0_node_62 | 20 | n |  | TRUE
110 | bus_MV_415_0_node_89 | 20 | n |  | TRUE
111 | bus_MV_415_0_node_151 | 20 | n |  | TRUE
112 | bus_MV_415_0_node_61 | 20 | n |  | TRUE
113 | bus_MV_415_0_node_159 | 20 | n |  | TRUE
114 | bus_MV_415_0_node_122 | 20 | n |  | TRUE
115 | bus_MV_415_0_node_84 | 20 | n |  | TRUE
116 | bus_MV_415_0_node_85 | 20 | n |  | TRUE
117 | bus_MV_415_0_node_87 | 20 | n |  | TRUE
118 | bus_MV_415_0_node_88 | 20 | n |  | TRUE
119 | bus_MV_415_0_node_121 | 20 | n |  | TRUE
120 | bus_MV_415_0_node_119 | 20 | n |  | TRUE
121 | bus_MV_415_0_node_149 | 20 | n |  | TRUE
122 | bus_MV_415_0_node_56 | 20 | n |  | TRUE
123 | bus_MV_415_0_node_66 | 20 | n |  | TRUE
124 | bus_MV_415_0_node_65 | 20 | n |  | TRUE
125 | bus_MV_415_0_node_144 | 20 | n |  | TRUE
126 | bus_MV_415_0_node_163 | 20 | n |  | TRUE
127 | bus_MV_415_0_node_152 | 20 | n |  | TRUE
128 | bus_MV_415_0_node_150 | 20 | n |  | TRUE
129 | bus_MV_415_0_node_117 | 20 | n |  | TRUE
130 | bus_MV_415_0_node_118 | 20 | n |  | TRUE
131 | bus_MV_415_0_node_146 | 20 | n |  | TRUE
132 | bus_MV_415_0_node_120 | 20 | n |  | TRUE
133 | bus_MV_415_0_node_72 | 20 | n |  | TRUE
134 | bus_MV_415_0_node_73 | 20 | n |  | TRUE
135 | bus_MV_415_0_node_74 | 20 | n |  | TRUE
136 | bus_MV_415_0_node_75 | 20 | n |  | TRUE
137 | bus_MV_415_0_node_123 | 20 | n |  | TRUE
138 | bus_MV_415_0_node_155 | 20 | n |  | TRUE
139 | bus_MV_415_0_node_124 | 20 | n |  | TRUE
140 | bus_MV_415_0_node_97 | 20 | n |  | TRUE
141 | bus_MV_415_0_node_91 | 20 | n |  | TRUE
142 | bus_MV_415_0_node_92 | 20 | n |  | TRUE
143 | bus_MV_415_0_node_93 | 20 | n |  | TRUE
144 | bus_MV_415_0_node_94 | 20 | n |  | TRUE
145 | bus_MV_415_0_node_95 | 20 | n |  | TRUE
146 | bus_MV_415_0_node_96 | 20 | n |  | TRUE
147 | bus_MV_415_0_node_139 | 20 | n |  | TRUE
148 | bus_MV_415_0_node_100 | 20 | n |  | TRUE
149 | bus_MV_415_0_node_99 | 20 | n |  | TRUE
150 | bus_MV_415_0_node_137 | 20 | n |  | TRUE
151 | bus_MV_415_0_node_112 | 20 | n |  | TRUE
152 | bus_MV_415_0_node_114 | 20 | n |  | TRUE
153 | bus_MV_415_0_node_147 | 20 | n |  | TRUE
154 | bus_MV_415_0_node_125 | 20 | n |  | TRUE
155 | bus_MV_415_0_node_127 | 20 | n |  | TRUE
156 | bus_MV_415_0_node_126 | 20 | n |  | TRUE
157 | bus_MV_415_0_node_128 | 20 | n |  | TRUE
158 | bus_MV_415_0_node_138 | 20 | n |  | TRUE
159 | bus_MV_415_0_node_148 | 20 | n |  | TRUE
160 | bus_HV_415_0_node_22 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_415_0_load_0 | 0 | 0.23809 | 0.11531 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_415_0_load_145 | 4 | 0.093021 | 0.045052 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_415_0_load_157 | 6 | 0.3656 | 0.17707 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_415_0_load_162 | 9 | 0.25692 | 0.12443 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_415_0_load_4 | 10 | 0.29372 | 0.14226 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_415_0_load_6 | 11 | 0.20944 | 0.10144 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_415_0_load_8 | 12 | 0.1327 | 0.064272 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_415_0_load_7 | 14 | 0.1553 | 0.075214 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_415_0_load_10 | 16 | 0.39603 | 0.1918 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_415_0_load_115 | 18 | 0.070257 | 0.034027 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_415_0_load_27 | 19 | 0.14377 | 0.069633 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_415_0_load_109 | 24 | 0.44098 | 0.21358 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_415_0_load_143 | 28 | 0.18498 | 0.089588 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_415_0_load_142 | 29 | 0.16971 | 0.082194 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_415_0_load_13 | 30 | 0.27842 | 0.13484 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_415_0_load_102 | 35 | 0.39677 | 0.19217 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_415_0_load_40 | 39 | 0.33931 | 0.16433 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_415_0_load_140 | 40 | 0.12763 | 0.061816 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_415_0_load_101 | 43 | 0.36464 | 0.1766 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_415_0_load_38 | 44 | 0.20823 | 0.10085 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_415_0_load_160 | 45 | 0.37399 | 0.18113 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_415_0_load_134 | 47 | 0.088445 | 0.042836 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_415_0_load_103 | 48 | 0.35476 | 0.17182 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_415_0_load_107 | 50 | 0.75328 | 0.36483 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_415_0_load_82 | 54 | 0.29216 | 0.1415 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_415_0_load_129 | 55 | 0.076459 | 0.037031 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_415_0_load_132 | 57 | 0.2517 | 0.1219 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_415_0_load_71 | 60 | 0.37952 | 0.18381 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_415_0_load_133 | 61 | 0.24738 | 0.11981 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_415_0_load_83 | 64 | 0.28475 | 0.13791 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_415_0_load_135 | 66 | 0.1089 | 0.05274 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_415_0_load_30 | 67 | 0.2705 | 0.13101 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_415_0_load_113 | 70 | 1.0277 | 0.49773 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_415_0_load_116 | 71 | 0.1207 | 0.058457 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_415_0_load_35 | 73 | 0.26171 | 0.12675 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_415_0_load_161 | 76 | 0.32165 | 0.15578 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_415_0_load_68 | 79 | 0.28708 | 0.13904 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_415_0_load_105 | 83 | 0.26477 | 0.12824 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_415_0_load_70 | 84 | 0.35379 | 0.17135 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_415_0_load_98 | 86 | 0.093061 | 0.045071 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_415_0_load_156 | 87 | 0.35357 | 0.17124 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_415_0_load_90 | 89 | 0.27751 | 0.13441 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_415_0_load_141 | 90 | 0.30769 | 0.14902 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_415_0_load_136 | 91 | 0.26943 | 0.13049 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_415_0_load_47 | 92 | 0.17138 | 0.083003 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_415_0_load_53 | 97 | 0.16589 | 0.080346 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_415_0_load_54 | 98 | 0.29435 | 0.14256 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_415_0_load_57 | 102 | 0.14222 | 0.068882 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_415_0_load_104 | 103 | 0.40888 | 0.19803 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_415_0_load_86 | 104 | 0.082712 | 0.040059 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_415_0_load_64 | 106 | 0.076307 | 0.036957 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_415_0_load_63 | 107 | 0.15965 | 0.077321 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_415_0_load_89 | 110 | 0.30802 | 0.14918 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_415_0_load_151 | 111 | 0.3675 | 0.17799 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_415_0_load_159 | 113 | 0.068728 | 0.033287 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_415_0_load_122 | 114 | 0.16292 | 0.078906 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_415_0_load_84 | 115 | 0.31857 | 0.15429 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_415_0_load_88 | 118 | 0.096442 | 0.046709 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_415_0_load_149 | 121 | 0.16503 | 0.079928 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_415_0_load_65 | 124 | 0.24039 | 0.11643 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_415_0_load_144 | 125 | 0.082828 | 0.040116 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_415_0_load_163 | 126 | 0.31984 | 0.15491 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_415_0_load_117 | 129 | 0.078388 | 0.037965 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_415_0_load_118 | 130 | 0.09366 | 0.045362 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_415_0_load_120 | 132 | 0.41443 | 0.20072 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_415_0_load_72 | 133 | 0.21707 | 0.10513 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_415_0_load_123 | 137 | 0.10384 | 0.05029 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_415_0_load_155 | 138 | 0.40134 | 0.19438 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_415_0_load_124 | 139 | 0.17518 | 0.084843 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_415_0_load_97 | 140 | 0.18851 | 0.0913 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_415_0_load_91 | 141 | 0.27627 | 0.13381 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_415_0_load_94 | 144 | 0.51731 | 0.25054 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_415_0_load_95 | 145 | 0.18614 | 0.09015 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_415_0_load_96 | 146 | 0.40425 | 0.19579 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_415_0_load_100 | 148 | 0.15584 | 0.075477 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_415_0_load_112 | 151 | 0.58765 | 0.28461 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_415_0_load_114 | 152 | 0.61972 | 0.30014 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_415_0_load_147 | 153 | 0.10358 | 0.050168 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_415_0_load_127 | 155 | 0.12136 | 0.058778 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_415_0_load_126 | 156 | 0.17553 | 0.085011 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_415_0_load_128 | 157 | 0.16454 | 0.07969 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_415_0_load_148 | 159 | 0.58636 | 0.28399 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_415_0_line_0 |  | 0 | 1 | 0.09137 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_415_0_line_1 |  | 1 | 2 | 1.2182 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_415_0_line_2 |  | 1 | 3 | 0.99376 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_415_0_line_3 |  | 2 | 6 | 0.028845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_415_0_line_4 |  | 2 | 7 | 0.50596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_415_0_line_5 |  | 2 | 8 | 0.60031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_415_0_line_6 |  | 3 | 4 | 0.032657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_415_0_line_7 |  | 3 | 5 | 0.42027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_415_0_line_8 |  | 5 | 138 | 0.033146 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_415_0_line_9 |  | 5 | 135 | 0.42875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_415_0_line_10 |  | 7 | 9 | 0.096944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_415_0_line_11 |  | 8 | 10 | 0.056432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_415_0_line_12 |  | 11 | 12 | 0.03458 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_415_0_line_13 |  | 11 | 13 | 0.11284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_415_0_line_14 |  | 11 | 14 | 0.05858 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_415_0_line_15 |  | 13 | 15 | 0.027963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_415_0_line_16 |  | 14 | 16 | 0.1811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_415_0_line_17 |  | 15 | 18 | 0.12727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_415_0_line_18 |  | 16 | 17 | 0.03416 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_415_0_line_19 |  | 17 | 22 | 0.22953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_415_0_line_20 |  | 17 | 23 | 0.16636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_415_0_line_21 |  | 18 | 21 | 0.0069895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_415_0_line_22 |  | 19 | 20 | 0.06031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_415_0_line_23 |  | 20 | 21 | 0.080027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_415_0_line_24 |  | 22 | 24 | 0.03658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_415_0_line_25 |  | 22 | 25 | 0.38686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_415_0_line_26 |  | 22 | 26 | 0.011964 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_415_0_line_27 |  | 22 | 27 | 0.16039 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
28 | MV_415_0_line_28 |  | 23 | 29 | 0.027474 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_415_0_line_29 |  | 24 | 49 | 0.020093 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_415_0_line_30 |  | 25 | 28 | 0.023695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_415_0_line_31 |  | 26 | 50 | 0.011379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_415_0_line_32 |  | 27 | 30 | 0.006356 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_415_0_line_33 |  | 30 | 31 | 0.048425 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
34 | MV_415_0_line_34 |  | 31 | 32 | 0.1981 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
35 | MV_415_0_line_35 |  | 32 | 48 | 0.011576 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_415_0_line_36 |  | 32 | 33 | 0.38514 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
37 | MV_415_0_line_37 |  | 32 | 46 | 0.04121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_415_0_line_38 |  | 33 | 34 | 0.38923 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
39 | MV_415_0_line_39 |  | 33 | 35 | 0.033228 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_415_0_line_40 |  | 33 | 36 | 0.21327 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
41 | MV_415_0_line_41 |  | 34 | 40 | 0.016648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_415_0_line_42 |  | 34 | 37 | 0.19365 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
43 | MV_415_0_line_43 |  | 36 | 56 | 0.10958 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
44 | MV_415_0_line_44 |  | 36 | 55 | 0.050699 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_415_0_line_45 |  | 37 | 38 | 0.2855 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
46 | MV_415_0_line_46 |  | 37 | 39 | 0.010326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_415_0_line_47 |  | 38 | 42 | 0.09277 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
48 | MV_415_0_line_48 |  | 38 | 44 | 0.00060365 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
49 | MV_415_0_line_49 |  | 39 | 63 | 0.01085 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_415_0_line_50 |  | 41 | 42 | 0.35258 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
51 | MV_415_0_line_51 |  | 41 | 43 | 0.035638 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_415_0_line_52 |  | 42 | 45 | 0.031705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_415_0_line_53 |  | 44 | 65 | 0.021713 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
54 | MV_415_0_line_54 |  | 46 | 47 | 0.024204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_415_0_line_55 |  | 47 | 66 | 0.027793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_415_0_line_56 |  | 49 | 72 | 0.011437 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_415_0_line_57 |  | 49 | 151 | 0.049137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_415_0_line_58 |  | 51 | 52 | 0.39777 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
59 | MV_415_0_line_59 |  | 51 | 53 | 0.5928 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
60 | MV_415_0_line_60 |  | 51 | 54 | 0.038657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_415_0_line_61 |  | 52 | 61 | 0.024411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_415_0_line_62 |  | 52 | 62 | 0.26773 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
63 | MV_415_0_line_63 |  | 53 | 58 | 0.20585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_415_0_line_64 |  | 53 | 59 | 0.95293 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
65 | MV_415_0_line_65 |  | 53 | 60 | 0.027156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_415_0_line_66 |  | 54 | 87 | 0.23873 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_415_0_line_67 |  | 56 | 57 | 0.063632 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
68 | MV_415_0_line_68 |  | 57 | 62 | 0.029104 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
69 | MV_415_0_line_69 |  | 58 | 64 | 0.002794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_415_0_line_70 |  | 59 | 85 | 0.39617 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_415_0_line_71 |  | 59 | 86 | 0.016837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_415_0_line_72 |  | 63 | 80 | 0.055206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_415_0_line_73 |  | 63 | 81 | 0.22577 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_415_0_line_74 |  | 65 | 73 | 0.008549 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
75 | MV_415_0_line_75 |  | 67 | 68 | 0.040913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_415_0_line_76 |  | 68 | 69 | 0.15909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_415_0_line_77 |  | 69 | 70 | 0.041602 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_415_0_line_78 |  | 69 | 71 | 0.026658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_415_0_line_79 |  | 70 | 72 | 0.058052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_415_0_line_80 |  | 73 | 74 | 0.05264 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_415_0_line_81 |  | 74 | 75 | 0.31445 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
82 | MV_415_0_line_82 |  | 75 | 76 | 0.038164 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
83 | MV_415_0_line_83 |  | 75 | 77 | 0.085032 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_415_0_line_84 |  | 76 | 78 | 0.037427 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
85 | MV_415_0_line_85 |  | 77 | 79 | 0.036265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_415_0_line_86 |  | 78 | 128 | 0.27765 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
87 | MV_415_0_line_87 |  | 80 | 82 | 0.48222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_415_0_line_88 |  | 80 | 83 | 0.019808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_415_0_line_89 |  | 81 | 84 | 0.06155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_415_0_line_90 |  | 82 | 91 | 0.032886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_415_0_line_91 |  | 85 | 88 | 0.22788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_415_0_line_92 |  | 85 | 89 | 0.028398 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_415_0_line_93 |  | 86 | 140 | 0.037956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_415_0_line_94 |  | 88 | 90 | 0.041662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_415_0_line_95 |  | 89 | 135 | 0.024073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_415_0_line_96 |  | 91 | 150 | 0.047378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_415_0_line_97 |  | 92 | 93 | 0.081622 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_415_0_line_98 |  | 93 | 94 | 0.29349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_415_0_line_99 |  | 93 | 95 | 0.68364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_415_0_line_100 |  | 93 | 96 | 0.30693 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_415_0_line_101 |  | 93 | 97 | 0.031038 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_415_0_line_102 |  | 94 | 98 | 0.067548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_415_0_line_103 |  | 95 | 99 | 0.26749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_415_0_line_104 |  | 96 | 100 | 0.28596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_415_0_line_105 |  | 96 | 101 | 0.28517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_415_0_line_106 |  | 96 | 102 | 0.064535 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_415_0_line_107 |  | 97 | 104 | 0.38538 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_415_0_line_108 |  | 98 | 105 | 1.179 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_415_0_line_109 |  | 99 | 103 | 0.035261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_415_0_line_110 |  | 100 | 106 | 0.0098164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_415_0_line_111 |  | 100 | 107 | 0.038878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_415_0_line_112 |  | 101 | 108 | 0.11306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_415_0_line_113 |  | 101 | 109 | 0.37137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_415_0_line_114 |  | 101 | 110 | 0.046721 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
115 | MV_415_0_line_115 |  | 104 | 115 | 0.024131 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_415_0_line_116 |  | 105 | 121 | 0.053349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_415_0_line_117 |  | 108 | 111 | 0.080194 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_415_0_line_118 |  | 109 | 114 | 0.0033793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_415_0_line_119 |  | 109 | 112 | 0.078723 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_415_0_line_120 |  | 111 | 128 | 0.057265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_415_0_line_121 |  | 112 | 113 | 0.013585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_415_0_line_122 |  | 115 | 116 | 0.039311 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
123 | MV_415_0_line_123 |  | 116 | 117 | 0.006684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_415_0_line_124 |  | 117 | 118 | 0.042044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_415_0_line_125 |  | 118 | 119 | 0.050652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_415_0_line_126 |  | 119 | 120 | 0.54648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_415_0_line_127 |  | 120 | 130 | 0.022596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_415_0_line_128 |  | 122 | 123 | 0.33657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_415_0_line_129 |  | 122 | 124 | 0.03104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_415_0_line_130 |  | 123 | 125 | 0.12737 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
131 | MV_415_0_line_131 |  | 124 | 126 | 0.30289 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
132 | MV_415_0_line_132 |  | 126 | 127 | 0.028916 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
133 | MV_415_0_line_133 |  | 127 | 128 | 0.19558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_415_0_line_134 |  | 129 | 130 | 0.024393 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_415_0_line_135 |  | 129 | 131 | 0.57319 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_415_0_line_136 |  | 130 | 132 | 0.04036 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_415_0_line_137 |  | 131 | 153 | 0.007379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_415_0_line_138 |  | 133 | 134 | 0.048241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_415_0_line_139 |  | 134 | 135 | 0.36075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_415_0_line_140 |  | 135 | 136 | 0.05005 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_415_0_line_141 |  | 136 | 137 | 0.027936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_415_0_line_142 |  | 137 | 139 | 0.024223 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_415_0_line_143 |  | 139 | 154 | 0.010966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_415_0_line_144 |  | 139 | 155 | 0.022683 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_415_0_line_145 |  | 139 | 156 | 0.045739 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_415_0_line_146 |  | 140 | 149 | 0.057385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_415_0_line_147 |  | 141 | 142 | 0.037885 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
148 | MV_415_0_line_148 |  | 142 | 143 | 0.012618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_415_0_line_149 |  | 142 | 144 | 0.03871 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_415_0_line_150 |  | 143 | 145 | 0.018536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_415_0_line_151 |  | 144 | 146 | 0.014644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_415_0_line_152 |  | 145 | 147 | 0.017214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_415_0_line_153 |  | 147 | 148 | 0.0091947 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_415_0_line_154 |  | 148 | 149 | 0.015471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_415_0_line_155 |  | 150 | 158 | 0.048565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_415_0_line_156 |  | 151 | 152 | 0.026837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_415_0_line_157 |  | 154 | 157 | 0.03095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_415_0_line_158 |  | 158 | 159 | 0.060675 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_415_0_trafo_22 | 25 MVA 110/20 kV | 160 | 41 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2599109.4861 | 1205899.7416
1 | 2599187.1876 | 1205851.67
2 | 2598239.9028 | 1205466.0753
3 | 2599968.9315 | 1205238.126
4 | 2599976.7955 | 1205206.4308
5 | 2600237.4115 | 1205285.531
6 | 2598222.8811 | 1205489.3933
7 | 2598003.4137 | 1205861.1794
8 | 2597863.6262 | 1205189.8855
9 | 2597939.1472 | 1205788.5735
10 | 2597813.5394 | 1205165.9689
11 | 2602064.7487 | 1206014.6149
12 | 2602098.0479 | 1206005.2917
13 | 2602102.6231 | 1206120.719
14 | 2602048.8943 | 1205958.2215
15 | 2602114.2041 | 1206146.1813
16 | 2601991.9693 | 1205786.3227
17 | 2601973.7233 | 1205758.5453
18 | 2602183.086 | 1206252.9208
19 | 2602191.2079 | 1206344.2943
20 | 2602243.3016 | 1206315.7529
21 | 2602187.0634 | 1206258.6682
22 | 2601804.1917 | 1205716.0594
23 | 2601926.124 | 1205654.1622
24 | 2601784.548 | 1205746.7067
25 | 2601810.6194 | 1205946.7206
26 | 2601802.1797 | 1205704.4525
27 | 2601800.155 | 1205605.1088
28 | 2601812.1699 | 1205923.7863
29 | 2601933.9962 | 1205627.8392
30 | 2601806.164 | 1205602.9871
31 | 2601789.7113 | 1205557.4353
32 | 2601734.2091 | 1205410.7395
33 | 2601480.738 | 1205394.0208
34 | 2601664.2287 | 1205184.3526
35 | 2601472.1435 | 1205361.9235
36 | 2601328.8583 | 1205543.7463
37 | 2601572.9417 | 1205123.7959
38 | 2601350.5301 | 1205171.8148
39 | 2601567.9391 | 1205114.7564
40 | 2601655.9876 | 1205169.887
41 | 2601238.474 | 1205311.1233
42 | 2601319.6592 | 1205198.9897
43 | 2601239.234 | 1205275.4929
44 | 2601350.359 | 1205171.2358
45 | 2601316.7215 | 1205171.5074
46 | 2601747.024 | 1205385.9963
47 | 2601742.2219 | 1205362.3396
48 | 2601728.2262 | 1205400.8214
49 | 2601774.1295 | 1205763.888
50 | 2601793.8491 | 1205696.7287
51 | 2600945.6133 | 1205404.791
52 | 2600958.6097 | 1205621.211
53 | 2600703.8951 | 1205489.1176
54 | 2600947.3683 | 1205366.1813
55 | 2601291.9678 | 1205553.084
56 | 2601313.7064 | 1205588.1451
57 | 2601253.7558 | 1205609.956
58 | 2600603.8754 | 1205643.0808
59 | 2600481.1295 | 1205898.5884
60 | 2600715.8613 | 1205464.7278
61 | 2600948.6649 | 1205599.9757
62 | 2601226.3362 | 1205619.9338
63 | 2601577.5013 | 1205109.5782
64 | 2600603.7382 | 1205645.8712
65 | 2601344.2065 | 1205150.4129
66 | 2601738.4187 | 1205334.8084
67 | 2601600.5339 | 1205697.5158
68 | 2601577.8234 | 1205731.5842
69 | 2601719.9008 | 1205803.1497
70 | 2601757.3589 | 1205821.4702
71 | 2601707.8836 | 1205826.9453
72 | 2601783.931 | 1205769.8273
73 | 2601341.6221 | 1205142.2634
74 | 2601328.3603 | 1205091.3217
75 | 2601277.6955 | 1204905.7769
76 | 2601239.4205 | 1204905.5247
77 | 2601354.0086 | 1204876.7659
78 | 2601203.1171 | 1204896.4239
79 | 2601388.7948 | 1204866.7569
80 | 2601618.8728 | 1205101.6178
81 | 2601615.1237 | 1204893.081
82 | 2601900.2707 | 1205092.0811
83 | 2601633.9439 | 1205088.7147
84 | 2601673.9889 | 1204876.7493
85 | 2600362.3214 | 1205620.374
86 | 2600489.6884 | 1205913.0873
87 | 2600947.9433 | 1205127.4513
88 | 2600306.5307 | 1205742.616
89 | 2600352.7094 | 1205593.6478
90 | 2600324.7968 | 1205718.8421
91 | 2601926.3628 | 1205111.6132
92 | 2601397.5269 | 1204044.9898
93 | 2601392.7542 | 1204126.4552
94 | 2601260.935 | 1204237.8547
95 | 2601448.0184 | 1203975.2189
96 | 2601378.9026 | 1204432.952
97 | 2601423.0527 | 1204133.1878
98 | 2601231.5213 | 1204298.6375
99 | 2601466.8179 | 1203709.2789
100 | 2601419.8632 | 1204377.9423
101 | 2601432.7195 | 1204609.3044
102 | 2601330.9195 | 1204389.796
103 | 2601486.7964 | 1203692.5224
104 | 2601808.3926 | 1204138.7572
105 | 2600115.8798 | 1203917.2179
106 | 2601414.9053 | 1204369.4699
107 | 2601458.8336 | 1204379.2297
108 | 2601337.772 | 1204647.5043
109 | 2601541.7733 | 1204809.8505
110 | 2601439.2659 | 1204655.5644
111 | 2601269.5849 | 1204689.7132
112 | 2601547.5725 | 1204858.9231
113 | 2601542.5568 | 1204871.551
114 | 2601544.4969 | 1204807.8501
115 | 2601818.859 | 1204117.004
116 | 2601852.0208 | 1204138.1141
117 | 2601858.0373 | 1204141.062
118 | 2601895.7966 | 1204159.5539
119 | 2601941.2866 | 1204181.8318
120 | 2602208.2499 | 1204474.9696
121 | 2600099.0749 | 1203867.5686
122 | 2600771.1652 | 1204527.0233
123 | 2600552.6697 | 1204302.6353
124 | 2600787.3329 | 1204500.8665
125 | 2600425.8446 | 1204290.8422
126 | 2601058.9059 | 1204634.9893
127 | 2601066.6068 | 1204662.8613
128 | 2601220.737 | 1204719.7644
129 | 2602229.6134 | 1204465.5944
130 | 2602225.5122 | 1204489.606
131 | 2602789.4235 | 1204342.4895
132 | 2602221.2922 | 1204529.7445
133 | 2600449.1597 | 1205387.0515
134 | 2600420.8497 | 1205412.8528
135 | 2600344.3216 | 1205571.0796
136 | 2600306.7423 | 1205585.6859
137 | 2600283.8203 | 1205601.6546
138 | 2600212.8603 | 1205263.2627
139 | 2600263.9453 | 1205615.5007
140 | 2600506.1239 | 1205946.8387
141 | 2600370.9152 | 1205930.4103
142 | 2600401.8665 | 1205952.2572
143 | 2600413.1368 | 1205957.9943
144 | 2600431.6082 | 1205927.4807
145 | 2600429.3029 | 1205967.0622
146 | 2600442.8596 | 1205918.1077
147 | 2600444.3162 | 1205975.4835
148 | 2600452.5174 | 1205979.6407
149 | 2600466.3166 | 1205986.6355
150 | 2601946.6105 | 1205153.918
151 | 2601731.7151 | 1205739.0792
152 | 2601708.549 | 1205725.5316
153 | 2602792.3401 | 1204335.7093
154 | 2600272.2276 | 1205616.0346
155 | 2600245.2599 | 1205628.3602
156 | 2600234.1327 | 1205580.8131
157 | 2600297.6814 | 1205598.4283
158 | 2601945.1885 | 1205201.3101
159 | 2601887.1834 | 1205182.971
160 | 2601238.474 | 1205311.1233

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98605 | -0.11166 | 0.23809 | 0.11531
1 | 0.98609 | -0.11139 | 0 | 0
2 | 0.98467 | -0.10115 | 0 | 0
3 | 0.98829 | -0.092028 | 0 | 0
4 | 0.98829 | -0.091992 | 0.093021 | 0.045052
5 | 0.98896 | -0.096686 | 0 | 0
6 | 0.98466 | -0.10102 | 0.3656 | 0.17707
7 | 0.9845 | -0.099817 | 0 | 0
8 | 0.98444 | -0.099301 | 0 | 0
9 | 0.98447 | -0.099517 | 0.25692 | 0.12443
10 | 0.98442 | -0.099099 | 0.29372 | 0.14226
11 | 0.99477 | -0.021364 | 0.20944 | 0.10144
12 | 0.99477 | -0.021309 | 0.1327 | 0.064272
13 | 0.99474 | -0.021134 | 0 | 0
14 | 0.99483 | -0.020912 | 0.1553 | 0.075214
15 | 0.99473 | -0.021073 | 0 | 0
16 | 0.995 | -0.02232 | 0.39603 | 0.1918
17 | 0.99505 | -0.022743 | 0 | 0
18 | 0.9947 | -0.020785 | 0.070257 | 0.034027
19 | 0.99467 | -0.020545 | 0.14377 | 0.069633
20 | 0.99468 | -0.020647 | 0 | 0
21 | 0.9947 | -0.020774 | 0 | 0
22 | 0.99542 | -0.025944 | 0 | 0
23 | 0.99501 | -0.02243 | 0 | 0
24 | 0.99528 | -0.024614 | 0.44098 | 0.21358
25 | 0.99533 | -0.025207 | 0 | 0
26 | 0.99541 | -0.025835 | 0 | 0
27 | 0.99588 | -0.020977 | 0 | 0
28 | 0.99532 | -0.025155 | 0.18498 | 0.089588
29 | 0.995 | -0.022374 | 0.16971 | 0.082194
30 | 0.99589 | -0.020955 | 0.27842 | 0.13484
31 | 0.99593 | -0.020776 | 0 | 0
32 | 0.99611 | -0.020025 | 0 | 0
33 | 0.9965 | -0.01833 | 0 | 0
34 | 0.99734 | -0.013954 | 0 | 0
35 | 0.99648 | -0.018172 | 0.39677 | 0.19217
36 | 0.99601 | -0.04687 | 0 | 0
37 | 0.99777 | -0.011712 | 0 | 0
38 | 0.99848 | -0.0079923 | 0 | 0
39 | 0.99774 | -0.011504 | 0.33931 | 0.16433
40 | 0.99734 | -0.013928 | 0.12763 | 0.061816
41 | 1 | 0 | -21.6221 | -9.6861
42 | 0.99879 | -0.006357 | 0 | 0
43 | 0.99997 | -0.0001571 | 0.36464 | 0.1766
44 | 0.99848 | -0.007995 | 0.20823 | 0.10085
45 | 0.99878 | -0.0062156 | 0.37399 | 0.18113
46 | 0.9961 | -0.019932 | 0 | 0
47 | 0.99609 | -0.019875 | 0.088445 | 0.042836
48 | 0.99611 | -0.019976 | 0.35476 | 0.17182
49 | 0.99521 | -0.023989 | 0 | 0
50 | 0.9954 | -0.025732 | 0.75328 | 0.36483
51 | 0.9948 | -0.084483 | 0 | 0
52 | 0.99521 | -0.082255 | 0 | 0
53 | 0.99425 | -0.087304 | 0 | 0
54 | 0.99477 | -0.084183 | 0.29216 | 0.1415
55 | 0.99601 | -0.046825 | 0.076459 | 0.037031
56 | 0.99589 | -0.047547 | 0 | 0
57 | 0.99582 | -0.047936 | 0.2517 | 0.1219
58 | 0.99418 | -0.086628 | 0 | 0
59 | 0.99166 | -0.11743 | 0 | 0
60 | 0.99424 | -0.08718 | 0.37952 | 0.18381
61 | 0.9952 | -0.082182 | 0.24738 | 0.11981
62 | 0.99579 | -0.048108 | 0 | 0
63 | 0.99772 | -0.011329 | 0 | 0
64 | 0.99418 | -0.086618 | 0.28475 | 0.13791
65 | 0.99846 | -0.0080885 | 0 | 0
66 | 0.99609 | -0.01984 | 0.1089 | 0.05274
67 | 0.99499 | -0.022026 | 0.2705 | 0.13101
68 | 0.99501 | -0.022158 | 0 | 0
69 | 0.99506 | -0.022649 | 0 | 0
70 | 0.99508 | -0.02283 | 1.0277 | 0.49773
71 | 0.99506 | -0.022611 | 0.1207 | 0.058457
72 | 0.99519 | -0.023799 | 0 | 0
73 | 0.99845 | -0.0081252 | 0.26171 | 0.12675
74 | 0.99841 | -0.0083416 | 0 | 0
75 | 0.99816 | -0.0095812 | 0 | 0
76 | 0.99813 | -0.0097183 | 0.32165 | 0.15578
77 | 0.99813 | -0.0092983 | 0 | 0
78 | 0.99794 | -0.014619 | 0 | 0
79 | 0.99812 | -0.0091743 | 0.28708 | 0.13904
80 | 0.99765 | -0.010645 | 0 | 0
81 | 0.99762 | -0.010428 | 0 | 0
82 | 0.99712 | -0.005998 | 0 | 0
83 | 0.99764 | -0.010583 | 0.26477 | 0.12824
84 | 0.9976 | -0.010169 | 0.35379 | 0.17135
85 | 0.99005 | -0.1047 | 0 | 0
86 | 0.99162 | -0.11706 | 0.093061 | 0.045071
87 | 0.99461 | -0.085217 | 0.35357 | 0.17124
88 | 0.98996 | -0.1039 | 0 | 0
89 | 0.98994 | -0.10388 | 0.27751 | 0.13441
90 | 0.98994 | -0.10375 | 0.30769 | 0.14902
91 | 0.99709 | -0.005668 | 0.26943 | 0.13049
92 | 0.99408 | -0.0037849 | 0.17138 | 0.083003
93 | 0.9941 | -0.0039491 | 0 | 0
94 | 0.99393 | -0.0024621 | 0 | 0
95 | 0.99375 | -0.0012343 | 0 | 0
96 | 0.99503 | -0.011689 | 0 | 0
97 | 0.99402 | -0.0045122 | 0.16589 | 0.080346
98 | 0.99389 | -0.0021012 | 0.29435 | 0.14256
99 | 0.99361 | 2.2135e-05 | 0 | 0
100 | 0.99495 | -0.010957 | 0 | 0
101 | 0.99604 | -0.019894 | 0 | 0
102 | 0.99502 | -0.011802 | 0.14222 | 0.068882
103 | 0.99359 | 0.00019591 | 0.40888 | 0.19803
104 | 0.99313 | -0.01072 | 0.082712 | 0.040059
105 | 0.99351 | -0.0046807 | 0 | 0
106 | 0.99495 | -0.010948 | 0.076307 | 0.036957
107 | 0.99494 | -0.010884 | 0.15965 | 0.077321
108 | 0.99652 | -0.023762 | 0 | 0
109 | 0.99593 | -0.019015 | 0 | 0
110 | 0.99601 | -0.020069 | 0.30802 | 0.14918
111 | 0.99703 | -0.019893 | 0.3675 | 0.17799
112 | 0.99592 | -0.018956 | 0 | 0
113 | 0.99592 | -0.018945 | 0.068728 | 0.033287
114 | 0.99593 | -0.019009 | 0.16292 | 0.078906
115 | 0.9931 | -0.010424 | 0.31857 | 0.15429
116 | 0.99304 | -0.010861 | 0 | 0
117 | 0.99303 | -0.010805 | 0 | 0
118 | 0.99299 | -0.010449 | 0.096442 | 0.046709
119 | 0.99295 | -0.010075 | 0 | 0
120 | 0.99246 | -0.0057945 | 0 | 0
121 | 0.9935 | -0.0045761 | 0.16503 | 0.079928
122 | 0.99691 | -0.022388 | 0 | 0
123 | 0.99687 | -0.022142 | 0 | 0
124 | 0.99691 | -0.022402 | 0.24039 | 0.11643
125 | 0.99685 | -0.022271 | 0.082828 | 0.040116
126 | 0.9971 | -0.020977 | 0.31984 | 0.15491
127 | 0.99713 | -0.020729 | 0 | 0
128 | 0.99729 | -0.022097 | 0 | 0
129 | 0.99244 | -0.0055555 | 0.078388 | 0.037965
130 | 0.99244 | -0.0056077 | 0.09366 | 0.045362
131 | 0.99232 | -0.0063093 | 0 | 0
132 | 0.99241 | -0.005813 | 0.41443 | 0.20072
133 | 0.98975 | -0.1023 | 0.21707 | 0.10513
134 | 0.98976 | -0.10242 | 0 | 0
135 | 0.98986 | -0.10325 | 0 | 0
136 | 0.98982 | -0.10281 | 0 | 0
137 | 0.98979 | -0.10256 | 0.10384 | 0.05029
138 | 0.98894 | -0.09685 | 0.40134 | 0.19438
139 | 0.98977 | -0.10238 | 0.17518 | 0.084843
140 | 0.99154 | -0.11627 | 0.18851 | 0.0913
141 | 0.99128 | -0.11416 | 0.27627 | 0.13381
142 | 0.9913 | -0.11403 | 0 | 0
143 | 0.99132 | -0.11422 | 0 | 0
144 | 0.99125 | -0.1136 | 0.51731 | 0.25054
145 | 0.99135 | -0.11448 | 0.18614 | 0.09015
146 | 0.99125 | -0.11353 | 0.40425 | 0.19579
147 | 0.99138 | -0.11477 | 0 | 0
148 | 0.99139 | -0.11492 | 0.15584 | 0.075477
149 | 0.99143 | -0.11521 | 0 | 0
150 | 0.99705 | -0.0053433 | 0 | 0
151 | 0.99513 | -0.023276 | 0.58765 | 0.28461
152 | 0.99511 | -0.023076 | 0.61972 | 0.30014
153 | 0.99232 | -0.0063001 | 0.10358 | 0.050168
154 | 0.98977 | -0.10236 | 0 | 0
155 | 0.98976 | -0.10241 | 0.12136 | 0.058778
156 | 0.98975 | -0.10248 | 0.17553 | 0.085011
157 | 0.98976 | -0.10229 | 0.16454 | 0.07969
158 | 0.99701 | -0.0050069 | 0 | 0
159 | 0.99697 | -0.0045815 | 0.58636 | 0.28399
160 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.23809 | -0.11531 | 0.2381 | 0.11521 | 9.7628e-06 | -9.9945e-05 | 0.0077447 | 0.0077434 | 0.0077447 | 0.98605 | -0.11166 | 0.98609 | -0.11139 | 3.688
1 | 0.91777 | 0.38615 | -0.91638 | -0.41397 | 0.0013972 | -0.027827 | 0.029149 | 0.029479 | 0.029479 | 0.98609 | -0.11139 | 0.98467 | -0.10115 | 13.3998
2 | -1.1559 | -0.50136 | 1.1583 | 0.50171 | 0.0024078 | 0.00035202 | 0.036884 | 0.03687 | 0.036884 | 0.98609 | -0.11139 | 0.98829 | -0.092028 | 17.5637
3 | 0.3656 | 0.1764 | -0.3656 | -0.17707 | 5.4577e-06 | -0.00066612 | 0.011901 | 0.011909 | 0.011909 | 0.98467 | -0.10115 | 0.98466 | -0.10102 | 5.4133
4 | 0.25697 | 0.11049 | -0.25693 | -0.12219 | 4.6195e-05 | -0.011697 | 0.0082006 | 0.0083422 | 0.0083422 | 0.98467 | -0.10115 | 0.9845 | -0.099817 | 3.7919
5 | 0.2938 | 0.12708 | -0.29373 | -0.14095 | 7.183e-05 | -0.013873 | 0.0093845 | 0.0095536 | 0.0095536 | 0.98467 | -0.10115 | 0.98444 | -0.099301 | 4.3425
6 | 0.093022 | 0.044291 | -0.093021 | -0.045052 | 3.9609e-07 | -0.00076145 | 0.0030094 | 0.003019 | 0.003019 | 0.98829 | -0.092028 | 0.98829 | -0.091992 | 1.3723
7 | -1.2513 | -0.546 | 1.2522 | 0.53646 | 0.00088968 | -0.0095437 | 0.039878 | 0.039764 | 0.039878 | 0.98829 | -0.092028 | 0.98896 | -0.096686 | 18.1263
8 | 0.40135 | 0.19435 | -0.40134 | -0.19438 | 1.0006e-05 | -3.2432e-05 | 0.013017 | 0.013017 | 0.013017 | 0.98896 | -0.096686 | 0.98894 | -0.09685 | 6.1986
9 | -1.6535 | -0.7308 | 1.6551 | 0.72125 | 0.0015904 | -0.0095495 | 0.05277 | 0.052653 | 0.05277 | 0.98896 | -0.096686 | 0.98986 | -0.10325 | 23.9865
10 | 0.25693 | 0.12219 | -0.25692 | -0.12443 | 9.0373e-06 | -0.0022407 | 0.0083422 | 0.0083707 | 0.0083707 | 0.9845 | -0.099817 | 0.98447 | -0.099517 | 3.8048
11 | 0.29373 | 0.14095 | -0.29372 | -0.14226 | 6.888e-06 | -0.0013037 | 0.0095536 | 0.0095702 | 0.0095702 | 0.98444 | -0.099301 | 0.98442 | -0.099099 | 4.3501
12 | 0.13271 | 0.063455 | -0.1327 | -0.064272 | 8.4318e-07 | -0.00081676 | 0.0042686 | 0.0042789 | 0.0042789 | 0.99477 | -0.021364 | 0.99477 | -0.021309 | 1.945
13 | 0.21405 | 0.093853 | -0.21405 | -0.096517 | 6.9617e-06 | -0.0026639 | 0.0067825 | 0.0068139 | 0.0068139 | 0.99477 | -0.021364 | 0.99474 | -0.021134 | 3.0972
14 | -0.5562 | -0.25874 | 0.55623 | 0.2587 | 3.3073e-05 | -4.8492e-05 | 0.017801 | 0.017801 | 0.017801 | 0.99477 | -0.021364 | 0.99483 | -0.020912 | 8.4769
15 | 0.21405 | 0.096517 | -0.21404 | -0.097177 | 1.7352e-06 | -0.00066012 | 0.0068139 | 0.0068218 | 0.0068218 | 0.99474 | -0.021134 | 0.99473 | -0.021073 | 3.1008
16 | -0.71153 | -0.33391 | 0.71165 | 0.32967 | 0.00012547 | -0.0042428 | 0.022807 | 0.022755 | 0.022807 | 0.99483 | -0.020912 | 0.995 | -0.02232 | 10.3669
17 | 0.21404 | 0.097177 | -0.21404 | -0.10018 | 7.949e-06 | -0.0030043 | 0.0068218 | 0.0068584 | 0.0068584 | 0.99473 | -0.021073 | 0.9947 | -0.020785 | 3.1174
18 | -1.1077 | -0.52147 | 1.1077 | 0.52068 | 5.7521e-05 | -0.00079046 | 0.03552 | 0.03551 | 0.03552 | 0.995 | -0.02232 | 0.99505 | -0.022743 | 16.1454
19 | -1.2775 | -0.5983 | 1.278 | 0.59302 | 0.00051234 | -0.0052761 | 0.040924 | 0.040857 | 0.040924 | 0.99505 | -0.022743 | 0.99542 | -0.025944 | 18.6017
20 | 0.16972 | 0.077615 | -0.16971 | -0.081545 | 6.5678e-06 | -0.0039306 | 0.0054142 | 0.0054626 | 0.0054626 | 0.99505 | -0.022743 | 0.99501 | -0.02243 | 2.483
21 | 0.14378 | 0.066154 | -0.14378 | -0.066319 | 1.9694e-07 | -0.00016506 | 0.0045931 | 0.0045952 | 0.0045952 | 0.9947 | -0.020785 | 0.9947 | -0.020774 | 2.0887
22 | -0.14377 | -0.069633 | 0.14378 | 0.068209 | 1.724e-06 | -0.0014242 | 0.0046363 | 0.0046184 | 0.0046363 | 0.99467 | -0.020545 | 0.99468 | -0.020647 | 2.1074
23 | -0.14378 | -0.068209 | 0.14378 | 0.066319 | 2.2673e-06 | -0.0018898 | 0.0046184 | 0.0045952 | 0.0046184 | 0.99468 | -0.020647 | 0.9947 | -0.020774 | 2.0993
24 | 3.0682 | 1.4747 | -3.0677 | -1.4754 | 0.00047602 | -0.00072409 | 0.098724 | 0.098735 | 0.098735 | 0.99542 | -0.025944 | 0.99528 | -0.024614 | 44.8793
25 | 0.185 | 0.079882 | -0.18498 | -0.089028 | 1.7964e-05 | -0.0091462 | 0.0058437 | 0.005954 | 0.005954 | 0.99542 | -0.025944 | 0.99533 | -0.025207 | 2.7063
26 | 0.7533 | 0.36428 | -0.75329 | -0.36456 | 9.4065e-06 | -0.00028025 | 0.024266 | 0.02427 | 0.02427 | 0.99542 | -0.025944 | 0.99541 | -0.025835 | 11.0317
27 | -5.2845 | -2.5119 | 5.2867 | 2.5081 | 0.0022296 | -0.0038343 | 0.16968 | 0.16962 | 0.16968 | 0.99542 | -0.025944 | 0.99588 | -0.020977 | 46.874
28 | 0.16971 | 0.081545 | -0.16971 | -0.082194 | 1.0961e-06 | -0.00064911 | 0.0054626 | 0.0054708 | 0.0054708 | 0.99501 | -0.02243 | 0.995 | -0.022374 | 2.4867
29 | 2.6268 | 1.2618 | -2.6266 | -1.2623 | 0.00019165 | -0.00041835 | 0.084523 | 0.084529 | 0.084529 | 0.99528 | -0.024614 | 0.99521 | -0.023989 | 38.4223
30 | 0.18498 | 0.089028 | -0.18498 | -0.089588 | 1.1227e-06 | -0.00056013 | 0.005954 | 0.005961 | 0.005961 | 0.99533 | -0.025207 | 0.99532 | -0.025155 | 2.7096
31 | 0.75329 | 0.36456 | -0.75328 | -0.36483 | 8.9491e-06 | -0.00026654 | 0.02427 | 0.024273 | 0.024273 | 0.99541 | -0.025835 | 0.9954 | -0.025732 | 11.0333
32 | -5.2867 | -2.5081 | 5.2867 | 2.5073 | 2.825e-05 | -0.00077625 | 0.16962 | 0.16961 | 0.16962 | 0.99588 | -0.020977 | 0.99589 | -0.020955 | 13.2928
33 | -5.5652 | -2.6421 | 5.5654 | 2.6362 | 0.00023848 | -0.0059013 | 0.17857 | 0.1785 | 0.17857 | 0.99589 | -0.020955 | 0.99593 | -0.020776 | 13.9948
34 | -5.5654 | -2.6362 | 5.5664 | 2.6121 | 0.0009735 | -0.024148 | 0.1785 | 0.17819 | 0.1785 | 0.99593 | -0.020776 | 0.99611 | -0.020025 | 13.9889
35 | 0.35476 | 0.17155 | -0.35476 | -0.17182 | 2.0161e-06 | -0.00027364 | 0.01142 | 0.011423 | 0.011423 | 0.99611 | -0.020025 | 0.99611 | -0.019976 | 5.1925
36 | -6.1185 | -2.877 | 6.1208 | 2.8302 | 0.0022776 | -0.046759 | 0.19594 | 0.19535 | 0.19594 | 0.99611 | -0.020025 | 0.9965 | -0.01833 | 15.3557
37 | 0.19734 | 0.093369 | -0.19734 | -0.094345 | 2.2065e-06 | -0.00097564 | 0.0063269 | 0.006339 | 0.006339 | 0.99611 | -0.020025 | 0.9961 | -0.019932 | 2.8814
38 | -13.4521 | -6.0847 | 13.4631 | 6.0422 | 0.010986 | -0.042425 | 0.42771 | 0.42713 | 0.42771 | 0.9965 | -0.01833 | 0.99734 | -0.013954 | 33.5193
39 | 0.39678 | 0.19138 | -0.39677 | -0.19217 | 7.2298e-06 | -0.00078565 | 0.012762 | 0.012771 | 0.012771 | 0.9965 | -0.01833 | 0.99648 | -0.018172 | 5.8052
40 | 6.9346 | 3.0631 | -6.9328 | -3.0587 | 0.0018361 | 0.0043523 | 0.21961 | 0.21962 | 0.21962 | 0.9965 | -0.01833 | 0.99601 | -0.04687 | 17.0248
41 | 0.12763 | 0.06142 | -0.12763 | -0.061816 | 3.7403e-07 | -0.00039528 | 0.0040998 | 0.0041048 | 0.0041048 | 0.99734 | -0.013954 | 0.99734 | -0.013928 | 1.8658
42 | -13.5908 | -6.1037 | 13.5963 | 6.0826 | 0.0055599 | -0.021085 | 0.43123 | 0.43094 | 0.43123 | 0.99734 | -0.013954 | 0.99777 | -0.011712 | 33.7952
43 | 6.8563 | 3.0229 | -6.8555 | -3.0361 | 0.00079908 | -0.013209 | 0.21717 | 0.21733 | 0.21733 | 0.99601 | -0.04687 | 0.99589 | -0.047547 | 17.0324
44 | 0.07646 | 0.03583 | -0.076459 | -0.037031 | 4.0783e-07 | -0.0012007 | 0.0024473 | 0.0024623 | 0.0024623 | 0.99601 | -0.04687 | 0.99601 | -0.046825 | 1.1192
45 | -15.4108 | -6.9362 | 15.4213 | 6.9063 | 0.010536 | -0.029809 | 0.48895 | 0.48852 | 0.48895 | 0.99777 | -0.011712 | 0.99848 | -0.0079923 | 38.3186
46 | 1.8145 | 0.85358 | -1.8144 | -0.85381 | 4.64e-05 | -0.00023168 | 0.058015 | 0.058018 | 0.058018 | 0.99777 | -0.011712 | 0.99774 | -0.011504 | 26.372
47 | -20.8387 | -9.3571 | 20.8449 | 9.349 | 0.0062502 | -0.0081065 | 0.66043 | 0.66029 | 0.66043 | 0.99848 | -0.0079923 | 0.99879 | -0.006357 | 51.7575
48 | 5.4173 | 2.4508 | -5.4173 | -2.4509 | 2.7548e-06 | -7.4074e-05 | 0.1719 | 0.17191 | 0.17191 | 0.99848 | -0.0079923 | 0.99848 | -0.007995 | 13.4722
49 | 1.4751 | 0.68947 | -1.4751 | -0.68972 | 3.2151e-05 | -0.00024835 | 0.047111 | 0.047114 | 0.047114 | 0.99774 | -0.011504 | 0.99772 | -0.011329 | 21.4157
50 | 21.2435 | 9.499 | -21.2189 | -9.5294 | 0.024601 | -0.0304 | 0.67176 | 0.67228 | 0.67228 | 1 | 0 | 0.99879 | -0.006357 | 52.6869
51 | 0.36465 | 0.17657 | -0.36464 | -0.1766 | 8.6859e-06 | -3.7104e-05 | 0.011696 | 0.011696 | 0.011696 | 1 | 0 | 0.99997 | -0.0001571 | 5.5696
52 | 0.37399 | 0.18038 | -0.37399 | -0.18113 | 6.1006e-06 | -0.00075334 | 0.012001 | 0.01201 | 0.01201 | 0.99879 | -0.006357 | 0.99878 | -0.0062156 | 5.4592
53 | 5.2091 | 2.35 | -5.209 | -2.3527 | 9.159e-05 | -0.0026686 | 0.16522 | 0.16525 | 0.16525 | 0.99848 | -0.007995 | 0.99846 | -0.0080885 | 12.9507
54 | 0.19734 | 0.094345 | -0.19734 | -0.094918 | 1.2999e-06 | -0.00057301 | 0.006339 | 0.0063462 | 0.0063462 | 0.9961 | -0.019932 | 0.99609 | -0.019875 | 2.8847
55 | 0.1089 | 0.052082 | -0.1089 | -0.05274 | 4.5513e-07 | -0.00065827 | 0.0034982 | 0.0035065 | 0.0035065 | 0.99609 | -0.019875 | 0.99609 | -0.01984 | 1.5939
56 | 1.4191 | 0.67927 | -1.4191 | -0.67954 | 3.1801e-05 | -0.00026102 | 0.045636 | 0.045639 | 0.045639 | 0.99521 | -0.023989 | 0.99519 | -0.023799 | 20.7451
57 | 1.2075 | 0.58299 | -1.2074 | -0.58412 | 9.9267e-05 | -0.0011325 | 0.038893 | 0.038908 | 0.038908 | 0.99521 | -0.023989 | 0.99513 | -0.023276 | 17.6855
58 | -6.3512 | -2.8493 | 6.3537 | 2.8012 | 0.0025003 | -0.048079 | 0.202 | 0.20141 | 0.202 | 0.9948 | -0.084483 | 0.99521 | -0.082255 | 15.8305
59 | 5.7054 | 2.5377 | -5.7023 | -2.6097 | 0.0030217 | -0.071979 | 0.1812 | 0.18208 | 0.18208 | 0.9948 | -0.084483 | 0.99425 | -0.087304 | 14.2695
60 | 0.64581 | 0.31159 | -0.64578 | -0.31249 | 2.2356e-05 | -0.00090675 | 0.020807 | 0.020819 | 0.020819 | 0.9948 | -0.084483 | 0.99477 | -0.084183 | 9.4632
61 | 0.24738 | 0.11923 | -0.24738 | -0.11981 | 2.0697e-06 | -0.00057665 | 0.0079656 | 0.0079729 | 0.0079729 | 0.99521 | -0.082255 | 0.9952 | -0.082182 | 3.624
62 | -6.601 | -2.9205 | 6.6031 | 2.9254 | 0.0020949 | 0.0048999 | 0.20938 | 0.20937 | 0.20938 | 0.99521 | -0.082255 | 0.99579 | -0.048108 | 16.2306
63 | 0.28477 | 0.13299 | -0.28475 | -0.13784 | 2.3036e-05 | -0.0048515 | 0.0091254 | 0.0091859 | 0.0091859 | 0.99425 | -0.087304 | 0.99418 | -0.086628 | 4.1754
64 | 5.038 | 2.2936 | -5.0261 | -2.3171 | 0.011918 | -0.023572 | 0.16072 | 0.16111 | 0.16111 | 0.99425 | -0.087304 | 0.99166 | -0.11743 | 44.5059
65 | 0.37952 | 0.18317 | -0.37952 | -0.18381 | 5.431e-06 | -0.00063933 | 0.012236 | 0.012244 | 0.012244 | 0.99425 | -0.087304 | 0.99424 | -0.08718 | 5.5653
66 | 0.35363 | 0.171 | -0.35357 | -0.17124 | 5.5284e-05 | -0.00024735 | 0.011399 | 0.011402 | 0.011402 | 0.99477 | -0.084183 | 0.99461 | -0.085217 | 5.4297
67 | 6.8555 | 3.0361 | -6.855 | -3.0438 | 0.00046456 | -0.0076685 | 0.21733 | 0.21743 | 0.21743 | 0.99589 | -0.047547 | 0.99582 | -0.047936 | 17.0397
68 | 6.6033 | 2.9219 | -6.6031 | -2.9254 | 0.00019706 | -0.0035157 | 0.20932 | 0.20937 | 0.20937 | 0.99582 | -0.047936 | 0.99579 | -0.048108 | 16.408
69 | 0.28475 | 0.13784 | -0.28475 | -0.13791 | 3.1474e-07 | -6.5842e-05 | 0.0091859 | 0.0091868 | 0.0091868 | 0.99418 | -0.086628 | 0.99418 | -0.086618 | 4.1758
70 | 3.2041 | 1.4404 | -3.1985 | -1.4481 | 0.005537 | -0.0076443 | 0.10226 | 0.10237 | 0.10237 | 0.99166 | -0.11743 | 0.99005 | -0.1047 | 46.5339
71 | 1.822 | 0.87669 | -1.822 | -0.87706 | 7.788e-05 | -0.0003722 | 0.058861 | 0.058866 | 0.058866 | 0.99166 | -0.11743 | 0.99162 | -0.11706 | 26.7571
72 | 1.1213 | 0.52518 | -1.1212 | -0.52647 | 9.4625e-05 | -0.0012839 | 0.035824 | 0.03584 | 0.03584 | 0.99772 | -0.011329 | 0.99765 | -0.010645 | 16.2909
73 | 0.35384 | 0.16454 | -0.3538 | -0.16989 | 3.8647e-05 | -0.005354 | 0.011291 | 0.011357 | 0.011357 | 0.99772 | -0.011329 | 0.99762 | -0.010428 | 5.1622
74 | 5.209 | 2.3527 | -5.209 | -2.3537 | 3.6072e-05 | -0.0010507 | 0.16525 | 0.16526 | 0.16526 | 0.99846 | -0.0080885 | 0.99845 | -0.0081252 | 12.9517
75 | -0.2705 | -0.13101 | 0.2705 | 0.13004 | 4.1471e-06 | -0.00096587 | 0.0087198 | 0.0087076 | 0.0087198 | 0.99499 | -0.022026 | 0.99501 | -0.022158 | 3.9636
76 | -0.2705 | -0.13004 | 0.27052 | 0.12629 | 1.6016e-05 | -0.003756 | 0.0087076 | 0.0086609 | 0.0087076 | 0.99501 | -0.022158 | 0.99506 | -0.022649 | 3.958
77 | -0.39122 | -0.18411 | 0.39122 | 0.18313 | 8.73e-06 | -0.00098094 | 0.012543 | 0.012531 | 0.012543 | 0.99506 | -0.022649 | 0.99508 | -0.02283 | 5.7016
78 | 0.1207 | 0.057827 | -0.1207 | -0.058457 | 5.3761e-07 | -0.00063006 | 0.0038827 | 0.0038906 | 0.0038906 | 0.99506 | -0.022649 | 0.99506 | -0.022611 | 1.7685
79 | -1.4189 | -0.68086 | 1.4191 | 0.67954 | 0.00016149 | -0.0013247 | 0.045656 | 0.045639 | 0.045656 | 0.99508 | -0.02283 | 0.99519 | -0.023799 | 20.7529
80 | 4.9473 | 2.227 | -4.9471 | -2.2335 | 0.00020021 | -0.0064815 | 0.15686 | 0.15694 | 0.15694 | 0.99845 | -0.0081252 | 0.99841 | -0.0083416 | 12.2992
81 | 4.9471 | 2.2335 | -4.9459 | -2.2722 | 0.0012001 | -0.038703 | 0.15694 | 0.15741 | 0.15741 | 0.99841 | -0.0083416 | 0.99816 | -0.0095812 | 12.3362
82 | 4.6588 | 2.136 | -4.6586 | -2.1407 | 0.00012959 | -0.0047051 | 0.14822 | 0.14828 | 0.14828 | 0.99816 | -0.0095812 | 0.99813 | -0.0097183 | 11.6206
83 | 0.28709 | 0.13616 | -0.28708 | -0.13818 | 9.6123e-06 | -0.0020199 | 0.0091894 | 0.0092146 | 0.0092146 | 0.99816 | -0.0095812 | 0.99813 | -0.0092983 | 4.1885
84 | 4.337 | 1.9849 | -4.3363 | -1.9842 | 0.00065379 | 0.00070095 | 0.13795 | 0.13795 | 0.13795 | 0.99813 | -0.0097183 | 0.99794 | -0.014619 | 39.413
85 | 0.28708 | 0.13818 | -0.28708 | -0.13904 | 4.1156e-06 | -0.0008614 | 0.0092146 | 0.0092255 | 0.0092255 | 0.99813 | -0.0092983 | 0.99812 | -0.0091743 | 4.1934
86 | 4.3363 | 1.9842 | -4.3338 | -1.9918 | 0.002554 | -0.0076238 | 0.13795 | 0.13806 | 0.13806 | 0.99794 | -0.014619 | 0.99729 | -0.022097 | 38.1381
87 | 0.85638 | 0.3987 | -0.8559 | -0.41001 | 0.00048346 | -0.01131 | 0.027334 | 0.027475 | 0.027475 | 0.99765 | -0.010645 | 0.99712 | -0.005998 | 12.4888
88 | 0.26478 | 0.12777 | -0.26477 | -0.12824 | 1.915e-06 | -0.00047014 | 0.0085068 | 0.0085127 | 0.0085127 | 0.99765 | -0.010645 | 0.99764 | -0.010583 | 3.8694
89 | 0.3538 | 0.16989 | -0.35379 | -0.17135 | 1.0615e-05 | -0.0014594 | 0.011357 | 0.011375 | 0.011375 | 0.99762 | -0.010428 | 0.9976 | -0.010169 | 5.1706
90 | 0.8559 | 0.41001 | -0.85586 | -0.41078 | 3.3154e-05 | -0.0007708 | 0.027475 | 0.027485 | 0.027485 | 0.99712 | -0.005998 | 0.99709 | -0.005668 | 12.4933
91 | 0.30772 | 0.14272 | -0.30769 | -0.14805 | 2.9959e-05 | -0.0053238 | 0.0098905 | 0.009957 | 0.009957 | 0.99005 | -0.1047 | 0.98996 | -0.1039 | 4.5259
92 | 2.8908 | 1.3054 | -2.8905 | -1.3059 | 0.0003243 | -0.00056834 | 0.092484 | 0.092492 | 0.092492 | 0.99005 | -0.1047 | 0.98994 | -0.10388 | 42.042
93 | 1.7289 | 0.83199 | -1.7287 | -0.83284 | 0.00015812 | -0.00084414 | 0.055855 | 0.055867 | 0.055867 | 0.99162 | -0.11706 | 0.99154 | -0.11627 | 25.3939
94 | 0.30769 | 0.14805 | -0.30769 | -0.14902 | 5.521e-06 | -0.0009732 | 0.009957 | 0.0099693 | 0.0099693 | 0.98996 | -0.1039 | 0.98994 | -0.10375 | 4.5315
95 | 2.613 | 1.1715 | -2.6128 | -1.172 | 0.00022411 | -0.00049674 | 0.083504 | 0.083511 | 0.083511 | 0.98994 | -0.10388 | 0.98986 | -0.10325 | 37.9596
96 | 0.58644 | 0.28029 | -0.58641 | -0.28141 | 2.2414e-05 | -0.0011179 | 0.018818 | 0.018832 | 0.018832 | 0.99709 | -0.005668 | 0.99705 | -0.0053433 | 8.5601
97 | -0.17138 | -0.083003 | 0.17138 | 0.081079 | 3.3174e-06 | -0.0019249 | 0.0055298 | 0.0055056 | 0.0055298 | 0.99408 | -0.0037849 | 0.9941 | -0.0039491 | 2.5135
98 | 0.45955 | 0.21139 | -0.45946 | -0.21829 | 8.5027e-05 | -0.0068985 | 0.014689 | 0.014774 | 0.014774 | 0.9941 | -0.0039491 | 0.99393 | -0.0024621 | 6.7155
99 | 0.4091 | 0.17483 | -0.40895 | -0.19091 | 0.00015455 | -0.016079 | 0.012919 | 0.01311 | 0.01311 | 0.9941 | -0.0039491 | 0.99375 | -0.0012343 | 5.9593
100 | -2.3954 | -1.1055 | 2.3978 | 1.099 | 0.0024021 | -0.0065365 | 0.076609 | 0.076522 | 0.076609 | 0.9941 | -0.0039491 | 0.99503 | -0.011689 | 34.8225
101 | 1.3553 | 0.63819 | -1.3552 | -0.63816 | 0.00010465 | 2.8938e-05 | 0.043502 | 0.043503 | 0.043503 | 0.9941 | -0.0039491 | 0.99402 | -0.0045122 | 20.7157
102 | 0.45946 | 0.21829 | -0.45944 | -0.21988 | 1.971e-05 | -0.0015873 | 0.014774 | 0.014794 | 0.014794 | 0.99393 | -0.0024621 | 0.99389 | -0.0021012 | 6.7246
103 | 0.40895 | 0.19091 | -0.40889 | -0.1972 | 6.1744e-05 | -0.0062877 | 0.01311 | 0.013189 | 0.013189 | 0.99375 | -0.0012343 | 0.99361 | 2.2135e-05 | 5.995
104 | 0.23598 | 0.10638 | -0.23596 | -0.11313 | 2.1763e-05 | -0.0067528 | 0.0075096 | 0.0075923 | 0.0075923 | 0.99503 | -0.011689 | 0.99495 | -0.010957 | 3.451
105 | -2.776 | -1.2741 | 2.779 | 1.2683 | 0.0029867 | -0.0058622 | 0.088614 | 0.088532 | 0.088614 | 0.99503 | -0.011689 | 0.99604 | -0.019894 | 40.279
106 | 0.14223 | 0.068807 | -0.14222 | -0.068882 | 2.4163e-06 | -7.4765e-05 | 0.0045837 | 0.0045847 | 0.0045847 | 0.99503 | -0.011689 | 0.99502 | -0.011802 | 2.1832
107 | 1.1893 | 0.55782 | -1.1883 | -0.55765 | 0.0009995 | 0.00017188 | 0.03815 | 0.038156 | 0.038156 | 0.99402 | -0.0045122 | 0.99313 | -0.01072 | 18.1694
108 | 0.16509 | 0.077318 | -0.16503 | -0.078671 | 5.9086e-05 | -0.0013529 | 0.0052949 | 0.0053121 | 0.0053121 | 0.99389 | -0.0021012 | 0.99351 | -0.0046807 | 2.5296
109 | 0.40889 | 0.1972 | -0.40888 | -0.19803 | 8.1948e-06 | -0.00082871 | 0.013189 | 0.013199 | 0.013199 | 0.99361 | 2.2135e-05 | 0.99359 | 0.00019591 | 5.9998
110 | 0.076307 | 0.036725 | -0.076307 | -0.036957 | 7.9205e-08 | -0.00023199 | 0.0024571 | 0.00246 | 0.00246 | 0.99495 | -0.010957 | 0.99495 | -0.010948 | 1.1182
111 | 0.15965 | 0.076403 | -0.15965 | -0.077321 | 1.3717e-06 | -0.00091849 | 0.0051352 | 0.0051468 | 0.0051468 | 0.99495 | -0.010957 | 0.99494 | -0.010884 | 2.3394
112 | -3.3187 | -1.5186 | 3.3204 | 1.5164 | 0.0016882 | -0.0021786 | 0.10577 | 0.10574 | 0.10577 | 0.99604 | -0.019894 | 0.99652 | -0.023762 | 48.0791
113 | 0.23168 | 0.10114 | -0.23165 | -0.10993 | 2.699e-05 | -0.0087877 | 0.0073264 | 0.0074321 | 0.0074321 | 0.99604 | -0.019894 | 0.99593 | -0.019015 | 3.3782
114 | 0.30803 | 0.14913 | -0.30802 | -0.14918 | 8.1901e-06 | -5.0203e-05 | 0.0099188 | 0.0099195 | 0.0099195 | 0.99604 | -0.019894 | 0.99601 | -0.020069 | 4.7236
115 | 1.1056 | 0.51759 | -1.1056 | -0.51814 | 4.0572e-05 | -0.00055621 | 0.035485 | 0.035492 | 0.035492 | 0.99313 | -0.01072 | 0.9931 | -0.010424 | 16.1326
116 | 0.16503 | 0.078671 | -0.16503 | -0.079928 | 2.0157e-06 | -0.0012567 | 0.0053121 | 0.005328 | 0.005328 | 0.99351 | -0.0046807 | 0.9935 | -0.0045761 | 2.4218
117 | -3.3204 | -1.5164 | 3.322 | 1.5173 | 0.0015976 | 0.00090556 | 0.10574 | 0.10574 | 0.10574 | 0.99652 | -0.023762 | 0.99703 | -0.019893 | 50.3532
118 | 0.16292 | 0.078826 | -0.16292 | -0.078906 | 1.2417e-07 | -7.9992e-05 | 0.005246 | 0.005247 | 0.005247 | 0.99593 | -0.019015 | 0.99593 | -0.019009 | 2.385
119 | 0.068729 | 0.031101 | -0.068728 | -0.032965 | 5.0768e-07 | -0.0018642 | 0.0021866 | 0.0022094 | 0.0022094 | 0.99593 | -0.019015 | 0.99592 | -0.018956 | 1.0043
120 | -3.6895 | -1.6953 | 3.6905 | 1.6942 | 0.0010564 | -0.0010461 | 0.11756 | 0.11754 | 0.11756 | 0.99703 | -0.019893 | 0.99729 | -0.022097 | 53.4366
121 | 0.068728 | 0.032965 | -0.068728 | -0.033287 | 8.8704e-08 | -0.00032169 | 0.0022094 | 0.0022135 | 0.0022135 | 0.99592 | -0.018956 | 0.99592 | -0.018945 | 1.0061
122 | 0.78702 | 0.36385 | -0.78698 | -0.36387 | 4.4493e-05 | -1.8412e-05 | 0.025204 | 0.025204 | 0.025204 | 0.9931 | -0.010424 | 0.99304 | -0.010861 | 12.0021
123 | 0.78698 | 0.36387 | -0.78697 | -0.36403 | 5.669e-06 | -0.00015569 | 0.025204 | 0.025206 | 0.025206 | 0.99304 | -0.010861 | 0.99303 | -0.010805 | 11.4574
124 | 0.78697 | 0.36403 | -0.78694 | -0.36501 | 3.5679e-05 | -0.00097929 | 0.025206 | 0.025218 | 0.025218 | 0.99303 | -0.010805 | 0.99299 | -0.010449 | 11.4629
125 | 0.6905 | 0.3183 | -0.69046 | -0.31948 | 3.3059e-05 | -0.0011826 | 0.022104 | 0.022118 | 0.022118 | 0.99299 | -0.010449 | 0.99295 | -0.010075 | 10.0537
126 | 0.69046 | 0.31948 | -0.6901 | -0.33223 | 0.00035947 | -0.012751 | 0.022118 | 0.022278 | 0.022278 | 0.99295 | -0.010075 | 0.99246 | -0.0057945 | 10.1263
127 | 0.6901 | 0.33223 | -0.69009 | -0.33276 | 1.4976e-05 | -0.00052695 | 0.022278 | 0.022285 | 0.022285 | 0.99246 | -0.0057945 | 0.99244 | -0.0056077 | 10.1294
128 | 0.082833 | 0.03198 | -0.08283 | -0.039966 | 3.0726e-06 | -0.0079851 | 0.0025712 | 0.0026632 | 0.0026632 | 0.99691 | -0.022388 | 0.99687 | -0.022142 | 1.2105
129 | -0.082833 | -0.03198 | 0.082833 | 0.031244 | 2.7313e-07 | -0.00073646 | 0.0025712 | 0.0025636 | 0.0025712 | 0.99691 | -0.022388 | 0.99691 | -0.022402 | 1.1687
130 | 0.08283 | 0.039966 | -0.082828 | -0.040116 | 1.6108e-06 | -0.0001501 | 0.0026632 | 0.0026651 | 0.0026651 | 0.99687 | -0.022142 | 0.99685 | -0.022271 | 1.2691
131 | -0.32322 | -0.14767 | 0.32328 | 0.14735 | 5.7118e-05 | -0.00032365 | 0.01029 | 0.010286 | 0.01029 | 0.99691 | -0.022402 | 0.9971 | -0.020977 | 4.9
132 | -0.64312 | -0.30225 | 0.64314 | 0.30223 | 2.1806e-05 | -2.0663e-05 | 0.020573 | 0.020573 | 0.020573 | 0.9971 | -0.020977 | 0.99713 | -0.020729 | 9.7967
133 | -0.64314 | -0.30223 | 0.64325 | 0.29762 | 0.0001102 | -0.0046109 | 0.020573 | 0.020516 | 0.020573 | 0.99713 | -0.020729 | 0.99729 | -0.022097 | 9.3512
134 | -0.18198 | -0.087293 | 0.18198 | 0.08672 | 1.121e-06 | -0.0005733 | 0.0058709 | 0.0058637 | 0.0058709 | 0.99244 | -0.0055555 | 0.99244 | -0.0056077 | 2.6686
135 | 0.1036 | 0.049328 | -0.10358 | -0.049995 | 1.1404e-05 | -0.00066674 | 0.0033375 | 0.003346 | 0.003346 | 0.99244 | -0.0055555 | 0.99232 | -0.0063093 | 1.5933
136 | 0.41444 | 0.20068 | -0.41443 | -0.20072 | 1.2901e-05 | -3.9374e-05 | 0.013394 | 0.013395 | 0.013395 | 0.99244 | -0.0056077 | 0.99241 | -0.005813 | 6.3783
137 | 0.10358 | 0.049995 | -0.10358 | -0.050168 | 1.1037e-07 | -0.00017345 | 0.003346 | 0.0033482 | 0.0033482 | 0.99232 | -0.0063093 | 0.99232 | -0.0063001 | 1.5219
138 | -0.21707 | -0.10513 | 0.21708 | 0.10401 | 3.1806e-06 | -0.0011274 | 0.0070348 | 0.0070205 | 0.0070348 | 0.98975 | -0.1023 | 0.98976 | -0.10242 | 3.1976
139 | -0.21708 | -0.10401 | 0.2171 | 0.095575 | 2.3385e-05 | -0.0084319 | 0.0070205 | 0.0069177 | 0.0070205 | 0.98976 | -0.10242 | 0.98986 | -0.10325 | 3.1911
140 | 0.74052 | 0.35519 | -0.74048 | -0.35635 | 3.8355e-05 | -0.0011595 | 0.023952 | 0.023966 | 0.023966 | 0.98986 | -0.10325 | 0.98982 | -0.10281 | 10.8938
141 | 0.74048 | 0.35635 | -0.74046 | -0.35699 | 2.1429e-05 | -0.00064711 | 0.023966 | 0.023975 | 0.023975 | 0.98982 | -0.10281 | 0.98979 | -0.10256 | 10.8976
142 | 0.63663 | 0.3067 | -0.63661 | -0.30726 | 1.374e-05 | -0.0005625 | 0.02061 | 0.020617 | 0.020617 | 0.98979 | -0.10256 | 0.98977 | -0.10238 | 9.3713
143 | 0.16454 | 0.078711 | -0.16454 | -0.078967 | 4.1456e-07 | -0.00025637 | 0.0053198 | 0.0053231 | 0.0053231 | 0.98977 | -0.10238 | 0.98977 | -0.10236 | 2.4196
144 | 0.12136 | 0.058752 | -0.12136 | -0.058778 | 6.2508e-07 | -2.6136e-05 | 0.0039326 | 0.003933 | 0.003933 | 0.98977 | -0.10238 | 0.98976 | -0.10241 | 1.8728
145 | 0.17553 | 0.084959 | -0.17553 | -0.085011 | 2.6365e-06 | -5.1839e-05 | 0.0056876 | 0.0056883 | 0.0056883 | 0.98977 | -0.10238 | 0.98975 | -0.10248 | 2.7087
146 | 1.5402 | 0.74154 | -1.54 | -0.74283 | 0.00018982 | -0.0012906 | 0.049769 | 0.049786 | 0.049786 | 0.99154 | -0.11627 | 0.99143 | -0.11521 | 22.6298
147 | -0.27627 | -0.13381 | 0.27628 | 0.13376 | 5.3938e-06 | -4.1064e-05 | 0.0089395 | 0.0089389 | 0.0089395 | 0.99128 | -0.11416 | 0.9913 | -0.11403 | 4.2569
148 | -1.1979 | -0.57886 | 1.1979 | 0.57857 | 2.5282e-05 | -0.00028856 | 0.038743 | 0.038739 | 0.038743 | 0.9913 | -0.11403 | 0.99132 | -0.11422 | 17.6104
149 | 0.92161 | 0.44509 | -0.92156 | -0.44599 | 4.5922e-05 | -0.00089456 | 0.029804 | 0.029816 | 0.029816 | 0.9913 | -0.11403 | 0.99125 | -0.1136 | 13.5525
150 | -1.1979 | -0.57857 | 1.198 | 0.57815 | 3.713e-05 | -0.00042391 | 0.038739 | 0.038734 | 0.038739 | 0.99132 | -0.11422 | 0.99135 | -0.11448 | 17.6087
151 | 0.40425 | 0.19544 | -0.40425 | -0.19579 | 3.344e-06 | -0.00034256 | 0.013076 | 0.013081 | 0.013081 | 0.99125 | -0.1136 | 0.99125 | -0.11353 | 5.9458
152 | -1.3841 | -0.6683 | 1.3841 | 0.66791 | 4.6027e-05 | -0.00039028 | 0.044756 | 0.044751 | 0.044756 | 0.99135 | -0.11448 | 0.99138 | -0.11477 | 20.3437
153 | -1.3841 | -0.66791 | 1.3842 | 0.6677 | 2.4581e-05 | -0.00020848 | 0.044751 | 0.044748 | 0.044751 | 0.99138 | -0.11477 | 0.99139 | -0.11492 | 20.3414
154 | -1.54 | -0.74317 | 1.54 | 0.74283 | 5.1197e-05 | -0.00034788 | 0.04979 | 0.049786 | 0.04979 | 0.99139 | -0.11492 | 0.99143 | -0.11521 | 22.6319
155 | 0.58641 | 0.28141 | -0.58639 | -0.28256 | 2.3011e-05 | -0.0011458 | 0.018832 | 0.018847 | 0.018847 | 0.99705 | -0.0053433 | 0.99701 | -0.0050069 | 8.5666
156 | 0.61973 | 0.29951 | -0.61972 | -0.30014 | 1.4289e-05 | -0.00063028 | 0.019967 | 0.019975 | 0.019975 | 0.99513 | -0.023276 | 0.99511 | -0.023076 | 9.0796
157 | 0.16454 | 0.078967 | -0.16454 | -0.07969 | 1.1728e-06 | -0.00072356 | 0.0053231 | 0.0053322 | 0.0053322 | 0.98977 | -0.10236 | 0.98976 | -0.10229 | 2.4237
158 | 0.58639 | 0.28256 | -0.58636 | -0.28399 | 2.8799e-05 | -0.0014314 | 0.018847 | 0.018865 | 0.018865 | 0.99701 | -0.0050069 | 0.99697 | -0.0045815 | 8.5749

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.6221 | 9.6861

## res_load
| p_mw | q_mvar
0 | 0.23809 | 0.11531
1 | 0.093021 | 0.045052
2 | 0.3656 | 0.17707
3 | 0.25692 | 0.12443
4 | 0.29372 | 0.14226
5 | 0.20944 | 0.10144
6 | 0.1327 | 0.064272
7 | 0.1553 | 0.075214
8 | 0.39603 | 0.1918
9 | 0.070257 | 0.034027
10 | 0.14377 | 0.069633
11 | 0.44098 | 0.21358
12 | 0.18498 | 0.089588
13 | 0.16971 | 0.082194
14 | 0.27842 | 0.13484
15 | 0.39677 | 0.19217
16 | 0.33931 | 0.16433
17 | 0.12763 | 0.061816
18 | 0.36464 | 0.1766
19 | 0.20823 | 0.10085
20 | 0.37399 | 0.18113
21 | 0.088445 | 0.042836
22 | 0.35476 | 0.17182
23 | 0.75328 | 0.36483
24 | 0.29216 | 0.1415
25 | 0.076459 | 0.037031
26 | 0.2517 | 0.1219
27 | 0.37952 | 0.18381
28 | 0.24738 | 0.11981
29 | 0.28475 | 0.13791
30 | 0.1089 | 0.05274
31 | 0.2705 | 0.13101
32 | 1.0277 | 0.49773
33 | 0.1207 | 0.058457
34 | 0.26171 | 0.12675
35 | 0.32165 | 0.15578
36 | 0.28708 | 0.13904
37 | 0.26477 | 0.12824
38 | 0.35379 | 0.17135
39 | 0.093061 | 0.045071
40 | 0.35357 | 0.17124
41 | 0.27751 | 0.13441
42 | 0.30769 | 0.14902
43 | 0.26943 | 0.13049
44 | 0.17138 | 0.083003
45 | 0.16589 | 0.080346
46 | 0.29435 | 0.14256
47 | 0.14222 | 0.068882
48 | 0.40888 | 0.19803
49 | 0.082712 | 0.040059
50 | 0.076307 | 0.036957
51 | 0.15965 | 0.077321
52 | 0.30802 | 0.14918
53 | 0.3675 | 0.17799
54 | 0.068728 | 0.033287
55 | 0.16292 | 0.078906
56 | 0.31857 | 0.15429
57 | 0.096442 | 0.046709
58 | 0.16503 | 0.079928
59 | 0.24039 | 0.11643
60 | 0.082828 | 0.040116
61 | 0.31984 | 0.15491
62 | 0.078388 | 0.037965
63 | 0.09366 | 0.045362
64 | 0.41443 | 0.20072
65 | 0.21707 | 0.10513
66 | 0.10384 | 0.05029
67 | 0.40134 | 0.19438
68 | 0.17518 | 0.084843
69 | 0.18851 | 0.0913
70 | 0.27627 | 0.13381
71 | 0.51731 | 0.25054
72 | 0.18614 | 0.09015
73 | 0.40425 | 0.19579
74 | 0.15584 | 0.075477
75 | 0.58765 | 0.28461
76 | 0.61972 | 0.30014
77 | 0.10358 | 0.050168
78 | 0.12136 | 0.058778
79 | 0.17553 | 0.085011
80 | 0.16454 | 0.07969
81 | 0.58636 | 0.28399

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1