## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_420_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_420_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_420_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_420_0_node_13 | 20 | n |  | TRUE
4 | bus_MV_420_0_node_15 | 20 | n |  | TRUE
5 | bus_MV_420_0_node_146 | 20 | n |  | TRUE
6 | bus_MV_420_0_node_9 | 20 | n |  | TRUE
7 | bus_MV_420_0_node_178 | 20 | n |  | TRUE
8 | bus_MV_420_0_node_3 | 20 | n |  | TRUE
9 | bus_MV_420_0_node_145 | 20 | n |  | TRUE
10 | bus_MV_420_0_node_4 | 20 | n |  | TRUE
11 | bus_MV_420_0_node_16 | 20 | n |  | TRUE
12 | bus_MV_420_0_node_144 | 20 | n |  | TRUE
13 | bus_MV_420_0_node_14 | 20 | n |  | TRUE
14 | bus_MV_420_0_node_6 | 20 | n |  | TRUE
15 | bus_MV_420_0_node_7 | 20 | n |  | TRUE
16 | bus_MV_420_0_node_10 | 20 | n |  | TRUE
17 | bus_MV_420_0_node_187 | 20 | n |  | TRUE
18 | bus_MV_420_0_node_12 | 20 | n |  | TRUE
19 | bus_MV_420_0_node_17 | 20 | n |  | TRUE
20 | bus_MV_420_0_node_26 | 20 | n |  | TRUE
21 | bus_MV_420_0_node_11 | 20 | n |  | TRUE
22 | bus_MV_420_0_node_27 | 20 | n |  | TRUE
23 | bus_MV_420_0_node_28 | 20 | n |  | TRUE
24 | bus_MV_420_0_node_179 | 20 | n |  | TRUE
25 | bus_MV_420_0_node_29 | 20 | n |  | TRUE
26 | bus_MV_420_0_node_133 | 20 | n |  | TRUE
27 | bus_MV_420_0_node_102 | 20 | n |  | TRUE
28 | bus_MV_420_0_node_141 | 20 | n |  | TRUE
29 | bus_MV_420_0_node_142 | 20 | n |  | TRUE
30 | bus_MV_420_0_node_101 | 20 | n |  | TRUE
31 | bus_MV_420_0_node_80 | 20 | n |  | TRUE
32 | bus_MV_420_0_node_81 | 20 | n |  | TRUE
33 | bus_MV_420_0_node_83 | 20 | n |  | TRUE
34 | bus_MV_420_0_node_73 | 20 | n |  | TRUE
35 | bus_MV_420_0_node_74 | 20 | n |  | TRUE
36 | bus_MV_420_0_node_85 | 20 | n |  | TRUE
37 | bus_MV_420_0_node_86 | 20 | n |  | TRUE
38 | bus_MV_420_0_node_89 | 20 | n |  | TRUE
39 | bus_MV_420_0_node_84 | 20 | n |  | TRUE
40 | bus_MV_420_0_node_75 | 20 | n |  | TRUE
41 | bus_MV_420_0_node_76 | 20 | n |  | TRUE
42 | bus_MV_420_0_node_184 | 20 | n |  | TRUE
43 | bus_MV_420_0_node_91 | 20 | n |  | TRUE
44 | bus_MV_420_0_node_92 | 20 | n |  | TRUE
45 | bus_MV_420_0_node_77 | 20 | n |  | TRUE
46 | bus_MV_420_0_node_79 | 20 | n |  | TRUE
47 | bus_MV_420_0_node_82 | 20 | n |  | TRUE
48 | bus_MV_420_0_node_95 | 20 | n |  | TRUE
49 | bus_MV_420_0_node_90 | 20 | n |  | TRUE
50 | bus_MV_420_0_node_93 | 20 | n |  | TRUE
51 | bus_MV_420_0_node_87 | 20 | n |  | TRUE
52 | bus_MV_420_0_node_172 | 20 | n |  | TRUE
53 | bus_MV_420_0_node_88 | 20 | n |  | TRUE
54 | bus_MV_420_0_node_105 | 20 | n |  | TRUE
55 | bus_MV_420_0_node_104 | 20 | n |  | TRUE
56 | bus_MV_420_0_node_155 | 20 | n |  | TRUE
57 | bus_MV_420_0_node_181 | 20 | n |  | TRUE
58 | bus_MV_420_0_node_106 | 20 | n |  | TRUE
59 | bus_MV_420_0_node_107 | 20 | n |  | TRUE
60 | bus_MV_420_0_node_180 | 20 | n |  | TRUE
61 | bus_MV_420_0_node_117 | 20 | n |  | TRUE
62 | bus_MV_420_0_node_126 | 20 | n |  | TRUE
63 | bus_MV_420_0_node_114 | 20 | n |  | TRUE
64 | bus_MV_420_0_node_127 | 20 | n |  | TRUE
65 | bus_MV_420_0_node_128 | 20 | n |  | TRUE
66 | bus_MV_420_0_node_99 | 20 | n |  | TRUE
67 | bus_MV_420_0_node_94 | 20 | n |  | TRUE
68 | bus_MV_420_0_node_96 | 20 | n |  | TRUE
69 | bus_MV_420_0_node_97 | 20 | n |  | TRUE
70 | bus_MV_420_0_node_98 | 20 | n |  | TRUE
71 | bus_MV_420_0_node_100 | 20 | n |  | TRUE
72 | bus_MV_420_0_node_156 | 20 | n |  | TRUE
73 | bus_MV_420_0_node_103 | 20 | n |  | TRUE
74 | bus_MV_420_0_node_170 | 20 | n |  | TRUE
75 | bus_MV_420_0_node_166 | 20 | n |  | TRUE
76 | bus_MV_420_0_node_171 | 20 | n |  | TRUE
77 | bus_MV_420_0_node_131 | 20 | n |  | TRUE
78 | bus_MV_420_0_node_143 | 20 | n |  | TRUE
79 | bus_MV_420_0_node_165 | 20 | n |  | TRUE
80 | bus_MV_420_0_node_169 | 20 | n |  | TRUE
81 | bus_MV_420_0_node_108 | 20 | n |  | TRUE
82 | bus_MV_420_0_node_109 | 20 | n |  | TRUE
83 | bus_MV_420_0_node_112 | 20 | n |  | TRUE
84 | bus_MV_420_0_node_110 | 20 | n |  | TRUE
85 | bus_MV_420_0_node_111 | 20 | n |  | TRUE
86 | bus_MV_420_0_node_113 | 20 | n |  | TRUE
87 | bus_MV_420_0_node_115 | 20 | n |  | TRUE
88 | bus_MV_420_0_node_160 | 20 | n |  | TRUE
89 | bus_MV_420_0_node_124 | 20 | n |  | TRUE
90 | bus_MV_420_0_node_161 | 20 | n |  | TRUE
91 | bus_MV_420_0_node_118 | 20 | n |  | TRUE
92 | bus_MV_420_0_node_125 | 20 | n |  | TRUE
93 | bus_MV_420_0_node_119 | 20 | n |  | TRUE
94 | bus_MV_420_0_node_122 | 20 | n |  | TRUE
95 | bus_MV_420_0_node_121 | 20 | n |  | TRUE
96 | bus_MV_420_0_node_123 | 20 | n |  | TRUE
97 | bus_MV_420_0_node_162 | 20 | n |  | TRUE
98 | bus_MV_420_0_node_159 | 20 | n |  | TRUE
99 | bus_MV_420_0_node_157 | 20 | n |  | TRUE
100 | bus_MV_420_0_node_129 | 20 | n |  | TRUE
101 | bus_MV_420_0_node_132 | 20 | n |  | TRUE
102 | bus_MV_420_0_node_140 | 20 | n |  | TRUE
103 | bus_MV_420_0_node_138 | 20 | n |  | TRUE
104 | bus_MV_420_0_node_134 | 20 | n |  | TRUE
105 | bus_MV_420_0_node_186 | 20 | n |  | TRUE
106 | bus_MV_420_0_node_139 | 20 | n |  | TRUE
107 | bus_MV_420_0_node_137 | 20 | n |  | TRUE
108 | bus_MV_420_0_node_135 | 20 | n |  | TRUE
109 | bus_MV_420_0_node_167 | 20 | n |  | TRUE
110 | bus_MV_420_0_node_168 | 20 | n |  | TRUE
111 | bus_MV_420_0_node_158 | 20 | n |  | TRUE
112 | bus_MV_420_0_node_163 | 20 | n |  | TRUE
113 | bus_MV_420_0_node_164 | 20 | n |  | TRUE
114 | bus_HV_420_0_node_132 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_420_0_load_0 | 0 | 0.36728 | 0.17788 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_420_0_load_146 | 5 | 0.26893 | 0.13025 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_420_0_load_178 | 7 | 0.31138 | 0.15081 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_420_0_load_4 | 10 | 0.33952 | 0.16443 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_420_0_load_144 | 12 | 0.53673 | 0.25995 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_420_0_load_14 | 13 | 0.28077 | 0.13598 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_420_0_load_6 | 14 | 0.12026 | 0.058243 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_420_0_load_187 | 17 | 0.39562 | 0.19161 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_420_0_load_17 | 19 | 0.065699 | 0.03182 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_420_0_load_26 | 20 | 0.2341 | 0.11338 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_420_0_load_11 | 21 | 0.18572 | 0.08995 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_420_0_load_179 | 24 | 0.32536 | 0.15758 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_420_0_load_29 | 25 | 0.26656 | 0.1291 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_420_0_load_141 | 28 | 0.40165 | 0.19453 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_420_0_load_83 | 33 | 0.37671 | 0.18245 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_420_0_load_73 | 34 | 0.33435 | 0.16194 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_420_0_load_84 | 39 | 0.34411 | 0.16666 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_420_0_load_184 | 42 | 0.23684 | 0.11471 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_420_0_load_77 | 45 | 0.34627 | 0.1677 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_420_0_load_95 | 48 | 0.29082 | 0.14085 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_420_0_load_90 | 49 | 0.30722 | 0.14879 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_420_0_load_93 | 50 | 0.3268 | 0.15828 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_420_0_load_172 | 52 | 0.29394 | 0.14236 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_420_0_load_105 | 54 | 0.18132 | 0.087819 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_420_0_load_104 | 55 | 0.10135 | 0.049088 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_420_0_load_155 | 56 | 0.13662 | 0.066168 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_420_0_load_181 | 57 | 0.36044 | 0.17457 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_420_0_load_180 | 60 | 0.27215 | 0.13181 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_420_0_load_126 | 62 | 0.34341 | 0.16632 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_420_0_load_94 | 67 | 0.10315 | 0.049959 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_420_0_load_96 | 68 | 0.13813 | 0.066899 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_420_0_load_97 | 69 | 0.51282 | 0.24837 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_420_0_load_156 | 72 | 0.073643 | 0.035667 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_420_0_load_170 | 74 | 0.076177 | 0.036894 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_420_0_load_171 | 76 | 0.088877 | 0.043045 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_420_0_load_143 | 78 | 0.3454 | 0.16728 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_420_0_load_165 | 79 | 0.58023 | 0.28102 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_420_0_load_108 | 81 | 0.15823 | 0.076633 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_420_0_load_112 | 83 | 0.25215 | 0.12212 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_420_0_load_160 | 88 | 0.23186 | 0.1123 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_420_0_load_124 | 89 | 0.37715 | 0.18266 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_420_0_load_118 | 91 | 0.2379 | 0.11522 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_420_0_load_125 | 92 | 0.19973 | 0.096733 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_420_0_load_119 | 93 | 0.19119 | 0.092599 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_420_0_load_122 | 94 | 0.093173 | 0.045126 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_420_0_load_162 | 97 | 0.078487 | 0.038013 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_420_0_load_157 | 99 | 0.092892 | 0.04499 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_420_0_load_129 | 100 | 0.38 | 0.18404 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_420_0_load_140 | 102 | 0.29669 | 0.14369 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_420_0_load_186 | 105 | 0.28443 | 0.13776 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_420_0_load_137 | 107 | 0.14597 | 0.070697 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_420_0_load_135 | 108 | 0.18891 | 0.091494 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_420_0_load_167 | 109 | 0.81734 | 0.39586 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_420_0_load_163 | 112 | 0.072219 | 0.034977 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 101 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_420_0_line_0 |  | 0 | 1 | 0.14565 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
1 | MV_420_0_line_1 |  | 1 | 2 | 0.67868 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
2 | MV_420_0_line_2 |  | 2 | 7 | 0.022632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_420_0_line_3 |  | 2 | 8 | 0.76658 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
4 | MV_420_0_line_4 |  | 2 | 9 | 0.45234 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
5 | MV_420_0_line_5 |  | 3 | 4 | 0.040885 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
6 | MV_420_0_line_6 |  | 3 | 5 | 0.032435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_420_0_line_7 |  | 3 | 6 | 1.2134 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
8 | MV_420_0_line_8 |  | 4 | 13 | 0.058122 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
9 | MV_420_0_line_9 |  | 6 | 17 | 0.036686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_420_0_line_10 |  | 6 | 18 | 0.47481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_420_0_line_11 |  | 6 | 15 | 0.48862 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
12 | MV_420_0_line_12 |  | 8 | 10 | 0.067664 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
13 | MV_420_0_line_13 |  | 9 | 11 | 0.69003 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
14 | MV_420_0_line_14 |  | 9 | 12 | 0.064144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_420_0_line_15 |  | 11 | 13 | 0.095549 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
16 | MV_420_0_line_16 |  | 14 | 15 | 0.11648 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_420_0_line_17 |  | 15 | 16 | 0.87235 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
18 | MV_420_0_line_18 |  | 16 | 19 | 0.018399 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
19 | MV_420_0_line_19 |  | 18 | 21 | 0.052111 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_420_0_line_20 |  | 19 | 20 | 1.7319 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
21 | MV_420_0_line_21 |  | 20 | 22 | 0.042115 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
22 | MV_420_0_line_22 |  | 22 | 23 | 0.23353 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
23 | MV_420_0_line_23 |  | 23 | 25 | 0.087778 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
24 | MV_420_0_line_24 |  | 24 | 25 | 1.1206 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
25 | MV_420_0_line_25 |  | 24 | 26 | 0.088772 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
26 | MV_420_0_line_26 |  | 26 | 77 | 0.40248 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
27 | MV_420_0_line_27 |  | 27 | 28 | 0.09812 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
28 | MV_420_0_line_28 |  | 27 | 29 | 0.37672 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
29 | MV_420_0_line_29 |  | 27 | 30 | 0.38001 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
30 | MV_420_0_line_30 |  | 28 | 77 | 0.008799 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
31 | MV_420_0_line_31 |  | 29 | 78 | 0.079588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_420_0_line_32 |  | 30 | 73 | 0.1739 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
33 | MV_420_0_line_33 |  | 30 | 74 | 0.023736 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
34 | MV_420_0_line_34 |  | 30 | 71 | 0.34153 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_420_0_line_35 |  | 31 | 32 | 0.56787 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_420_0_line_36 |  | 31 | 33 | 0.0016151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_420_0_line_37 |  | 32 | 48 | 0.031774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_420_0_line_38 |  | 32 | 45 | 0.41447 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_420_0_line_39 |  | 34 | 35 | 0.026015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_420_0_line_40 |  | 35 | 36 | 0.24262 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_420_0_line_41 |  | 36 | 37 | 0.29005 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_420_0_line_42 |  | 36 | 38 | 0.17185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_420_0_line_43 |  | 36 | 39 | 0.10569 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_420_0_line_44 |  | 37 | 51 | 0.16213 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_420_0_line_45 |  | 37 | 52 | 0.059535 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
46 | MV_420_0_line_46 |  | 38 | 56 | 0.0089437 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_420_0_line_47 |  | 39 | 40 | 0.067408 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_420_0_line_48 |  | 40 | 41 | 0.28924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_420_0_line_49 |  | 41 | 42 | 0.037452 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_420_0_line_50 |  | 42 | 43 | 0.095499 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_420_0_line_51 |  | 43 | 44 | 0.53537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_420_0_line_52 |  | 44 | 50 | 0.043466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_420_0_line_53 |  | 44 | 47 | 0.61213 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_420_0_line_54 |  | 45 | 46 | 0.04537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_420_0_line_55 |  | 46 | 47 | 0.34191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_420_0_line_56 |  | 47 | 49 | 0.065914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_420_0_line_57 |  | 50 | 67 | 0.07643 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_420_0_line_58 |  | 51 | 53 | 0.13826 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
59 | MV_420_0_line_59 |  | 51 | 54 | 0.031801 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
60 | MV_420_0_line_60 |  | 52 | 57 | 0.003239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_420_0_line_61 |  | 53 | 55 | 0.0036204 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
62 | MV_420_0_line_62 |  | 54 | 58 | 0.019917 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
63 | MV_420_0_line_63 |  | 55 | 66 | 0.054368 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
64 | MV_420_0_line_64 |  | 58 | 59 | 0.19471 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
65 | MV_420_0_line_65 |  | 59 | 60 | 0.03187 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
66 | MV_420_0_line_66 |  | 60 | 65 | 0.064777 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
67 | MV_420_0_line_67 |  | 61 | 62 | 0.029618 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
68 | MV_420_0_line_68 |  | 61 | 63 | 0.55194 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
69 | MV_420_0_line_69 |  | 62 | 64 | 0.088141 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
70 | MV_420_0_line_70 |  | 63 | 83 | 0.006923 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
71 | MV_420_0_line_71 |  | 63 | 86 | 0.061419 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
72 | MV_420_0_line_72 |  | 64 | 65 | 0.34456 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
73 | MV_420_0_line_73 |  | 66 | 70 | 0.002939 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
74 | MV_420_0_line_74 |  | 68 | 69 | 0.018046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_420_0_line_75 |  | 68 | 70 | 0.04339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_420_0_line_76 |  | 70 | 71 | 0.16864 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_420_0_line_77 |  | 71 | 72 | 0.078466 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
78 | MV_420_0_line_78 |  | 73 | 75 | 0.12621 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
79 | MV_420_0_line_79 |  | 73 | 76 | 0.045973 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
80 | MV_420_0_line_80 |  | 75 | 79 | 0.047266 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
81 | MV_420_0_line_81 |  | 76 | 80 | 0.046249 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
82 | MV_420_0_line_82 |  | 79 | 100 | 0.12084 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
83 | MV_420_0_line_83 |  | 80 | 110 | 0.055648 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
84 | MV_420_0_line_84 |  | 81 | 82 | 0.096217 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
85 | MV_420_0_line_85 |  | 81 | 83 | 0.4305 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
86 | MV_420_0_line_86 |  | 82 | 84 | 1.1176 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
87 | MV_420_0_line_87 |  | 82 | 85 | 0.22037 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_420_0_line_88 |  | 84 | 88 | 0.10703 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
89 | MV_420_0_line_89 |  | 85 | 89 | 0.058773 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_420_0_line_90 |  | 86 | 87 | 0.28905 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
91 | MV_420_0_line_91 |  | 87 | 91 | 0.065353 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
92 | MV_420_0_line_92 |  | 88 | 90 | 0.047586 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
93 | MV_420_0_line_93 |  | 90 | 113 | 0.15645 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
94 | MV_420_0_line_94 |  | 91 | 92 | 0.9005 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
95 | MV_420_0_line_95 |  | 93 | 94 | 0.10093 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_420_0_line_96 |  | 94 | 95 | 0.093865 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_420_0_line_97 |  | 95 | 96 | 0.088038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_420_0_line_98 |  | 96 | 97 | 0.06881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_420_0_line_99 |  | 96 | 98 | 0.05893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_420_0_line_100 |  | 98 | 99 | 0.029933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_420_0_line_101 |  | 99 | 111 | 0.013448 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_420_0_line_102 |  | 101 | 102 | 0.1078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_420_0_line_103 |  | 101 | 103 | 0.2219 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
104 | MV_420_0_line_104 |  | 103 | 106 | 0.17018 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
105 | MV_420_0_line_105 |  | 103 | 107 | 0.017984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_420_0_line_106 |  | 103 | 104 | 0.64888 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
107 | MV_420_0_line_107 |  | 104 | 105 | 0.034555 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
108 | MV_420_0_line_108 |  | 105 | 108 | 0.75286 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
109 | MV_420_0_line_109 |  | 106 | 109 | 0.051233 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
110 | MV_420_0_line_110 |  | 109 | 110 | 0.024439 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
111 | MV_420_0_line_111 |  | 111 | 112 | 0.12722 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
112 | MV_420_0_line_112 |  | 112 | 113 | 0.18548 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_420_0_trafo_132 | 25 MVA 110/20 kV | 114 | 101 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2668467.9389 | 1249764.5705
1 | 2668457.4616 | 1249619.3018
2 | 2668487.7606 | 1249246.9873
3 | 2667521.8915 | 1249139.9345
4 | 2667488.0474 | 1249117.4778
5 | 2667504.357 | 1249167.2209
6 | 2667165.4252 | 1249114.257
7 | 2668465.2881 | 1249247.1056
8 | 2668563.5707 | 1248959.8374
9 | 2668221.5965 | 1248944.5158
10 | 2668599.6633 | 1248902.6031
11 | 2667532.2917 | 1248976.0481
12 | 2668260.9983 | 1248894.5015
13 | 2667522.6718 | 1249070.7945
14 | 2666999.9884 | 1248770.6207
15 | 2666984.2231 | 1248886.024
16 | 2666659.9153 | 1248076.1995
17 | 2667195.5257 | 1249135.3463
18 | 2667344.3246 | 1248776.4695
19 | 2666660.4607 | 1248057.9261
20 | 2668097.2739 | 1247090.9124
21 | 2667377.7097 | 1248805.6471
22 | 2668110.687 | 1247050.9827
23 | 2668165.6265 | 1246872.7663
24 | 2669307.5702 | 1246604.5651
25 | 2668202.9725 | 1246793.3287
26 | 2669329.6142 | 1246518.5732
27 | 2669744.4923 | 1246466.2995
28 | 2669646.505 | 1246471.3963
29 | 2669400.0383 | 1246313.7637
30 | 2670032.6343 | 1246546.6396
31 | 2671151.0475 | 1244523.1891
32 | 2670906.791 | 1244611.2383
33 | 2671149.8126 | 1244524.2301
34 | 2670190.5155 | 1245752.5016
35 | 2670193.4885 | 1245778.3439
36 | 2670112.9852 | 1246007.2197
37 | 2670096.7636 | 1246137.0194
38 | 2670222.7597 | 1246054.3623
39 | 2670040.1458 | 1245930.6388
40 | 2669987.3875 | 1245888.4977
41 | 2669790.5009 | 1245739.6071
42 | 2669761.8414 | 1245715.3974
43 | 2669727.8949 | 1245626.1357
44 | 2670008.5283 | 1245339.3612
45 | 2670633.1698 | 1244922.5491
46 | 2670596.2882 | 1244949.1178
47 | 2670357.3389 | 1245046.1589
48 | 2670886.2168 | 1244586.9755
49 | 2670388.9986 | 1244988.3049
50 | 2670037.3768 | 1245371.9468
51 | 2670217.1717 | 1246232.733
52 | 2670050.3892 | 1246174.3535
53 | 2670130.1044 | 1246232.6919
54 | 2670243.0236 | 1246251.2521
55 | 2670128.6 | 1246235.985
56 | 2670218.7288 | 1246062.3462
57 | 2670047.2952 | 1246175.3399
58 | 2670262.2859 | 1246256.5283
59 | 2670422.0662 | 1246301.7547
60 | 2670452.2506 | 1246312.2427
61 | 2670790.2784 | 1246571.2274
62 | 2670816.0705 | 1246556.536
63 | 2670934.7439 | 1246890.2344
64 | 2670764.7102 | 1246484.9058
65 | 2670510.6971 | 1246340.4793
66 | 2670105.4373 | 1246285.1707
67 | 2669979.4046 | 1245421.7547
68 | 2670064.5293 | 1246270.4579
69 | 2670047.6518 | 1246264.0844
70 | 2670104.2722 | 1246287.87
71 | 2669996.8111 | 1246278.6279
72 | 2670065.9886 | 1246308.6879
73 | 2669968.449 | 1246612.2729
74 | 2670048.4608 | 1246564.3287
75 | 2669960.4519 | 1246713.172
76 | 2670007.2539 | 1246636.9242
77 | 2669638.0982 | 1246468.718
78 | 2669390.2423 | 1246234.8269
79 | 2669918.7418 | 1246735.4057
80 | 2670046.2693 | 1246661.7596
81 | 2671052.3225 | 1247310.9621
82 | 2671131.8474 | 1247345.3062
83 | 2670933.8233 | 1246897.0949
84 | 2671397.0785 | 1247507.3414
85 | 2671284.4116 | 1247218.2254
86 | 2670982.9477 | 1246852.173
87 | 2671133.3956 | 1246768.7606
88 | 2671490.8465 | 1247465.0742
89 | 2671251.3754 | 1247169.6162
90 | 2671485.5178 | 1247417.7874
91 | 2671101.6817 | 1246711.6177
92 | 2671833.6556 | 1246187.1091
93 | 2671808.8439 | 1247579.6527
94 | 2671712.9647 | 1247611.1972
95 | 2671650.2944 | 1247541.875
96 | 2671581.4774 | 1247583.229
97 | 2671525.5743 | 1247586.1058
98 | 2671552.3976 | 1247531.9862
99 | 2671548.5972 | 1247502.2954
100 | 2669814.0958 | 1246674.9875
101 | 2669666.5445 | 1246894.541
102 | 2669576.3778 | 1246953.6259
103 | 2669888.4417 | 1246893.6172
104 | 2669434.3447 | 1247357.1228
105 | 2669429.0729 | 1247391.2629
106 | 2669978.3528 | 1246774.1484
107 | 2669903.8471 | 1246902.9609
108 | 2669880.2723 | 1247993.9327
109 | 2670005.1021 | 1246730.4549
110 | 2670017.507 | 1246709.3981
111 | 2671546.8897 | 1247488.9558
112 | 2671629.5216 | 1247392.223
113 | 2671468.3752 | 1247300.3863
114 | 2669666.5445 | 1246894.541

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98861 | -0.36881 | 0.36728 | 0.17788
1 | 0.98865 | -0.36675 | 0 | 0
2 | 0.98873 | -0.36624 | 0 | 0
3 | 0.98949 | -0.34308 | 0 | 0
4 | 0.98948 | -0.34341 | 0 | 0
5 | 0.98948 | -0.34298 | 0.26893 | 0.13025
6 | 0.99004 | -0.33152 | 0 | 0
7 | 0.98872 | -0.36615 | 0.31138 | 0.15081
8 | 0.98859 | -0.36796 | 0 | 0
9 | 0.98888 | -0.36513 | 0 | 0
10 | 0.98856 | -0.36864 | 0.33952 | 0.16443
11 | 0.98939 | -0.34597 | 0 | 0
12 | 0.98883 | -0.36471 | 0.53673 | 0.25995
13 | 0.98943 | -0.34531 | 0.28077 | 0.13598
14 | 0.99028 | -0.32561 | 0.12026 | 0.058243
15 | 0.99031 | -0.32543 | 0 | 0
16 | 0.99147 | -0.28073 | 0 | 0
17 | 0.99002 | -0.33134 | 0.39562 | 0.19161
18 | 0.98992 | -0.33065 | 0 | 0
19 | 0.99148 | -0.28049 | 0.065699 | 0.03182
20 | 0.99383 | -0.19001 | 0.2341 | 0.11338
21 | 0.98991 | -0.33054 | 0.18572 | 0.08995
22 | 0.99386 | -0.18941 | 0 | 0
23 | 0.99401 | -0.18608 | 0 | 0
24 | 0.99593 | -0.11309 | 0.32536 | 0.15758
25 | 0.99414 | -0.18113 | 0.26656 | 0.1291
26 | 0.99609 | -0.10723 | 0 | 0
27 | 0.9966 | -0.093196 | 0 | 0
28 | 0.99641 | -0.10037 | 0.40165 | 0.19453
29 | 0.99654 | -0.095359 | 0 | 0
30 | 0.99696 | -0.085668 | 0 | 0
31 | 0.98943 | -0.077303 | 0 | 0
32 | 0.98971 | -0.079669 | 0 | 0
33 | 0.98943 | -0.077295 | 0.37671 | 0.18245
34 | 0.9946 | -0.10121 | 0.33435 | 0.16194
35 | 0.99461 | -0.10131 | 0 | 0
36 | 0.99477 | -0.10031 | 0 | 0
37 | 0.9958 | -0.10881 | 0 | 0
38 | 0.99474 | -0.10005 | 0 | 0
39 | 0.99429 | -0.10391 | 0.34411 | 0.16666
40 | 0.99412 | -0.10255 | 0 | 0
41 | 0.99339 | -0.096659 | 0 | 0
42 | 0.99329 | -0.095886 | 0.23684 | 0.11471
43 | 0.99297 | -0.098385 | 0 | 0
44 | 0.99178 | -0.088619 | 0 | 0
45 | 0.99024 | -0.075742 | 0.34627 | 0.1677
46 | 0.9903 | -0.076259 | 0 | 0
47 | 0.99074 | -0.080053 | 0 | 0
48 | 0.98969 | -0.079557 | 0.29082 | 0.14085
49 | 0.99072 | -0.079809 | 0.30722 | 0.14879
50 | 0.99175 | -0.088394 | 0.3268 | 0.15828
51 | 0.99593 | -0.10654 | 0 | 0
52 | 0.99578 | -0.10945 | 0.29394 | 0.14236
53 | 0.99611 | -0.10281 | 0 | 0
54 | 0.99589 | -0.10814 | 0.18132 | 0.087819
55 | 0.99612 | -0.10271 | 0.10135 | 0.049088
56 | 0.99474 | -0.10003 | 0.13662 | 0.066168
57 | 0.99578 | -0.10944 | 0.36044 | 0.17457
58 | 0.99587 | -0.10839 | 0 | 0
59 | 0.99577 | -0.11075 | 0 | 0
60 | 0.99575 | -0.11114 | 0.27215 | 0.13181
61 | 0.99545 | -0.11959 | 0 | 0
62 | 0.99546 | -0.11931 | 0.34341 | 0.16632
63 | 0.99522 | -0.12469 | 0 | 0
64 | 0.99555 | -0.1156 | 0 | 0
65 | 0.99572 | -0.11185 | 0 | 0
66 | 0.99619 | -0.10122 | 0 | 0
67 | 0.99174 | -0.088491 | 0.10315 | 0.049959
68 | 0.99616 | -0.1008 | 0.13813 | 0.066899
69 | 0.99615 | -0.10069 | 0.51282 | 0.24837
70 | 0.99619 | -0.10114 | 0 | 0
71 | 0.99645 | -0.096077 | 0 | 0
72 | 0.99644 | -0.096087 | 0.073643 | 0.035667
73 | 0.99739 | -0.076827 | 0 | 0
74 | 0.99696 | -0.085679 | 0.076177 | 0.036894
75 | 0.99736 | -0.077299 | 0 | 0
76 | 0.99751 | -0.074315 | 0.088877 | 0.043045
77 | 0.9964 | -0.10052 | 0 | 0
78 | 0.9965 | -0.095033 | 0.3454 | 0.16728
79 | 0.99735 | -0.077473 | 0.58023 | 0.28102
80 | 0.99764 | -0.07177 | 0 | 0
81 | 0.99496 | -0.13501 | 0.15823 | 0.076633
82 | 0.99494 | -0.13555 | 0 | 0
83 | 0.99522 | -0.12474 | 0.25215 | 0.12212
84 | 0.99476 | -0.13964 | 0 | 0
85 | 0.99483 | -0.13458 | 0 | 0
86 | 0.9952 | -0.12516 | 0 | 0
87 | 0.99518 | -0.12568 | 0 | 0
88 | 0.99474 | -0.13999 | 0.23186 | 0.1123
89 | 0.99479 | -0.13485 | 0.37715 | 0.18266
90 | 0.99473 | -0.14043 | 0 | 0
91 | 0.99516 | -0.12615 | 0.2379 | 0.11522
92 | 0.99507 | -0.12915 | 0.19973 | 0.096733
93 | 0.99451 | -0.14139 | 0.19119 | 0.092599
94 | 0.99455 | -0.14115 | 0.093173 | 0.045126
95 | 0.99458 | -0.14147 | 0 | 0
96 | 0.99461 | -0.14175 | 0 | 0
97 | 0.99461 | -0.14169 | 0.078487 | 0.038013
98 | 0.99464 | -0.14198 | 0 | 0
99 | 0.99466 | -0.1421 | 0.092892 | 0.04499
100 | 0.99733 | -0.07823 | 0.38 | 0.18404
101 | 1 | 0 | -14.4538 | -6.2228
102 | 0.99996 | 0.00037382 | 0.29669 | 0.14369
103 | 0.99849 | -0.054476 | 0 | 0
104 | 0.99834 | -0.059588 | 0 | 0
105 | 0.99833 | -0.059651 | 0.28443 | 0.13776
106 | 0.998 | -0.064382 | 0 | 0
107 | 0.99849 | -0.054445 | 0.14597 | 0.070697
108 | 0.99826 | -0.062003 | 0.18891 | 0.091494
109 | 0.99785 | -0.067362 | 0.81734 | 0.39586
110 | 0.99779 | -0.068708 | 0 | 0
111 | 0.99466 | -0.14217 | 0 | 0
112 | 0.99469 | -0.14119 | 0.072219 | 0.034977
113 | 0.99471 | -0.14079 | 0 | 0
114 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.36728 | -0.17788 | 0.36729 | 0.1777 | 7.3816e-06 | -0.00017692 | 0.011916 | 0.011914 | 0.011916 | 0.98861 | -0.36881 | 0.98865 | -0.36675 | 1.8475
1 | -0.36729 | -0.1777 | 0.36731 | 0.13604 | 2.8519e-05 | -0.041668 | 0.011914 | 0.011436 | 0.011914 | 0.98865 | -0.36675 | 0.98873 | -0.36624 | 1.8673
2 | 0.31138 | 0.15028 | -0.31138 | -0.15081 | 3.081e-06 | -0.00052733 | 0.010095 | 0.010101 | 0.010101 | 0.98873 | -0.36624 | 0.98872 | -0.36615 | 4.5916
3 | 0.33957 | 0.13869 | -0.33952 | -0.16436 | 4.3641e-05 | -0.025673 | 0.010709 | 0.011015 | 0.011015 | 0.98873 | -0.36624 | 0.98859 | -0.36796 | 3.0428
4 | -1.0183 | -0.425 | 1.0184 | 0.3973 | 0.00014368 | -0.027708 | 0.032216 | 0.031912 | 0.032216 | 0.98873 | -0.36624 | 0.98888 | -0.36513 | 5.0495
5 | 1.8367 | 0.78067 | -1.8366 | -0.78371 | 2.5378e-05 | -0.0030351 | 0.058223 | 0.058258 | 0.058258 | 0.98949 | -0.34308 | 0.98948 | -0.34341 | 6.919
6 | 0.26893 | 0.12949 | -0.26893 | -0.13025 | 3.287e-06 | -0.00075724 | 0.0087079 | 0.0087176 | 0.0087176 | 0.98949 | -0.34308 | 0.98948 | -0.34298 | 3.9625
7 | -2.1056 | -0.91016 | 2.1066 | 0.82024 | 0.00097928 | -0.089924 | 0.066922 | 0.065916 | 0.066922 | 0.98949 | -0.34308 | 0.99004 | -0.33152 | 7.948
8 | 1.8366 | 0.78371 | -1.8366 | -0.78375 | 7.0307e-05 | -4.5511e-05 | 0.058258 | 0.058259 | 0.058259 | 0.98948 | -0.34341 | 0.98943 | -0.34531 | 7.1048
9 | 0.39562 | 0.19075 | -0.39562 | -0.19161 | 8.0391e-06 | -0.00085615 | 0.012806 | 0.012817 | 0.012817 | 0.99004 | -0.33152 | 0.99002 | -0.33134 | 5.8261
10 | 0.18575 | 0.077628 | -0.18573 | -0.088732 | 2.2323e-05 | -0.011104 | 0.00587 | 0.0060024 | 0.0060024 | 0.99004 | -0.33152 | 0.98992 | -0.33065 | 2.7284
11 | -2.688 | -1.0886 | 2.6886 | 1.0526 | 0.00063636 | -0.036018 | 0.084559 | 0.084165 | 0.084559 | 0.99004 | -0.33152 | 0.99031 | -0.32543 | 10.0427
12 | 0.33952 | 0.16436 | -0.33952 | -0.16443 | 7.5371e-06 | -7.4476e-05 | 0.011015 | 0.011016 | 0.011016 | 0.98859 | -0.36796 | 0.98856 | -0.36864 | 3.1474
13 | -1.5552 | -0.65576 | 1.5558 | 0.65487 | 0.00059675 | -0.00088367 | 0.04927 | 0.04925 | 0.04927 | 0.98888 | -0.36513 | 0.98939 | -0.34597 | 6.0085
14 | 0.53676 | 0.25846 | -0.53673 | -0.25995 | 2.5928e-05 | -0.0014899 | 0.017391 | 0.01741 | 0.01741 | 0.98888 | -0.36513 | 0.98883 | -0.36471 | 7.9137
15 | -1.5558 | -0.65487 | 1.5558 | 0.64777 | 4.2343e-05 | -0.0071076 | 0.04925 | 0.049169 | 0.04925 | 0.98939 | -0.34597 | 0.98943 | -0.34531 | 5.8492
16 | -0.12026 | -0.058243 | 0.12026 | 0.058109 | 3.1471e-06 | -0.00013439 | 0.0038951 | 0.0038933 | 0.0038951 | 0.99028 | -0.32561 | 0.99031 | -0.32543 | 1.8548
17 | -2.8089 | -1.1107 | 2.8113 | 1.112 | 0.0024096 | 0.0012713 | 0.088047 | 0.088023 | 0.088047 | 0.99031 | -0.32543 | 0.99147 | -0.28073 | 10.7374
18 | -2.8113 | -1.112 | 2.8113 | 1.1106 | 2.6083e-05 | -0.0013579 | 0.088023 | 0.088008 | 0.088023 | 0.99147 | -0.28073 | 0.99148 | -0.28049 | 10.4541
19 | 0.18573 | 0.088732 | -0.18572 | -0.08995 | 2.5129e-06 | -0.0012185 | 0.0060024 | 0.0060178 | 0.0060178 | 0.98992 | -0.33065 | 0.98991 | -0.33054 | 2.7354
20 | -2.877 | -1.1424 | 2.882 | 1.1453 | 0.0050114 | 0.0028378 | 0.090128 | 0.090081 | 0.090128 | 0.99148 | -0.28049 | 0.99383 | -0.19001 | 10.9912
21 | -3.1161 | -1.2587 | 3.1162 | 1.2555 | 7.3416e-05 | -0.0031108 | 0.097618 | 0.097583 | 0.097618 | 0.99383 | -0.19001 | 0.99386 | -0.18941 | 11.5935
22 | -3.1162 | -1.2555 | 3.1166 | 1.2383 | 0.00040616 | -0.017254 | 0.097583 | 0.097393 | 0.097583 | 0.99386 | -0.18941 | 0.99401 | -0.18608 | 11.5894
23 | -3.1166 | -1.2383 | 3.1169 | 1.2385 | 0.00029674 | 0.00020507 | 0.097393 | 0.09739 | 0.097393 | 0.99401 | -0.18608 | 0.99414 | -0.18113 | 11.8772
24 | 3.3879 | 1.3712 | -3.3834 | -1.3676 | 0.0044836 | 0.0036193 | 0.10594 | 0.10597 | 0.10597 | 0.99593 | -0.11309 | 0.99414 | -0.18113 | 12.9232
25 | -3.7133 | -1.5288 | 3.7137 | 1.5292 | 0.00042863 | 0.0003926 | 0.1164 | 0.11639 | 0.1164 | 0.99593 | -0.11309 | 0.99609 | -0.10723 | 14.1947
26 | -3.7137 | -1.5292 | 3.7147 | 1.4996 | 0.00099495 | -0.029607 | 0.11639 | 0.11606 | 0.11639 | 0.99609 | -0.10723 | 0.9964 | -0.10052 | 13.8235
27 | 4.117 | 1.6941 | -4.1164 | -1.6935 | 0.00058152 | 0.0005897 | 0.12895 | 0.12896 | 0.12896 | 0.9966 | -0.093196 | 0.99641 | -0.10037 | 15.7263
28 | 0.34543 | 0.16446 | -0.34541 | -0.1654 | 1.6506e-05 | -0.00094462 | 0.011082 | 0.011094 | 0.011094 | 0.9966 | -0.093196 | 0.99654 | -0.095359 | 1.3529
29 | -4.4624 | -1.8585 | 4.4638 | 1.8309 | 0.0013603 | -0.027599 | 0.14002 | 0.1397 | 0.14002 | 0.9966 | -0.093196 | 0.99696 | -0.085668 | 16.6294
30 | 3.7147 | 1.4989 | -3.7147 | -1.4996 | 2.1688e-05 | -0.00064754 | 0.11605 | 0.11606 | 0.11606 | 0.99641 | -0.10037 | 0.9964 | -0.10052 | 13.7838
31 | 0.34541 | 0.1654 | -0.3454 | -0.16728 | 1.3104e-05 | -0.0018832 | 0.011094 | 0.011118 | 0.011118 | 0.99654 | -0.095359 | 0.9965 | -0.095033 | 5.0534
32 | -11.625 | -4.8933 | 11.6293 | 4.884 | 0.004243 | -0.0093165 | 0.36521 | 0.36507 | 0.36521 | 0.99696 | -0.085668 | 0.99739 | -0.076827 | 43.3745
33 | 0.076177 | 0.036085 | -0.076177 | -0.036894 | 6.8576e-08 | -0.00080929 | 0.0024407 | 0.0024508 | 0.0024508 | 0.99696 | -0.085668 | 0.99696 | -0.085679 | 0.67702
34 | 7.0851 | 3.0263 | -7.082 | -3.0493 | 0.0031145 | -0.023063 | 0.22308 | 0.22338 | 0.22338 | 0.99696 | -0.085668 | 0.99645 | -0.096077 | 26.5296
35 | -0.37671 | -0.18241 | 0.37682 | 0.16917 | 0.00011152 | -0.013244 | 0.012212 | 0.012048 | 0.012212 | 0.98943 | -0.077303 | 0.98971 | -0.079669 | 5.5507
36 | 0.37671 | 0.18241 | -0.37671 | -0.18245 | 3.2158e-07 | -3.7656e-05 | 0.012212 | 0.012212 | 0.012212 | 0.98943 | -0.077303 | 0.98943 | -0.077295 | 5.5509
37 | 0.29083 | 0.14011 | -0.29082 | -0.14085 | 3.7645e-06 | -0.00074198 | 0.0094159 | 0.0094253 | 0.0094253 | 0.98971 | -0.079669 | 0.98969 | -0.079557 | 4.2842
38 | -0.66765 | -0.30928 | 0.66799 | 0.309 | 0.00034004 | -0.00027193 | 0.021462 | 0.021456 | 0.021462 | 0.98971 | -0.079669 | 0.99024 | -0.075742 | 10.2199
39 | -0.33435 | -0.16194 | 0.33436 | 0.16132 | 4.035e-06 | -0.00061326 | 0.010783 | 0.010775 | 0.010783 | 0.9946 | -0.10121 | 0.99461 | -0.10131 | 4.9012
40 | -0.33436 | -0.16132 | 0.33441 | 0.16107 | 5.017e-05 | -0.00025515 | 0.010775 | 0.010771 | 0.010775 | 0.99461 | -0.10131 | 0.99477 | -0.10031 | 5.1309
41 | -2.8114 | -1.2928 | 2.8145 | 1.2868 | 0.0031194 | -0.0059347 | 0.089797 | 0.089714 | 0.089797 | 0.99477 | -0.10031 | 0.9958 | -0.10881 | 40.817
42 | 0.13663 | 0.061898 | -0.13662 | -0.065957 | 4.396e-06 | -0.0040589 | 0.0043527 | 0.0044026 | 0.0044026 | 0.99477 | -0.10031 | 0.99474 | -0.10005 | 2.0012
43 | 2.3404 | 1.0698 | -2.3393 | -1.0693 | 0.0010501 | 0.00053295 | 0.074675 | 0.074677 | 0.074677 | 0.99477 | -0.10031 | 0.99429 | -0.10391 | 35.5604
44 | -3.4689 | -1.6035 | 3.4693 | 1.5916 | 0.00036365 | -0.011951 | 0.11079 | 0.11064 | 0.11079 | 0.9958 | -0.10881 | 0.99593 | -0.10654 | 13.1574
45 | 0.65439 | 0.31672 | -0.65439 | -0.31686 | 9.4254e-06 | -0.00013918 | 0.021075 | 0.021077 | 0.021077 | 0.9958 | -0.10881 | 0.99578 | -0.10945 | 2.5704
46 | 0.13662 | 0.065957 | -0.13662 | -0.066168 | 2.3156e-07 | -0.00021123 | 0.0044026 | 0.0044053 | 0.0044053 | 0.99474 | -0.10005 | 0.99474 | -0.10003 | 2.0024
47 | 1.9952 | 0.9026 | -1.9949 | -0.90409 | 0.00036388 | -0.0014829 | 0.063579 | 0.063599 | 0.063599 | 0.99429 | -0.10391 | 0.99412 | -0.10255 | 28.9084
48 | 1.9949 | 0.90409 | -1.9933 | -0.91044 | 0.0015638 | -0.0063561 | 0.063599 | 0.063681 | 0.063681 | 0.99412 | -0.10255 | 0.99339 | -0.096659 | 28.9457
49 | 1.9933 | 0.91044 | -1.9931 | -0.91126 | 0.00020279 | -0.00082219 | 0.063681 | 0.063691 | 0.063691 | 0.99339 | -0.096659 | 0.99329 | -0.095886 | 28.9506
50 | 1.7563 | 0.79656 | -1.7557 | -0.79633 | 0.00053447 | 0.00022233 | 0.056045 | 0.056047 | 0.056047 | 0.99329 | -0.095886 | 0.99297 | -0.098385 | 26.6889
51 | 1.7557 | 0.79633 | -1.7535 | -0.80826 | 0.0022512 | -0.011921 | 0.056047 | 0.056199 | 0.056199 | 0.99297 | -0.098385 | 0.99178 | -0.088619 | 25.545
52 | 0.42996 | 0.20713 | -0.42995 | -0.20815 | 1.1208e-05 | -0.0010175 | 0.013891 | 0.013904 | 0.013904 | 0.99178 | -0.088619 | 0.99175 | -0.088394 | 6.3201
53 | 1.3235 | 0.60113 | -1.322 | -0.61505 | 0.0014689 | -0.013925 | 0.04231 | 0.042485 | 0.042485 | 0.99178 | -0.088619 | 0.99074 | -0.080053 | 19.3114
54 | -1.0143 | -0.47671 | 1.0143 | 0.47567 | 6.4623e-05 | -0.0010431 | 0.032671 | 0.032657 | 0.032671 | 0.99024 | -0.075742 | 0.9903 | -0.076259 | 14.8503
55 | -1.0143 | -0.47567 | 1.0148 | 0.4678 | 0.00048533 | -0.0078654 | 0.032657 | 0.032559 | 0.032657 | 0.9903 | -0.076259 | 0.99074 | -0.080053 | 14.8443
56 | 0.30723 | 0.14725 | -0.30722 | -0.14879 | 8.6883e-06 | -0.0015422 | 0.0099269 | 0.0099464 | 0.0099464 | 0.99074 | -0.080053 | 0.99072 | -0.079809 | 4.5211
57 | 0.10315 | 0.049871 | -0.10315 | -0.049959 | 1.5152e-06 | -8.8794e-05 | 0.0033351 | 0.0033362 | 0.0033362 | 0.99175 | -0.088394 | 0.99174 | -0.088491 | 1.5887
58 | -6.2531 | -2.6808 | 6.2541 | 2.6713 | 0.00098336 | -0.0095768 | 0.1972 | 0.19708 | 0.1972 | 0.99593 | -0.10654 | 0.99611 | -0.10281 | 23.4209
59 | 2.7838 | 1.0893 | -2.7837 | -1.0892 | 8.509e-05 | 4.1547e-05 | 0.086647 | 0.086648 | 0.086648 | 0.99593 | -0.10654 | 0.99589 | -0.10814 | 10.5668
60 | 0.36044 | 0.17449 | -0.36044 | -0.17457 | 5.8284e-07 | -7.6511e-05 | 0.011609 | 0.01161 | 0.01161 | 0.99578 | -0.10945 | 0.99578 | -0.10944 | 5.2773
61 | -6.2541 | -2.6713 | 6.2541 | 2.671 | 2.5734e-05 | -0.00025084 | 0.19708 | 0.19708 | 0.19708 | 0.99611 | -0.10281 | 0.99612 | -0.10271 | 23.4067
62 | 2.6024 | 1.0014 | -2.6024 | -1.0029 | 2.3816e-05 | -0.0014874 | 0.080827 | 0.080842 | 0.080842 | 0.99589 | -0.10814 | 0.99587 | -0.10839 | 9.6012
63 | -6.3554 | -2.7201 | 6.3558 | 2.7164 | 0.00039924 | -0.0037555 | 0.20034 | 0.20029 | 0.20034 | 0.99612 | -0.10271 | 0.99619 | -0.10122 | 23.7935
64 | 2.6024 | 1.0029 | -2.6021 | -1.0174 | 0.00023332 | -0.014538 | 0.080842 | 0.080997 | 0.080997 | 0.99587 | -0.10839 | 0.99577 | -0.11075 | 9.6196
65 | 2.6021 | 1.0174 | -2.6021 | -1.0198 | 3.8274e-05 | -0.0023792 | 0.080997 | 0.081023 | 0.081023 | 0.99577 | -0.11075 | 0.99575 | -0.11114 | 9.6226
66 | 2.3299 | 0.88799 | -2.3299 | -0.89284 | 6.1984e-05 | -0.0048502 | 0.072286 | 0.072336 | 0.072336 | 0.99575 | -0.11114 | 0.99572 | -0.11185 | 8.591
67 | -1.9859 | -0.75452 | 1.986 | 0.75229 | 2.0564e-05 | -0.0022235 | 0.061608 | 0.061585 | 0.061608 | 0.99545 | -0.11959 | 0.99546 | -0.11931 | 7.3168
68 | 1.9859 | 0.75452 | -1.9855 | -0.79594 | 0.00038608 | -0.041423 | 0.061608 | 0.062048 | 0.062048 | 0.99545 | -0.11959 | 0.99522 | -0.12469 | 7.3692
69 | -2.3294 | -0.91862 | 2.3295 | 0.91863 | 0.00016563 | 1.3674e-05 | 0.072613 | 0.072611 | 0.072613 | 0.99546 | -0.11931 | 0.99555 | -0.1156 | 8.8552
70 | 1.5479 | 0.60845 | -1.5479 | -0.60897 | 2.9489e-06 | -0.00052119 | 0.048243 | 0.048248 | 0.048248 | 0.99522 | -0.12469 | 0.99522 | -0.12474 | 5.7302
71 | 0.43766 | 0.18749 | -0.43766 | -0.18764 | 4.1758e-06 | -0.00015143 | 0.013811 | 0.013813 | 0.013813 | 0.99522 | -0.12469 | 0.9952 | -0.12516 | 1.6845
72 | -2.3295 | -0.91863 | 2.3299 | 0.89284 | 0.00033118 | -0.025792 | 0.072611 | 0.072336 | 0.072611 | 0.99555 | -0.1156 | 0.99572 | -0.11185 | 8.6236
73 | -6.3558 | -2.7164 | 6.3559 | 2.7161 | 2.1576e-05 | -0.00020303 | 0.20029 | 0.20029 | 0.20029 | 0.99619 | -0.10122 | 0.99619 | -0.10114 | 23.788
74 | 0.51283 | 0.24794 | -0.51282 | -0.24837 | 6.5666e-06 | -0.00042562 | 0.016507 | 0.016512 | 0.016512 | 0.99616 | -0.1008 | 0.99615 | -0.10069 | 7.5056
75 | -0.65095 | -0.31484 | 0.65098 | 0.31382 | 2.5419e-05 | -0.0010205 | 0.020955 | 0.020942 | 0.020955 | 0.99616 | -0.1008 | 0.99619 | -0.10114 | 9.5248
76 | -7.0068 | -3.03 | 7.0084 | 3.0186 | 0.0015092 | -0.011405 | 0.22121 | 0.22107 | 0.22121 | 0.99619 | -0.10114 | 0.99645 | -0.096077 | 26.2725
77 | 0.073643 | 0.030772 | -0.073643 | -0.035667 | 1.3281e-07 | -0.0048951 | 0.0023122 | 0.0023705 | 0.0023705 | 0.99645 | -0.096077 | 0.99644 | -0.096087 | 0.37156
78 | 0.96027 | 0.4516 | -0.96024 | -0.46117 | 2.1871e-05 | -0.0095722 | 0.030713 | 0.030832 | 0.030832 | 0.99739 | -0.076827 | 0.99736 | -0.077299 | 3.6618
79 | -12.5896 | -5.3356 | 12.5909 | 5.3333 | 0.0013175 | -0.0022851 | 0.39575 | 0.39571 | 0.39575 | 0.99739 | -0.076827 | 0.99751 | -0.074315 | 47.0016
80 | 0.96024 | 0.46117 | -0.96024 | -0.46476 | 8.2346e-06 | -0.0035847 | 0.030832 | 0.030877 | 0.030877 | 0.99736 | -0.077299 | 0.99735 | -0.077473 | 3.6672
81 | -12.6797 | -5.3763 | 12.6811 | 5.374 | 0.0013444 | -0.0022823 | 0.39857 | 0.39853 | 0.39857 | 0.99751 | -0.074315 | 0.99764 | -0.07177 | 47.3359
82 | 0.38 | 0.18374 | -0.38 | -0.18404 | 6.4299e-06 | -0.00030183 | 0.012217 | 0.012221 | 0.012221 | 0.99735 | -0.077473 | 0.99733 | -0.07823 | 1.4904
83 | -12.6811 | -5.374 | 12.6827 | 5.3713 | 0.0016172 | -0.0027476 | 0.39853 | 0.39848 | 0.39853 | 0.99764 | -0.07177 | 0.99779 | -0.068708 | 47.3311
84 | 1.1373 | 0.41096 | -1.1372 | -0.41822 | 2.1718e-05 | -0.0072573 | 0.035084 | 0.035157 | 0.035157 | 0.99496 | -0.13501 | 0.99494 | -0.13555 | 4.1754
85 | -1.2955 | -0.4876 | 1.2957 | 0.48685 | 0.0002474 | -0.0007453 | 0.040161 | 0.04015 | 0.040161 | 0.99496 | -0.13501 | 0.99522 | -0.12474 | 4.8977
86 | 0.76003 | 0.24082 | -0.75992 | -0.32522 | 0.00011325 | -0.084404 | 0.023132 | 0.023987 | 0.023987 | 0.99494 | -0.13555 | 0.99476 | -0.13964 | 2.8488
87 | 0.3772 | 0.17741 | -0.37716 | -0.1826 | 4.3263e-05 | -0.005195 | 0.012094 | 0.012159 | 0.012159 | 0.99494 | -0.13555 | 0.99483 | -0.13458 | 5.527
88 | 0.75992 | 0.32522 | -0.75991 | -0.3333 | 1.1314e-05 | -0.0080816 | 0.023987 | 0.024081 | 0.024081 | 0.99476 | -0.13964 | 0.99474 | -0.13999 | 2.8599
89 | 0.37716 | 0.1826 | -0.37715 | -0.18266 | 1.5484e-05 | -5.9738e-05 | 0.012159 | 0.01216 | 0.01216 | 0.99483 | -0.13458 | 0.99479 | -0.13485 | 5.7906
90 | 0.43766 | 0.18764 | -0.43765 | -0.2095 | 1.028e-05 | -0.021863 | 0.013813 | 0.014075 | 0.014075 | 0.9952 | -0.12516 | 0.99518 | -0.12568 | 1.6716
91 | 0.43765 | 0.2095 | -0.43765 | -0.20967 | 4.6148e-06 | -0.00016087 | 0.014075 | 0.014077 | 0.014077 | 0.99518 | -0.12568 | 0.99516 | -0.12615 | 1.7167
92 | 0.52804 | 0.221 | -0.52804 | -0.22112 | 4.6805e-06 | -0.00011512 | 0.016612 | 0.016613 | 0.016613 | 0.99474 | -0.13999 | 0.99473 | -0.14043 | 2.026
93 | 0.52804 | 0.22112 | -0.52803 | -0.23294 | 7.9657e-06 | -0.01182 | 0.016613 | 0.016749 | 0.016749 | 0.99473 | -0.14043 | 0.99471 | -0.14079 | 1.9892
94 | 0.19974 | 0.094444 | -0.19973 | -0.096733 | 1.3242e-05 | -0.0022892 | 0.0064091 | 0.006438 | 0.006438 | 0.99516 | -0.12615 | 0.99507 | -0.12915 | 0.78513
95 | -0.19119 | -0.092599 | 0.1912 | 0.092484 | 6.8364e-06 | -0.0001149 | 0.0061664 | 0.0061649 | 0.0061664 | 0.99451 | -0.14139 | 0.99455 | -0.14115 | 2.9364
96 | -0.28437 | -0.13761 | 0.28438 | 0.1354 | 1.0504e-05 | -0.0022137 | 0.0091697 | 0.0091419 | 0.0091697 | 0.99455 | -0.14115 | 0.99458 | -0.14147 | 4.1681
97 | -0.28438 | -0.1354 | 0.28439 | 0.13332 | 9.7948e-06 | -0.0020765 | 0.0091419 | 0.0091161 | 0.0091419 | 0.99458 | -0.14147 | 0.99461 | -0.14175 | 4.1554
98 | 0.078488 | 0.036388 | -0.078487 | -0.038013 | 5.8379e-07 | -0.0016251 | 0.0025109 | 0.0025311 | 0.0025311 | 0.99461 | -0.14175 | 0.99461 | -0.14169 | 1.1505
99 | -0.36288 | -0.16971 | 0.36289 | 0.16832 | 1.062e-05 | -0.0013888 | 0.011627 | 0.01161 | 0.011627 | 0.99461 | -0.14175 | 0.99464 | -0.14198 | 5.285
100 | -0.36289 | -0.16832 | 0.3629 | 0.16761 | 5.3823e-06 | -0.00070546 | 0.01161 | 0.011601 | 0.01161 | 0.99464 | -0.14198 | 0.99466 | -0.1421 | 5.2773
101 | -0.45579 | -0.2126 | 0.45579 | 0.21229 | 3.8241e-06 | -0.00031654 | 0.014596 | 0.014593 | 0.014596 | 0.99466 | -0.1421 | 0.99466 | -0.14217 | 6.6348
102 | 0.2967 | 0.14112 | -0.29669 | -0.14369 | 1.299e-05 | -0.0025699 | 0.0094845 | 0.0095167 | 0.0095167 | 1 | 0 | 0.99996 | 0.00037382 | 4.3258
103 | 14.1431 | 6.0712 | -14.1274 | -6.0492 | 0.015612 | 0.02203 | 0.4443 | 0.44431 | 0.44431 | 1 | 0 | 0.99849 | -0.054476 | 54.184
104 | 13.5081 | 5.7558 | -13.5025 | -5.7636 | 0.0056141 | -0.0078027 | 0.42451 | 0.42466 | 0.42466 | 0.99849 | -0.054476 | 0.998 | -0.064382 | 50.4343
105 | 0.14597 | 0.070269 | -0.14597 | -0.070697 | 5.2729e-07 | -0.00042793 | 0.0046837 | 0.0046891 | 0.0046891 | 0.99849 | -0.054476 | 0.99849 | -0.054445 | 2.1314
106 | 0.47341 | 0.22309 | -0.47335 | -0.22469 | 5.3014e-05 | -0.0015976 | 0.01513 | 0.015151 | 0.015151 | 0.99849 | -0.054476 | 0.99834 | -0.059588 | 1.8477
107 | 0.47335 | 0.22469 | -0.47335 | -0.22732 | 1.4547e-06 | -0.00263 | 0.015151 | 0.015184 | 0.015184 | 0.99834 | -0.059588 | 0.99833 | -0.059651 | 1.8033
108 | 0.18892 | 0.089566 | -0.18891 | -0.091494 | 9.8462e-06 | -0.001928 | 0.0060456 | 0.0060699 | 0.0060699 | 0.99833 | -0.059651 | 0.99826 | -0.062003 | 0.74023
109 | 13.5025 | 5.7636 | -13.5008 | -5.7659 | 0.0016909 | -0.0023458 | 0.42466 | 0.4247 | 0.4247 | 0.998 | -0.064382 | 0.99785 | -0.067362 | 50.4395
110 | 12.6834 | 5.3701 | -12.6827 | -5.3713 | 0.00071012 | -0.0012072 | 0.39846 | 0.39848 | 0.39848 | 0.99785 | -0.067362 | 0.99779 | -0.068708 | 47.3255
111 | -0.45579 | -0.21229 | 0.4558 | 0.21197 | 9.6526e-06 | -0.00031186 | 0.014593 | 0.014589 | 0.014593 | 0.99466 | -0.14217 | 0.99469 | -0.14119 | 1.7796
112 | -0.52802 | -0.24695 | 0.52803 | 0.23294 | 9.6164e-06 | -0.014013 | 0.016917 | 0.016749 | 0.016917 | 0.99469 | -0.14119 | 0.99471 | -0.14079 | 2.0092

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 14.4538 | 6.2228

## res_load
| p_mw | q_mvar
0 | 0.36728 | 0.17788
1 | 0.26893 | 0.13025
2 | 0.31138 | 0.15081
3 | 0.33952 | 0.16443
4 | 0.53673 | 0.25995
5 | 0.28077 | 0.13598
6 | 0.12026 | 0.058243
7 | 0.39562 | 0.19161
8 | 0.065699 | 0.03182
9 | 0.2341 | 0.11338
10 | 0.18572 | 0.08995
11 | 0.32536 | 0.15758
12 | 0.26656 | 0.1291
13 | 0.40165 | 0.19453
14 | 0.37671 | 0.18245
15 | 0.33435 | 0.16194
16 | 0.34411 | 0.16666
17 | 0.23684 | 0.11471
18 | 0.34627 | 0.1677
19 | 0.29082 | 0.14085
20 | 0.30722 | 0.14879
21 | 0.3268 | 0.15828
22 | 0.29394 | 0.14236
23 | 0.18132 | 0.087819
24 | 0.10135 | 0.049088
25 | 0.13662 | 0.066168
26 | 0.36044 | 0.17457
27 | 0.27215 | 0.13181
28 | 0.34341 | 0.16632
29 | 0.10315 | 0.049959
30 | 0.13813 | 0.066899
31 | 0.51282 | 0.24837
32 | 0.073643 | 0.035667
33 | 0.076177 | 0.036894
34 | 0.088877 | 0.043045
35 | 0.3454 | 0.16728
36 | 0.58023 | 0.28102
37 | 0.15823 | 0.076633
38 | 0.25215 | 0.12212
39 | 0.23186 | 0.1123
40 | 0.37715 | 0.18266
41 | 0.2379 | 0.11522
42 | 0.19973 | 0.096733
43 | 0.19119 | 0.092599
44 | 0.093173 | 0.045126
45 | 0.078487 | 0.038013
46 | 0.092892 | 0.04499
47 | 0.38 | 0.18404
48 | 0.29669 | 0.14369
49 | 0.28443 | 0.13776
50 | 0.14597 | 0.070697
51 | 0.18891 | 0.091494
52 | 0.81734 | 0.39586
53 | 0.072219 | 0.034977

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1