## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_428_1_node_116 | 20 | n |  | TRUE
1 | bus_MV_428_1_node_117 | 20 | n |  | TRUE
2 | bus_MV_428_1_node_114 | 20 | n |  | TRUE
3 | bus_MV_428_1_node_115 | 20 | n |  | TRUE
4 | bus_MV_428_1_node_17 | 20 | n |  | TRUE
5 | bus_MV_428_1_node_31 | 20 | n |  | TRUE
6 | bus_MV_428_1_node_19 | 20 | n |  | TRUE
7 | bus_MV_428_1_node_20 | 20 | n |  | TRUE
8 | bus_MV_428_1_node_27 | 20 | n |  | TRUE
9 | bus_MV_428_1_node_30 | 20 | n |  | TRUE
10 | bus_MV_428_1_node_165 | 20 | n |  | TRUE
11 | bus_MV_428_1_node_54 | 20 | n |  | TRUE
12 | bus_MV_428_1_node_35 | 20 | n |  | TRUE
13 | bus_MV_428_1_node_217 | 20 | n |  | TRUE
14 | bus_MV_428_1_node_51 | 20 | n |  | TRUE
15 | bus_MV_428_1_node_36 | 20 | n |  | TRUE
16 | bus_MV_428_1_node_220 | 20 | n |  | TRUE
17 | bus_MV_428_1_node_32 | 20 | n |  | TRUE
18 | bus_MV_428_1_node_37 | 20 | n |  | TRUE
19 | bus_MV_428_1_node_38 | 20 | n |  | TRUE
20 | bus_MV_428_1_node_166 | 20 | n |  | TRUE
21 | bus_MV_428_1_node_49 | 20 | n |  | TRUE
22 | bus_MV_428_1_node_57 | 20 | n |  | TRUE
23 | bus_MV_428_1_node_21 | 20 | n |  | TRUE
24 | bus_MV_428_1_node_22 | 20 | n |  | TRUE
25 | bus_MV_428_1_node_26 | 20 | n |  | TRUE
26 | bus_MV_428_1_node_23 | 20 | n |  | TRUE
27 | bus_MV_428_1_node_24 | 20 | n |  | TRUE
28 | bus_MV_428_1_node_43 | 20 | n |  | TRUE
29 | bus_MV_428_1_node_28 | 20 | n |  | TRUE
30 | bus_MV_428_1_node_25 | 20 | n |  | TRUE
31 | bus_MV_428_1_node_53 | 20 | n |  | TRUE
32 | bus_MV_428_1_node_167 | 20 | n |  | TRUE
33 | bus_MV_428_1_node_164 | 20 | n |  | TRUE
34 | bus_MV_428_1_node_216 | 20 | n |  | TRUE
35 | bus_MV_428_1_node_29 | 20 | n |  | TRUE
36 | bus_MV_428_1_node_50 | 20 | n |  | TRUE
37 | bus_MV_428_1_node_33 | 20 | n |  | TRUE
38 | bus_MV_428_1_node_204 | 20 | n |  | TRUE
39 | bus_MV_428_1_node_42 | 20 | n |  | TRUE
40 | bus_MV_428_1_node_55 | 20 | n |  | TRUE
41 | bus_MV_428_1_node_56 | 20 | n |  | TRUE
42 | bus_MV_428_1_node_203 | 20 | n |  | TRUE
43 | bus_MV_428_1_node_39 | 20 | n |  | TRUE
44 | bus_MV_428_1_node_40 | 20 | n |  | TRUE
45 | bus_MV_428_1_node_162 | 20 | n |  | TRUE
46 | bus_MV_428_1_node_41 | 20 | n |  | TRUE
47 | bus_MV_428_1_node_163 | 20 | n |  | TRUE
48 | bus_MV_428_1_node_66 | 20 | n |  | TRUE
49 | bus_MV_428_1_node_209 | 20 | n |  | TRUE
50 | bus_MV_428_1_node_157 | 20 | n |  | TRUE
51 | bus_MV_428_1_node_158 | 20 | n |  | TRUE
52 | bus_MV_428_1_node_159 | 20 | n |  | TRUE
53 | bus_MV_428_1_node_155 | 20 | n |  | TRUE
54 | bus_MV_428_1_node_213 | 20 | n |  | TRUE
55 | bus_MV_428_1_node_201 | 20 | n |  | TRUE
56 | bus_MV_428_1_node_45 | 20 | n |  | TRUE
57 | bus_MV_428_1_node_47 | 20 | n |  | TRUE
58 | bus_MV_428_1_node_139 | 20 | n |  | TRUE
59 | bus_MV_428_1_node_63 | 20 | n |  | TRUE
60 | bus_MV_428_1_node_126 | 20 | n |  | TRUE
61 | bus_MV_428_1_node_125 | 20 | n |  | TRUE
62 | bus_MV_428_1_node_62 | 20 | n |  | TRUE
63 | bus_MV_428_1_node_61 | 20 | n |  | TRUE
64 | bus_MV_428_1_node_187 | 20 | n |  | TRUE
65 | bus_MV_428_1_node_48 | 20 | n |  | TRUE
66 | bus_MV_428_1_node_44 | 20 | n |  | TRUE
67 | bus_MV_428_1_node_46 | 20 | n |  | TRUE
68 | bus_MV_428_1_node_168 | 20 | n |  | TRUE
69 | bus_MV_428_1_node_156 | 20 | n |  | TRUE
70 | bus_MV_428_1_node_154 | 20 | n |  | TRUE
71 | bus_MV_428_1_node_160 | 20 | n |  | TRUE
72 | bus_MV_428_1_node_58 | 20 | n |  | TRUE
73 | bus_MV_428_1_node_169 | 20 | n |  | TRUE
74 | bus_MV_428_1_node_149 | 20 | n |  | TRUE
75 | bus_MV_428_1_node_100 | 20 | n |  | TRUE
76 | bus_MV_428_1_node_74 | 20 | n |  | TRUE
77 | bus_MV_428_1_node_64 | 20 | n |  | TRUE
78 | bus_MV_428_1_node_65 | 20 | n |  | TRUE
79 | bus_MV_428_1_node_67 | 20 | n |  | TRUE
80 | bus_MV_428_1_node_170 | 20 | n |  | TRUE
81 | bus_MV_428_1_node_171 | 20 | n |  | TRUE
82 | bus_MV_428_1_node_68 | 20 | n |  | TRUE
83 | bus_MV_428_1_node_69 | 20 | n |  | TRUE
84 | bus_MV_428_1_node_70 | 20 | n |  | TRUE
85 | bus_MV_428_1_node_73 | 20 | n |  | TRUE
86 | bus_MV_428_1_node_71 | 20 | n |  | TRUE
87 | bus_MV_428_1_node_122 | 20 | n |  | TRUE
88 | bus_MV_428_1_node_200 | 20 | n |  | TRUE
89 | bus_MV_428_1_node_72 | 20 | n |  | TRUE
90 | bus_MV_428_1_node_128 | 20 | n |  | TRUE
91 | bus_MV_428_1_node_199 | 20 | n |  | TRUE
92 | bus_MV_428_1_node_174 | 20 | n |  | TRUE
93 | bus_MV_428_1_node_173 | 20 | n |  | TRUE
94 | bus_MV_428_1_node_75 | 20 | n |  | TRUE
95 | bus_MV_428_1_node_102 | 20 | n |  | TRUE
96 | bus_MV_428_1_node_196 | 20 | n |  | TRUE
97 | bus_MV_428_1_node_127 | 20 | n |  | TRUE
98 | bus_MV_428_1_node_175 | 20 | n |  | TRUE
99 | bus_MV_428_1_node_105 | 20 | n |  | TRUE
100 | bus_MV_428_1_node_101 | 20 | n |  | TRUE
101 | bus_MV_428_1_node_103 | 20 | n |  | TRUE
102 | bus_MV_428_1_node_150 | 20 | n |  | TRUE
103 | bus_MV_428_1_node_176 | 20 | n |  | TRUE
104 | bus_MV_428_1_node_148 | 20 | n |  | TRUE
105 | bus_MV_428_1_node_84 | 20 | n |  | TRUE
106 | bus_MV_428_1_node_76 | 20 | n |  | TRUE
107 | bus_MV_428_1_node_191 | 20 | n |  | TRUE
108 | bus_MV_428_1_node_80 | 20 | n |  | TRUE
109 | bus_MV_428_1_node_190 | 20 | n |  | TRUE
110 | bus_MV_428_1_node_78 | 20 | n |  | TRUE
111 | bus_MV_428_1_node_79 | 20 | n |  | TRUE
112 | bus_MV_428_1_node_195 | 20 | n |  | TRUE
113 | bus_MV_428_1_node_188 | 20 | n |  | TRUE
114 | bus_MV_428_1_node_186 | 20 | n |  | TRUE
115 | bus_MV_428_1_node_211 | 20 | n |  | TRUE
116 | bus_MV_428_1_node_81 | 20 | n |  | TRUE
117 | bus_MV_428_1_node_172 | 20 | n |  | TRUE
118 | bus_MV_428_1_node_109 | 20 | n |  | TRUE
119 | bus_MV_428_1_node_189 | 20 | n |  | TRUE
120 | bus_MV_428_1_node_82 | 20 | n |  | TRUE
121 | bus_MV_428_1_node_83 | 20 | n |  | TRUE
122 | bus_MV_428_1_node_197 | 20 | n |  | TRUE
123 | bus_MV_428_1_node_221 | 20 | n |  | TRUE
124 | bus_MV_428_1_node_85 | 20 | n |  | TRUE
125 | bus_MV_428_1_node_86 | 20 | n |  | TRUE
126 | bus_MV_428_1_node_87 | 20 | n |  | TRUE
127 | bus_MV_428_1_node_144 | 20 | n |  | TRUE
128 | bus_MV_428_1_node_91 | 20 | n |  | TRUE
129 | bus_MV_428_1_node_177 | 20 | n |  | TRUE
130 | bus_MV_428_1_node_90 | 20 | n |  | TRUE
131 | bus_MV_428_1_node_92 | 20 | n |  | TRUE
132 | bus_MV_428_1_node_94 | 20 | n |  | TRUE
133 | bus_MV_428_1_node_89 | 20 | n |  | TRUE
134 | bus_MV_428_1_node_95 | 20 | n |  | TRUE
135 | bus_MV_428_1_node_88 | 20 | n |  | TRUE
136 | bus_MV_428_1_node_143 | 20 | n |  | TRUE
137 | bus_MV_428_1_node_93 | 20 | n |  | TRUE
138 | bus_MV_428_1_node_119 | 20 | n |  | TRUE
139 | bus_MV_428_1_node_182 | 20 | n |  | TRUE
140 | bus_MV_428_1_node_99 | 20 | n |  | TRUE
141 | bus_MV_428_1_node_202 | 20 | n |  | TRUE
142 | bus_MV_428_1_node_97 | 20 | n |  | TRUE
143 | bus_MV_428_1_node_185 | 20 | n |  | TRUE
144 | bus_MV_428_1_node_181 | 20 | n |  | TRUE
145 | bus_MV_428_1_node_123 | 20 | n |  | TRUE
146 | bus_MV_428_1_node_206 | 20 | n |  | TRUE
147 | bus_MV_428_1_node_104 | 20 | n |  | TRUE
148 | bus_MV_428_1_node_107 | 20 | n |  | TRUE
149 | bus_MV_428_1_node_106 | 20 | n |  | TRUE
150 | bus_MV_428_1_node_110 | 20 | n |  | TRUE
151 | bus_MV_428_1_node_111 | 20 | n |  | TRUE
152 | bus_MV_428_1_node_210 | 20 | n |  | TRUE
153 | bus_MV_428_1_node_108 | 20 | n |  | TRUE
154 | bus_MV_428_1_node_113 | 20 | n |  | TRUE
155 | bus_MV_428_1_node_112 | 20 | n |  | TRUE
156 | bus_MV_428_1_node_183 | 20 | n |  | TRUE
157 | bus_MV_428_1_node_121 | 20 | n |  | TRUE
158 | bus_MV_428_1_node_124 | 20 | n |  | TRUE
159 | bus_MV_428_1_node_118 | 20 | n |  | TRUE
160 | bus_MV_428_1_node_120 | 20 | n |  | TRUE
161 | bus_MV_428_1_node_129 | 20 | n |  | TRUE
162 | bus_MV_428_1_node_130 | 20 | n |  | TRUE
163 | bus_MV_428_1_node_132 | 20 | n |  | TRUE
164 | bus_MV_428_1_node_137 | 20 | n |  | TRUE
165 | bus_MV_428_1_node_214 | 20 | n |  | TRUE
166 | bus_MV_428_1_node_133 | 20 | n |  | TRUE
167 | bus_MV_428_1_node_134 | 20 | n |  | TRUE
168 | bus_MV_428_1_node_135 | 20 | n |  | TRUE
169 | bus_MV_428_1_node_208 | 20 | n |  | TRUE
170 | bus_MV_428_1_node_146 | 20 | n |  | TRUE
171 | bus_MV_428_1_node_219 | 20 | n |  | TRUE
172 | bus_MV_428_1_node_179 | 20 | n |  | TRUE
173 | bus_MV_428_1_node_136 | 20 | n |  | TRUE
174 | bus_MV_428_1_node_184 | 20 | n |  | TRUE
175 | bus_MV_428_1_node_207 | 20 | n |  | TRUE
176 | bus_MV_428_1_node_215 | 20 | n |  | TRUE
177 | bus_MV_428_1_node_138 | 20 | n |  | TRUE
178 | bus_MV_428_1_node_147 | 20 | n |  | TRUE
179 | bus_MV_428_1_node_145 | 20 | n |  | TRUE
180 | bus_MV_428_1_node_178 | 20 | n |  | TRUE
181 | bus_MV_428_1_node_140 | 20 | n |  | TRUE
182 | bus_MV_428_1_node_141 | 20 | n |  | TRUE
183 | bus_MV_428_1_node_142 | 20 | n |  | TRUE
184 | bus_MV_428_1_node_198 | 20 | n |  | TRUE
185 | bus_MV_428_1_node_193 | 20 | n |  | TRUE
186 | bus_MV_428_1_node_192 | 20 | n |  | TRUE
187 | bus_MV_428_1_node_194 | 20 | n |  | TRUE
188 | bus_MV_428_1_node_212 | 20 | n |  | TRUE
189 | bus_MV_428_1_node_205 | 20 | n |  | TRUE
190 | bus_MV_428_1_node_218 | 20 | n |  | TRUE
191 | bus_MV_428_1_node_161 | 20 | n |  | TRUE
192 | bus_MV_428_1_node_180 | 20 | n |  | TRUE
193 | bus_HV_428_1_node_138 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_428_1_load_116 | 0 | 0.2591 | 0.12549 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_428_1_load_114 | 2 | 0.1042 | 0.050465 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_428_1_load_17 | 4 | 0.19383 | 0.093878 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_428_1_load_30 | 9 | 0.31032 | 0.15029 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_428_1_load_165 | 10 | 0.1031 | 0.049932 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_428_1_load_54 | 11 | 0.12896 | 0.062458 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_428_1_load_217 | 13 | 0.30256 | 0.14653 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_428_1_load_51 | 14 | 0.2862 | 0.13861 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_428_1_load_220 | 16 | 0.31267 | 0.15143 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_428_1_load_166 | 20 | 0.23817 | 0.11535 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_428_1_load_49 | 21 | 0.34362 | 0.16642 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_428_1_load_21 | 23 | 0.12565 | 0.060854 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_428_1_load_43 | 28 | 0.22539 | 0.10916 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_428_1_load_53 | 31 | 0.41279 | 0.19992 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_428_1_load_167 | 32 | 0.071242 | 0.034504 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_428_1_load_164 | 33 | 0.075842 | 0.036732 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_428_1_load_216 | 34 | 0.17451 | 0.084521 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_428_1_load_50 | 36 | 0.27697 | 0.13414 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_428_1_load_33 | 37 | 0.31198 | 0.1511 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_428_1_load_55 | 40 | 0.28321 | 0.13717 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_428_1_load_203 | 42 | 0.14767 | 0.07152 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_428_1_load_162 | 45 | 0.15667 | 0.07588 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_428_1_load_163 | 47 | 0.40561 | 0.19645 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_428_1_load_66 | 48 | 0.1706 | 0.082627 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_428_1_load_209 | 49 | 0.21319 | 0.10325 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_428_1_load_155 | 53 | 0.12933 | 0.062639 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_428_1_load_213 | 54 | 0.3985 | 0.193 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_428_1_load_201 | 55 | 0.31497 | 0.15255 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_428_1_load_126 | 60 | 0.14539 | 0.070414 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_428_1_load_125 | 61 | 0.12583 | 0.060945 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_428_1_load_61 | 63 | 0.099277 | 0.048082 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_428_1_load_187 | 64 | 0.11728 | 0.056803 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_428_1_load_44 | 66 | 0.072759 | 0.035239 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_428_1_load_46 | 67 | 0.15096 | 0.073112 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_428_1_load_168 | 68 | 0.081107 | 0.039282 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_428_1_load_154 | 70 | 0.2629 | 0.12733 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_428_1_load_160 | 71 | 0.11304 | 0.054749 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_428_1_load_58 | 72 | 0.27259 | 0.13202 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_428_1_load_169 | 73 | 0.075705 | 0.036666 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_428_1_load_100 | 75 | 0.22568 | 0.1093 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_428_1_load_64 | 77 | 0.17822 | 0.086317 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_428_1_load_170 | 80 | 0.30402 | 0.14725 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_428_1_load_171 | 81 | 0.14324 | 0.069373 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_428_1_load_68 | 82 | 0.40915 | 0.19816 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_428_1_load_122 | 87 | 0.34843 | 0.16875 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_428_1_load_200 | 88 | 0.24084 | 0.11664 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_428_1_load_199 | 91 | 0.077249 | 0.037413 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_428_1_load_173 | 93 | 0.091631 | 0.044379 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_428_1_load_196 | 96 | 0.073408 | 0.035553 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_428_1_load_127 | 97 | 0.15531 | 0.075222 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_428_1_load_175 | 98 | 0.37341 | 0.18085 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_428_1_load_150 | 102 | 0.23644 | 0.11451 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_428_1_load_176 | 103 | 0.082153 | 0.039788 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_428_1_load_148 | 104 | 0.17208 | 0.083344 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_428_1_load_76 | 106 | 0.22456 | 0.10876 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_428_1_load_190 | 109 | 0.080864 | 0.039164 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_428_1_load_195 | 112 | 0.26853 | 0.13005 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_428_1_load_186 | 114 | 0.15461 | 0.074881 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_428_1_load_211 | 115 | 0.12133 | 0.058764 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_428_1_load_172 | 117 | 0.12158 | 0.058882 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_428_1_load_189 | 119 | 0.20544 | 0.099501 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_428_1_load_82 | 120 | 0.3609 | 0.17479 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_428_1_load_221 | 123 | 0.29001 | 0.14046 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_428_1_load_85 | 124 | 0.21575 | 0.10449 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_428_1_load_144 | 127 | 0.076591 | 0.037095 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_428_1_load_177 | 129 | 0.071059 | 0.034415 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_428_1_load_88 | 135 | 0.21439 | 0.10383 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_428_1_load_143 | 136 | 0.31416 | 0.15215 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_428_1_load_119 | 138 | 0.31015 | 0.15021 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_428_1_load_182 | 139 | 0.071768 | 0.034759 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_428_1_load_99 | 140 | 0.27236 | 0.13191 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_428_1_load_202 | 141 | 0.35407 | 0.17148 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_428_1_load_185 | 143 | 0.26634 | 0.129 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_428_1_load_123 | 145 | 0.32562 | 0.1577 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_428_1_load_206 | 146 | 0.13994 | 0.067778 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_428_1_load_104 | 147 | 0.15423 | 0.074697 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_428_1_load_210 | 152 | 0.22619 | 0.10955 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_428_1_load_183 | 156 | 0.091173 | 0.044157 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_428_1_load_121 | 157 | 0.26858 | 0.13008 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_428_1_load_124 | 158 | 0.23104 | 0.1119 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_428_1_load_129 | 161 | 0.15421 | 0.074686 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_428_1_load_214 | 165 | 0.40164 | 0.19452 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_428_1_load_208 | 169 | 0.17104 | 0.082838 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_428_1_load_219 | 171 | 0.17021 | 0.082435 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_428_1_load_179 | 172 | 0.095921 | 0.046457 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_428_1_load_184 | 174 | 0.068949 | 0.033393 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_428_1_load_207 | 175 | 0.29524 | 0.14299 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_428_1_load_215 | 176 | 0.1632 | 0.079041 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_428_1_load_145 | 179 | 0.15431 | 0.074736 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_428_1_load_178 | 180 | 0.099233 | 0.048061 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_428_1_load_140 | 181 | 0.27096 | 0.13123 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_428_1_load_198 | 184 | 0.29254 | 0.14169 | 0 | 0 |  | 1 | TRUE | wye
92 | MV_428_1_load_212 | 188 | 0.15759 | 0.076324 | 0 | 0 |  | 1 | TRUE | wye
93 | MV_428_1_load_205 | 189 | 0.30433 | 0.14739 | 0 | 0 |  | 1 | TRUE | wye
94 | MV_428_1_load_218 | 190 | 0.34561 | 0.16739 | 0 | 0 |  | 1 | TRUE | wye
95 | MV_428_1_load_161 | 191 | 0.32954 | 0.1596 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 177 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_428_1_line_0 |  | 0 | 1 | 0.016325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_428_1_line_1 |  | 1 | 159 | 0.32233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_428_1_line_2 |  | 2 | 3 | 0.034982 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_428_1_line_3 |  | 3 | 99 | 0.18944 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_428_1_line_4 |  | 4 | 5 | 0.21955 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_428_1_line_5 |  | 5 | 6 | 0.25545 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_428_1_line_6 |  | 5 | 7 | 0.37292 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_428_1_line_7 |  | 5 | 8 | 0.49912 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_428_1_line_8 |  | 5 | 9 | 0.03194 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_428_1_line_9 |  | 6 | 10 | 0.055696 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_428_1_line_10 |  | 7 | 11 | 0.017959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_428_1_line_11 |  | 8 | 33 | 0.036348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_428_1_line_12 |  | 8 | 24 | 0.12927 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_428_1_line_13 |  | 9 | 20 | 0.39764 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_428_1_line_14 |  | 10 | 22 | 0.035431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_428_1_line_15 |  | 12 | 13 | 0.039656 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_428_1_line_16 |  | 12 | 14 | 0.27575 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_428_1_line_17 |  | 13 | 37 | 0.44507 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_428_1_line_18 |  | 15 | 16 | 0.047404 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_428_1_line_19 |  | 15 | 17 | 0.19931 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_428_1_line_20 |  | 17 | 39 | 0.50958 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
21 | MV_428_1_line_21 |  | 17 | 37 | 0.013155 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
22 | MV_428_1_line_22 |  | 18 | 19 | 0.037985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_428_1_line_23 |  | 18 | 20 | 0.05176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_428_1_line_24 |  | 19 | 21 | 0.054372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_428_1_line_25 |  | 21 | 27 | 0.003269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_428_1_line_26 |  | 22 | 41 | 0.038584 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_428_1_line_27 |  | 23 | 24 | 0.009054 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_428_1_line_28 |  | 24 | 25 | 0.41702 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_428_1_line_29 |  | 25 | 32 | 0.078983 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_428_1_line_30 |  | 25 | 30 | 0.14071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_428_1_line_31 |  | 26 | 27 | 0.13128 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_428_1_line_32 |  | 26 | 28 | 0.08695 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_428_1_line_33 |  | 27 | 29 | 0.30045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_428_1_line_34 |  | 28 | 37 | 0.34409 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_428_1_line_35 |  | 29 | 34 | 0.059394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_428_1_line_36 |  | 29 | 35 | 0.40867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_428_1_line_37 |  | 30 | 31 | 0.11314 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_428_1_line_38 |  | 31 | 38 | 0.99706 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_428_1_line_39 |  | 35 | 36 | 0.049999 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_428_1_line_40 |  | 38 | 42 | 0.005712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_428_1_line_41 |  | 39 | 49 | 0.032485 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
42 | MV_428_1_line_42 |  | 40 | 41 | 0.013826 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_428_1_line_43 |  | 43 | 44 | 0.27357 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
44 | MV_428_1_line_44 |  | 43 | 45 | 0.23324 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
45 | MV_428_1_line_45 |  | 44 | 46 | 0.33002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_428_1_line_46 |  | 44 | 47 | 0.024315 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
47 | MV_428_1_line_47 |  | 45 | 56 | 0.20179 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_428_1_line_48 |  | 45 | 57 | 0.18294 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
49 | MV_428_1_line_49 |  | 46 | 48 | 0.081966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_428_1_line_50 |  | 47 | 58 | 0.36267 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
51 | MV_428_1_line_51 |  | 49 | 65 | 0.17976 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
52 | MV_428_1_line_52 |  | 50 | 51 | 0.12665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_428_1_line_53 |  | 50 | 52 | 0.2579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_428_1_line_54 |  | 50 | 53 | 0.06823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_428_1_line_55 |  | 51 | 54 | 0.017982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_428_1_line_56 |  | 52 | 55 | 0.091362 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_428_1_line_57 |  | 53 | 70 | 0.053839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_428_1_line_58 |  | 56 | 66 | 0.16559 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_428_1_line_59 |  | 57 | 65 | 0.22299 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
60 | MV_428_1_line_60 |  | 57 | 68 | 0.055189 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_428_1_line_61 |  | 58 | 81 | 0.073501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_428_1_line_62 |  | 58 | 177 | 0.40811 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
63 | MV_428_1_line_63 |  | 59 | 60 | 0.044546 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_428_1_line_64 |  | 59 | 61 | 0.35277 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_428_1_line_65 |  | 61 | 149 | 0.031335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_428_1_line_66 |  | 62 | 63 | 0.064432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_428_1_line_67 |  | 62 | 64 | 0.47157 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_428_1_line_68 |  | 63 | 77 | 0.249 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_428_1_line_69 |  | 64 | 114 | 0.038124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_428_1_line_70 |  | 65 | 69 | 0.11084 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_428_1_line_71 |  | 65 | 70 | 0.048273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_428_1_line_72 |  | 66 | 67 | 0.025355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_428_1_line_73 |  | 69 | 71 | 0.026585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_428_1_line_74 |  | 71 | 191 | 0.024685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_428_1_line_75 |  | 72 | 73 | 0.0546 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_428_1_line_76 |  | 73 | 74 | 0.066863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_428_1_line_77 |  | 74 | 101 | 0.096784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_428_1_line_78 |  | 75 | 76 | 0.008654 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_428_1_line_79 |  | 76 | 94 | 0.42333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_428_1_line_80 |  | 76 | 95 | 0.27278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_428_1_line_81 |  | 76 | 85 | 0.88324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_428_1_line_82 |  | 77 | 78 | 0.090426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_428_1_line_83 |  | 78 | 79 | 0.015031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_428_1_line_84 |  | 79 | 80 | 0.077875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_428_1_line_85 |  | 80 | 81 | 0.0042253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_428_1_line_86 |  | 82 | 83 | 0.041588 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
87 | MV_428_1_line_87 |  | 83 | 84 | 0.44408 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_428_1_line_88 |  | 83 | 85 | 0.80204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_428_1_line_89 |  | 84 | 86 | 0.93231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_428_1_line_90 |  | 84 | 87 | 0.078471 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_428_1_line_91 |  | 85 | 92 | 0.05231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_428_1_line_92 |  | 85 | 93 | 0.04877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_428_1_line_93 |  | 86 | 88 | 0.028086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_428_1_line_94 |  | 86 | 89 | 0.28278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_428_1_line_95 |  | 86 | 90 | 0.45518 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_428_1_line_96 |  | 89 | 91 | 0.050532 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
97 | MV_428_1_line_97 |  | 90 | 97 | 0.073499 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_428_1_line_98 |  | 92 | 98 | 0.006216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_428_1_line_99 |  | 94 | 96 | 0.050524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_428_1_line_100 |  | 95 | 103 | 0.12567 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_428_1_line_101 |  | 95 | 100 | 0.30813 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_428_1_line_102 |  | 96 | 105 | 0.031096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_428_1_line_103 |  | 98 | 131 | 0.038058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_428_1_line_104 |  | 99 | 148 | 0.53174 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_428_1_line_105 |  | 99 | 147 | 0.047749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_428_1_line_106 |  | 100 | 101 | 0.34581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_428_1_line_107 |  | 100 | 102 | 0.082839 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_428_1_line_108 |  | 101 | 104 | 0.019971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_428_1_line_109 |  | 105 | 122 | 0.38133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_428_1_line_110 |  | 105 | 121 | 1.346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_428_1_line_111 |  | 106 | 107 | 0.11217 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
112 | MV_428_1_line_112 |  | 107 | 108 | 0.37114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_428_1_line_113 |  | 107 | 109 | 0.0039349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_428_1_line_114 |  | 108 | 115 | 0.024905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_428_1_line_115 |  | 108 | 116 | 0.012244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_428_1_line_116 |  | 108 | 111 | 0.18239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_428_1_line_117 |  | 109 | 186 | 0.0327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_428_1_line_118 |  | 110 | 111 | 0.25091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_428_1_line_119 |  | 110 | 112 | 0.078729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_428_1_line_120 |  | 111 | 113 | 0.053603 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_428_1_line_121 |  | 111 | 114 | 0.0073487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_428_1_line_122 |  | 112 | 118 | 0.071491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_428_1_line_123 |  | 113 | 119 | 0.012842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_428_1_line_124 |  | 116 | 117 | 0.023417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_428_1_line_125 |  | 118 | 153 | 0.37383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_428_1_line_126 |  | 120 | 121 | 0.045147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_428_1_line_127 |  | 122 | 123 | 0.022705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_428_1_line_128 |  | 124 | 125 | 0.050661 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_428_1_line_129 |  | 125 | 126 | 0.095627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_428_1_line_130 |  | 126 | 127 | 0.010455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_428_1_line_131 |  | 126 | 128 | 0.098741 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_428_1_line_132 |  | 128 | 129 | 0.0067449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_428_1_line_133 |  | 128 | 130 | 0.077607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_428_1_line_134 |  | 130 | 132 | 0.28404 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
135 | MV_428_1_line_135 |  | 130 | 136 | 0.048933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_428_1_line_136 |  | 130 | 133 | 0.057105 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
137 | MV_428_1_line_137 |  | 131 | 132 | 0.094213 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_428_1_line_138 |  | 132 | 140 | 0.07477 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
139 | MV_428_1_line_139 |  | 132 | 137 | 0.39923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_428_1_line_140 |  | 133 | 134 | 0.33846 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
141 | MV_428_1_line_141 |  | 133 | 135 | 0.004703 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_428_1_line_142 |  | 134 | 141 | 0.009609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_428_1_line_143 |  | 134 | 142 | 0.2316 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
144 | MV_428_1_line_144 |  | 137 | 138 | 0.049341 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_428_1_line_145 |  | 137 | 139 | 0.14399 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_428_1_line_146 |  | 138 | 160 | 0.021913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_428_1_line_147 |  | 139 | 150 | 0.013082 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_428_1_line_148 |  | 142 | 143 | 0.029041 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
149 | MV_428_1_line_149 |  | 143 | 144 | 0.004647 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
150 | MV_428_1_line_150 |  | 144 | 192 | 0.14388 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
151 | MV_428_1_line_151 |  | 145 | 146 | 0.42982 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
152 | MV_428_1_line_152 |  | 146 | 153 | 0.048512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_428_1_line_153 |  | 148 | 151 | 0.30688 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_428_1_line_154 |  | 148 | 152 | 0.037561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_428_1_line_155 |  | 149 | 150 | 0.48008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_428_1_line_156 |  | 151 | 155 | 0.16027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_428_1_line_157 |  | 151 | 156 | 0.0092378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_428_1_line_158 |  | 152 | 159 | 0.015467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_428_1_line_159 |  | 153 | 154 | 0.22557 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_428_1_line_160 |  | 154 | 158 | 0.010681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_428_1_line_161 |  | 155 | 157 | 0.005012 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_428_1_line_162 |  | 157 | 160 | 0.065621 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_428_1_line_163 |  | 161 | 162 | 0.037019 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
164 | MV_428_1_line_164 |  | 162 | 163 | 0.4289 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
165 | MV_428_1_line_165 |  | 162 | 164 | 0.16049 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
166 | MV_428_1_line_166 |  | 162 | 165 | 0.34326 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
167 | MV_428_1_line_167 |  | 163 | 166 | 1.03 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_428_1_line_168 |  | 163 | 167 | 0.1382 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
169 | MV_428_1_line_169 |  | 163 | 168 | 0.39011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_428_1_line_170 |  | 163 | 169 | 0.027764 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
171 | MV_428_1_line_171 |  | 164 | 176 | 0.022588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_428_1_line_172 |  | 165 | 177 | 0.028331 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
173 | MV_428_1_line_173 |  | 166 | 170 | 0.21078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_428_1_line_174 |  | 166 | 171 | 0.045652 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
175 | MV_428_1_line_175 |  | 167 | 172 | 0.021086 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
176 | MV_428_1_line_176 |  | 168 | 173 | 0.21601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_428_1_line_177 |  | 168 | 174 | 0.041888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_428_1_line_178 |  | 170 | 178 | 0.40389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_428_1_line_179 |  | 170 | 179 | 0.075424 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
180 | MV_428_1_line_180 |  | 172 | 180 | 0.014965 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
181 | MV_428_1_line_181 |  | 173 | 175 | 0.004632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
182 | MV_428_1_line_182 |  | 178 | 190 | 0.02705 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
183 | MV_428_1_line_183 |  | 180 | 192 | 0.018189 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
184 | MV_428_1_line_184 |  | 181 | 182 | 0.021637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
185 | MV_428_1_line_185 |  | 182 | 183 | 0.24817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
186 | MV_428_1_line_186 |  | 183 | 184 | 0.004964 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
187 | MV_428_1_line_187 |  | 183 | 185 | 0.43108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
188 | MV_428_1_line_188 |  | 183 | 186 | 0.13019 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
189 | MV_428_1_line_189 |  | 185 | 187 | 0.57744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
190 | MV_428_1_line_190 |  | 185 | 188 | 0.12253 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
191 | MV_428_1_line_191 |  | 187 | 189 | 0.049796 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_428_1_trafo_138 | 25 MVA 110/20 kV | 193 | 177 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2663358.0984 | 1245724.7228
1 | 2663354.9528 | 1245708.7115
2 | 2663747.3405 | 1245248.1405
3 | 2663718.5781 | 1245228.229
4 | 2661713.7276 | 1244344.335
5 | 2661515.936 | 1244439.6246
6 | 2661314.373 | 1244282.6983
7 | 2661498.39 | 1244067.1216
8 | 2661168.9433 | 1244080.86
9 | 2661498.8501 | 1244466.6104
10 | 2661298.0901 | 1244229.6836
11 | 2661507.4106 | 1244051.5921
12 | 2660840.0092 | 1244707.8405
13 | 2660879.5051 | 1244704.2764
14 | 2660568.0367 | 1244753.3342
15 | 2661243.3396 | 1244887.723
16 | 2661211.6479 | 1244922.9757
17 | 2661335.0652 | 1244710.7714
18 | 2661107.0253 | 1244282.0484
19 | 2661079.9653 | 1244275.3097
20 | 2661125.2317 | 1244330.5007
21 | 2661030.7729 | 1244297.0296
22 | 2661281.1377 | 1244198.5754
23 | 2661106.3587 | 1244011.5236
24 | 2661100.679 | 1244017.8027
25 | 2660897.0785 | 1243958.9591
26 | 2661105.3863 | 1244391.2505
27 | 2661030.7317 | 1244300.298
28 | 2661070.41 | 1244470.856
29 | 2660867.9033 | 1244478.5031
30 | 2661003.9858 | 1243890.488
31 | 2660959.3926 | 1243786.5035
32 | 2660831.3547 | 1243926.3185
33 | 2661189.2875 | 1244050.758
34 | 2660904.4554 | 1244438.7176
35 | 2660746.3608 | 1244452.051
36 | 2660755.2754 | 1244402.8531
37 | 2661324.5686 | 1244702.8019
38 | 2661048.3082 | 1242793.4199
39 | 2661596.6446 | 1245057.7849
40 | 2661304.7174 | 1244169.1655
41 | 2661308.8572 | 1244178.8037
42 | 2661053.9426 | 1242792.3882
43 | 2661699.7158 | 1245177.56
44 | 2661794.5196 | 1245018.6374
45 | 2661734.2417 | 1245229.7757
46 | 2661910.1315 | 1245235.28
47 | 2661818.1221 | 1245024.4823
48 | 2661966.7073 | 1245175.9706
49 | 2661580.6337 | 1245081.0569
50 | 2661315.4758 | 1245308.1671
51 | 2661314.3259 | 1245396.727
52 | 2661127.2229 | 1245475.7398
53 | 2661367.2871 | 1245263.7723
54 | 2661300.6128 | 1245408.4045
55 | 2661138.876 | 1245566.3554
56 | 2661746.3083 | 1245431.2077
57 | 2661598.0324 | 1245351.9011
58 | 2662127.1579 | 1244834.6842
59 | 2662662.7877 | 1245103.8007
60 | 2662687.765 | 1245066.8724
61 | 2662917.813 | 1245347.5446
62 | 2662295.9761 | 1245257.9557
63 | 2662251.8767 | 1245210.8606
64 | 2662601.1717 | 1245617.4483
65 | 2661441.3792 | 1245194.7359
66 | 2661648.591 | 1245564.8864
67 | 2661665.5429 | 1245583.741
68 | 2661558.7904 | 1245390.7064
69 | 2661367.8258 | 1245112.7631
70 | 2661408.1704 | 1245228.7413
71 | 2661347.1233 | 1245129.4416
72 | 2663071.4559 | 1244348.6332
73 | 2663035.4795 | 1244307.5625
74 | 2663077.5078 | 1244255.6671
75 | 2663628.64 | 1244331.113
76 | 2663635.3789 | 1244325.6593
77 | 2662150.269 | 1244983.5395
78 | 2662212.2935 | 1244917.5774
79 | 2662222.7439 | 1244906.7462
80 | 2662202.2144 | 1244854.8697
81 | 2662198.1436 | 1244853.7374
82 | 2663847.8167 | 1244560.369
83 | 2663889.1551 | 1244555.8218
84 | 2664070.0382 | 1244852.4318
85 | 2663599.0641 | 1244755.8548
86 | 2664502.9791 | 1244426.1834
87 | 2664135.8694 | 1244809.7245
88 | 2664476.9132 | 1244436.8297
89 | 2664690.3253 | 1244427.1343
90 | 2664557.469 | 1244074.4114
91 | 2664724.3309 | 1244389.757
92 | 2663554.387 | 1244782.2944
93 | 2663574.6773 | 1244713.798
94 | 2663800.7548 | 1244253.3073
95 | 2663534.4438 | 1244164.545
96 | 2663827.048 | 1244210.1687
97 | 2664612.137 | 1244025.2835
98 | 2663557.389 | 1244787.7414
99 | 2663589.983 | 1245367.3344
100 | 2663375.5718 | 1244242.9003
101 | 2663149.9663 | 1244193.028
102 | 2663439.4158 | 1244295.6853
103 | 2663563.4679 | 1244220.3233
104 | 2663137.9074 | 1244185.0053
105 | 2663842.7393 | 1244183.3217
106 | 2662691.4256 | 1245942.7031
107 | 2662623.3516 | 1246031.8569
108 | 2662566.2643 | 1245780.9038
109 | 2662620.5096 | 1246034.5784
110 | 2662790.4507 | 1245795.3819
111 | 2662615.4328 | 1245649.2429
112 | 2662843.9063 | 1245737.6824
113 | 2662650.1806 | 1245608.3481
114 | 2662609.9957 | 1245644.2991
115 | 2662547.6501 | 1245764.2961
116 | 2662574.915 | 1245782.3183
117 | 2662573.5289 | 1245798.99
118 | 2662893.5624 | 1245686.3543
119 | 2662658.4669 | 1245598.5177
120 | 2664199.2078 | 1244338.4069
121 | 2664230.9459 | 1244370.6058
122 | 2663716.3514 | 1243984.4826
123 | 2663702.8016 | 1244002.7274
124 | 2663439.9331 | 1244573.0036
125 | 2663434.751 | 1244524.0923
126 | 2663353.0578 | 1244530.98
127 | 2663353.2206 | 1244520.5326
128 | 2663335.3014 | 1244592.3771
129 | 2663333.6656 | 1244598.9207
130 | 2663297.1572 | 1244609.2373
131 | 2663522.3777 | 1244802.8102
132 | 2663437.0808 | 1244789.4998
133 | 2663259.6421 | 1244637.2677
134 | 2663057.806 | 1244675.7795
135 | 2663261.3105 | 1244641.6663
136 | 2663281.0713 | 1244563.0118
137 | 2663332.4821 | 1245046.7041
138 | 2663346.4387 | 1245094.0301
139 | 2663210.4369 | 1245123.1198
140 | 2663373.1999 | 1244828.3551
141 | 2663063.2703 | 1244667.8655
142 | 2662957.0531 | 1244740.7878
143 | 2662933.5694 | 1244724.2607
144 | 2662935.4282 | 1244719.9997
145 | 2663053.7216 | 1244974.6416
146 | 2663087.4495 | 1245403.1395
147 | 2663552.9273 | 1245337.2212
148 | 2663279.8408 | 1245441.6702
149 | 2662934.1817 | 1245374.2922
150 | 2663217.1727 | 1245134.3349
151 | 2663358.2059 | 1245276.9595
152 | 2663284.5813 | 1245478.8909
153 | 2663049.9706 | 1245434.018
154 | 2662889.815 | 1245578.0733
155 | 2663375.9593 | 1245153.464
156 | 2663352.5742 | 1245284.2822
157 | 2663371.5421 | 1245151.0707
158 | 2662883.2254 | 1245569.6532
159 | 2663287.729 | 1245494.0349
160 | 2663326.6758 | 1245103.6146
161 | 2662609.7192 | 1244541.5433
162 | 2662626.9317 | 1244508.7691
163 | 2662874.1977 | 1244567.546
164 | 2662471.7244 | 1244467.9498
165 | 2662344.1931 | 1244703.4146
166 | 2663269.5584 | 1243854.9809
167 | 2662987.1333 | 1244629.9642
168 | 2662819.7225 | 1244688.7969
169 | 2662882.2509 | 1244594.1163
170 | 2663195.456 | 1243657.8565
171 | 2663280.9521 | 1243899.1883
172 | 2662976.9024 | 1244648.4016
173 | 2662713.0954 | 1244782.2222
174 | 2662857.0916 | 1244702.0759
175 | 2662708.6458 | 1244783.5539
176 | 2662451.5659 | 1244457.6417
177 | 2662331.4366 | 1244728.698
178 | 2662961.0406 | 1243896.0062
179 | 2663267.6492 | 1243679.6961
180 | 2662964.1733 | 1244645.609
181 | 2662383.6464 | 1245912.7831
182 | 2662370.6103 | 1245895.9233
183 | 2662507.762 | 1246084.3854
184 | 2662503.5786 | 1246087.0765
185 | 2662541.5653 | 1246370.5058
186 | 2662596.8919 | 1246057.1952
187 | 2662185.0251 | 1246371.2587
188 | 2662644.2844 | 1246303.6989
189 | 2662149.995 | 1246406.6494
190 | 2662980.4064 | 1243914.8912
191 | 2661327.9004 | 1245144.928
192 | 2662950.4035 | 1244657.4934
193 | 2662331.4366 | 1244728.698

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99202 | -0.13399 | 0.2591 | 0.12549
1 | 0.99202 | -0.13404 | 0 | 0
2 | 0.99194 | -0.13409 | 0.1042 | 0.050465
3 | 0.99194 | -0.13405 | 0 | 0
4 | 0.98805 | -0.21261 | 0.19383 | 0.093878
5 | 0.98813 | -0.21208 | 0 | 0
6 | 0.98794 | -0.21338 | 0 | 0
7 | 0.98804 | -0.2127 | 0 | 0
8 | 0.98733 | -0.21813 | 0 | 0
9 | 0.98823 | -0.2114 | 0.31032 | 0.15029
10 | 0.98791 | -0.21313 | 0.1031 | 0.049932
11 | 0.98803 | -0.21267 | 0.12896 | 0.062458
12 | 0.99258 | -0.19434 | 0 | 0
13 | 0.9926 | -0.1942 | 0.30256 | 0.14653
14 | 0.99242 | -0.19531 | 0.2862 | 0.13861
15 | 0.99302 | -0.19141 | 0 | 0
16 | 0.99299 | -0.19159 | 0.31267 | 0.15143
17 | 0.99314 | -0.19065 | 0 | 0
18 | 0.9898 | -0.20263 | 0 | 0
19 | 0.9899 | -0.20354 | 0 | 0
20 | 0.98966 | -0.2014 | 0.23817 | 0.11535
21 | 0.99005 | -0.20483 | 0.34362 | 0.16642
22 | 0.9879 | -0.21301 | 0 | 0
23 | 0.9872 | -0.21707 | 0.12565 | 0.060854
24 | 0.9872 | -0.21708 | 0 | 0
25 | 0.98686 | -0.21416 | 0 | 0
26 | 0.99054 | -0.20913 | 0 | 0
27 | 0.99006 | -0.20492 | 0 | 0
28 | 0.99103 | -0.20565 | 0.22539 | 0.10916
29 | 0.98989 | -0.20355 | 0 | 0
30 | 0.98676 | -0.21322 | 0 | 0
31 | 0.98664 | -0.21402 | 0.41279 | 0.19992
32 | 0.98685 | -0.21409 | 0.071242 | 0.034504
33 | 0.98732 | -0.2181 | 0.075842 | 0.036732
34 | 0.98987 | -0.20342 | 0.17451 | 0.084521
35 | 0.98974 | -0.20229 | 0 | 0
36 | 0.98971 | -0.20246 | 0.27697 | 0.13414
37 | 0.99311 | -0.19096 | 0.31198 | 0.1511
38 | 0.98635 | -0.21591 | 0 | 0
39 | 0.99386 | -0.18753 | 0 | 0
40 | 0.98788 | -0.21283 | 0.28321 | 0.13717
41 | 0.98788 | -0.21288 | 0 | 0
42 | 0.98635 | -0.2159 | 0.14767 | 0.07152
43 | 0.99617 | -0.10844 | 0 | 0
44 | 0.99676 | -0.1058 | 0 | 0
45 | 0.99567 | -0.11065 | 0.15667 | 0.07588
46 | 0.99669 | -0.10524 | 0 | 0
47 | 0.99681 | -0.10555 | 0.40561 | 0.19645
48 | 0.99667 | -0.10508 | 0.1706 | 0.082627
49 | 0.99391 | -0.18732 | 0.21319 | 0.10325
50 | 0.99427 | -0.15426 | 0 | 0
51 | 0.99421 | -0.15367 | 0 | 0
52 | 0.99417 | -0.15333 | 0 | 0
53 | 0.99434 | -0.15481 | 0.12933 | 0.062639
54 | 0.9942 | -0.15358 | 0.3985 | 0.193
55 | 0.99411 | -0.15368 | 0.31497 | 0.15255
56 | 0.99558 | -0.11121 | 0 | 0
57 | 0.99491 | -0.15397 | 0 | 0
58 | 0.99855 | -0.0066149 | 0 | 0
59 | 0.99251 | -0.13872 | 0 | 0
60 | 0.9925 | -0.13864 | 0.14539 | 0.070414
61 | 0.9926 | -0.13805 | 0.12583 | 0.060945
62 | 0.99567 | -0.0063029 | 0 | 0
63 | 0.99592 | -0.0083347 | 0.099277 | 0.048082
64 | 0.99293 | -0.026861 | 0.11728 | 0.056803
65 | 0.99446 | -0.15592 | 0 | 0
66 | 0.99551 | -0.11168 | 0.072759 | 0.035239
67 | 0.99551 | -0.11163 | 0.15096 | 0.073112
68 | 0.9949 | -0.15391 | 0.081107 | 0.039282
69 | 0.9944 | -0.15534 | 0 | 0
70 | 0.99439 | -0.15531 | 0.2629 | 0.12733
71 | 0.99438 | -0.1552 | 0.11304 | 0.054749
72 | 0.99003 | -0.119 | 0.27259 | 0.13202
73 | 0.99006 | -0.11881 | 0.075705 | 0.036666
74 | 0.99009 | -0.11909 | 0 | 0
75 | 0.99095 | -0.12632 | 0.22568 | 0.1093
76 | 0.99095 | -0.12634 | 0 | 0
77 | 0.99741 | 0.0028169 | 0.17822 | 0.086317
78 | 0.99779 | -0.00032213 | 0 | 0
79 | 0.99785 | -0.00084247 | 0 | 0
80 | 0.99818 | -0.0035318 | 0.30402 | 0.14725
81 | 0.9982 | -0.0036928 | 0.14324 | 0.069373
82 | 0.99167 | -0.13153 | 0.40915 | 0.19816
83 | 0.99171 | -0.13132 | 0 | 0
84 | 0.99124 | -0.12818 | 0 | 0
85 | 0.99296 | -0.1402 | 0 | 0
86 | 0.99069 | -0.12456 | 0 | 0
87 | 0.99119 | -0.12852 | 0.34843 | 0.16875
88 | 0.99068 | -0.12448 | 0.24084 | 0.11664
89 | 0.99066 | -0.12436 | 0 | 0
90 | 0.9906 | -0.12386 | 0 | 0
91 | 0.99065 | -0.1244 | 0.077249 | 0.037413
92 | 0.99316 | -0.14159 | 0 | 0
93 | 0.99295 | -0.14015 | 0.091631 | 0.044379
94 | 0.99057 | -0.12395 | 0 | 0
95 | 0.99066 | -0.12401 | 0 | 0
96 | 0.99052 | -0.12365 | 0.073408 | 0.035553
97 | 0.99057 | -0.124 | 0.15531 | 0.075222
98 | 0.99319 | -0.14175 | 0.37341 | 0.18085
99 | 0.99198 | -0.1338 | 0 | 0
100 | 0.99037 | -0.12149 | 0 | 0
101 | 0.99013 | -0.11949 | 0 | 0
102 | 0.99033 | -0.12173 | 0.23644 | 0.11451
103 | 0.99065 | -0.1239 | 0.082153 | 0.039788
104 | 0.99013 | -0.11944 | 0.17208 | 0.083344
105 | 0.9905 | -0.12349 | 0 | 0
106 | 0.99172 | -0.017801 | 0.22456 | 0.10876
107 | 0.99177 | -0.017491 | 0 | 0
108 | 0.9924 | -0.022564 | 0 | 0
109 | 0.99176 | -0.017447 | 0.080864 | 0.039164
110 | 0.99245 | -0.022923 | 0 | 0
111 | 0.99276 | -0.025499 | 0 | 0
112 | 0.99236 | -0.022095 | 0.26853 | 0.13005
113 | 0.99275 | -0.025369 | 0 | 0
114 | 0.99279 | -0.025708 | 0.15461 | 0.074881
115 | 0.99239 | -0.022528 | 0.12133 | 0.058764
116 | 0.99239 | -0.022547 | 0 | 0
117 | 0.99239 | -0.022513 | 0.12158 | 0.058882
118 | 0.99229 | -0.021567 | 0 | 0
119 | 0.99274 | -0.025337 | 0.20544 | 0.099501
120 | 0.98986 | -0.11883 | 0.3609 | 0.17479
121 | 0.98988 | -0.11903 | 0 | 0
122 | 0.99035 | -0.12226 | 0 | 0
123 | 0.99035 | -0.12218 | 0.29001 | 0.14046
124 | 0.9945 | -0.13433 | 0.21575 | 0.10449
125 | 0.99451 | -0.13446 | 0 | 0
126 | 0.99454 | -0.13469 | 0 | 0
127 | 0.99454 | -0.13468 | 0.076591 | 0.037095
128 | 0.99458 | -0.13501 | 0 | 0
129 | 0.99457 | -0.135 | 0.071059 | 0.034415
130 | 0.99461 | -0.13531 | 0 | 0
131 | 0.99336 | -0.14293 | 0 | 0
132 | 0.99377 | -0.14582 | 0 | 0
133 | 0.99473 | -0.13468 | 0 | 0
134 | 0.99543 | -0.13075 | 0 | 0
135 | 0.99472 | -0.13466 | 0.21439 | 0.10383
136 | 0.99459 | -0.13513 | 0.31416 | 0.15215
137 | 0.99288 | -0.13874 | 0 | 0
138 | 0.99275 | -0.13975 | 0.31015 | 0.15021
139 | 0.99279 | -0.13952 | 0.071768 | 0.034759
140 | 0.99373 | -0.14607 | 0.27236 | 0.13191
141 | 0.99542 | -0.1307 | 0.35407 | 0.17148
142 | 0.99594 | -0.1279 | 0 | 0
143 | 0.996 | -0.12754 | 0.26634 | 0.129
144 | 0.99601 | -0.12748 | 0 | 0
145 | 0.99166 | -0.020139 | 0.32562 | 0.1577
146 | 0.99193 | -0.018411 | 0.13994 | 0.067778
147 | 0.99197 | -0.13371 | 0.15423 | 0.074697
148 | 0.99216 | -0.13521 | 0 | 0
149 | 0.99262 | -0.13815 | 0 | 0
150 | 0.99278 | -0.13949 | 0 | 0
151 | 0.99245 | -0.13745 | 0 | 0
152 | 0.99213 | -0.13501 | 0.22619 | 0.10955
153 | 0.99196 | -0.018682 | 0 | 0
154 | 0.99189 | -0.018091 | 0 | 0
155 | 0.99262 | -0.13874 | 0 | 0
156 | 0.99245 | -0.13744 | 0.091173 | 0.044157
157 | 0.99262 | -0.13878 | 0.26858 | 0.13008
158 | 0.99189 | -0.018061 | 0.23104 | 0.1119
159 | 0.99213 | -0.13497 | 0 | 0
160 | 0.99272 | -0.13951 | 0 | 0
161 | 0.99794 | -0.11647 | 0.15421 | 0.074686
162 | 0.99795 | -0.1164 | 0 | 0
163 | 0.99679 | -0.12312 | 0 | 0
164 | 0.9979 | -0.11673 | 0 | 0
165 | 0.99992 | -0.00046284 | 0.40164 | 0.19452
166 | 0.99591 | -0.11658 | 0 | 0
167 | 0.99646 | -0.12494 | 0 | 0
168 | 0.99661 | -0.12168 | 0 | 0
169 | 0.99678 | -0.12317 | 0.17104 | 0.082838
170 | 0.99578 | -0.11547 | 0 | 0
171 | 0.9959 | -0.11667 | 0.17021 | 0.082435
172 | 0.99641 | -0.12521 | 0.095921 | 0.046457
173 | 0.99652 | -0.12095 | 0 | 0
174 | 0.9966 | -0.12164 | 0.068949 | 0.033393
175 | 0.99652 | -0.12093 | 0.29524 | 0.14299
176 | 0.9979 | -0.11669 | 0.1632 | 0.079041
177 | 1 | 0 | -20.1513 | -9.132
178 | 0.9956 | -0.11391 | 0 | 0
179 | 0.99576 | -0.11561 | 0.15431 | 0.074736
180 | 0.99638 | -0.12541 | 0.099233 | 0.048061
181 | 0.99146 | -0.01492 | 0.27096 | 0.13123
182 | 0.99146 | -0.014991 | 0 | 0
183 | 0.99155 | -0.015755 | 0 | 0
184 | 0.99155 | -0.015737 | 0.29254 | 0.14169
185 | 0.9913 | -0.013856 | 0 | 0
186 | 0.99172 | -0.01711 | 0 | 0
187 | 0.99107 | -0.011972 | 0 | 0
188 | 0.99126 | -0.014095 | 0.15759 | 0.076324
189 | 0.99104 | -0.012159 | 0.30433 | 0.14739
190 | 0.99558 | -0.11403 | 0.34561 | 0.16739
191 | 0.99437 | -0.15511 | 0.32954 | 0.1596
192 | 0.99634 | -0.12564 | 0 | 0
193 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.2591 | -0.12549 | 0.25911 | 0.12511 | 1.5287e-06 | -0.00038313 | 0.0083776 | 0.0083728 | 0.0083776 | 0.99202 | -0.13399 | 0.99202 | -0.13404 | 3.808
1 | -0.25911 | -0.12511 | 0.25914 | 0.11754 | 2.9826e-05 | -0.0075656 | 0.0083728 | 0.0082793 | 0.0083728 | 0.99202 | -0.13404 | 0.99213 | -0.13497 | 3.8058
2 | -0.1042 | -0.050465 | 0.1042 | 0.050424 | 7.0743e-07 | -4.0648e-05 | 0.0033693 | 0.0033688 | 0.0033693 | 0.99194 | -0.13409 | 0.99194 | -0.13405 | 1.6044
3 | -0.1042 | -0.050424 | 0.1042 | 0.050204 | 3.8272e-06 | -0.00022014 | 0.0033688 | 0.0033659 | 0.0033688 | 0.99194 | -0.13405 | 0.99198 | -0.1338 | 1.6042
4 | -0.19383 | -0.093878 | 0.19385 | 0.093632 | 1.548e-05 | -0.0002462 | 0.0062924 | 0.0062892 | 0.0062924 | 0.98805 | -0.21261 | 0.98813 | -0.21208 | 2.9964
5 | 0.3864 | 0.18351 | -0.38633 | -0.18376 | 7.1099e-05 | -0.00025317 | 0.012497 | 0.012501 | 0.012501 | 0.98813 | -0.21208 | 0.98794 | -0.21338 | 5.9526
6 | 0.12897 | 0.061612 | -0.12896 | -0.062039 | 1.16e-05 | -0.00042738 | 0.0041756 | 0.0041811 | 0.0041811 | 0.98813 | -0.21208 | 0.98804 | -0.2127 | 1.991
7 | 0.83434 | 0.38324 | -0.8337 | -0.38342 | 0.00063998 | -0.00018045 | 0.026823 | 0.02683 | 0.02683 | 0.98813 | -0.21208 | 0.98733 | -0.21813 | 12.7763
8 | -1.5436 | -0.722 | 1.5437 | 0.72205 | 0.00014104 | 5.1107e-05 | 0.049783 | 0.049783 | 0.049783 | 0.98813 | -0.21208 | 0.98823 | -0.2114 | 23.7063
9 | 0.38633 | 0.18376 | -0.38632 | -0.18505 | 1.1634e-05 | -0.0012944 | 0.012501 | 0.012517 | 0.012517 | 0.98794 | -0.21338 | 0.98791 | -0.21313 | 5.6895
10 | 0.12896 | 0.062039 | -0.12896 | -0.062458 | 4.1967e-07 | -0.00041847 | 0.0041811 | 0.0041865 | 0.0041865 | 0.98804 | -0.2127 | 0.98803 | -0.21267 | 1.9029
11 | 0.075843 | 0.035886 | -0.075842 | -0.036732 | 2.9329e-07 | -0.00084589 | 0.0024532 | 0.0024639 | 0.0024639 | 0.98733 | -0.21813 | 0.98732 | -0.2181 | 1.1199
12 | 0.75786 | 0.34754 | -0.75776 | -0.35052 | 0.0001027 | -0.0029778 | 0.024377 | 0.024414 | 0.024414 | 0.98733 | -0.21813 | 0.9872 | -0.21708 | 11.0972
13 | -1.854 | -0.87234 | 1.8566 | 0.87347 | 0.0025379 | 0.0011254 | 0.059854 | 0.059848 | 0.059854 | 0.98823 | -0.2114 | 0.98966 | -0.2014 | 28.5019
14 | 0.28322 | 0.13512 | -0.28322 | -0.13595 | 3.9816e-06 | -0.00082443 | 0.0091696 | 0.0091801 | 0.0091801 | 0.98791 | -0.21313 | 0.9879 | -0.21301 | 4.1728
15 | -0.28624 | -0.13831 | 0.28624 | 0.13827 | 6.0395e-06 | -4.286e-05 | 0.0092457 | 0.0092451 | 0.0092457 | 0.99258 | -0.19434 | 0.9926 | -0.1942 | 4.4027
16 | 0.28624 | 0.13831 | -0.2862 | -0.13861 | 4.2017e-05 | -0.00029796 | 0.0092457 | 0.0092498 | 0.0092498 | 0.99258 | -0.19434 | 0.99242 | -0.19531 | 4.4047
17 | -0.5888 | -0.28481 | 0.58909 | 0.28446 | 0.00028683 | -0.0003441 | 0.019022 | 0.019015 | 0.019022 | 0.9926 | -0.1942 | 0.99311 | -0.19096 | 9.0581
18 | 0.31268 | 0.15138 | -0.31267 | -0.15143 | 8.6146e-06 | -5.0406e-05 | 0.010099 | 0.0101 | 0.0101 | 0.99302 | -0.19141 | 0.99299 | -0.19159 | 4.8094
19 | -0.31268 | -0.15138 | 0.31272 | 0.15117 | 3.6208e-05 | -0.00021198 | 0.010099 | 0.010096 | 0.010099 | 0.99302 | -0.19141 | 0.99314 | -0.19065 | 4.8091
20 | -4.3392 | -2.0498 | 4.3422 | 2.0199 | 0.0030552 | -0.029882 | 0.13949 | 0.1391 | 0.13949 | 0.99314 | -0.19065 | 0.99386 | -0.18753 | 21.8639
21 | 4.0265 | 1.8987 | -4.0264 | -1.899 | 0.00010639 | -0.0003678 | 0.1294 | 0.1294 | 0.1294 | 0.99314 | -0.19065 | 0.99311 | -0.19096 | 35.7463
22 | -2.095 | -0.9877 | 2.0953 | 0.98688 | 0.00023137 | -0.00082 | 0.067552 | 0.067541 | 0.067552 | 0.9898 | -0.20263 | 0.9899 | -0.20354 | 30.7054
23 | 2.095 | 0.9877 | -2.0947 | -0.98882 | 0.00031539 | -0.001117 | 0.067552 | 0.067567 | 0.067567 | 0.9898 | -0.20263 | 0.98966 | -0.2014 | 30.7123
24 | -2.0953 | -0.98688 | 2.0956 | 0.98571 | 0.00033105 | -0.0011741 | 0.067541 | 0.067525 | 0.067541 | 0.9899 | -0.20354 | 0.99005 | -0.20483 | 30.7004
25 | -2.4392 | -1.1521 | 2.4393 | 1.1521 | 2.7e-05 | -6.8497e-05 | 0.078657 | 0.078656 | 0.078657 | 0.99005 | -0.20483 | 0.99006 | -0.20492 | 35.7531
26 | 0.28322 | 0.13595 | -0.28322 | -0.13685 | 4.3463e-06 | -0.00089777 | 0.0091801 | 0.0091915 | 0.0091915 | 0.9879 | -0.21301 | 0.98788 | -0.21288 | 4.1779
27 | -0.12565 | -0.060854 | 0.12565 | 0.060643 | 2.0131e-07 | -0.00021062 | 0.0040824 | 0.0040797 | 0.0040824 | 0.9872 | -0.21707 | 0.9872 | -0.21708 | 1.8556
28 | 0.63211 | 0.28987 | -0.63188 | -0.2995 | 0.00023156 | -0.0096316 | 0.020335 | 0.020455 | 0.020455 | 0.9872 | -0.21708 | 0.98686 | -0.21416 | 9.2976
29 | 0.071242 | 0.032668 | -0.071242 | -0.034504 | 5.597e-07 | -0.0018364 | 0.0022926 | 0.0023155 | 0.0023155 | 0.98686 | -0.21416 | 0.98685 | -0.21409 | 1.0525
30 | 0.56063 | 0.26684 | -0.56057 | -0.27009 | 6.2107e-05 | -0.0032532 | 0.018162 | 0.018204 | 0.018204 | 0.98686 | -0.21416 | 0.98676 | -0.21322 | 8.2744
31 | 2.8924 | 1.3501 | -2.8909 | -1.3527 | 0.0015172 | -0.0026239 | 0.093024 | 0.093062 | 0.093062 | 0.99054 | -0.20913 | 0.99006 | -0.20492 | 42.3009
32 | -2.8924 | -1.3501 | 2.8937 | 1.3508 | 0.0013406 | 0.00073779 | 0.093024 | 0.093023 | 0.093024 | 0.99054 | -0.20913 | 0.99103 | -0.20565 | 44.2972
33 | 0.45162 | 0.20067 | -0.45153 | -0.20767 | 8.3764e-05 | -0.0070055 | 0.014409 | 0.014494 | 0.014494 | 0.99006 | -0.20492 | 0.98989 | -0.20355 | 6.5881
34 | -3.1191 | -1.46 | 3.1253 | 1.4635 | 0.0061692 | 0.0034599 | 0.10032 | 0.10031 | 0.10032 | 0.99103 | -0.20565 | 0.99311 | -0.19096 | 47.7699
35 | 0.17452 | 0.083132 | -0.17451 | -0.084521 | 2.5276e-06 | -0.0013888 | 0.0056373 | 0.0056548 | 0.0056548 | 0.98989 | -0.20355 | 0.98987 | -0.20342 | 2.5704
36 | 0.27702 | 0.12454 | -0.27697 | -0.13409 | 4.3364e-05 | -0.0095467 | 0.0088573 | 0.0089753 | 0.0089753 | 0.98989 | -0.20355 | 0.98974 | -0.20229 | 4.0797
37 | 0.56057 | 0.27009 | -0.5605 | -0.27018 | 6.6807e-05 | -8.9656e-05 | 0.018204 | 0.018205 | 0.018205 | 0.98676 | -0.21322 | 0.98664 | -0.21402 | 8.6692
38 | 0.14771 | 0.070255 | -0.14767 | -0.071388 | 4.0812e-05 | -0.0011328 | 0.0047858 | 0.0048004 | 0.0048004 | 0.98664 | -0.21402 | 0.98635 | -0.21591 | 2.2859
39 | 0.27697 | 0.13409 | -0.27697 | -0.13414 | 7.1767e-06 | -5.3974e-05 | 0.0089753 | 0.008976 | 0.008976 | 0.98974 | -0.20229 | 0.98971 | -0.20246 | 4.2743
40 | 0.14767 | 0.071388 | -0.14767 | -0.07152 | 1.7577e-07 | -0.00013263 | 0.0048004 | 0.0048021 | 0.0048021 | 0.98635 | -0.21591 | 0.98635 | -0.2159 | 2.1828
41 | -4.3422 | -2.0199 | 4.3424 | 2.018 | 0.00019419 | -0.0019069 | 0.1391 | 0.13908 | 0.1391 | 0.99386 | -0.18753 | 0.99391 | -0.18732 | 21.8028
42 | -0.28321 | -0.13717 | 0.28322 | 0.13685 | 1.56e-06 | -0.0003217 | 0.0091956 | 0.0091915 | 0.0091956 | 0.98788 | -0.21283 | 0.98788 | -0.21288 | 4.1798
43 | -6.5755 | -3.0599 | 6.5792 | 3.045 | 0.0037302 | -0.014967 | 0.21017 | 0.20996 | 0.21017 | 0.99617 | -0.10844 | 0.99676 | -0.1058 | 32.9419
44 | 6.5755 | 3.0599 | -6.5723 | -3.0727 | 0.0031861 | -0.012741 | 0.21017 | 0.21035 | 0.21035 | 0.99617 | -0.10844 | 0.99567 | -0.11065 | 32.9698
45 | 0.17062 | 0.07286 | -0.17061 | -0.080684 | 1.2936e-05 | -0.0078241 | 0.0053731 | 0.0054661 | 0.0054661 | 0.99676 | -0.1058 | 0.99669 | -0.10524 | 2.4846
46 | -6.7498 | -3.1178 | 6.7502 | 3.1165 | 0.00034835 | -0.0013218 | 0.21533 | 0.21531 | 0.21533 | 0.99676 | -0.1058 | 0.99681 | -0.10555 | 33.7511
47 | 0.22375 | 0.10734 | -0.22373 | -0.10756 | 1.8621e-05 | -0.00022714 | 0.0071951 | 0.0071981 | 0.0071981 | 0.99567 | -0.11065 | 0.99558 | -0.11121 | 3.4277
48 | 6.1919 | 2.8895 | -6.1893 | -2.8828 | 0.0025632 | 0.0066422 | 0.19811 | 0.19811 | 0.19811 | 0.99567 | -0.11065 | 0.99491 | -0.15397 | 30.7146
49 | 0.17061 | 0.080684 | -0.1706 | -0.082627 | 3.2839e-06 | -0.0019431 | 0.0054661 | 0.0054904 | 0.0054904 | 0.99669 | -0.10524 | 0.99667 | -0.10508 | 2.4956
50 | -7.1558 | -3.313 | 7.1625 | 3.3306 | 0.0067517 | 0.017657 | 0.22836 | 0.22836 | 0.22836 | 0.99681 | -0.10555 | 0.99855 | -0.0066149 | 35.4051
51 | -4.5556 | -2.1213 | 4.557 | 2.1247 | 0.0013671 | 0.0034307 | 0.14596 | 0.14595 | 0.14596 | 0.99391 | -0.18732 | 0.99446 | -0.15592 | 22.6289
52 | 0.39853 | 0.1896 | -0.3985 | -0.19258 | 2.7842e-05 | -0.002981 | 0.012814 | 0.012851 | 0.012851 | 0.99427 | -0.15426 | 0.99421 | -0.15367 | 5.8414
53 | 0.31502 | 0.14637 | -0.31499 | -0.15245 | 3.5282e-05 | -0.0060763 | 0.010085 | 0.010161 | 0.010161 | 0.99427 | -0.15426 | 0.99417 | -0.15333 | 4.6187
54 | -0.71355 | -0.33597 | 0.7136 | 0.33437 | 4.772e-05 | -0.0015964 | 0.022899 | 0.022879 | 0.022899 | 0.99427 | -0.15426 | 0.99434 | -0.15481 | 10.4085
55 | 0.3985 | 0.19258 | -0.3985 | -0.193 | 3.9663e-06 | -0.0004232 | 0.012851 | 0.012856 | 0.012856 | 0.99421 | -0.15367 | 0.9942 | -0.15358 | 5.8439
56 | 0.31499 | 0.15245 | -0.31497 | -0.15255 | 1.6809e-05 | -9.7266e-05 | 0.010161 | 0.010162 | 0.010162 | 0.99417 | -0.15333 | 0.99411 | -0.15368 | 4.8393
57 | -0.84293 | -0.39701 | 0.84299 | 0.39576 | 5.2562e-05 | -0.0012554 | 0.027051 | 0.027035 | 0.027051 | 0.99434 | -0.15481 | 0.99439 | -0.15531 | 12.2957
58 | 0.22373 | 0.10756 | -0.22372 | -0.10775 | 1.5291e-05 | -0.00018634 | 0.0071981 | 0.0072005 | 0.0072005 | 0.99558 | -0.11121 | 0.99551 | -0.11168 | 3.4288
59 | 6.1082 | 2.8448 | -6.1056 | -2.8572 | 0.0026361 | -0.012378 | 0.19551 | 0.19568 | 0.19568 | 0.99491 | -0.15397 | 0.99446 | -0.15592 | 30.671
60 | 0.081107 | 0.037978 | -0.081107 | -0.039282 | 5.006e-07 | -0.0013041 | 0.0025986 | 0.0026148 | 0.0026148 | 0.99491 | -0.15397 | 0.9949 | -0.15391 | 1.1886
61 | 3.7616 | 1.7366 | -3.7602 | -1.7379 | 0.001408 | -0.0013316 | 0.11978 | 0.1198 | 0.1198 | 0.99855 | -0.0066149 | 0.9982 | -0.0036928 | 54.453
62 | -10.9242 | -5.0672 | 10.9394 | 5.0502 | 0.01527 | -0.017006 | 0.34813 | 0.34782 | 0.34813 | 0.99855 | -0.0066149 | 1 | 0 | 54.5662
63 | 0.14539 | 0.069366 | -0.14539 | -0.070414 | 1.3091e-06 | -0.0010473 | 0.0046853 | 0.0046985 | 0.0046985 | 0.99251 | -0.13872 | 0.9925 | -0.13864 | 2.1357
64 | -0.14539 | -0.069366 | 0.1454 | 0.06896 | 1.3782e-05 | -0.00040626 | 0.0046853 | 0.0046801 | 0.0046853 | 0.99251 | -0.13872 | 0.9926 | -0.13805 | 2.2311
65 | -0.27124 | -0.1299 | 0.27124 | 0.12917 | 3.1967e-06 | -0.00073619 | 0.0087463 | 0.008737 | 0.0087463 | 0.9926 | -0.13805 | 0.99262 | -0.13815 | 3.9756
66 | -3.0274 | -1.3894 | 3.0282 | 1.3881 | 0.00080212 | -0.0012875 | 0.096576 | 0.096558 | 0.096576 | 0.99567 | -0.0063029 | 0.99592 | -0.0083347 | 43.8983
67 | 3.0274 | 1.3894 | -3.0196 | -1.385 | 0.0078371 | 0.0043523 | 0.096576 | 0.096583 | 0.096583 | 0.99567 | -0.0063029 | 0.99293 | -0.026861 | 45.9919
68 | -3.1275 | -1.4362 | 3.1319 | 1.4386 | 0.0044145 | 0.0024698 | 0.099755 | 0.099751 | 0.099755 | 0.99592 | -0.0083347 | 0.99741 | 0.0028169 | 47.5022
69 | 2.9023 | 1.3282 | -2.9019 | -1.329 | 0.00043831 | -0.00076728 | 0.092795 | 0.092806 | 0.092806 | 0.99293 | -0.026861 | 0.99279 | -0.025708 | 42.1846
70 | 0.44262 | 0.21053 | -0.44259 | -0.21314 | 3.0023e-05 | -0.0026081 | 0.014228 | 0.014261 | 0.014261 | 0.99446 | -0.15592 | 0.9944 | -0.15534 | 6.4821
71 | 1.106 | 0.52197 | -1.1059 | -0.52309 | 8.1249e-05 | -0.0011157 | 0.0355 | 0.035514 | 0.035514 | 0.99446 | -0.15592 | 0.99439 | -0.15531 | 16.1429
72 | 0.15096 | 0.072512 | -0.15096 | -0.073112 | 7.995e-07 | -0.00059971 | 0.0048563 | 0.0048638 | 0.0048638 | 0.99551 | -0.11168 | 0.99551 | -0.11163 | 2.2108
73 | 0.44259 | 0.21314 | -0.44258 | -0.21377 | 7.2217e-06 | -0.00062551 | 0.014261 | 0.014269 | 0.014269 | 0.9944 | -0.15534 | 0.99438 | -0.1552 | 6.4857
74 | 0.32954 | 0.15902 | -0.32954 | -0.1596 | 3.7209e-06 | -0.00058167 | 0.010622 | 0.01063 | 0.01063 | 0.99438 | -0.1552 | 0.99437 | -0.15511 | 4.8317
75 | -0.27259 | -0.13202 | 0.2726 | 0.13196 | 7.5864e-06 | -5.9138e-05 | 0.0088313 | 0.0088305 | 0.0088313 | 0.99003 | -0.119 | 0.99006 | -0.11881 | 4.2054
76 | -0.3483 | -0.16863 | 0.34831 | 0.16707 | 1.1344e-05 | -0.0015615 | 0.011283 | 0.011263 | 0.011283 | 0.99006 | -0.11881 | 0.99009 | -0.11909 | 5.1287
77 | -0.34831 | -0.16707 | 0.34833 | 0.16481 | 1.635e-05 | -0.0022605 | 0.011263 | 0.011235 | 0.011263 | 0.99009 | -0.11909 | 0.99013 | -0.11949 | 5.1197
78 | -0.22568 | -0.1093 | 0.22568 | 0.1091 | 6.1626e-07 | -0.00020272 | 0.0073049 | 0.0073023 | 0.0073049 | 0.99095 | -0.12632 | 0.99095 | -0.12634 | 3.3204
79 | 0.72496 | 0.29713 | -0.72466 | -0.30697 | 0.00029583 | -0.0098339 | 0.022824 | 0.022935 | 0.022935 | 0.99095 | -0.12634 | 0.99057 | -0.12395 | 10.425
80 | 0.83965 | 0.37743 | -0.83939 | -0.38374 | 0.00026265 | -0.006316 | 0.026817 | 0.026894 | 0.026894 | 0.99095 | -0.12634 | 0.99066 | -0.12401 | 12.2247
81 | -1.7903 | -0.78366 | 1.7941 | 0.76404 | 0.0038055 | -0.019622 | 0.056931 | 0.056691 | 0.056931 | 0.99095 | -0.12634 | 0.99296 | -0.1402 | 25.8776
82 | -3.3101 | -1.5249 | 3.3115 | 1.5232 | 0.0013428 | -0.0017504 | 0.10548 | 0.10546 | 0.10548 | 0.99741 | 0.0028169 | 0.99779 | -0.00032213 | 47.946
83 | -3.3115 | -1.5232 | 3.3117 | 1.5229 | 0.00022314 | -0.00029113 | 0.10546 | 0.10545 | 0.10546 | 0.99779 | -0.00032213 | 0.99785 | -0.00084247 | 47.9342
84 | -3.3117 | -1.5229 | 3.3129 | 1.5214 | 0.0011558 | -0.0015091 | 0.10545 | 0.10543 | 0.10545 | 0.99785 | -0.00084247 | 0.99818 | -0.0035318 | 47.9322
85 | -3.6169 | -1.6686 | 3.617 | 1.6686 | 7.4852e-05 | -7.8315e-05 | 0.1152 | 0.11519 | 0.1152 | 0.99818 | -0.0035318 | 0.9982 | -0.0036928 | 52.3618
86 | -0.40915 | -0.19816 | 0.40917 | 0.19812 | 1.2976e-05 | -4.0698e-05 | 0.013234 | 0.013233 | 0.013234 | 0.99167 | -0.13153 | 0.99171 | -0.13132 | 6.3018
87 | 0.82256 | 0.34778 | -0.82215 | -0.35809 | 0.00040247 | -0.010303 | 0.025996 | 0.026116 | 0.026116 | 0.99171 | -0.13132 | 0.99124 | -0.12818 | 11.8707
88 | -1.2317 | -0.54591 | 1.2334 | 0.52753 | 0.0016376 | -0.018371 | 0.039218 | 0.038999 | 0.039218 | 0.99171 | -0.13132 | 0.99296 | -0.1402 | 17.8263
89 | 0.4737 | 0.18941 | -0.47342 | -0.21119 | 0.00027924 | -0.021777 | 0.014857 | 0.015105 | 0.015105 | 0.99124 | -0.12818 | 0.99069 | -0.12456 | 6.8661
90 | 0.34845 | 0.16867 | -0.34843 | -0.16875 | 1.7773e-05 | -8.0908e-05 | 0.011274 | 0.011275 | 0.011275 | 0.99124 | -0.12818 | 0.99119 | -0.12852 | 5.3692
91 | -3.1191 | -1.3348 | 3.1198 | 1.3338 | 0.00067929 | -0.0010302 | 0.098634 | 0.098619 | 0.098634 | 0.99296 | -0.1402 | 0.99316 | -0.14159 | 44.8334
92 | 0.091632 | 0.043231 | -0.091631 | -0.044379 | 5.6764e-07 | -0.0011479 | 0.0029455 | 0.0029599 | 0.0029599 | 0.99296 | -0.1402 | 0.99295 | -0.14015 | 1.3454
93 | 0.24084 | 0.11598 | -0.24084 | -0.11664 | 2.2773e-06 | -0.00065747 | 0.0077892 | 0.0077975 | 0.0077975 | 0.99069 | -0.12456 | 0.99068 | -0.12448 | 3.5443
94 | 0.077252 | 0.030729 | -0.077249 | -0.037354 | 2.2843e-06 | -0.0066255 | 0.0024226 | 0.0025004 | 0.0025004 | 0.99069 | -0.12456 | 0.99066 | -0.12436 | 1.1365
95 | 0.15533 | 0.064477 | -0.15532 | -0.075138 | 1.4964e-05 | -0.010661 | 0.0049007 | 0.005028 | 0.005028 | 0.99069 | -0.12456 | 0.9906 | -0.12386 | 2.2855
96 | 0.077249 | 0.037354 | -0.077249 | -0.037413 | 5.6304e-07 | -5.885e-05 | 0.0025004 | 0.0025011 | 0.0025011 | 0.99066 | -0.12436 | 0.99065 | -0.1244 | 1.191
97 | 0.15532 | 0.075138 | -0.15531 | -0.075222 | 3.3114e-06 | -8.4025e-05 | 0.005028 | 0.0050291 | 0.0050291 | 0.9906 | -0.12386 | 0.99057 | -0.124 | 2.3948
98 | -3.1198 | -1.3338 | 3.1199 | 1.3337 | 8.0707e-05 | -0.00012246 | 0.098619 | 0.098618 | 0.098619 | 0.99316 | -0.14159 | 0.99319 | -0.14175 | 44.827
99 | 0.72466 | 0.30697 | -0.72463 | -0.30814 | 3.55e-05 | -0.0011731 | 0.022935 | 0.022949 | 0.022949 | 0.99057 | -0.12395 | 0.99052 | -0.12365 | 10.4311
100 | 0.082154 | 0.036844 | -0.082153 | -0.039788 | 1.1706e-06 | -0.0029443 | 0.0026237 | 0.0026599 | 0.0026599 | 0.99066 | -0.12401 | 0.99065 | -0.1239 | 1.2091
101 | 0.75723 | 0.3469 | -0.75699 | -0.35405 | 0.0002432 | -0.007146 | 0.024271 | 0.024359 | 0.024359 | 0.99066 | -0.12401 | 0.99037 | -0.12149 | 11.0723
102 | 0.65122 | 0.27259 | -0.6512 | -0.27331 | 1.758e-05 | -0.00072322 | 0.020575 | 0.020583 | 0.020583 | 0.99052 | -0.12365 | 0.9905 | -0.12349 | 9.3558
103 | -3.4933 | -1.5145 | 3.4939 | 1.5138 | 0.00062217 | -0.00071194 | 0.11066 | 0.11065 | 0.11066 | 0.99319 | -0.14175 | 0.99336 | -0.14293 | 50.3023
104 | -0.25843 | -0.12378 | 0.25848 | 0.1113 | 4.8455e-05 | -0.012481 | 0.0083388 | 0.0081883 | 0.0083388 | 0.99198 | -0.1338 | 0.99216 | -0.13521 | 3.7903
105 | 0.15423 | 0.073576 | -0.15423 | -0.074697 | 1.5808e-06 | -0.0011214 | 0.0049728 | 0.004987 | 0.004987 | 0.99198 | -0.1338 | 0.99197 | -0.13371 | 2.2668
106 | 0.52054 | 0.23962 | -0.52041 | -0.24768 | 0.00012957 | -0.008058 | 0.016703 | 0.016803 | 0.016803 | 0.99037 | -0.12149 | 0.99013 | -0.11949 | 7.6379
107 | 0.23645 | 0.11442 | -0.23644 | -0.11451 | 8.654e-06 | -9.1573e-05 | 0.0076566 | 0.0076579 | 0.0076579 | 0.99037 | -0.12149 | 0.99033 | -0.12173 | 3.6466
108 | 0.17208 | 0.082876 | -0.17208 | -0.083344 | 8.2764e-07 | -0.00046722 | 0.0055687 | 0.0055746 | 0.0055746 | 0.99013 | -0.11949 | 0.99013 | -0.11944 | 2.5339
109 | 0.29006 | 0.13101 | -0.29002 | -0.13993 | 4.4317e-05 | -0.008918 | 0.0092759 | 0.0093861 | 0.0093861 | 0.9905 | -0.12349 | 0.99035 | -0.12226 | 4.2664
110 | 0.36114 | 0.1423 | -0.36091 | -0.17374 | 0.0002372 | -0.031439 | 0.011313 | 0.011681 | 0.011681 | 0.9905 | -0.12349 | 0.98988 | -0.11903 | 5.3096
111 | -0.22456 | -0.10876 | 0.22457 | 0.10863 | 1.054e-05 | -0.00012511 | 0.0072629 | 0.0072613 | 0.0072629 | 0.99172 | -0.017801 | 0.99177 | -0.017491 | 3.4585
112 | -1.3313 | -0.61035 | 1.3322 | 0.6019 | 0.00089819 | -0.0084551 | 0.04263 | 0.042525 | 0.04263 | 0.99177 | -0.017491 | 0.9924 | -0.022564 | 19.3772
113 | 1.1068 | 0.50172 | -1.1068 | -0.50181 | 6.5722e-06 | -9.046e-05 | 0.03537 | 0.035372 | 0.035372 | 0.99177 | -0.017491 | 0.99176 | -0.017447 | 16.078
114 | 0.12133 | 0.058179 | -0.12133 | -0.058764 | 5.1036e-07 | -0.00058547 | 0.0039142 | 0.0039216 | 0.0039216 | 0.9924 | -0.022564 | 0.99239 | -0.022528 | 1.7825
115 | 0.12158 | 0.058043 | -0.12158 | -0.058331 | 2.5127e-07 | -0.00028784 | 0.0039189 | 0.0039225 | 0.0039225 | 0.9924 | -0.022564 | 0.99239 | -0.022547 | 1.7829
116 | -1.5751 | -0.71812 | 1.5758 | 0.71401 | 0.00061678 | -0.0041073 | 0.050356 | 0.050304 | 0.050356 | 0.9924 | -0.022564 | 0.99276 | -0.025499 | 22.8891
117 | 1.0259 | 0.46264 | -1.0259 | -0.4634 | 4.6856e-05 | -0.00075402 | 0.032757 | 0.032766 | 0.032766 | 0.99176 | -0.017447 | 0.99172 | -0.01711 | 14.8938
118 | -0.96565 | -0.4481 | 0.96597 | 0.4423 | 0.00032043 | -0.0058075 | 0.030965 | 0.030893 | 0.030965 | 0.99245 | -0.022923 | 0.99276 | -0.025499 | 14.0749
119 | 0.96565 | 0.4481 | -0.96555 | -0.44993 | 0.00010085 | -0.0018214 | 0.030965 | 0.030987 | 0.030987 | 0.99245 | -0.022923 | 0.99236 | -0.022095 | 14.0852
120 | 0.20545 | 0.097939 | -0.20545 | -0.099199 | 3.1418e-06 | -0.0012604 | 0.0066181 | 0.006634 | 0.006634 | 0.99276 | -0.025499 | 0.99275 | -0.025369 | 3.0154
121 | -2.7472 | -1.2542 | 2.7473 | 1.2541 | 7.565e-05 | -0.00015049 | 0.087814 | 0.087812 | 0.087814 | 0.99276 | -0.025499 | 0.99279 | -0.025708 | 39.9156
122 | 0.69702 | 0.31987 | -0.69697 | -0.32154 | 4.7545e-05 | -0.0016667 | 0.022309 | 0.02233 | 0.02233 | 0.99236 | -0.022095 | 0.99229 | -0.021567 | 10.1499
123 | 0.20545 | 0.099199 | -0.20544 | -0.099501 | 7.5493e-07 | -0.00030196 | 0.006634 | 0.0066378 | 0.0066378 | 0.99275 | -0.025369 | 0.99274 | -0.025337 | 3.0172
124 | 0.12158 | 0.058331 | -0.12158 | -0.058882 | 4.8184e-07 | -0.00055049 | 0.0039225 | 0.0039294 | 0.0039294 | 0.99239 | -0.022547 | 0.99239 | -0.022513 | 1.7861
125 | 0.69697 | 0.32154 | -0.69672 | -0.33025 | 0.00025004 | -0.0087114 | 0.02233 | 0.022438 | 0.022438 | 0.99229 | -0.021567 | 0.99196 | -0.018682 | 10.1991
126 | -0.3609 | -0.17479 | 0.36091 | 0.17374 | 8.2332e-06 | -0.0010538 | 0.011694 | 0.011681 | 0.011694 | 0.98986 | -0.11883 | 0.98988 | -0.11903 | 5.3156
127 | 0.29002 | 0.13993 | -0.29001 | -0.14046 | 2.6723e-06 | -0.0005309 | 0.0093861 | 0.0093928 | 0.0093928 | 0.99035 | -0.12226 | 0.99035 | -0.12218 | 4.2695
128 | -0.21575 | -0.10449 | 0.21575 | 0.1033 | 3.2676e-06 | -0.0011954 | 0.0069584 | 0.0069434 | 0.0069584 | 0.9945 | -0.13433 | 0.99451 | -0.13446 | 3.1629
129 | -0.21575 | -0.1033 | 0.21576 | 0.10104 | 6.1296e-06 | -0.0022564 | 0.0069434 | 0.0069153 | 0.0069434 | 0.99451 | -0.13446 | 0.99454 | -0.13469 | 3.1561
130 | 0.076591 | 0.036848 | -0.076591 | -0.037095 | 8.5068e-08 | -0.00024687 | 0.002467 | 0.0024702 | 0.0024702 | 0.99454 | -0.13469 | 0.99454 | -0.13468 | 1.1228
131 | -0.29235 | -0.13789 | 0.29236 | 0.13556 | 1.1568e-05 | -0.0023285 | 0.0093823 | 0.0093536 | 0.0093823 | 0.99454 | -0.13469 | 0.99458 | -0.13501 | 4.2647
132 | 0.071059 | 0.034256 | -0.071059 | -0.034415 | 4.726e-08 | -0.00015929 | 0.0022896 | 0.0022917 | 0.0022917 | 0.99458 | -0.13501 | 0.99457 | -0.135 | 1.0417
133 | -0.36342 | -0.16982 | 0.36343 | 0.16799 | 1.4018e-05 | -0.0018288 | 0.011643 | 0.011621 | 0.011643 | 0.99458 | -0.13501 | 0.99461 | -0.13531 | 5.2923
134 | 5.5312 | 2.429 | -5.527 | -2.4356 | 0.0042202 | -0.0065645 | 0.17533 | 0.17545 | 0.17545 | 0.99461 | -0.13531 | 0.99377 | -0.14582 | 48.4661
135 | 0.31417 | 0.151 | -0.31416 | -0.15215 | 6.6958e-06 | -0.0011538 | 0.010117 | 0.010131 | 0.010131 | 0.99461 | -0.13531 | 0.99459 | -0.13513 | 4.6052
136 | -6.2088 | -2.748 | 6.2095 | 2.7448 | 0.00068511 | -0.0031641 | 0.19707 | 0.19702 | 0.19707 | 0.99461 | -0.13531 | 0.99473 | -0.13468 | 30.8879
137 | -3.4939 | -1.5138 | 3.4954 | 1.512 | 0.0015397 | -0.0017639 | 0.11065 | 0.11063 | 0.11065 | 0.99336 | -0.14293 | 0.99377 | -0.14582 | 50.2976
138 | 0.27237 | 0.13183 | -0.27236 | -0.13191 | 1.0294e-05 | -8.1701e-05 | 0.0087899 | 0.008791 | 0.008791 | 0.99377 | -0.14582 | 0.99373 | -0.14607 | 4.1862
139 | 1.7592 | 0.79171 | -1.7575 | -0.80062 | 0.0016771 | -0.0089079 | 0.056038 | 0.056151 | 0.056151 | 0.99377 | -0.14582 | 0.99288 | -0.13874 | 25.5233
140 | -6.4239 | -2.8485 | 6.4282 | 2.8299 | 0.0043442 | -0.018611 | 0.20393 | 0.20368 | 0.20393 | 0.99473 | -0.13468 | 0.99543 | -0.13075 | 31.9641
141 | 0.21439 | 0.10372 | -0.21439 | -0.10383 | 2.9997e-07 | -0.00011102 | 0.0069116 | 0.006913 | 0.006913 | 0.99473 | -0.13468 | 0.99472 | -0.13466 | 3.1423
142 | 0.35407 | 0.17126 | -0.35407 | -0.17148 | 1.6693e-06 | -0.00022684 | 0.011406 | 0.011409 | 0.011409 | 0.99543 | -0.13075 | 0.99542 | -0.1307 | 5.1859
143 | -6.7823 | -3.0012 | 6.7856 | 2.9886 | 0.003308 | -0.012563 | 0.21508 | 0.21491 | 0.21508 | 0.99543 | -0.13075 | 0.99594 | -0.1279 | 33.7121
144 | 1.4144 | 0.64843 | -1.4143 | -0.64837 | 0.00017992 | 5.4637e-05 | 0.045239 | 0.04524 | 0.04524 | 0.99288 | -0.13874 | 0.99275 | -0.13975 | 21.5429
145 | 0.34309 | 0.15219 | -0.34306 | -0.15234 | 3.0557e-05 | -0.00015031 | 0.010912 | 0.010914 | 0.010914 | 0.99288 | -0.13874 | 0.99279 | -0.13952 | 5.1974
146 | 1.1041 | 0.49816 | -1.1041 | -0.49867 | 3.6299e-05 | -0.00050485 | 0.035222 | 0.035229 | 0.035229 | 0.99275 | -0.13975 | 0.99272 | -0.13951 | 16.013
147 | 0.27129 | 0.11758 | -0.27129 | -0.11789 | 1.2915e-06 | -0.00030748 | 0.0085974 | 0.0086009 | 0.0086009 | 0.99279 | -0.13952 | 0.99278 | -0.13949 | 3.9095
148 | -6.7856 | -2.9886 | 6.786 | 2.987 | 0.00041444 | -0.0015766 | 0.21491 | 0.21489 | 0.21491 | 0.99594 | -0.1279 | 0.996 | -0.12754 | 33.6857
149 | -7.0524 | -3.116 | 7.0524 | 3.1158 | 7.1704e-05 | -0.00024927 | 0.22347 | 0.22346 | 0.22347 | 0.996 | -0.12754 | 0.99601 | -0.12748 | 35.0259
150 | -7.0524 | -3.1158 | 7.0547 | 3.1081 | 0.0022191 | -0.0077219 | 0.22346 | 0.22336 | 0.22346 | 0.99601 | -0.12748 | 0.99634 | -0.12564 | 35.0254
151 | -0.32562 | -0.1577 | 0.3257 | 0.15725 | 8.4897e-05 | -0.00045156 | 0.010532 | 0.010526 | 0.010532 | 0.99166 | -0.020139 | 0.99193 | -0.018411 | 5.0153
152 | -0.46565 | -0.22503 | 0.46566 | 0.2239 | 1.4657e-05 | -0.0011353 | 0.015051 | 0.015036 | 0.015051 | 0.99193 | -0.018411 | 0.99196 | -0.018682 | 6.8413
153 | -0.74382 | -0.33715 | 0.74405 | 0.33 | 0.00023047 | -0.0071464 | 0.023761 | 0.023676 | 0.023761 | 0.99216 | -0.13521 | 0.99245 | -0.13745 | 10.8007
154 | 0.48534 | 0.22585 | -0.48533 | -0.22673 | 1.2173e-05 | -0.00087917 | 0.015575 | 0.015586 | 0.015586 | 0.99216 | -0.13521 | 0.99213 | -0.13501 | 7.0847
155 | -0.27124 | -0.12917 | 0.27129 | 0.11789 | 4.815e-05 | -0.011281 | 0.008737 | 0.0086009 | 0.008737 | 0.99262 | -0.13815 | 0.99278 | -0.13949 | 3.9714
156 | -0.83523 | -0.37394 | 0.83538 | 0.37022 | 0.00015134 | -0.0037248 | 0.026618 | 0.026574 | 0.026618 | 0.99245 | -0.13745 | 0.99262 | -0.13874 | 12.0991
157 | 0.091173 | 0.04394 | -0.091173 | -0.044157 | 1.0697e-07 | -0.00021721 | 0.0029439 | 0.0029466 | 0.0029466 | 0.99245 | -0.13745 | 0.99245 | -0.13744 | 1.3394
158 | 0.25914 | 0.11718 | -0.25914 | -0.11754 | 1.4146e-06 | -0.00036308 | 0.008275 | 0.0082793 | 0.0082793 | 0.99213 | -0.13501 | 0.99213 | -0.13497 | 3.7633
159 | 0.23106 | 0.10635 | -0.23104 | -0.11165 | 1.6646e-05 | -0.0052942 | 0.0074023 | 0.0074681 | 0.0074681 | 0.99196 | -0.018682 | 0.99189 | -0.018091 | 3.3946
160 | 0.23104 | 0.11165 | -0.23104 | -0.1119 | 7.9561e-07 | -0.00025067 | 0.0074681 | 0.0074713 | 0.0074713 | 0.99189 | -0.018091 | 0.99189 | -0.018061 | 3.396
161 | -0.83538 | -0.37022 | 0.83538 | 0.3701 | 4.7246e-06 | -0.00011651 | 0.026574 | 0.026572 | 0.026574 | 0.99262 | -0.13874 | 0.99262 | -0.13878 | 12.0789
162 | -1.104 | -0.50018 | 1.1041 | 0.49867 | 0.00010878 | -0.0015116 | 0.035247 | 0.035229 | 0.035247 | 0.99262 | -0.13878 | 0.99272 | -0.13951 | 16.0214
163 | -0.15421 | -0.074686 | 0.15421 | 0.074643 | 1.6201e-06 | -4.2998e-05 | 0.0049564 | 0.0049559 | 0.0049564 | 0.99794 | -0.11647 | 0.99795 | -0.1164 | 2.3602
164 | 8.4686 | 3.7003 | -8.4591 | -3.7217 | 0.0094825 | -0.021467 | 0.26733 | 0.26764 | 0.26764 | 0.99795 | -0.1164 | 0.99679 | -0.12312 | 41.9505
165 | 0.16321 | 0.078319 | -0.1632 | -0.078505 | 7.8443e-06 | -0.00018588 | 0.0052365 | 0.0052389 | 0.0052389 | 0.99795 | -0.1164 | 0.9979 | -0.11673 | 2.4947
166 | -8.786 | -3.8532 | 8.7955 | 3.8781 | 0.0094377 | 0.024905 | 0.27752 | 0.27751 | 0.27752 | 0.99795 | -0.1164 | 0.99992 | -0.00046284 | 43.026
167 | 0.6709 | 0.28565 | -0.67028 | -0.30988 | 0.00062144 | -0.024229 | 0.021117 | 0.021405 | 0.021405 | 0.99679 | -0.12312 | 0.99591 | -0.11658 | 9.7293
168 | 7.2529 | 3.1923 | -7.2507 | -3.1997 | 0.00225 | -0.0073576 | 0.22949 | 0.2296 | 0.2296 | 0.99679 | -0.12312 | 0.99646 | -0.12494 | 35.9868
169 | 0.36428 | 0.16093 | -0.36421 | -0.17017 | 6.9937e-05 | -0.0092321 | 0.011534 | 0.011644 | 0.011644 | 0.99679 | -0.12312 | 0.99661 | -0.12168 | 5.2929
170 | 0.17104 | 0.082806 | -0.17104 | -0.082838 | 1.4983e-06 | -3.1993e-05 | 0.0055034 | 0.0055038 | 0.0055038 | 0.99679 | -0.12312 | 0.99678 | -0.12317 | 2.6209
171 | 0.1632 | 0.078505 | -0.1632 | -0.079041 | 8.287e-07 | -0.00053681 | 0.0052389 | 0.0052457 | 0.0052457 | 0.9979 | -0.11673 | 0.9979 | -0.11669 | 2.3844
172 | -9.1971 | -4.0726 | 9.1979 | 4.0713 | 0.00073816 | -0.0013643 | 0.29039 | 0.29037 | 0.29039 | 0.99992 | -0.00046284 | 1 | 0 | 45.5154
173 | 0.50007 | 0.2275 | -0.5 | -0.23247 | 7.1628e-05 | -0.0049696 | 0.015924 | 0.015985 | 0.015985 | 0.99591 | -0.11658 | 0.99578 | -0.11547 | 7.2659
174 | 0.17021 | 0.082382 | -0.17021 | -0.082435 | 2.444e-06 | -5.2523e-05 | 0.0054812 | 0.0054819 | 0.0054819 | 0.99591 | -0.11658 | 0.9959 | -0.11667 | 2.6104
175 | 7.2507 | 3.1997 | -7.2503 | -3.2008 | 0.00034348 | -0.001122 | 0.2296 | 0.22961 | 0.22961 | 0.99646 | -0.12494 | 0.99641 | -0.12521 | 35.9892
176 | 0.29526 | 0.13777 | -0.29524 | -0.14288 | 2.5857e-05 | -0.0051143 | 0.0094377 | 0.0095014 | 0.0095014 | 0.99661 | -0.12168 | 0.99652 | -0.12095 | 4.3188
177 | 0.068949 | 0.0324 | -0.068949 | -0.033393 | 2.7382e-07 | -0.00099326 | 0.0022067 | 0.0022191 | 0.0022191 | 0.99661 | -0.12168 | 0.9966 | -0.12164 | 1.0087
178 | 0.34568 | 0.15782 | -0.34562 | -0.16736 | 6.6129e-05 | -0.0095407 | 0.011016 | 0.011134 | 0.011134 | 0.99578 | -0.11547 | 0.9956 | -0.11391 | 5.061
179 | 0.15431 | 0.074649 | -0.15431 | -0.074736 | 3.3195e-06 | -8.7202e-05 | 0.0049695 | 0.0049706 | 0.0049706 | 0.99578 | -0.11547 | 0.99576 | -0.11561 | 2.367
180 | 7.1544 | 3.1544 | -7.1542 | -3.1552 | 0.00023729 | -0.00079987 | 0.22653 | 0.22654 | 0.22654 | 0.99641 | -0.12521 | 0.99638 | -0.12541 | 35.5072
181 | 0.29524 | 0.14288 | -0.29524 | -0.14299 | 5.5833e-07 | -0.00010966 | 0.0095014 | 0.0095028 | 0.0095028 | 0.99652 | -0.12095 | 0.99652 | -0.12093 | 4.3194
182 | 0.34562 | 0.16736 | -0.34561 | -0.16739 | 5.9749e-06 | -2.8265e-05 | 0.011134 | 0.011135 | 0.011135 | 0.9956 | -0.11391 | 0.99558 | -0.11403 | 5.3022
183 | 7.0549 | 3.1071 | -7.0547 | -3.1081 | 0.00028038 | -0.00097667 | 0.22334 | 0.22336 | 0.22336 | 0.99638 | -0.12541 | 0.99634 | -0.12564 | 35.0089
184 | -0.27096 | -0.13123 | 0.27096 | 0.13073 | 2.218e-06 | -0.00050716 | 0.008766 | 0.0087596 | 0.008766 | 0.99146 | -0.01492 | 0.99146 | -0.014991 | 3.9846
185 | -0.27096 | -0.13073 | 0.27099 | 0.12491 | 2.521e-05 | -0.0058177 | 0.0087596 | 0.0086872 | 0.0087596 | 0.99146 | -0.014991 | 0.99155 | -0.015755 | 3.9816
186 | 0.29254 | 0.14157 | -0.29254 | -0.14169 | 5.9339e-07 | -0.00011635 | 0.0094619 | 0.0094633 | 0.0094633 | 0.99155 | -0.015755 | 0.99155 | -0.015737 | 4.3015
187 | 0.46213 | 0.19992 | -0.46201 | -0.21 | 0.00012467 | -0.01008 | 0.014659 | 0.014779 | 0.014779 | 0.99155 | -0.015755 | 0.9913 | -0.013856 | 6.7176
188 | -1.0257 | -0.4664 | 1.0259 | 0.4634 | 0.00018681 | -0.0030013 | 0.032803 | 0.032766 | 0.032803 | 0.99155 | -0.015755 | 0.99172 | -0.01711 | 14.9105
189 | 0.30441 | 0.13382 | -0.30434 | -0.14734 | 7.3501e-05 | -0.013523 | 0.0096835 | 0.0098489 | 0.0098489 | 0.9913 | -0.013856 | 0.99107 | -0.011972 | 4.4768
190 | 0.15759 | 0.076184 | -0.15759 | -0.076324 | 5.6747e-06 | -0.00014019 | 0.0050974 | 0.0050992 | 0.0050992 | 0.9913 | -0.013856 | 0.99126 | -0.014095 | 2.4282
191 | 0.30434 | 0.14734 | -0.30433 | -0.14739 | 8.6066e-06 | -5.2997e-05 | 0.0098489 | 0.0098496 | 0.0098496 | 0.99107 | -0.011972 | 0.99104 | -0.012159 | 4.6903

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 20.1513 | 9.132

## res_load
| p_mw | q_mvar
0 | 0.2591 | 0.12549
1 | 0.1042 | 0.050465
2 | 0.19383 | 0.093878
3 | 0.31032 | 0.15029
4 | 0.1031 | 0.049932
5 | 0.12896 | 0.062458
6 | 0.30256 | 0.14653
7 | 0.2862 | 0.13861
8 | 0.31267 | 0.15143
9 | 0.23817 | 0.11535
10 | 0.34362 | 0.16642
11 | 0.12565 | 0.060854
12 | 0.22539 | 0.10916
13 | 0.41279 | 0.19992
14 | 0.071242 | 0.034504
15 | 0.075842 | 0.036732
16 | 0.17451 | 0.084521
17 | 0.27697 | 0.13414
18 | 0.31198 | 0.1511
19 | 0.28321 | 0.13717
20 | 0.14767 | 0.07152
21 | 0.15667 | 0.07588
22 | 0.40561 | 0.19645
23 | 0.1706 | 0.082627
24 | 0.21319 | 0.10325
25 | 0.12933 | 0.062639
26 | 0.3985 | 0.193
27 | 0.31497 | 0.15255
28 | 0.14539 | 0.070414
29 | 0.12583 | 0.060945
30 | 0.099277 | 0.048082
31 | 0.11728 | 0.056803
32 | 0.072759 | 0.035239
33 | 0.15096 | 0.073112
34 | 0.081107 | 0.039282
35 | 0.2629 | 0.12733
36 | 0.11304 | 0.054749
37 | 0.27259 | 0.13202
38 | 0.075705 | 0.036666
39 | 0.22568 | 0.1093
40 | 0.17822 | 0.086317
41 | 0.30402 | 0.14725
42 | 0.14324 | 0.069373
43 | 0.40915 | 0.19816
44 | 0.34843 | 0.16875
45 | 0.24084 | 0.11664
46 | 0.077249 | 0.037413
47 | 0.091631 | 0.044379
48 | 0.073408 | 0.035553
49 | 0.15531 | 0.075222
50 | 0.37341 | 0.18085
51 | 0.23644 | 0.11451
52 | 0.082153 | 0.039788
53 | 0.17208 | 0.083344
54 | 0.22456 | 0.10876
55 | 0.080864 | 0.039164
56 | 0.26853 | 0.13005
57 | 0.15461 | 0.074881
58 | 0.12133 | 0.058764
59 | 0.12158 | 0.058882
60 | 0.20544 | 0.099501
61 | 0.3609 | 0.17479
62 | 0.29001 | 0.14046
63 | 0.21575 | 0.10449
64 | 0.076591 | 0.037095
65 | 0.071059 | 0.034415
66 | 0.21439 | 0.10383
67 | 0.31416 | 0.15215
68 | 0.31015 | 0.15021
69 | 0.071768 | 0.034759
70 | 0.27236 | 0.13191
71 | 0.35407 | 0.17148
72 | 0.26634 | 0.129
73 | 0.32562 | 0.1577
74 | 0.13994 | 0.067778
75 | 0.15423 | 0.074697
76 | 0.22619 | 0.10955
77 | 0.091173 | 0.044157
78 | 0.26858 | 0.13008
79 | 0.23104 | 0.1119
80 | 0.15421 | 0.074686
81 | 0.40164 | 0.19452
82 | 0.17104 | 0.082838
83 | 0.17021 | 0.082435
84 | 0.095921 | 0.046457
85 | 0.068949 | 0.033393
86 | 0.29524 | 0.14299
87 | 0.1632 | 0.079041
88 | 0.15431 | 0.074736
89 | 0.099233 | 0.048061
90 | 0.27096 | 0.13123
91 | 0.29254 | 0.14169
92 | 0.15759 | 0.076324
93 | 0.30433 | 0.14739
94 | 0.34561 | 0.16739
95 | 0.32954 | 0.1596

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1