## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_434_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_434_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_434_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_434_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_434_0_node_5 | 20 | n |  | TRUE
5 | bus_MV_434_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_434_0_node_107 | 20 | n |  | TRUE
7 | bus_MV_434_0_node_108 | 20 | n |  | TRUE
8 | bus_MV_434_0_node_23 | 20 | n |  | TRUE
9 | bus_MV_434_0_node_20 | 20 | n |  | TRUE
10 | bus_MV_434_0_node_113 | 20 | n |  | TRUE
11 | bus_MV_434_0_node_114 | 20 | n |  | TRUE
12 | bus_MV_434_0_node_115 | 20 | n |  | TRUE
13 | bus_MV_434_0_node_10 | 20 | n |  | TRUE
14 | bus_MV_434_0_node_111 | 20 | n |  | TRUE
15 | bus_MV_434_0_node_101 | 20 | n |  | TRUE
16 | bus_MV_434_0_node_6 | 20 | n |  | TRUE
17 | bus_MV_434_0_node_7 | 20 | n |  | TRUE
18 | bus_MV_434_0_node_8 | 20 | n |  | TRUE
19 | bus_MV_434_0_node_9 | 20 | n |  | TRUE
20 | bus_MV_434_0_node_11 | 20 | n |  | TRUE
21 | bus_MV_434_0_node_92 | 20 | n |  | TRUE
22 | bus_MV_434_0_node_91 | 20 | n |  | TRUE
23 | bus_MV_434_0_node_65 | 20 | n |  | TRUE
24 | bus_MV_434_0_node_12 | 20 | n |  | TRUE
25 | bus_MV_434_0_node_13 | 20 | n |  | TRUE
26 | bus_MV_434_0_node_15 | 20 | n |  | TRUE
27 | bus_MV_434_0_node_16 | 20 | n |  | TRUE
28 | bus_MV_434_0_node_18 | 20 | n |  | TRUE
29 | bus_MV_434_0_node_19 | 20 | n |  | TRUE
30 | bus_MV_434_0_node_17 | 20 | n |  | TRUE
31 | bus_MV_434_0_node_90 | 20 | n |  | TRUE
32 | bus_MV_434_0_node_109 | 20 | n |  | TRUE
33 | bus_MV_434_0_node_22 | 20 | n |  | TRUE
34 | bus_MV_434_0_node_110 | 20 | n |  | TRUE
35 | bus_MV_434_0_node_21 | 20 | n |  | TRUE
36 | bus_MV_434_0_node_68 | 20 | n |  | TRUE
37 | bus_MV_434_0_node_69 | 20 | n |  | TRUE
38 | bus_MV_434_0_node_72 | 20 | n |  | TRUE
39 | bus_MV_434_0_node_70 | 20 | n |  | TRUE
40 | bus_MV_434_0_node_71 | 20 | n |  | TRUE
41 | bus_MV_434_0_node_102 | 20 | n |  | TRUE
42 | bus_MV_434_0_node_105 | 20 | n |  | TRUE
43 | bus_MV_434_0_node_75 | 20 | n |  | TRUE
44 | bus_MV_434_0_node_74 | 20 | n |  | TRUE
45 | bus_MV_434_0_node_73 | 20 | n |  | TRUE
46 | bus_MV_434_0_node_99 | 20 | n |  | TRUE
47 | bus_MV_434_0_node_98 | 20 | n |  | TRUE
48 | bus_MV_434_0_node_76 | 20 | n |  | TRUE
49 | bus_MV_434_0_node_83 | 20 | n |  | TRUE
50 | bus_MV_434_0_node_85 | 20 | n |  | TRUE
51 | bus_MV_434_0_node_84 | 20 | n |  | TRUE
52 | bus_MV_434_0_node_88 | 20 | n |  | TRUE
53 | bus_MV_434_0_node_77 | 20 | n |  | TRUE
54 | bus_MV_434_0_node_78 | 20 | n |  | TRUE
55 | bus_MV_434_0_node_79 | 20 | n |  | TRUE
56 | bus_MV_434_0_node_112 | 20 | n |  | TRUE
57 | bus_MV_434_0_node_86 | 20 | n |  | TRUE
58 | bus_MV_434_0_node_89 | 20 | n |  | TRUE
59 | bus_MV_434_0_node_87 | 20 | n |  | TRUE
60 | bus_MV_434_0_node_97 | 20 | n |  | TRUE
61 | bus_MV_434_0_node_80 | 20 | n |  | TRUE
62 | bus_MV_434_0_node_100 | 20 | n |  | TRUE
63 | bus_MV_434_0_node_106 | 20 | n |  | TRUE
64 | bus_MV_434_0_node_103 | 20 | n |  | TRUE
65 | bus_MV_434_0_node_104 | 20 | n |  | TRUE
66 | bus_MV_434_0_node_82 | 20 | n |  | TRUE
67 | bus_MV_434_0_node_25 | 20 | n |  | TRUE
68 | bus_MV_434_0_node_26 | 20 | n |  | TRUE
69 | bus_MV_434_0_node_27 | 20 | n |  | TRUE
70 | bus_MV_434_0_node_28 | 20 | n |  | TRUE
71 | bus_MV_434_0_node_96 | 20 | n |  | TRUE
72 | bus_MV_434_0_node_117 | 20 | n |  | TRUE
73 | bus_MV_434_0_node_39 | 20 | n |  | TRUE
74 | bus_MV_434_0_node_42 | 20 | n |  | TRUE
75 | bus_MV_434_0_node_60 | 20 | n |  | TRUE
76 | bus_MV_434_0_node_50 | 20 | n |  | TRUE
77 | bus_MV_434_0_node_47 | 20 | n |  | TRUE
78 | bus_MV_434_0_node_40 | 20 | n |  | TRUE
79 | bus_MV_434_0_node_59 | 20 | n |  | TRUE
80 | bus_MV_434_0_node_49 | 20 | n |  | TRUE
81 | bus_MV_434_0_node_48 | 20 | n |  | TRUE
82 | bus_MV_434_0_node_94 | 20 | n |  | TRUE
83 | bus_MV_434_0_node_93 | 20 | n |  | TRUE
84 | bus_MV_434_0_node_52 | 20 | n |  | TRUE
85 | bus_MV_434_0_node_51 | 20 | n |  | TRUE
86 | bus_MV_434_0_node_30 | 20 | n |  | TRUE
87 | bus_MV_434_0_node_32 | 20 | n |  | TRUE
88 | bus_MV_434_0_node_36 | 20 | n |  | TRUE
89 | bus_MV_434_0_node_41 | 20 | n |  | TRUE
90 | bus_MV_434_0_node_35 | 20 | n |  | TRUE
91 | bus_MV_434_0_node_54 | 20 | n |  | TRUE
92 | bus_MV_434_0_node_116 | 20 | n |  | TRUE
93 | bus_MV_434_0_node_56 | 20 | n |  | TRUE
94 | bus_MV_434_0_node_55 | 20 | n |  | TRUE
95 | bus_MV_434_0_node_37 | 20 | n |  | TRUE
96 | bus_MV_434_0_node_38 | 20 | n |  | TRUE
97 | bus_MV_434_0_node_43 | 20 | n |  | TRUE
98 | bus_MV_434_0_node_44 | 20 | n |  | TRUE
99 | bus_MV_434_0_node_45 | 20 | n |  | TRUE
100 | bus_MV_434_0_node_46 | 20 | n |  | TRUE
101 | bus_MV_434_0_node_53 | 20 | n |  | TRUE
102 | bus_MV_434_0_node_95 | 20 | n |  | TRUE
103 | bus_MV_434_0_node_66 | 20 | n |  | TRUE
104 | bus_MV_434_0_node_57 | 20 | n |  | TRUE
105 | bus_MV_434_0_node_58 | 20 | n |  | TRUE
106 | bus_MV_434_0_node_64 | 20 | n |  | TRUE
107 | bus_MV_434_0_node_62 | 20 | n |  | TRUE
108 | bus_MV_434_0_node_61 | 20 | n |  | TRUE
109 | bus_MV_434_0_node_63 | 20 | n |  | TRUE
110 | bus_MV_434_0_node_81 | 20 | n |  | TRUE
111 | bus_HV_434_0_node_65 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_434_0_load_0 | 0 | 0.3053 | 0.14786 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_434_0_load_107 | 6 | 0.4026 | 0.19499 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_434_0_load_23 | 8 | 0.34552 | 0.16734 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_434_0_load_20 | 9 | 0.3058 | 0.1481 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_434_0_load_113 | 10 | 0.23785 | 0.1152 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_434_0_load_6 | 16 | 0.39741 | 0.19248 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_434_0_load_92 | 21 | 0.089639 | 0.043414 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_434_0_load_91 | 22 | 0.31005 | 0.15016 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_434_0_load_12 | 24 | 0.21033 | 0.10187 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_434_0_load_15 | 26 | 0.30101 | 0.14579 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_434_0_load_90 | 31 | 0.078561 | 0.038049 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_434_0_load_109 | 32 | 0.24727 | 0.11976 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_434_0_load_110 | 34 | 0.23264 | 0.11267 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_434_0_load_21 | 35 | 0.2434 | 0.11788 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_434_0_load_68 | 36 | 0.17249 | 0.083539 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_434_0_load_102 | 41 | 0.079397 | 0.038454 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_434_0_load_105 | 42 | 0.67974 | 0.32921 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_434_0_load_74 | 44 | 0.15581 | 0.075461 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_434_0_load_99 | 46 | 0.11947 | 0.057862 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_434_0_load_83 | 49 | 0.14834 | 0.071843 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_434_0_load_88 | 52 | 0.1844 | 0.089309 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_434_0_load_77 | 53 | 0.066551 | 0.032232 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_434_0_load_112 | 56 | 0.38197 | 0.185 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_434_0_load_89 | 58 | 0.12857 | 0.062271 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_434_0_load_87 | 59 | 0.34929 | 0.16917 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_434_0_load_97 | 60 | 0.3745 | 0.18138 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_434_0_load_80 | 61 | 0.31213 | 0.15117 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_434_0_load_100 | 62 | 0.26363 | 0.12768 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_434_0_load_106 | 63 | 0.2418 | 0.11711 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_434_0_load_103 | 64 | 0.38613 | 0.18701 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_434_0_load_25 | 67 | 0.30071 | 0.14564 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_434_0_load_96 | 71 | 0.20713 | 0.10032 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_434_0_load_117 | 72 | 0.50607 | 0.2451 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_434_0_load_60 | 75 | 0.20969 | 0.10156 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_434_0_load_47 | 77 | 0.25056 | 0.12135 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_434_0_load_94 | 82 | 0.06884 | 0.033341 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_434_0_load_93 | 83 | 0.12815 | 0.062064 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_434_0_load_51 | 85 | 0.1426 | 0.069064 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_434_0_load_30 | 86 | 0.26946 | 0.13051 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_434_0_load_36 | 88 | 0.084371 | 0.040863 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_434_0_load_35 | 90 | 0.35215 | 0.17055 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_434_0_load_54 | 91 | 0.40415 | 0.19574 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_434_0_load_116 | 92 | 0.39274 | 0.19021 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_434_0_load_56 | 93 | 0.17576 | 0.085126 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_434_0_load_37 | 95 | 0.34361 | 0.16642 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_434_0_load_43 | 97 | 0.21793 | 0.10555 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_434_0_load_46 | 100 | 0.16937 | 0.082028 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_434_0_load_95 | 102 | 0.073991 | 0.035835 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_434_0_load_66 | 103 | 0.39189 | 0.1898 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_434_0_load_57 | 104 | 0.16477 | 0.079803 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_434_0_load_62 | 107 | 0.071583 | 0.034669 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_434_0_load_61 | 108 | 0.3689 | 0.17867 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_434_0_line_0 |  | 0 | 1 | 0.050453 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
1 | MV_434_0_line_1 |  | 0 | 2 | 0.084904 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
2 | MV_434_0_line_2 |  | 1 | 3 | 0.3938 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
3 | MV_434_0_line_3 |  | 2 | 4 | 0.24464 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
4 | MV_434_0_line_4 |  | 3 | 8 | 0.10324 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_434_0_line_5 |  | 3 | 5 | 0.33948 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
6 | MV_434_0_line_6 |  | 4 | 9 | 0.008644 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
7 | MV_434_0_line_7 |  | 5 | 6 | 0.031277 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
8 | MV_434_0_line_8 |  | 5 | 7 | 0.083995 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_434_0_line_9 |  | 6 | 13 | 0.013445 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
10 | MV_434_0_line_10 |  | 7 | 14 | 0.63436 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_434_0_line_11 |  | 9 | 15 | 0.44253 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
12 | MV_434_0_line_12 |  | 10 | 11 | 0.12312 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_434_0_line_13 |  | 11 | 12 | 0.19164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_434_0_line_14 |  | 12 | 56 | 0.070051 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_434_0_line_15 |  | 13 | 18 | 0.30726 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
16 | MV_434_0_line_16 |  | 14 | 34 | 0.025756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_434_0_line_17 |  | 15 | 41 | 0.17641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_434_0_line_18 |  | 15 | 62 | 0.13825 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_434_0_line_19 |  | 16 | 17 | 0.051137 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
20 | MV_434_0_line_20 |  | 16 | 18 | 0.098108 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
21 | MV_434_0_line_21 |  | 17 | 19 | 0.050639 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
22 | MV_434_0_line_22 |  | 18 | 20 | 0.45754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_434_0_line_23 |  | 19 | 21 | 0.050737 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
24 | MV_434_0_line_24 |  | 20 | 22 | 0.070788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_434_0_line_25 |  | 21 | 23 | 0.027885 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
26 | MV_434_0_line_26 |  | 23 | 109 | 0.66895 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_434_0_line_27 |  | 24 | 25 | 0.044353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_434_0_line_28 |  | 25 | 26 | 0.12145 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_434_0_line_29 |  | 26 | 27 | 0.029113 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_434_0_line_30 |  | 27 | 28 | 0.54837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_434_0_line_31 |  | 27 | 29 | 0.56146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_434_0_line_32 |  | 28 | 32 | 0.10562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_434_0_line_33 |  | 28 | 30 | 0.36676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_434_0_line_34 |  | 29 | 33 | 0.33326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_434_0_line_35 |  | 29 | 34 | 0.04428 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_434_0_line_36 |  | 30 | 31 | 0.34315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_434_0_line_37 |  | 33 | 35 | 0.029633 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_434_0_line_38 |  | 36 | 37 | 0.077853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_434_0_line_39 |  | 37 | 38 | 0.3528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_434_0_line_40 |  | 38 | 43 | 0.64505 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_434_0_line_41 |  | 38 | 44 | 0.03734 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_434_0_line_42 |  | 38 | 40 | 0.17495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_434_0_line_43 |  | 39 | 40 | 0.23345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_434_0_line_44 |  | 39 | 41 | 0.11888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_434_0_line_45 |  | 40 | 42 | 0.083133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_434_0_line_46 |  | 42 | 65 | 0.0084368 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_434_0_line_47 |  | 43 | 48 | 0.9034 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_434_0_line_48 |  | 43 | 49 | 0.013329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_434_0_line_49 |  | 45 | 46 | 0.060706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_434_0_line_50 |  | 45 | 47 | 0.032743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_434_0_line_51 |  | 46 | 55 | 0.085084 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_434_0_line_52 |  | 47 | 60 | 0.047315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_434_0_line_53 |  | 48 | 50 | 0.46786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_434_0_line_54 |  | 48 | 51 | 0.59596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_434_0_line_55 |  | 48 | 52 | 0.03056 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_434_0_line_56 |  | 50 | 57 | 0.71748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_434_0_line_57 |  | 50 | 58 | 0.062794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_434_0_line_58 |  | 51 | 56 | 0.020019 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_434_0_line_59 |  | 53 | 54 | 0.10707 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_434_0_line_60 |  | 54 | 55 | 0.47251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_434_0_line_61 |  | 57 | 59 | 0.058351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_434_0_line_62 |  | 60 | 61 | 0.20538 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_434_0_line_63 |  | 61 | 110 | 0.031455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_434_0_line_64 |  | 62 | 63 | 0.23099 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_434_0_line_65 |  | 63 | 66 | 0.041292 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_434_0_line_66 |  | 64 | 65 | 0.021302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_434_0_line_67 |  | 66 | 110 | 0.035446 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_434_0_line_68 |  | 67 | 68 | 0.15195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_434_0_line_69 |  | 68 | 69 | 0.070192 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
70 | MV_434_0_line_70 |  | 68 | 70 | 0.25776 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
71 | MV_434_0_line_71 |  | 69 | 72 | 0.14122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_434_0_line_72 |  | 69 | 74 | 0.1734 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_434_0_line_73 |  | 70 | 75 | 0.061263 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
74 | MV_434_0_line_74 |  | 71 | 72 | 0.11727 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_434_0_line_75 |  | 71 | 73 | 0.046563 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_434_0_line_76 |  | 73 | 96 | 0.34386 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_434_0_line_77 |  | 74 | 76 | 0.021362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_434_0_line_78 |  | 74 | 77 | 0.057962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_434_0_line_79 |  | 74 | 78 | 0.19798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_434_0_line_80 |  | 75 | 79 | 0.065894 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
81 | MV_434_0_line_81 |  | 76 | 83 | 0.053015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_434_0_line_82 |  | 77 | 80 | 0.20131 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_434_0_line_83 |  | 78 | 97 | 0.088569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_434_0_line_84 |  | 79 | 105 | 0.33131 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
85 | MV_434_0_line_85 |  | 80 | 84 | 0.2317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_434_0_line_86 |  | 80 | 85 | 0.014322 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_434_0_line_87 |  | 81 | 82 | 0.016856 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_434_0_line_88 |  | 81 | 83 | 0.19162 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_434_0_line_89 |  | 82 | 102 | 0.049501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_434_0_line_90 |  | 84 | 101 | 0.41963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_434_0_line_91 |  | 84 | 92 | 0.1288 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_434_0_line_92 |  | 86 | 87 | 0.052871 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_434_0_line_93 |  | 86 | 88 | 0.41605 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_434_0_line_94 |  | 87 | 89 | 0.22094 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_434_0_line_95 |  | 88 | 90 | 0.03045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_434_0_line_96 |  | 89 | 91 | 0.045442 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
97 | MV_434_0_line_97 |  | 89 | 92 | 0.30556 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_434_0_line_98 |  | 91 | 94 | 0.031857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_434_0_line_99 |  | 93 | 94 | 0.031959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_434_0_line_100 |  | 95 | 96 | 0.059901 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
101 | MV_434_0_line_101 |  | 97 | 98 | 0.026273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_434_0_line_102 |  | 98 | 99 | 0.10658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_434_0_line_103 |  | 99 | 100 | 0.09067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_434_0_line_104 |  | 101 | 103 | 0.047671 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_434_0_line_105 |  | 104 | 105 | 0.083483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_434_0_line_106 |  | 105 | 106 | 0.25749 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
107 | MV_434_0_line_107 |  | 106 | 107 | 0.078754 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
108 | MV_434_0_line_108 |  | 107 | 108 | 0.0034702 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
109 | MV_434_0_line_109 |  | 108 | 109 | 0.034974 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_434_0_trafo_65 | 25 MVA 110/20 kV | 111 | 23 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2652041.7436 | 1248470.6806
1 | 2651992.4831 | 1248482.2231
2 | 2652126.1115 | 1248460.7701
3 | 2651726.7849 | 1248375.3945
4 | 2652281.8424 | 1248555.0825
5 | 2651822.156 | 1248656.6068
6 | 2651839.5544 | 1248682.432
7 | 2651755.4568 | 1248707.6593
8 | 2651723.8491 | 1248272.1989
9 | 2652290.4088 | 1248556.4144
10 | 2652868.476 | 1247200.1837
11 | 2652961.7034 | 1247119.7717
12 | 2653078.8349 | 1247191.7116
13 | 2651848.3834 | 1248692.5938
14 | 2651437.3242 | 1248394.2905
15 | 2652682.4199 | 1248761.745
16 | 2652051.0858 | 1248947.8316
17 | 2652082.1622 | 1248988.5099
18 | 2651989.1207 | 1248871.6252
19 | 2652088.929 | 1249026.1616
20 | 2651610.8888 | 1248989.8916
21 | 2652084.882 | 1249076.2827
22 | 2651549.6458 | 1248954.3916
23 | 2652086.4623 | 1249104.093
24 | 2651562.9857 | 1248665.3989
25 | 2651521.7407 | 1248682.0073
26 | 2651511.1297 | 1248802.9974
27 | 2651481.9561 | 1248801.7655
28 | 2651071.8206 | 1248726.3691
29 | 2651367.2152 | 1248393.5826
30 | 2651332.4472 | 1248892.5316
31 | 2651030.1876 | 1248799.4537
32 | 2650970.5778 | 1248708.6752
33 | 2651345.8555 | 1248108.0819
34 | 2651411.4921 | 1248394.1332
35 | 2651337.9998 | 1248079.5056
36 | 2653210.4364 | 1248419.6692
37 | 2653207.2689 | 1248497.4493
38 | 2653000.1155 | 1248541.9141
39 | 2652926.8738 | 1248706.1832
40 | 2653022.4034 | 1248688.3575
41 | 2652808.0805 | 1248701.7325
42 | 2653105.4433 | 1248687.7111
43 | 2652905.3948 | 1247976.3505
44 | 2652962.7317 | 1248544.1484
45 | 2653067.1201 | 1248921.2496
46 | 2653126.6771 | 1248933.006
47 | 2653059.4882 | 1248953.0919
48 | 2653143.1503 | 1247689.5472
49 | 2652894.0849 | 1247969.2448
50 | 2653325.6852 | 1247879.9923
51 | 2653168.1009 | 1247201.3173
52 | 2653132.5696 | 1247660.8775
53 | 2653403.0649 | 1248802.0499
54 | 2653500.888 | 1248758.5128
55 | 2653210.1508 | 1248949.4835
56 | 2653148.0494 | 1247200.2814
57 | 2653672.608 | 1247772.3809
58 | 2653334.2183 | 1247942.2002
59 | 2653615.358 | 1247760.2661
60 | 2653066.6701 | 1248988.6929
61 | 2652896.6467 | 1249103.896
62 | 2652719.1089 | 1248867.7453
63 | 2652834.8266 | 1249067.6587
64 | 2653092.7779 | 1248684.1899
65 | 2653113.8651 | 1248687.2083
66 | 2652839.5698 | 1249105.8219
67 | 2651646.4941 | 1250263.9931
68 | 2651769.8459 | 1250352.1289
69 | 2651816.9496 | 1250404.1314
70 | 2651832.284 | 1250216.537
71 | 2651649.944 | 1250508.0916
72 | 2651679.2661 | 1250394.5457
73 | 2651687.502 | 1250535.614
74 | 2651979.6379 | 1250464.1296
75 | 2651844.3746 | 1250156.4794
76 | 2651999.6449 | 1250471.5767
77 | 2652002.6382 | 1250410.9059
78 | 2651970.8957 | 1250646.6892
79 | 2651856.7856 | 1250091.7659
80 | 2652148.7874 | 1250272.4611
81 | 2652199.639 | 1250426.6029
82 | 2652215.7499 | 1250431.5593
83 | 2652026.511 | 1250508.732
84 | 2652320.7941 | 1250380.9171
85 | 2652147.0328 | 1250258.247
86 | 2652506.3301 | 1250879.488
87 | 2652456.2554 | 1250862.3553
88 | 2652878.3518 | 1251065.7702
89 | 2652274.735 | 1250736.3991
90 | 2652891.649 | 1251038.3772
91 | 2652231.6935 | 1250750.9743
92 | 2652417.3458 | 1250466.1615
93 | 2652224.3536 | 1250789.5003
94 | 2652205.1722 | 1250766.7961
95 | 2651468.1457 | 1250547.5811
96 | 2651446.4341 | 1250603.4087
97 | 2651919.1156 | 1250716.9838
98 | 2651896.9421 | 1250731.1772
99 | 2651808.3025 | 1250789.6534
100 | 2651758.1272 | 1250864.9669
101 | 2652403.9393 | 1250067.4476
102 | 2652265.001 | 1250426.5953
103 | 2652424.2779 | 1250024.6869
104 | 2651785.0723 | 1249779.6047
105 | 2651863.5731 | 1249807.8423
106 | 2652115.639 | 1249860.4322
107 | 2652127.1634 | 1249782.5263
108 | 2652127.6712 | 1249779.0935
109 | 2652136.8529 | 1249745.4734
110 | 2652871.4345 | 1249120.9161
111 | 2652086.4623 | 1249104.093

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99725 | -0.014914 | 0.3053 | 0.14786
1 | 0.99733 | -0.014504 | 0 | 0
2 | 0.99712 | -0.015569 | 0 | 0
3 | 0.99796 | -0.011224 | 0 | 0
4 | 0.99676 | -0.017419 | 0 | 0
5 | 0.99853 | -0.0081461 | 0 | 0
6 | 0.9986 | -0.0077759 | 0.4026 | 0.19499
7 | 0.99833 | -0.010004 | 0 | 0
8 | 0.99789 | -0.011657 | 0.34552 | 0.16734
9 | 0.99674 | -0.017671 | 0.3058 | 0.1481
10 | 0.98895 | -0.035997 | 0.23785 | 0.1152
11 | 0.98901 | -0.035634 | 0 | 0
12 | 0.98906 | -0.036162 | 0 | 0
13 | 0.99863 | -0.0076102 | 0 | 0
14 | 0.99728 | -0.0026055 | 0 | 0
15 | 0.99452 | -0.07589 | 0 | 0
16 | 0.99955 | -0.0024869 | 0.39741 | 0.19248
17 | 0.99968 | -0.0017856 | 0 | 0
18 | 0.99932 | -0.0037807 | 0 | 0
19 | 0.9998 | -0.0010889 | 0 | 0
20 | 0.99914 | -0.0022894 | 0 | 0
21 | 0.99993 | -0.00038869 | 0.089639 | 0.043414
22 | 0.99911 | -0.0020302 | 0.31005 | 0.15016
23 | 1 | 0 | -13.126 | -5.8894
24 | 0.99647 | 0.0010652 | 0.21033 | 0.10187
25 | 0.99648 | 0.00095427 | 0 | 0
26 | 0.99653 | 0.0012768 | 0.30101 | 0.14579
27 | 0.99655 | 0.0011004 | 0 | 0
28 | 0.99633 | 0.0023441 | 0 | 0
29 | 0.99714 | -0.0030869 | 0 | 0
30 | 0.99629 | 0.0023975 | 0 | 0
31 | 0.99626 | 0.0026329 | 0.078561 | 0.038049
32 | 0.99629 | 0.0026504 | 0.24727 | 0.11976
33 | 0.99704 | -0.0022103 | 0 | 0
34 | 0.99723 | -0.0022918 | 0.23264 | 0.11267
35 | 0.99703 | -0.0021242 | 0.2434 | 0.11788
36 | 0.99212 | -0.058081 | 0.17249 | 0.083539
37 | 0.99214 | -0.05824 | 0 | 0
38 | 0.99221 | -0.058843 | 0 | 0
39 | 0.99344 | -0.067804 | 0 | 0
40 | 0.9926 | -0.061438 | 0 | 0
41 | 0.99387 | -0.071009 | 0.079397 | 0.038454
42 | 0.99249 | -0.060371 | 0.67974 | 0.32921
43 | 0.99105 | -0.050971 | 0 | 0
44 | 0.99221 | -0.058773 | 0.15581 | 0.075461
45 | 0.99342 | -0.077897 | 0 | 0
46 | 0.99341 | -0.077815 | 0.11947 | 0.057862
47 | 0.99343 | -0.077939 | 0 | 0
48 | 0.98957 | -0.040469 | 0 | 0
49 | 0.99104 | -0.050947 | 0.14834 | 0.071843
50 | 0.98929 | -0.0385 | 0 | 0
51 | 0.9891 | -0.036485 | 0 | 0
52 | 0.98956 | -0.040538 | 0.1844 | 0.089309
53 | 0.99335 | -0.077694 | 0.066551 | 0.032232
54 | 0.99336 | -0.077607 | 0 | 0
55 | 0.9934 | -0.077814 | 0 | 0
56 | 0.98909 | -0.036341 | 0.38197 | 0.185
57 | 0.98897 | -0.035891 | 0 | 0
58 | 0.98928 | -0.038404 | 0.12857 | 0.062271
59 | 0.98894 | -0.035644 | 0.34929 | 0.16917
60 | 0.99344 | -0.077997 | 0.3745 | 0.18138
61 | 0.99366 | -0.076292 | 0.31213 | 0.15117
62 | 0.99428 | -0.073773 | 0.26363 | 0.12768
63 | 0.99378 | -0.07731 | 0.2418 | 0.11711
64 | 0.99248 | -0.060232 | 0.38613 | 0.18701
65 | 0.99249 | -0.060332 | 0 | 0
66 | 0.99373 | -0.076924 | 0 | 0
67 | 0.99643 | -0.063266 | 0.30071 | 0.14564
68 | 0.99649 | -0.063799 | 0 | 0
69 | 0.99633 | -0.065539 | 0 | 0
70 | 0.99711 | -0.056921 | 0 | 0
71 | 0.99601 | -0.064722 | 0.20713 | 0.10032
72 | 0.99614 | -0.063841 | 0.50607 | 0.2451
73 | 0.99599 | -0.064556 | 0 | 0
74 | 0.99528 | -0.072725 | 0 | 0
75 | 0.9972 | -0.056538 | 0.20969 | 0.10156
76 | 0.99527 | -0.07266 | 0 | 0
77 | 0.9951 | -0.07108 | 0.25056 | 0.12135
78 | 0.99518 | -0.071923 | 0 | 0
79 | 0.99731 | -0.056106 | 0 | 0
80 | 0.99423 | -0.076906 | 0 | 0
81 | 0.9952 | -0.072856 | 0 | 0
82 | 0.9952 | -0.072829 | 0.06884 | 0.033341
83 | 0.99525 | -0.072495 | 0.12815 | 0.062064
84 | 0.99362 | -0.071363 | 0 | 0
85 | 0.99423 | -0.076881 | 0.1426 | 0.069064
86 | 0.99208 | -0.080513 | 0.26946 | 0.13051
87 | 0.99213 | -0.08096 | 0 | 0
88 | 0.99173 | -0.082778 | 0.084371 | 0.040863
89 | 0.99243 | -0.078997 | 0 | 0
90 | 0.99171 | -0.082648 | 0.35215 | 0.17055
91 | 0.99238 | -0.079326 | 0.40415 | 0.19574
92 | 0.9932 | -0.074062 | 0.39274 | 0.19021
93 | 0.99237 | -0.079193 | 0.17576 | 0.085126
94 | 0.99237 | -0.07926 | 0 | 0
95 | 0.9958 | -0.063473 | 0.34361 | 0.16642
96 | 0.99584 | -0.063222 | 0 | 0
97 | 0.99514 | -0.071545 | 0.21793 | 0.10555
98 | 0.99513 | -0.071499 | 0 | 0
99 | 0.99511 | -0.071305 | 0 | 0
100 | 0.99509 | -0.071125 | 0.16937 | 0.082028
101 | 0.99341 | -0.069534 | 0 | 0
102 | 0.99519 | -0.072786 | 0.073991 | 0.035835
103 | 0.99338 | -0.069309 | 0.39189 | 0.1898
104 | 0.9978 | -0.053716 | 0.16477 | 0.079803
105 | 0.99781 | -0.053876 | 0 | 0
106 | 0.99865 | -0.0061637 | 0 | 0
107 | 0.99878 | -0.0056075 | 0.071583 | 0.034669
108 | 0.99878 | -0.0055826 | 0.3689 | 0.17867
109 | 0.99885 | -0.0053158 | 0 | 0
110 | 0.9937 | -0.07659 | 0 | 0
111 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -4.9153 | -2.2213 | 4.9157 | 2.2184 | 0.00037998 | -0.0029389 | 0.15614 | 0.1561 | 0.15614 | 0.99725 | -0.014914 | 0.99733 | -0.014504 | 24.4731
1 | 4.61 | 2.0735 | -4.6094 | -2.0784 | 0.00056195 | -0.0049883 | 0.14632 | 0.14639 | 0.14639 | 0.99725 | -0.014914 | 0.99712 | -0.015569 | 22.9445
2 | -4.9157 | -2.2184 | 4.9186 | 2.1954 | 0.0029596 | -0.02296 | 0.1561 | 0.15581 | 0.1561 | 0.99733 | -0.014504 | 0.99796 | -0.011224 | 24.4673
3 | 4.6094 | 2.0784 | -4.6078 | -2.0928 | 0.0016219 | -0.014364 | 0.14639 | 0.14657 | 0.14657 | 0.99712 | -0.015569 | 0.99676 | -0.017419 | 22.9731
4 | 0.34554 | 0.16723 | -0.34552 | -0.16734 | 2.2684e-05 | -0.00010853 | 0.011104 | 0.011106 | 0.011106 | 0.99796 | -0.011224 | 0.99789 | -0.011657 | 5.2886
5 | -5.2642 | -2.3627 | 5.2671 | 2.343 | 0.002918 | -0.019612 | 0.16691 | 0.16666 | 0.16691 | 0.99796 | -0.011224 | 0.99853 | -0.0081461 | 26.1613
6 | 4.6078 | 2.0928 | -4.6077 | -2.093 | 8.9692e-05 | -0.00022944 | 0.14657 | 0.14657 | 0.14657 | 0.99676 | -0.017419 | 0.99674 | -0.017671 | 40.4895
7 | -6.5828 | -2.9079 | 6.5833 | 2.9062 | 0.00041829 | -0.001724 | 0.20805 | 0.20803 | 0.20805 | 0.99853 | -0.0081461 | 0.9986 | -0.0077759 | 32.6098
8 | 1.3157 | 0.56489 | -1.3155 | -0.56483 | 0.00025645 | 6.0675e-05 | 0.041396 | 0.041397 | 0.041397 | 0.99853 | -0.0081461 | 0.99833 | -0.010004 | 19.7127
9 | -6.9859 | -3.1012 | 6.9861 | 3.1005 | 0.00020281 | -0.00072823 | 0.22095 | 0.22094 | 0.22095 | 0.9986 | -0.0077759 | 0.99863 | -0.0076102 | 34.6319
10 | 1.3155 | 0.56483 | -1.314 | -0.57948 | 0.0014573 | -0.014647 | 0.041397 | 0.041571 | 0.041571 | 0.99833 | -0.010004 | 0.99728 | -0.0026055 | 18.8958
11 | 4.3019 | 1.9449 | -4.2943 | -1.9368 | 0.0075956 | 0.0081366 | 0.13673 | 0.13674 | 0.13674 | 0.99674 | -0.017671 | 0.99452 | -0.07589 | 39.0689
12 | -0.23785 | -0.1152 | 0.23786 | 0.11506 | 1.3051e-05 | -0.00013558 | 0.0077143 | 0.0077125 | 0.0077143 | 0.98895 | -0.035997 | 0.98901 | -0.035634 | 3.6735
13 | -0.23786 | -0.11506 | 0.23788 | 0.11059 | 1.5107e-05 | -0.0044713 | 0.0077125 | 0.0076565 | 0.0077125 | 0.98901 | -0.035634 | 0.98906 | -0.036162 | 3.5057
14 | -0.23788 | -0.11059 | 0.23789 | 0.10896 | 5.4679e-06 | -0.0016346 | 0.0076565 | 0.0076365 | 0.0076565 | 0.98906 | -0.036162 | 0.98909 | -0.036341 | 3.4802
15 | -6.9861 | -3.1005 | 6.9907 | 3.0838 | 0.0046299 | -0.016659 | 0.22094 | 0.22072 | 0.22094 | 0.99863 | -0.0076102 | 0.99932 | -0.0037807 | 34.6304
16 | 1.314 | 0.57948 | -1.314 | -0.58007 | 5.9431e-05 | -0.00059395 | 0.041571 | 0.041578 | 0.041578 | 0.99728 | -0.0026055 | 0.99723 | -0.0022918 | 18.8991
17 | 2.9151 | 1.2917 | -2.9131 | -1.2953 | 0.0020184 | -0.0035645 | 0.092551 | 0.0926 | 0.0926 | 0.99452 | -0.07589 | 0.99387 | -0.071009 | 42.0911
18 | 1.3792 | 0.64507 | -1.3788 | -0.64823 | 0.00036084 | -0.003157 | 0.044196 | 0.044236 | 0.044236 | 0.99452 | -0.07589 | 0.99428 | -0.073773 | 20.1074
19 | -7.6998 | -3.4086 | 7.7008 | 3.4059 | 0.00093437 | -0.0026844 | 0.24319 | 0.24315 | 0.24319 | 0.99955 | -0.0024869 | 0.99968 | -0.0017856 | 38.1176
20 | 7.3024 | 3.2161 | -7.3008 | -3.2214 | 0.0016104 | -0.0052505 | 0.23045 | 0.23052 | 0.23052 | 0.99955 | -0.0024869 | 0.99932 | -0.0037807 | 36.1312
21 | -7.7008 | -3.4059 | 7.7017 | 3.4033 | 0.00092499 | -0.0026592 | 0.24315 | 0.24312 | 0.24315 | 0.99968 | -0.0017856 | 0.9998 | -0.0010889 | 38.1117
22 | 0.31011 | 0.13759 | -0.31005 | -0.14848 | 5.9447e-05 | -0.01089 | 0.0098004 | 0.0099324 | 0.0099324 | 0.99932 | -0.0037807 | 0.99914 | -0.0022894 | 4.5147
23 | -7.7017 | -3.4033 | 7.7026 | 3.4006 | 0.0009265 | -0.0026654 | 0.24312 | 0.24308 | 0.24312 | 0.9998 | -0.0010889 | 0.99993 | -0.00038869 | 38.1059
24 | 0.31005 | 0.14848 | -0.31005 | -0.15016 | 9.3426e-06 | -0.0016844 | 0.0099324 | 0.0099535 | 0.0099535 | 0.99914 | -0.0022894 | 0.99911 | -0.0020302 | 4.5243
25 | -7.7923 | -3.444 | 7.7928 | 3.4426 | 0.00052118 | -0.0014585 | 0.24595 | 0.24593 | 0.24595 | 0.99993 | -0.00038869 | 1 | 0 | 38.5505
26 | 5.3192 | 2.4363 | -5.3133 | -2.4749 | 0.0059139 | -0.038653 | 0.16889 | 0.1694 | 0.1694 | 1 | 0 | 0.99885 | -0.0053158 | 26.5519
27 | -0.21033 | -0.10187 | 0.21033 | 0.10082 | 2.7086e-06 | -0.0010507 | 0.0067702 | 0.0067569 | 0.0067702 | 0.99647 | 0.0010652 | 0.99648 | 0.00095427 | 3.0773
28 | -0.21033 | -0.10082 | 0.21034 | 0.10068 | 9.8771e-06 | -0.00013779 | 0.0067569 | 0.0067551 | 0.0067569 | 0.99648 | 0.00095427 | 0.99653 | 0.0012768 | 3.2176
29 | -0.51135 | -0.24646 | 0.51136 | 0.24578 | 1.0504e-05 | -0.00068719 | 0.016444 | 0.016435 | 0.016444 | 0.99653 | 0.0012768 | 0.99655 | 0.0011004 | 7.4744
30 | 0.32592 | 0.12551 | -0.32585 | -0.13848 | 7.5959e-05 | -0.012977 | 0.010117 | 0.010258 | 0.010258 | 0.99655 | 0.0011004 | 0.99633 | 0.0023441 | 4.6629
31 | -0.83728 | -0.37128 | 0.83781 | 0.35812 | 0.00052455 | -0.013165 | 0.026532 | 0.026378 | 0.026532 | 0.99655 | 0.0011004 | 0.99714 | -0.0030869 | 12.0598
32 | 0.24728 | 0.11726 | -0.24727 | -0.11976 | 8.9006e-06 | -0.0025006 | 0.0079294 | 0.0079607 | 0.0079607 | 0.99633 | 0.0023441 | 0.99629 | 0.0026504 | 3.6185
33 | 0.078566 | 0.021226 | -0.078564 | -0.029917 | 2.806e-06 | -0.0086915 | 0.002358 | 0.0024358 | 0.0024358 | 0.99633 | 0.0023441 | 0.99629 | 0.0023975 | 1.1072
34 | 0.24343 | 0.10928 | -0.2434 | -0.11718 | 2.6877e-05 | -0.0079029 | 0.0077248 | 0.0078214 | 0.0078214 | 0.99714 | -0.0030869 | 0.99704 | -0.0022103 | 3.5552
35 | -1.0812 | -0.4674 | 1.0813 | 0.4674 | 9.1745e-05 | 4.9012e-06 | 0.034101 | 0.034101 | 0.034101 | 0.99714 | -0.0030869 | 0.99723 | -0.0022918 | 16.2388
36 | 0.078564 | 0.029917 | -0.078561 | -0.038049 | 2.8181e-06 | -0.0081314 | 0.0024358 | 0.0025293 | 0.0025293 | 0.99629 | 0.0023975 | 0.99626 | 0.0026329 | 1.1497
37 | 0.2434 | 0.11718 | -0.2434 | -0.11788 | 2.4228e-06 | -0.00070261 | 0.0078214 | 0.0078302 | 0.0078302 | 0.99704 | -0.0022103 | 0.99703 | -0.0021242 | 3.5592
38 | -0.17249 | -0.083539 | 0.17249 | 0.08171 | 3.2186e-06 | -0.0018287 | 0.0055764 | 0.0055534 | 0.0055764 | 0.99212 | -0.058081 | 0.99214 | -0.05824 | 2.5347
39 | -0.17249 | -0.08171 | 0.1725 | 0.073422 | 1.4262e-05 | -0.0082881 | 0.0055534 | 0.0054545 | 0.0055534 | 0.99214 | -0.05824 | 0.99221 | -0.058843 | 2.5243
40 | 1.4349 | 0.60628 | -1.4331 | -0.6209 | 0.0017754 | -0.014618 | 0.045319 | 0.045493 | 0.045493 | 0.99221 | -0.058843 | 0.99105 | -0.050971 | 20.6785
41 | 0.15581 | 0.074583 | -0.15581 | -0.075461 | 1.2618e-06 | -0.00087733 | 0.0050257 | 0.0050368 | 0.0050368 | 0.99221 | -0.058843 | 0.99221 | -0.058773 | 2.2894
42 | -1.7632 | -0.75429 | 1.7639 | 0.75039 | 0.00072646 | -0.0038985 | 0.055794 | 0.055747 | 0.055794 | 0.99221 | -0.058843 | 0.9926 | -0.061438 | 25.3611
43 | 2.8324 | 1.2593 | -2.8299 | -1.264 | 0.0025303 | -0.0047458 | 0.090072 | 0.090137 | 0.090137 | 0.99344 | -0.067804 | 0.9926 | -0.061438 | 40.9716
44 | -2.8324 | -1.2593 | 2.8337 | 1.2568 | 0.0012871 | -0.0024206 | 0.090072 | 0.090039 | 0.090072 | 0.99344 | -0.067804 | 0.99387 | -0.071009 | 40.942
45 | 1.066 | 0.51361 | -1.0659 | -0.51553 | 0.00013153 | -0.0019164 | 0.034413 | 0.034438 | 0.034438 | 0.9926 | -0.061438 | 0.99249 | -0.060371 | 15.6536
46 | 0.38614 | 0.18632 | -0.38614 | -0.18651 | 1.7519e-06 | -0.0001979 | 0.01247 | 0.012473 | 0.012473 | 0.99249 | -0.060371 | 0.99249 | -0.060332 | 5.6695
47 | 1.2847 | 0.54937 | -1.2827 | -0.56993 | 0.0020098 | -0.020558 | 0.0407 | 0.040946 | 0.040946 | 0.99105 | -0.050971 | 0.98957 | -0.040469 | 18.612
48 | 0.14834 | 0.071531 | -0.14834 | -0.071843 | 4.098e-07 | -0.00031245 | 0.004797 | 0.0048009 | 0.0048009 | 0.99105 | -0.050971 | 0.99104 | -0.050947 | 2.1822
49 | 0.18603 | 0.075403 | -0.18603 | -0.076832 | 2.7648e-06 | -0.0014296 | 0.0058329 | 0.0058487 | 0.0058487 | 0.99342 | -0.077897 | 0.99341 | -0.077815 | 2.6585
50 | -0.18603 | -0.075403 | 0.18603 | 0.074632 | 1.4851e-06 | -0.00077109 | 0.0058329 | 0.0058246 | 0.0058329 | 0.99342 | -0.077897 | 0.99343 | -0.077939 | 2.6513
51 | 0.066555 | 0.01897 | -0.066555 | -0.020975 | 4.6314e-07 | -0.0020046 | 0.0020111 | 0.0020278 | 0.0020278 | 0.99341 | -0.077815 | 0.9934 | -0.077814 | 0.92173
52 | -0.18603 | -0.074632 | 0.18603 | 0.073517 | 2.1385e-06 | -0.0011143 | 0.0058246 | 0.0058126 | 0.0058246 | 0.99343 | -0.077939 | 0.99344 | -0.077997 | 2.6475
53 | 0.47814 | 0.201 | -0.478 | -0.21189 | 0.00014417 | -0.010893 | 0.01513 | 0.015257 | 0.015257 | 0.98957 | -0.040469 | 0.98929 | -0.0385 | 6.935
54 | 0.62018 | 0.27965 | -0.61987 | -0.29349 | 0.00031603 | -0.013834 | 0.019846 | 0.020017 | 0.020017 | 0.98957 | -0.040469 | 0.9891 | -0.036485 | 9.0984
55 | 0.1844 | 0.089275 | -0.1844 | -0.089309 | 1.945e-06 | -3.4507e-05 | 0.0059766 | 0.005977 | 0.005977 | 0.98957 | -0.040469 | 0.98956 | -0.040538 | 2.8462
56 | 0.34942 | 0.15108 | -0.3493 | -0.16781 | 0.00012032 | -0.016725 | 0.011108 | 0.011311 | 0.011311 | 0.98929 | -0.0385 | 0.98897 | -0.035891 | 5.1416
57 | 0.12858 | 0.060804 | -0.12857 | -0.062271 | 1.4503e-06 | -0.0014669 | 0.0041502 | 0.0041687 | 0.0041687 | 0.98929 | -0.0385 | 0.98928 | -0.038404 | 1.8949
58 | 0.61987 | 0.29349 | -0.61986 | -0.29395 | 1.0711e-05 | -0.00046443 | 0.020017 | 0.020022 | 0.020022 | 0.9891 | -0.036485 | 0.98909 | -0.036341 | 9.1011
59 | -0.066551 | -0.032232 | 0.066552 | 0.032107 | 8.8032e-07 | -0.00012558 | 0.0021489 | 0.0021473 | 0.0021489 | 0.99335 | -0.077694 | 0.99336 | -0.077607 | 1.0233
60 | -0.066552 | -0.032107 | 0.066555 | 0.020975 | 2.7348e-06 | -0.011132 | 0.0021473 | 0.0020278 | 0.0021473 | 0.99336 | -0.077607 | 0.9934 | -0.077814 | 0.97606
61 | 0.3493 | 0.16781 | -0.34929 | -0.16917 | 9.9823e-06 | -0.0013596 | 0.011311 | 0.011329 | 0.011329 | 0.98897 | -0.035891 | 0.98894 | -0.035644 | 5.1494
62 | -0.56053 | -0.2549 | 0.56065 | 0.25473 | 0.00011713 | -0.00016866 | 0.017893 | 0.01789 | 0.017893 | 0.99344 | -0.077997 | 0.99366 | -0.076292 | 8.5205
63 | -0.87278 | -0.4059 | 0.87281 | 0.40517 | 3.2826e-05 | -0.00073182 | 0.027964 | 0.027955 | 0.027964 | 0.99366 | -0.076292 | 0.9937 | -0.07659 | 12.7107
64 | 1.1152 | 0.52055 | -1.1147 | -0.52049 | 0.00052552 | 5.6699e-05 | 0.035732 | 0.035736 | 0.035736 | 0.99428 | -0.073773 | 0.99378 | -0.07731 | 17.0171
65 | 0.87289 | 0.40338 | -0.87285 | -0.40434 | 4.3028e-05 | -0.00096087 | 0.027932 | 0.027944 | 0.027944 | 0.99378 | -0.07731 | 0.99373 | -0.076924 | 12.702
66 | -0.38613 | -0.18701 | 0.38614 | 0.18651 | 4.4264e-06 | -0.00049968 | 0.012479 | 0.012473 | 0.012479 | 0.99248 | -0.060232 | 0.99249 | -0.060332 | 5.6724
67 | 0.87285 | 0.40434 | -0.87281 | -0.40517 | 3.6965e-05 | -0.00082474 | 0.027944 | 0.027955 | 0.027955 | 0.99373 | -0.076924 | 0.9937 | -0.07659 | 12.7066
68 | -0.30071 | -0.14564 | 0.30073 | 0.14204 | 1.8919e-05 | -0.0035968 | 0.0096798 | 0.0096348 | 0.0096798 | 0.99643 | -0.063266 | 0.99649 | -0.063799 | 4.3999
69 | 4.1887 | 1.9752 | -4.1881 | -1.9771 | 0.00061034 | -0.0019472 | 0.13416 | 0.13419 | 0.13419 | 0.99649 | -0.063799 | 0.99633 | -0.065539 | 37.0688
70 | -4.4895 | -2.1172 | 4.4921 | 2.1103 | 0.0025723 | -0.006917 | 0.14379 | 0.14369 | 0.14379 | 0.99649 | -0.063799 | 0.99711 | -0.056921 | 39.7222
71 | 1.0572 | 0.49916 | -1.0569 | -0.50245 | 0.00021658 | -0.0032822 | 0.033873 | 0.033914 | 0.033914 | 0.99633 | -0.065539 | 0.99614 | -0.063841 | 15.4157
72 | 3.131 | 1.478 | -3.1279 | -1.4762 | 0.0031091 | 0.0017422 | 0.10032 | 0.10032 | 0.10032 | 0.99633 | -0.065539 | 0.99528 | -0.072725 | 47.7708
73 | -4.4921 | -2.1103 | 4.4924 | 2.1067 | 0.0003907 | -0.0036074 | 0.14369 | 0.14364 | 0.14369 | 0.99711 | -0.056921 | 0.9972 | -0.056538 | 22.5213
74 | -0.55081 | -0.25744 | 0.55087 | 0.25734 | 6.4876e-05 | -9.8266e-05 | 0.017622 | 0.01762 | 0.017622 | 0.99601 | -0.064722 | 0.99614 | -0.063841 | 8.3913
75 | 0.34368 | 0.15713 | -0.34367 | -0.15823 | 7.4659e-06 | -0.0011007 | 0.010953 | 0.010966 | 0.010966 | 0.99601 | -0.064722 | 0.99599 | -0.064556 | 4.9845
76 | 0.34367 | 0.15823 | -0.34362 | -0.16635 | 5.5705e-05 | -0.0081266 | 0.010966 | 0.011067 | 0.011067 | 0.99599 | -0.064556 | 0.99584 | -0.063222 | 5.0303
77 | 0.27099 | 0.12769 | -0.27099 | -0.1282 | 2.1546e-06 | -0.00050461 | 0.0086889 | 0.0086951 | 0.0086951 | 0.99528 | -0.072725 | 0.99527 | -0.07266 | 3.9523
78 | 2.4695 | 1.173 | -2.469 | -1.1742 | 0.00048666 | -0.0012263 | 0.079296 | 0.079313 | 0.079313 | 0.99528 | -0.072725 | 0.9951 | -0.07108 | 36.0515
79 | 0.38737 | 0.17554 | -0.38733 | -0.18021 | 4.04e-05 | -0.0046701 | 0.012335 | 0.012392 | 0.012392 | 0.99528 | -0.072725 | 0.99518 | -0.071923 | 5.6327
80 | -4.7021 | -2.2083 | 4.7026 | 2.2044 | 0.00046032 | -0.0038583 | 0.15038 | 0.15033 | 0.15038 | 0.9972 | -0.056538 | 0.99731 | -0.056106 | 23.571
81 | 0.27099 | 0.1282 | -0.27099 | -0.12945 | 5.3605e-06 | -0.0012522 | 0.0086951 | 0.0087107 | 0.0087107 | 0.99527 | -0.07266 | 0.99525 | -0.072495 | 3.9594
82 | 2.2185 | 1.0529 | -2.2166 | -1.052 | 0.0018203 | 0.00090239 | 0.071237 | 0.07124 | 0.07124 | 0.9951 | -0.07108 | 0.99423 | -0.076906 | 33.9239
83 | 0.38733 | 0.18021 | -0.38731 | -0.1823 | 1.8194e-05 | -0.0020889 | 0.012392 | 0.012418 | 0.012418 | 0.99518 | -0.071923 | 0.99514 | -0.071545 | 5.6444
84 | -4.7026 | -2.2044 | 4.7049 | 2.185 | 0.0023097 | -0.019414 | 0.15033 | 0.15008 | 0.15033 | 0.99731 | -0.056106 | 0.99781 | -0.053876 | 23.5631
85 | 2.074 | 0.98325 | -2.0727 | -0.98831 | 0.0013752 | -0.0050571 | 0.066644 | 0.066712 | 0.066712 | 0.99423 | -0.076906 | 0.99362 | -0.071363 | 30.3238
86 | 0.1426 | 0.068726 | -0.1426 | -0.069064 | 4.0426e-07 | -0.0003379 | 0.0045961 | 0.0046004 | 0.0046004 | 0.99423 | -0.076906 | 0.99423 | -0.076881 | 2.0911
87 | 0.14283 | 0.067607 | -0.14283 | -0.068006 | 4.7332e-07 | -0.00039846 | 0.0045838 | 0.0045887 | 0.0045887 | 0.9952 | -0.072856 | 0.9952 | -0.072829 | 2.0858
88 | -0.14283 | -0.067607 | 0.14284 | 0.067385 | 7.1689e-06 | -0.00022209 | 0.0045838 | 0.004581 | 0.0045838 | 0.9952 | -0.072856 | 0.99525 | -0.072495 | 2.1827
89 | 0.073991 | 0.034665 | -0.073991 | -0.035835 | 3.735e-07 | -0.0011704 | 0.0023701 | 0.0023847 | 0.0023847 | 0.9952 | -0.072829 | 0.99519 | -0.072786 | 1.084
90 | 0.39199 | 0.17882 | -0.3919 | -0.18868 | 8.8627e-05 | -0.0098634 | 0.012518 | 0.01264 | 0.01264 | 0.99362 | -0.071363 | 0.99341 | -0.069534 | 5.7452
91 | 1.6807 | 0.80949 | -1.68 | -0.80922 | 0.00067407 | 0.00027048 | 0.054197 | 0.054199 | 0.054199 | 0.99362 | -0.071363 | 0.9932 | -0.074062 | 25.809
92 | -0.70613 | -0.34081 | 0.70617 | 0.33958 | 3.6715e-05 | -0.0012316 | 0.022815 | 0.022799 | 0.022815 | 0.99208 | -0.080513 | 0.99213 | -0.08096 | 10.3705
93 | 0.43667 | 0.21031 | -0.43652 | -0.2107 | 0.0001475 | -0.00039629 | 0.014103 | 0.014109 | 0.014109 | 0.99208 | -0.080513 | 0.99173 | -0.082778 | 6.7187
94 | -0.70617 | -0.33958 | 0.70637 | 0.33945 | 0.00020459 | -0.00013155 | 0.022799 | 0.022796 | 0.022799 | 0.99213 | -0.08096 | 0.99243 | -0.078997 | 10.8568
95 | 0.35215 | 0.16984 | -0.35215 | -0.17055 | 5.269e-06 | -0.00071347 | 0.01138 | 0.011389 | 0.011389 | 0.99173 | -0.082778 | 0.99171 | -0.082648 | 5.177
96 | 0.57995 | 0.27933 | -0.57992 | -0.27937 | 2.8387e-05 | -3.5648e-05 | 0.018724 | 0.018725 | 0.018725 | 0.99243 | -0.078997 | 0.99238 | -0.079326 | 8.9166
97 | -1.2863 | -0.61878 | 1.2873 | 0.61901 | 0.00093843 | 0.00022825 | 0.04152 | 0.041516 | 0.04152 | 0.99243 | -0.078997 | 0.9932 | -0.074062 | 19.7715
98 | 0.17577 | 0.083627 | -0.17577 | -0.084375 | 1.3657e-06 | -0.00074866 | 0.0056621 | 0.0056715 | 0.0056715 | 0.99238 | -0.079326 | 0.99237 | -0.07926 | 2.578
99 | -0.17576 | -0.085126 | 0.17577 | 0.084375 | 1.3746e-06 | -0.00075104 | 0.005681 | 0.0056715 | 0.005681 | 0.99237 | -0.079193 | 0.99237 | -0.07926 | 2.5823
100 | -0.34361 | -0.16642 | 0.34362 | 0.16635 | 1.3072e-05 | -6.2726e-05 | 0.011068 | 0.011067 | 0.011068 | 0.9958 | -0.063473 | 0.99584 | -0.063222 | 5.2703
101 | 0.16938 | 0.076746 | -0.16937 | -0.077367 | 1.022e-06 | -0.00062091 | 0.0053942 | 0.0054017 | 0.0054017 | 0.99514 | -0.071545 | 0.99513 | -0.071499 | 2.4553
102 | 0.16937 | 0.077367 | -0.16937 | -0.079886 | 4.1752e-06 | -0.0025188 | 0.0054017 | 0.0054324 | 0.0054324 | 0.99513 | -0.071499 | 0.99511 | -0.071305 | 2.4693
103 | 0.16937 | 0.079886 | -0.16937 | -0.082028 | 3.5897e-06 | -0.0021426 | 0.0054324 | 0.0054593 | 0.0054593 | 0.99511 | -0.071305 | 0.99509 | -0.071125 | 2.4815
104 | 0.3919 | 0.18868 | -0.39189 | -0.1898 | 1.0179e-05 | -0.0011202 | 0.01264 | 0.012654 | 0.012654 | 0.99341 | -0.069534 | 0.99338 | -0.069309 | 5.7517
105 | -0.16477 | -0.079803 | 0.16477 | 0.077819 | 3.1121e-06 | -0.0019836 | 0.0052967 | 0.005272 | 0.0052967 | 0.9978 | -0.053716 | 0.99781 | -0.053876 | 2.4076
106 | -4.8697 | -2.2628 | 4.8719 | 2.2684 | 0.0022184 | 0.0056109 | 0.15535 | 0.15535 | 0.15535 | 0.99781 | -0.053876 | 0.99865 | -0.0061637 | 24.0854
107 | -4.8719 | -2.2684 | 4.8725 | 2.2638 | 0.00058703 | -0.004605 | 0.15535 | 0.15529 | 0.15535 | 0.99865 | -0.0061637 | 0.99878 | -0.0056075 | 24.349
108 | -4.9441 | -2.2985 | 4.9441 | 2.2983 | 2.6628e-05 | -0.00020251 | 0.15758 | 0.15758 | 0.15758 | 0.99878 | -0.0056075 | 0.99878 | -0.0055826 | 24.6998
109 | -5.313 | -2.477 | 5.3133 | 2.4749 | 0.00031017 | -0.0020176 | 0.16943 | 0.1694 | 0.16943 | 0.99878 | -0.0055826 | 0.99885 | -0.0053158 | 26.5561

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 13.126 | 5.8894

## res_load
| p_mw | q_mvar
0 | 0.3053 | 0.14786
1 | 0.4026 | 0.19499
2 | 0.34552 | 0.16734
3 | 0.3058 | 0.1481
4 | 0.23785 | 0.1152
5 | 0.39741 | 0.19248
6 | 0.089639 | 0.043414
7 | 0.31005 | 0.15016
8 | 0.21033 | 0.10187
9 | 0.30101 | 0.14579
10 | 0.078561 | 0.038049
11 | 0.24727 | 0.11976
12 | 0.23264 | 0.11267
13 | 0.2434 | 0.11788
14 | 0.17249 | 0.083539
15 | 0.079397 | 0.038454
16 | 0.67974 | 0.32921
17 | 0.15581 | 0.075461
18 | 0.11947 | 0.057862
19 | 0.14834 | 0.071843
20 | 0.1844 | 0.089309
21 | 0.066551 | 0.032232
22 | 0.38197 | 0.185
23 | 0.12857 | 0.062271
24 | 0.34929 | 0.16917
25 | 0.3745 | 0.18138
26 | 0.31213 | 0.15117
27 | 0.26363 | 0.12768
28 | 0.2418 | 0.11711
29 | 0.38613 | 0.18701
30 | 0.30071 | 0.14564
31 | 0.20713 | 0.10032
32 | 0.50607 | 0.2451
33 | 0.20969 | 0.10156
34 | 0.25056 | 0.12135
35 | 0.06884 | 0.033341
36 | 0.12815 | 0.062064
37 | 0.1426 | 0.069064
38 | 0.26946 | 0.13051
39 | 0.084371 | 0.040863
40 | 0.35215 | 0.17055
41 | 0.40415 | 0.19574
42 | 0.39274 | 0.19021
43 | 0.17576 | 0.085126
44 | 0.34361 | 0.16642
45 | 0.21793 | 0.10555
46 | 0.16937 | 0.082028
47 | 0.073991 | 0.035835
48 | 0.39189 | 0.1898
49 | 0.16477 | 0.079803
50 | 0.071583 | 0.034669
51 | 0.3689 | 0.17867

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1