## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_438_1_node_77 | 20 | n |  | TRUE
1 | bus_MV_438_1_node_113 | 20 | n |  | TRUE
2 | bus_MV_438_1_node_114 | 20 | n |  | TRUE
3 | bus_MV_438_1_node_73 | 20 | n |  | TRUE
4 | bus_MV_438_1_node_10 | 20 | n |  | TRUE
5 | bus_MV_438_1_node_11 | 20 | n |  | TRUE
6 | bus_MV_438_1_node_126 | 20 | n |  | TRUE
7 | bus_MV_438_1_node_12 | 20 | n |  | TRUE
8 | bus_MV_438_1_node_122 | 20 | n |  | TRUE
9 | bus_MV_438_1_node_13 | 20 | n |  | TRUE
10 | bus_MV_438_1_node_16 | 20 | n |  | TRUE
11 | bus_MV_438_1_node_127 | 20 | n |  | TRUE
12 | bus_MV_438_1_node_102 | 20 | n |  | TRUE
13 | bus_MV_438_1_node_18 | 20 | n |  | TRUE
14 | bus_MV_438_1_node_110 | 20 | n |  | TRUE
15 | bus_MV_438_1_node_17 | 20 | n |  | TRUE
16 | bus_MV_438_1_node_76 | 20 | n |  | TRUE
17 | bus_MV_438_1_node_20 | 20 | n |  | TRUE
18 | bus_MV_438_1_node_22 | 20 | n |  | TRUE
19 | bus_MV_438_1_node_19 | 20 | n |  | TRUE
20 | bus_MV_438_1_node_21 | 20 | n |  | TRUE
21 | bus_MV_438_1_node_116 | 20 | n |  | TRUE
22 | bus_MV_438_1_node_105 | 20 | n |  | TRUE
23 | bus_MV_438_1_node_74 | 20 | n |  | TRUE
24 | bus_MV_438_1_node_72 | 20 | n |  | TRUE
25 | bus_MV_438_1_node_67 | 20 | n |  | TRUE
26 | bus_MV_438_1_node_23 | 20 | n |  | TRUE
27 | bus_MV_438_1_node_25 | 20 | n |  | TRUE
28 | bus_MV_438_1_node_24 | 20 | n |  | TRUE
29 | bus_MV_438_1_node_28 | 20 | n |  | TRUE
30 | bus_MV_438_1_node_26 | 20 | n |  | TRUE
31 | bus_MV_438_1_node_27 | 20 | n |  | TRUE
32 | bus_MV_438_1_node_91 | 20 | n |  | TRUE
33 | bus_MV_438_1_node_135 | 20 | n |  | TRUE
34 | bus_MV_438_1_node_139 | 20 | n |  | TRUE
35 | bus_MV_438_1_node_60 | 20 | n |  | TRUE
36 | bus_MV_438_1_node_120 | 20 | n |  | TRUE
37 | bus_MV_438_1_node_118 | 20 | n |  | TRUE
38 | bus_MV_438_1_node_29 | 20 | n |  | TRUE
39 | bus_MV_438_1_node_30 | 20 | n |  | TRUE
40 | bus_MV_438_1_node_31 | 20 | n |  | TRUE
41 | bus_MV_438_1_node_32 | 20 | n |  | TRUE
42 | bus_MV_438_1_node_63 | 20 | n |  | TRUE
43 | bus_MV_438_1_node_64 | 20 | n |  | TRUE
44 | bus_MV_438_1_node_51 | 20 | n |  | TRUE
45 | bus_MV_438_1_node_59 | 20 | n |  | TRUE
46 | bus_MV_438_1_node_36 | 20 | n |  | TRUE
47 | bus_MV_438_1_node_50 | 20 | n |  | TRUE
48 | bus_MV_438_1_node_82 | 20 | n |  | TRUE
49 | bus_MV_438_1_node_124 | 20 | n |  | TRUE
50 | bus_MV_438_1_node_33 | 20 | n |  | TRUE
51 | bus_MV_438_1_node_34 | 20 | n |  | TRUE
52 | bus_MV_438_1_node_35 | 20 | n |  | TRUE
53 | bus_MV_438_1_node_38 | 20 | n |  | TRUE
54 | bus_MV_438_1_node_37 | 20 | n |  | TRUE
55 | bus_MV_438_1_node_136 | 20 | n |  | TRUE
56 | bus_MV_438_1_node_93 | 20 | n |  | TRUE
57 | bus_MV_438_1_node_39 | 20 | n |  | TRUE
58 | bus_MV_438_1_node_138 | 20 | n |  | TRUE
59 | bus_MV_438_1_node_103 | 20 | n |  | TRUE
60 | bus_MV_438_1_node_97 | 20 | n |  | TRUE
61 | bus_MV_438_1_node_40 | 20 | n |  | TRUE
62 | bus_MV_438_1_node_41 | 20 | n |  | TRUE
63 | bus_MV_438_1_node_42 | 20 | n |  | TRUE
64 | bus_MV_438_1_node_62 | 20 | n |  | TRUE
65 | bus_MV_438_1_node_52 | 20 | n |  | TRUE
66 | bus_MV_438_1_node_49 | 20 | n |  | TRUE
67 | bus_MV_438_1_node_58 | 20 | n |  | TRUE
68 | bus_MV_438_1_node_43 | 20 | n |  | TRUE
69 | bus_MV_438_1_node_48 | 20 | n |  | TRUE
70 | bus_MV_438_1_node_45 | 20 | n |  | TRUE
71 | bus_MV_438_1_node_89 | 20 | n |  | TRUE
72 | bus_MV_438_1_node_44 | 20 | n |  | TRUE
73 | bus_MV_438_1_node_53 | 20 | n |  | TRUE
74 | bus_MV_438_1_node_137 | 20 | n |  | TRUE
75 | bus_MV_438_1_node_46 | 20 | n |  | TRUE
76 | bus_MV_438_1_node_47 | 20 | n |  | TRUE
77 | bus_MV_438_1_node_90 | 20 | n |  | TRUE
78 | bus_MV_438_1_node_57 | 20 | n |  | TRUE
79 | bus_MV_438_1_node_54 | 20 | n |  | TRUE
80 | bus_MV_438_1_node_55 | 20 | n |  | TRUE
81 | bus_MV_438_1_node_56 | 20 | n |  | TRUE
82 | bus_MV_438_1_node_61 | 20 | n |  | TRUE
83 | bus_MV_438_1_node_92 | 20 | n |  | TRUE
84 | bus_MV_438_1_node_65 | 20 | n |  | TRUE
85 | bus_MV_438_1_node_66 | 20 | n |  | TRUE
86 | bus_MV_438_1_node_71 | 20 | n |  | TRUE
87 | bus_MV_438_1_node_70 | 20 | n |  | TRUE
88 | bus_MV_438_1_node_75 | 20 | n |  | TRUE
89 | bus_MV_438_1_node_112 | 20 | n |  | TRUE
90 | bus_MV_438_1_node_115 | 20 | n |  | TRUE
91 | bus_MV_438_1_node_109 | 20 | n |  | TRUE
92 | bus_MV_438_1_node_83 | 20 | n |  | TRUE
93 | bus_MV_438_1_node_119 | 20 | n |  | TRUE
94 | bus_MV_438_1_node_128 | 20 | n |  | TRUE
95 | bus_MV_438_1_node_86 | 20 | n |  | TRUE
96 | bus_MV_438_1_node_87 | 20 | n |  | TRUE
97 | bus_MV_438_1_node_88 | 20 | n |  | TRUE
98 | bus_MV_438_1_node_121 | 20 | n |  | TRUE
99 | bus_MV_438_1_node_117 | 20 | n |  | TRUE
100 | bus_MV_438_1_node_94 | 20 | n |  | TRUE
101 | bus_MV_438_1_node_95 | 20 | n |  | TRUE
102 | bus_MV_438_1_node_96 | 20 | n |  | TRUE
103 | bus_MV_438_1_node_98 | 20 | n |  | TRUE
104 | bus_MV_438_1_node_132 | 20 | n |  | TRUE
105 | bus_MV_438_1_node_133 | 20 | n |  | TRUE
106 | bus_MV_438_1_node_99 | 20 | n |  | TRUE
107 | bus_MV_438_1_node_134 | 20 | n |  | TRUE
108 | bus_MV_438_1_node_100 | 20 | n |  | TRUE
109 | bus_MV_438_1_node_101 | 20 | n |  | TRUE
110 | bus_MV_438_1_node_104 | 20 | n |  | TRUE
111 | bus_MV_438_1_node_106 | 20 | n |  | TRUE
112 | bus_MV_438_1_node_107 | 20 | n |  | TRUE
113 | bus_MV_438_1_node_108 | 20 | n |  | TRUE
114 | bus_MV_438_1_node_111 | 20 | n |  | TRUE
115 | bus_HV_438_1_node_100 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_438_1_load_113 | 1 | 0.22346 | 0.10822 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_438_1_load_114 | 2 | 0.15171 | 0.073475 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_438_1_load_10 | 4 | 0.22807 | 0.11046 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_438_1_load_126 | 6 | 0.089846 | 0.043515 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_438_1_load_122 | 8 | 0.27234 | 0.1319 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_438_1_load_13 | 9 | 0.36082 | 0.17476 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_438_1_load_16 | 10 | 0.29296 | 0.14188 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_438_1_load_127 | 11 | 0.087691 | 0.042471 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_438_1_load_76 | 16 | 0.19997 | 0.096851 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_438_1_load_19 | 19 | 0.21537 | 0.10431 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_438_1_load_116 | 21 | 0.12372 | 0.059922 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_438_1_load_105 | 22 | 0.13393 | 0.064866 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_438_1_load_74 | 23 | 0.11513 | 0.055759 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_438_1_load_23 | 26 | 0.31436 | 0.15225 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_438_1_load_91 | 32 | 0.078969 | 0.038246 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_438_1_load_135 | 33 | 0.24008 | 0.11628 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_438_1_load_139 | 34 | 0.23428 | 0.11346 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_438_1_load_29 | 38 | 0.39261 | 0.19015 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_438_1_load_63 | 42 | 0.20847 | 0.10097 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_438_1_load_64 | 43 | 0.19127 | 0.092637 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_438_1_load_82 | 48 | 0.15585 | 0.075483 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_438_1_load_124 | 49 | 0.28452 | 0.1378 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_438_1_load_33 | 50 | 0.24739 | 0.11982 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_438_1_load_136 | 55 | 0.26221 | 0.127 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_438_1_load_93 | 56 | 0.11735 | 0.056835 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_438_1_load_138 | 58 | 0.2337 | 0.11319 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_438_1_load_103 | 59 | 0.16524 | 0.080028 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_438_1_load_40 | 61 | 0.20379 | 0.098698 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_438_1_load_62 | 64 | 0.18813 | 0.091115 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_438_1_load_52 | 65 | 0.34936 | 0.16921 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_438_1_load_49 | 66 | 0.34969 | 0.16936 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_438_1_load_48 | 69 | 0.37176 | 0.18005 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_438_1_load_89 | 71 | 0.076859 | 0.037225 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_438_1_load_53 | 73 | 0.17945 | 0.086913 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_438_1_load_137 | 74 | 0.13244 | 0.064144 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_438_1_load_90 | 77 | 0.20335 | 0.098485 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_438_1_load_54 | 79 | 0.39151 | 0.18962 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_438_1_load_92 | 83 | 0.085544 | 0.041431 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_438_1_load_65 | 84 | 0.37628 | 0.18224 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_438_1_load_71 | 86 | 0.13843 | 0.067043 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_438_1_load_70 | 87 | 0.13238 | 0.064117 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_438_1_load_75 | 88 | 0.1358 | 0.065769 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_438_1_load_115 | 90 | 0.071658 | 0.034706 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_438_1_load_83 | 92 | 0.3271 | 0.15842 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_438_1_load_128 | 94 | 0.11714 | 0.056733 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_438_1_load_86 | 95 | 0.44687 | 0.21643 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_438_1_load_117 | 99 | 0.66899 | 0.32401 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_438_1_load_94 | 100 | 1.1517 | 0.5578 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_438_1_load_132 | 104 | 0.50419 | 0.24419 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_438_1_load_99 | 106 | 2.077 | 1.0059 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_438_1_load_134 | 107 | 0.75268 | 0.36454 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_438_1_load_100 | 108 | 0.55711 | 0.26982 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_438_1_load_101 | 109 | 0.32442 | 0.15712 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_438_1_load_104 | 110 | 2.2682 | 1.0985 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_438_1_load_106 | 111 | 0.19037 | 0.092201 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_438_1_load_107 | 112 | 0.14225 | 0.068897 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_438_1_load_111 | 114 | 0.25043 | 0.12129 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 108 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_438_1_line_0 |  | 0 | 1 | 0.063122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_438_1_line_1 |  | 0 | 2 | 0.039149 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_438_1_line_2 |  | 0 | 3 | 0.37578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_438_1_line_3 |  | 1 | 89 | 0.22185 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_438_1_line_4 |  | 3 | 24 | 0.12821 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_438_1_line_5 |  | 3 | 86 | 0.004288 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_438_1_line_6 |  | 4 | 5 | 0.10314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_438_1_line_7 |  | 4 | 6 | 1.5742 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_438_1_line_8 |  | 5 | 7 | 1.1681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_438_1_line_9 |  | 6 | 8 | 0.61654 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_438_1_line_10 |  | 7 | 9 | 0.069246 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_438_1_line_11 |  | 8 | 98 | 0.037062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_438_1_line_12 |  | 10 | 11 | 0.10483 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_438_1_line_13 |  | 10 | 12 | 1.1885 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_438_1_line_14 |  | 11 | 13 | 0.057449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_438_1_line_15 |  | 12 | 110 | 0.070794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_438_1_line_16 |  | 12 | 109 | 0.046374 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
17 | MV_438_1_line_17 |  | 13 | 15 | 0.06647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_438_1_line_18 |  | 14 | 15 | 0.12721 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_438_1_line_19 |  | 14 | 16 | 0.12335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_438_1_line_20 |  | 16 | 88 | 0.042488 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_438_1_line_21 |  | 17 | 18 | 0.22204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_438_1_line_22 |  | 17 | 19 | 0.02 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_438_1_line_23 |  | 18 | 22 | 0.053122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_438_1_line_24 |  | 18 | 20 | 0.14876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_438_1_line_25 |  | 20 | 21 | 0.041648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_438_1_line_26 |  | 21 | 23 | 0.11416 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_438_1_line_27 |  | 22 | 25 | 0.023073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_438_1_line_28 |  | 23 | 24 | 0.008357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_438_1_line_29 |  | 24 | 88 | 0.069359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_438_1_line_30 |  | 25 | 85 | 0.42595 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_438_1_line_31 |  | 26 | 27 | 0.052219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_438_1_line_32 |  | 26 | 28 | 0.080136 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_438_1_line_33 |  | 27 | 29 | 0.33042 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_438_1_line_34 |  | 28 | 30 | 0.60764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_438_1_line_35 |  | 29 | 34 | 0.004884 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_438_1_line_36 |  | 30 | 31 | 0.33409 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_438_1_line_37 |  | 30 | 32 | 0.036597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_438_1_line_38 |  | 31 | 33 | 0.020413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_438_1_line_39 |  | 33 | 35 | 0.023993 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_438_1_line_40 |  | 34 | 36 | 0.022836 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_438_1_line_41 |  | 35 | 82 | 0.22926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_438_1_line_42 |  | 36 | 37 | 0.25148 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_438_1_line_43 |  | 37 | 93 | 0.2144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_438_1_line_44 |  | 37 | 99 | 0.036411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_438_1_line_45 |  | 38 | 39 | 0.056114 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_438_1_line_46 |  | 39 | 40 | 0.37917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_438_1_line_47 |  | 40 | 41 | 0.36284 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
48 | MV_438_1_line_48 |  | 40 | 42 | 0.017888 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
49 | MV_438_1_line_49 |  | 41 | 43 | 0.030207 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
50 | MV_438_1_line_50 |  | 41 | 44 | 0.24622 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_438_1_line_51 |  | 42 | 45 | 0.014537 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
52 | MV_438_1_line_52 |  | 43 | 46 | 0.034306 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
53 | MV_438_1_line_53 |  | 44 | 49 | 0.01628 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_438_1_line_54 |  | 44 | 47 | 0.18467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_438_1_line_55 |  | 45 | 82 | 0.38333 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
56 | MV_438_1_line_56 |  | 46 | 51 | 0.29425 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
57 | MV_438_1_line_57 |  | 47 | 48 | 0.0083271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_438_1_line_58 |  | 50 | 51 | 0.031206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_438_1_line_59 |  | 51 | 52 | 0.21562 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
60 | MV_438_1_line_60 |  | 52 | 53 | 0.34486 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
61 | MV_438_1_line_61 |  | 52 | 54 | 0.50536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_438_1_line_62 |  | 52 | 55 | 0.037212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_438_1_line_63 |  | 53 | 57 | 0.53483 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
64 | MV_438_1_line_64 |  | 53 | 58 | 0.034593 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_438_1_line_65 |  | 54 | 56 | 0.045587 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_438_1_line_66 |  | 57 | 59 | 0.013023 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
67 | MV_438_1_line_67 |  | 59 | 60 | 0.037049 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
68 | MV_438_1_line_68 |  | 60 | 101 | 0.041721 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
69 | MV_438_1_line_69 |  | 61 | 62 | 0.024364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_438_1_line_70 |  | 62 | 63 | 0.32483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_438_1_line_71 |  | 63 | 68 | 0.13245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_438_1_line_72 |  | 63 | 69 | 0.00388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_438_1_line_73 |  | 64 | 65 | 0.33497 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_438_1_line_74 |  | 64 | 66 | 0.39827 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_438_1_line_75 |  | 64 | 67 | 0.003795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_438_1_line_76 |  | 65 | 70 | 0.037734 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_438_1_line_77 |  | 66 | 76 | 0.002225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_438_1_line_78 |  | 67 | 82 | 0.26886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_438_1_line_79 |  | 68 | 70 | 0.1788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_438_1_line_80 |  | 68 | 71 | 0.0088988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_438_1_line_81 |  | 72 | 73 | 0.0422 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_438_1_line_82 |  | 72 | 74 | 0.33 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_438_1_line_83 |  | 74 | 78 | 0.011053 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_438_1_line_84 |  | 75 | 76 | 0.46847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_438_1_line_85 |  | 75 | 77 | 0.003581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_438_1_line_86 |  | 78 | 80 | 0.24835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_438_1_line_87 |  | 79 | 80 | 0.007896 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_438_1_line_88 |  | 79 | 81 | 0.040998 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_438_1_line_89 |  | 81 | 82 | 0.22768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_438_1_line_90 |  | 82 | 83 | 0.035367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_438_1_line_91 |  | 84 | 85 | 0.022616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_438_1_line_92 |  | 86 | 87 | 0.14849 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
93 | MV_438_1_line_93 |  | 89 | 90 | 0.14421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_438_1_line_94 |  | 89 | 91 | 0.2128 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_438_1_line_95 |  | 91 | 114 | 0.033626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_438_1_line_96 |  | 91 | 113 | 0.056585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_438_1_line_97 |  | 92 | 93 | 0.046089 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_438_1_line_98 |  | 93 | 94 | 0.034597 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_438_1_line_99 |  | 95 | 96 | 0.0233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_438_1_line_100 |  | 96 | 97 | 0.10191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_438_1_line_101 |  | 97 | 98 | 0.0871 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_438_1_line_102 |  | 97 | 99 | 0.048215 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_438_1_line_103 |  | 100 | 101 | 0.028065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_438_1_line_104 |  | 101 | 102 | 0.015572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_438_1_line_105 |  | 101 | 103 | 0.037959 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
106 | MV_438_1_line_106 |  | 102 | 104 | 0.018134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_438_1_line_107 |  | 102 | 105 | 0.03676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_438_1_line_108 |  | 103 | 106 | 0.051753 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
109 | MV_438_1_line_109 |  | 105 | 107 | 0.001257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_438_1_line_110 |  | 106 | 108 | 0.014223 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
111 | MV_438_1_line_111 |  | 108 | 109 | 0.068762 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
112 | MV_438_1_line_112 |  | 111 | 112 | 0.0078224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_438_1_line_113 |  | 111 | 113 | 0.021861 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_438_1_trafo_100 | 25 MVA 110/20 kV | 115 | 108 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2711025.114 | 1270101.7494
1 | 2710999.2617 | 1270059.9024
2 | 2711006.3009 | 1270136.0817
3 | 2711034.0318 | 1269799.3171
4 | 2708476.426 | 1271357.7944
5 | 2708575.9894 | 1271384.6414
6 | 2708770.2344 | 1269811.2919
7 | 2709011.7858 | 1272047.2527
8 | 2708787.9088 | 1269195.0006
9 | 2709057.5676 | 1271997.4541
10 | 2710735.9924 | 1269421.4129
11 | 2710840.8194 | 1269420.4778
12 | 2709593.9448 | 1269092.2745
13 | 2710886.6503 | 1269455.3018
14 | 2710742.5847 | 1269582.3446
15 | 2710838.3734 | 1269498.634
16 | 2710842.0447 | 1269655.2951
17 | 2711094.3742 | 1269363.579
18 | 2711062.7253 | 1269484.7239
19 | 2711104.8935 | 1269346.5507
20 | 2710967.3762 | 1269593.3055
21 | 2711000.6533 | 1269618.3488
22 | 2711101.4214 | 1269521.1188
23 | 2710937.8602 | 1269713.6905
24 | 2710932.9462 | 1269720.4597
25 | 2711118.2301 | 1269536.9246
26 | 2708504.1876 | 1268834.5928
27 | 2708502.0544 | 1268886.7657
28 | 2708424.1325 | 1268830.9979
29 | 2708705.1365 | 1268974.0633
30 | 2708398.0598 | 1268349.1454
31 | 2708605.6473 | 1268464.7575
32 | 2708392.4733 | 1268316.3262
33 | 2708606.891 | 1268485.1314
34 | 2708709.9779 | 1268974.8086
35 | 2708608.355 | 1268509.0791
36 | 2708732.7669 | 1268973.3489
37 | 2708741.0851 | 1269076.2917
38 | 2708931.5641 | 1268747.5361
39 | 2708937.0208 | 1268691.688
40 | 2708955.2957 | 1268483.3659
41 | 2709217.9507 | 1268610.6478
42 | 2708937.5782 | 1268481.1595
43 | 2709216.7901 | 1268640.8304
44 | 2709322.2886 | 1268387.6274
45 | 2708936.6481 | 1268495.6661
46 | 2709218.3391 | 1268675.1
47 | 2709359.4631 | 1268335.1251
48 | 2709358.5789 | 1268343.4051
49 | 2709338.5161 | 1268389.407
50 | 2709362.523 | 1268757.5721
51 | 2709356.1702 | 1268788.0256
52 | 2709422.0391 | 1268925.098
53 | 2709247.6355 | 1269038.8033
54 | 2709529.6898 | 1268779.6878
55 | 2709401.8218 | 1268942.9169
56 | 2709484.2907 | 1268783.7964
57 | 2709467.3693 | 1269238.8228
58 | 2709216.1913 | 1269053.2235
59 | 2709480.3891 | 1269238.5325
60 | 2709513.8624 | 1269227.4856
61 | 2709058.8793 | 1267745.316
62 | 2709082.6882 | 1267740.159
63 | 2708838.3658 | 1267767.8673
64 | 2708895.5672 | 1268336.5817
65 | 2708897.9509 | 1268001.6234
66 | 2709243.6233 | 1268143.0041
67 | 2708895.8286 | 1268340.3675
68 | 2708863.2933 | 1267848.3185
69 | 2708836.6001 | 1267764.4096
70 | 2708860.2495 | 1267998.3037
71 | 2708855.041 | 1267847.1432
72 | 2708478.2726 | 1267903.2083
73 | 2708520.3122 | 1267906.8833
74 | 2708413.503 | 1268226.7892
75 | 2709144.6847 | 1267872.2851
76 | 2709243.8975 | 1268140.7962
77 | 2709148.2384 | 1267872.7263
78 | 2708413.8121 | 1268237.8378
79 | 2708569.7362 | 1268306.5156
80 | 2708565.4849 | 1268299.854
81 | 2708573.3337 | 1268346.2718
82 | 2708702.169 | 1268393.626
83 | 2708737.4812 | 1268391.6517
84 | 2711359.5115 | 1269429.5174
85 | 2711362.6737 | 1269407.1239
86 | 2711036.6546 | 1269795.9189
87 | 2711100.0215 | 1269661.6313
88 | 2710876.6537 | 1269679.9408
89 | 2710820.5258 | 1269928.4774
90 | 2710715.0333 | 1269835.3263
91 | 2710669.9557 | 1269818.2912
92 | 2708969.9764 | 1269072.0528
93 | 2708924.0134 | 1269068.6434
94 | 2708894.2204 | 1269086.2318
95 | 2708662.0307 | 1269184.5316
96 | 2708641.6987 | 1269175.2273
97 | 2708709.8775 | 1269139.6726
98 | 2708751.2703 | 1269189.411
99 | 2708731.7143 | 1269107.3561
100 | 2709483.5934 | 1269202.1229
101 | 2709503.6302 | 1269191.5423
102 | 2709513.2795 | 1269183.8478
103 | 2709486.7604 | 1269170.5446
104 | 2709506.3341 | 1269171.9753
105 | 2709529.9935 | 1269198.2257
106 | 2709492.5204 | 1269119.1136
107 | 2709530.0154 | 1269199.4828
108 | 2709494.1034 | 1269104.979
109 | 2709551.9249 | 1269074.311
110 | 2709552.5644 | 1269147.6555
111 | 2710619.058 | 1269810.6367
112 | 2710614.0394 | 1269816.6371
113 | 2710633.0835 | 1269793.868
114 | 2710648.6467 | 1269844.3028
115 | 2709494.1034 | 1269104.979

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98976 | -0.048463 | 0 | 0
1 | 0.98969 | -0.047836 | 0.22346 | 0.10822
2 | 0.98975 | -0.048537 | 0.15171 | 0.073475
3 | 0.99026 | -0.052765 | 0 | 0
4 | 0.98482 | -0.043574 | 0.22807 | 0.11046
5 | 0.98477 | -0.043317 | 0 | 0
6 | 0.98659 | -0.027633 | 0.089846 | 0.043515
7 | 0.98423 | -0.039276 | 0 | 0
8 | 0.9874 | -0.02065 | 0.27234 | 0.1319
9 | 0.9842 | -0.038971 | 0.36082 | 0.17476
10 | 0.99292 | -0.051726 | 0.29296 | 0.14188
11 | 0.99237 | -0.055679 | 0.087691 | 0.042471
12 | 0.99978 | -0.0029225 | 0 | 0
13 | 0.99218 | -0.054057 | 0 | 0
14 | 0.99132 | -0.056805 | 0 | 0
15 | 0.99196 | -0.052173 | 0 | 0
16 | 0.99091 | -0.053288 | 0.19997 | 0.096851
17 | 0.99014 | -0.04982 | 0 | 0
18 | 0.99021 | -0.050359 | 0 | 0
19 | 0.99014 | -0.049767 | 0.21537 | 0.10431
20 | 0.99034 | -0.051485 | 0 | 0
21 | 0.99038 | -0.051795 | 0.12372 | 0.059922
22 | 0.99017 | -0.050069 | 0.13393 | 0.064866
23 | 0.99057 | -0.050377 | 0.11513 | 0.055759
24 | 0.99058 | -0.050463 | 0 | 0
25 | 0.99016 | -0.049979 | 0 | 0
26 | 0.99002 | -0.041054 | 0.31436 | 0.15225
27 | 0.98983 | -0.039508 | 0 | 0
28 | 0.99049 | -0.037589 | 0 | 0
29 | 0.98867 | -0.029616 | 0 | 0
30 | 0.99287 | -0.057548 | 0 | 0
31 | 0.99422 | -0.068542 | 0 | 0
32 | 0.99287 | -0.057514 | 0.078969 | 0.038246
33 | 0.9943 | -0.069208 | 0.24008 | 0.11628
34 | 0.98865 | -0.029469 | 0.23428 | 0.11346
35 | 0.9944 | -0.070059 | 0 | 0
36 | 0.98854 | -0.030284 | 0 | 0
37 | 0.98773 | -0.023348 | 0 | 0
38 | 0.99643 | -0.06175 | 0.39261 | 0.19015
39 | 0.99647 | -0.061482 | 0 | 0
40 | 0.99666 | -0.063164 | 0 | 0
41 | 0.99718 | -0.053528 | 0 | 0
42 | 0.99664 | -0.063609 | 0.20847 | 0.10097
43 | 0.99722 | -0.05267 | 0.19127 | 0.092637
44 | 0.99697 | -0.054953 | 0 | 0
45 | 0.99662 | -0.063959 | 0 | 0
46 | 0.99728 | -0.05167 | 0 | 0
47 | 0.99693 | -0.054635 | 0 | 0
48 | 0.99693 | -0.05462 | 0.15585 | 0.075483
49 | 0.99696 | -0.054898 | 0.28452 | 0.1378
50 | 0.99773 | -0.042973 | 0.24739 | 0.11982
51 | 0.99774 | -0.043065 | 0 | 0
52 | 0.99808 | -0.036524 | 0 | 0
53 | 0.99867 | -0.025467 | 0 | 0
54 | 0.99801 | -0.036041 | 0 | 0
55 | 0.99807 | -0.036408 | 0.26221 | 0.127
56 | 0.998 | -0.035978 | 0.11735 | 0.056835
57 | 0.99959 | -0.0077139 | 0 | 0
58 | 0.99865 | -0.025565 | 0.2337 | 0.11319
59 | 0.99962 | -0.0072796 | 0.16524 | 0.080028
60 | 0.99968 | -0.0060204 | 0 | 0
61 | 0.99377 | -0.074421 | 0.20379 | 0.098698
62 | 0.99378 | -0.074481 | 0 | 0
63 | 0.99386 | -0.075191 | 0 | 0
64 | 0.99479 | -0.07295 | 0.18813 | 0.091115
65 | 0.99414 | -0.077541 | 0.34936 | 0.16921
66 | 0.99436 | -0.076033 | 0.34969 | 0.16936
67 | 0.9948 | -0.073023 | 0 | 0
68 | 0.99396 | -0.076029 | 0 | 0
69 | 0.99386 | -0.075173 | 0.37176 | 0.18005
70 | 0.99411 | -0.077283 | 0 | 0
71 | 0.99396 | -0.076021 | 0.076859 | 0.037225
72 | 0.99493 | -0.075808 | 0 | 0
73 | 0.99492 | -0.0759 | 0.17945 | 0.086913
74 | 0.99505 | -0.075078 | 0.13244 | 0.064144
75 | 0.99424 | -0.075046 | 0 | 0
76 | 0.99436 | -0.076029 | 0 | 0
77 | 0.99424 | -0.075037 | 0.20335 | 0.098485
78 | 0.99505 | -0.075119 | 0 | 0
79 | 0.99515 | -0.076023 | 0.39151 | 0.18962
80 | 0.99515 | -0.075997 | 0 | 0
81 | 0.99519 | -0.076353 | 0 | 0
82 | 0.99539 | -0.078134 | 0 | 0
83 | 0.99539 | -0.078099 | 0.085544 | 0.041431
84 | 0.98994 | -0.048072 | 0.37628 | 0.18224
85 | 0.98995 | -0.048175 | 0 | 0
86 | 0.99025 | -0.052751 | 0.13843 | 0.067043
87 | 0.99022 | -0.052995 | 0.13238 | 0.064117
88 | 0.99078 | -0.052174 | 0.1358 | 0.065769
89 | 0.98941 | -0.049846 | 0 | 0
90 | 0.98939 | -0.049736 | 0.071658 | 0.034706
91 | 0.98925 | -0.048403 | 0 | 0
92 | 0.98758 | -0.022403 | 0.3271 | 0.15842
93 | 0.98761 | -0.022216 | 0 | 0
94 | 0.9876 | -0.022266 | 0.11714 | 0.056733
95 | 0.98747 | -0.021144 | 0.44687 | 0.21643
96 | 0.98749 | -0.021271 | 0 | 0
97 | 0.98755 | -0.021819 | 0 | 0
98 | 0.98744 | -0.021001 | 0 | 0
99 | 0.98763 | -0.022521 | 0.66899 | 0.32401
100 | 0.99971 | -0.0042153 | 1.1517 | 0.5578
101 | 0.99975 | -0.0046016 | 0 | 0
102 | 0.99973 | -0.0043689 | 0 | 0
103 | 0.99984 | -0.0029625 | 0 | 0
104 | 0.99972 | -0.0042597 | 0.50419 | 0.24419
105 | 0.99969 | -0.0040387 | 0 | 0
106 | 0.99996 | -0.00072664 | 2.077 | 1.0059
107 | 0.99969 | -0.0040274 | 0.75268 | 0.36454
108 | 1 | 0 | -18.3307 | -8.4877
109 | 0.99992 | -0.0014951 | 0.32442 | 0.15712
110 | 0.99958 | -0.0010039 | 2.2682 | 1.0985
111 | 0.98921 | -0.04809 | 0.19037 | 0.092201
112 | 0.98921 | -0.048076 | 0.14225 | 0.068897
113 | 0.98922 | -0.048178 | 0 | 0
114 | 0.98924 | -0.048301 | 0.25043 | 0.12129
115 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.87853 | 0.4126 | -0.87846 | -0.41406 | 6.7573e-05 | -0.0014562 | 0.028308 | 0.028327 | 0.028327 | 0.98976 | -0.048463 | 0.98969 | -0.047836 | 12.8758
1 | 0.15171 | 0.07343 | -0.15171 | -0.073475 | 1.6858e-06 | -4.4727e-05 | 0.0049158 | 0.0049164 | 0.0049164 | 0.98976 | -0.048463 | 0.98975 | -0.048537 | 2.3411
2 | -1.0302 | -0.48603 | 1.0308 | 0.4774 | 0.00055194 | -0.00863 | 0.033224 | 0.033115 | 0.033224 | 0.98976 | -0.048463 | 0.99026 | -0.052765 | 15.1018
3 | 0.655 | 0.30583 | -0.65483 | -0.30598 | 0.00017576 | -0.00014925 | 0.021085 | 0.021089 | 0.021089 | 0.98969 | -0.047836 | 0.98941 | -0.049846 | 10.0422
4 | -1.3016 | -0.60829 | 1.302 | 0.60839 | 0.00040068 | 0.00010084 | 0.041883 | 0.041881 | 0.041883 | 0.99026 | -0.052765 | 0.99058 | -0.050463 | 19.9442
5 | 0.27082 | 0.13089 | -0.27081 | -0.13099 | 4.402e-07 | -0.00010026 | 0.0087684 | 0.0087697 | 0.0087697 | 0.99026 | -0.052765 | 0.99025 | -0.052751 | 3.9862
6 | 0.36106 | 0.1438 | -0.36105 | -0.14619 | 1.791e-05 | -0.0023828 | 0.011392 | 0.011418 | 0.011418 | 0.98482 | -0.043574 | 0.98477 | -0.043317 | 5.1902
7 | -0.58914 | -0.25427 | 0.59013 | 0.25306 | 0.00099111 | -0.0012051 | 0.018809 | 0.018788 | 0.018809 | 0.98482 | -0.043574 | 0.98659 | -0.027633 | 8.9566
8 | 0.36105 | 0.14619 | -0.36084 | -0.17316 | 0.00020886 | -0.026971 | 0.011418 | 0.011739 | 0.011739 | 0.98477 | -0.043317 | 0.98423 | -0.039276 | 5.3358
9 | -0.67998 | -0.29657 | 0.68049 | 0.29618 | 0.00051736 | -0.00039296 | 0.021706 | 0.021698 | 0.021706 | 0.98659 | -0.027633 | 0.9874 | -0.02065 | 10.3362
10 | 0.36084 | 0.17316 | -0.36082 | -0.17476 | 1.2761e-05 | -0.0015978 | 0.011739 | 0.011759 | 0.011759 | 0.98423 | -0.039276 | 0.9842 | -0.038971 | 5.3451
11 | -0.95283 | -0.42808 | 0.95288 | 0.42723 | 4.613e-05 | -0.0008491 | 0.030539 | 0.030529 | 0.030539 | 0.9874 | -0.02065 | 0.98744 | -0.021001 | 13.8815
12 | 2.6964 | 1.2521 | -2.695 | -1.2514 | 0.0013954 | 0.00075074 | 0.086435 | 0.086436 | 0.086436 | 0.99292 | -0.051726 | 0.99237 | -0.055679 | 41.16
13 | -2.9894 | -1.394 | 3.0089 | 1.4048 | 0.01947 | 0.010787 | 0.095897 | 0.09588 | 0.095897 | 0.99292 | -0.051726 | 0.99978 | -0.0029225 | 45.6652
14 | 2.6074 | 1.2089 | -2.6068 | -1.2101 | 0.00053615 | -0.0011915 | 0.083602 | 0.083619 | 0.083619 | 0.99237 | -0.055679 | 0.99218 | -0.054057 | 38.0085
15 | 2.2687 | 1.097 | -2.2682 | -1.0985 | 0.00050051 | -0.0015407 | 0.072762 | 0.072783 | 0.072783 | 0.99978 | -0.0029225 | 0.99958 | -0.0010039 | 33.0834
16 | -5.2776 | -2.5018 | 5.2782 | 2.5007 | 0.00063691 | -0.0011276 | 0.16864 | 0.16862 | 0.16864 | 0.99978 | -0.0029225 | 0.99992 | -0.0014951 | 46.5851
17 | 2.6068 | 1.2101 | -2.6062 | -1.2115 | 0.0006206 | -0.0013779 | 0.083619 | 0.083638 | 0.083638 | 0.99218 | -0.054057 | 0.99196 | -0.052173 | 38.0172
18 | -2.6046 | -1.2106 | 2.6062 | 1.2115 | 0.0015855 | 0.0008438 | 0.08364 | 0.083638 | 0.08364 | 0.99132 | -0.056805 | 0.99196 | -0.052173 | 39.8284
19 | 2.6046 | 1.2106 | -2.6035 | -1.2132 | 0.0011525 | -0.0025511 | 0.08364 | 0.083675 | 0.083675 | 0.99132 | -0.056805 | 0.99091 | -0.053288 | 38.0342
20 | 2.4035 | 1.1163 | -2.4032 | -1.1172 | 0.00033813 | -0.00089566 | 0.077203 | 0.077215 | 0.077215 | 0.99091 | -0.053288 | 0.99078 | -0.052174 | 35.0979
21 | -0.21537 | -0.10384 | 0.21539 | 0.098649 | 1.427e-05 | -0.0051936 | 0.006971 | 0.0069065 | 0.006971 | 0.99014 | -0.04982 | 0.99021 | -0.050359 | 3.1686
22 | 0.21537 | 0.10384 | -0.21537 | -0.10431 | 1.2986e-06 | -0.00046777 | 0.006971 | 0.0069769 | 0.0069769 | 0.99014 | -0.04982 | 0.99014 | -0.049767 | 3.1713
23 | 0.51033 | 0.23486 | -0.51031 | -0.2361 | 1.9039e-05 | -0.0012379 | 0.016377 | 0.016393 | 0.016393 | 0.99021 | -0.050359 | 0.99017 | -0.050069 | 7.4512
24 | -0.72571 | -0.33351 | 0.72582 | 0.33006 | 0.00010747 | -0.0034511 | 0.023284 | 0.023242 | 0.023284 | 0.99021 | -0.050359 | 0.99034 | -0.051485 | 10.5836
25 | -0.72582 | -0.33006 | 0.72585 | 0.32909 | 3.0019e-05 | -0.00096641 | 0.023242 | 0.02323 | 0.023242 | 0.99034 | -0.051485 | 0.99038 | -0.051795 | 10.5644
26 | -0.84957 | -0.38901 | 0.84973 | 0.38897 | 0.00015087 | -3.9201e-05 | 0.027236 | 0.027234 | 0.027236 | 0.99038 | -0.051795 | 0.99057 | -0.050377 | 12.9694
27 | 0.37637 | 0.17123 | -0.37637 | -0.17177 | 4.4787e-06 | -0.00053878 | 0.012055 | 0.012062 | 0.012062 | 0.99017 | -0.050069 | 0.99016 | -0.049979 | 5.4825
28 | -0.96485 | -0.44473 | 0.96486 | 0.44454 | 1.0694e-05 | -0.00019262 | 0.030961 | 0.030959 | 0.030961 | 0.99057 | -0.050377 | 0.99058 | -0.050463 | 14.0733
29 | -2.2669 | -1.0529 | 2.2674 | 1.0514 | 0.00049113 | -0.0014796 | 0.07284 | 0.07282 | 0.07284 | 0.99058 | -0.050463 | 0.99078 | -0.052174 | 33.1089
30 | 0.37637 | 0.17177 | -0.37629 | -0.18171 | 8.3567e-05 | -0.009944 | 0.012062 | 0.012185 | 0.012185 | 0.99016 | -0.049979 | 0.98995 | -0.048175 | 5.5387
31 | 2.7543 | 1.2715 | -2.7538 | -1.2726 | 0.00054558 | -0.00106 | 0.088458 | 0.088473 | 0.088473 | 0.99002 | -0.041054 | 0.98983 | -0.039508 | 40.215
32 | -3.0687 | -1.4238 | 3.0701 | 1.4246 | 0.0013892 | 0.00077636 | 0.098641 | 0.09864 | 0.098641 | 0.99002 | -0.041054 | 0.99049 | -0.037589 | 46.972
33 | 2.7538 | 1.2726 | -2.7503 | -1.2793 | 0.0034565 | -0.0066951 | 0.088473 | 0.088568 | 0.088568 | 0.98983 | -0.039508 | 0.98867 | -0.029616 | 40.258
34 | -3.0701 | -1.4246 | 3.078 | 1.4126 | 0.0078789 | -0.011931 | 0.09864 | 0.098466 | 0.09864 | 0.99049 | -0.037589 | 0.99287 | -0.057548 | 44.8364
35 | 2.7503 | 1.2793 | -2.7503 | -1.2794 | 5.1146e-05 | -9.881e-05 | 0.088568 | 0.088569 | 0.088569 | 0.98867 | -0.029616 | 0.98865 | -0.029469 | 40.2587
36 | -3.1569 | -1.45 | 3.1615 | 1.4435 | 0.0045461 | -0.0065257 | 0.10101 | 0.10091 | 0.10101 | 0.99287 | -0.057548 | 0.99422 | -0.068542 | 45.9119
37 | 0.078969 | 0.037385 | -0.078969 | -0.038246 | 3.1661e-07 | -0.00086128 | 0.0025403 | 0.0025511 | 0.0025511 | 0.99287 | -0.057548 | 0.99287 | -0.057514 | 1.1596
38 | -3.1615 | -1.4435 | 3.1618 | 1.4431 | 0.00027748 | -0.00039949 | 0.10091 | 0.10091 | 0.10091 | 0.99422 | -0.068542 | 0.9943 | -0.069208 | 45.8686
39 | -3.4018 | -1.5594 | 3.4022 | 1.5589 | 0.00037808 | -0.00045426 | 0.10865 | 0.10864 | 0.10865 | 0.9943 | -0.069208 | 0.9944 | -0.070059 | 49.3854
40 | 2.516 | 1.1659 | -2.5157 | -1.1658 | 0.00026674 | 0.00014044 | 0.080969 | 0.08097 | 0.08097 | 0.98865 | -0.029469 | 0.98854 | -0.030284 | 38.557
41 | -3.4022 | -1.5589 | 3.4058 | 1.5546 | 0.0036102 | -0.0043471 | 0.10864 | 0.10858 | 0.10864 | 0.9944 | -0.070059 | 0.99539 | -0.078134 | 49.3823
42 | 2.5157 | 1.1658 | -2.5135 | -1.171 | 0.002203 | -0.0052093 | 0.08097 | 0.081042 | 0.081042 | 0.98854 | -0.030284 | 0.98773 | -0.023348 | 36.8372
43 | 0.44431 | 0.21009 | -0.44425 | -0.21507 | 5.9314e-05 | -0.004976 | 0.014364 | 0.014427 | 0.014427 | 0.98773 | -0.023348 | 0.98761 | -0.022216 | 6.5577
44 | 2.0692 | 0.9609 | -2.069 | -0.96169 | 0.00021615 | -0.00078396 | 0.066678 | 0.066689 | 0.066689 | 0.98773 | -0.023348 | 0.98763 | -0.022521 | 30.313
45 | -0.39261 | -0.19015 | 0.39262 | 0.19009 | 1.5967e-05 | -5.6513e-05 | 0.012638 | 0.012637 | 0.012638 | 0.99643 | -0.06175 | 0.99647 | -0.061482 | 6.0181
46 | -0.39262 | -0.19009 | 0.3927 | 0.18112 | 8.0119e-05 | -0.0089673 | 0.012637 | 0.012526 | 0.012637 | 0.99647 | -0.061482 | 0.99666 | -0.063164 | 5.7441
47 | -6.5482 | -3.0042 | 6.5511 | 2.9793 | 0.0028867 | -0.024901 | 0.20867 | 0.20834 | 0.20867 | 0.99666 | -0.063164 | 0.99718 | -0.053528 | 24.7828
48 | 6.1555 | 2.8231 | -6.1554 | -2.8243 | 0.00012595 | -0.0012419 | 0.19615 | 0.19616 | 0.19616 | 0.99666 | -0.063164 | 0.99664 | -0.063609 | 23.2972
49 | -6.9916 | -3.1874 | 6.9918 | 3.1854 | 0.00027349 | -0.002044 | 0.22244 | 0.22241 | 0.22244 | 0.99718 | -0.053528 | 0.99722 | -0.05267 | 26.4182
50 | 0.44047 | 0.20808 | -0.44038 | -0.20832 | 8.7267e-05 | -0.00023756 | 0.014102 | 0.014106 | 0.014106 | 0.99718 | -0.053528 | 0.99697 | -0.054953 | 6.7171
51 | 5.9469 | 2.7234 | -5.9468 | -2.7244 | 9.5492e-05 | -0.0010155 | 0.18945 | 0.18947 | 0.18947 | 0.99664 | -0.063609 | 0.99662 | -0.063959 | 22.5021
52 | -7.1831 | -3.278 | 7.1834 | 3.2757 | 0.00032793 | -0.0023057 | 0.22856 | 0.22853 | 0.22856 | 0.99722 | -0.05267 | 0.99728 | -0.05167 | 27.1453
53 | 0.28452 | 0.13741 | -0.28452 | -0.1378 | 1.8201e-06 | -0.00038581 | 0.0091488 | 0.0091537 | 0.0091537 | 0.99697 | -0.054953 | 0.99696 | -0.054898 | 4.1608
54 | 0.15586 | 0.070904 | -0.15585 | -0.075285 | 6.1255e-06 | -0.0043806 | 0.004958 | 0.0050118 | 0.0050118 | 0.99697 | -0.054953 | 0.99693 | -0.054635 | 2.2781
55 | 5.9468 | 2.7244 | -5.9402 | -2.7326 | 0.0066521 | -0.0082118 | 0.18947 | 0.18963 | 0.18963 | 0.99662 | -0.063959 | 0.99539 | -0.078134 | 52.3827
56 | -7.1834 | -3.2757 | 7.1862 | 3.2559 | 0.002809 | -0.019791 | 0.22853 | 0.22826 | 0.22853 | 0.99728 | -0.05167 | 0.99774 | -0.043065 | 27.1416
57 | 0.15585 | 0.075285 | -0.15585 | -0.075483 | 2.7937e-07 | -0.00019752 | 0.0050118 | 0.0050143 | 0.0050143 | 0.99693 | -0.054635 | 0.99693 | -0.05462 | 2.2792
58 | -0.24739 | -0.11982 | 0.24739 | 0.11908 | 2.632e-06 | -0.00074092 | 0.0079531 | 0.0079438 | 0.0079531 | 0.99773 | -0.042973 | 0.99774 | -0.043065 | 3.615
59 | -7.4336 | -3.375 | 7.4358 | 3.3606 | 0.0021997 | -0.014386 | 0.23621 | 0.23601 | 0.23621 | 0.99774 | -0.043065 | 0.99808 | -0.036524 | 28.053
60 | -7.8154 | -3.5304 | 7.8193 | 3.5077 | 0.0038777 | -0.022703 | 0.24804 | 0.24773 | 0.24804 | 0.99808 | -0.036524 | 0.99867 | -0.025467 | 29.4582
61 | 0.11736 | 0.043735 | -0.11735 | -0.055751 | 9.1697e-06 | -0.012016 | 0.0036224 | 0.0037579 | 0.0037579 | 0.99808 | -0.036524 | 0.99801 | -0.036041 | 1.7082
62 | 0.26222 | 0.12611 | -0.26221 | -0.127 | 3.523e-06 | -0.00088402 | 0.0084156 | 0.0084267 | 0.0084267 | 0.99808 | -0.036524 | 0.99807 | -0.036408 | 3.8303
63 | -8.053 | -3.6209 | 8.0594 | 3.5859 | 0.0063636 | -0.03495 | 0.25523 | 0.25475 | 0.25523 | 0.99867 | -0.025467 | 0.99959 | -0.0077139 | 30.3122
64 | 0.2337 | 0.11315 | -0.2337 | -0.11319 | 3.4723e-06 | -3.9012e-05 | 0.0075055 | 0.007506 | 0.007506 | 0.99867 | -0.025467 | 0.99865 | -0.025565 | 3.5743
65 | 0.11735 | 0.055751 | -0.11735 | -0.056835 | 8.6255e-07 | -0.0010838 | 0.0037579 | 0.0037715 | 0.0037715 | 0.99801 | -0.036041 | 0.998 | -0.035978 | 1.7143
66 | -8.0594 | -3.5859 | 8.0595 | 3.5851 | 0.00015465 | -0.00085224 | 0.25475 | 0.25474 | 0.25475 | 0.99959 | -0.0077139 | 0.99962 | -0.0072796 | 30.255
67 | -8.2247 | -3.6651 | 8.2252 | 3.6627 | 0.00045839 | -0.0024079 | 0.26003 | 0.26 | 0.26003 | 0.99962 | -0.0072796 | 0.99968 | -0.0060204 | 30.883
68 | -8.2252 | -3.6627 | 8.2257 | 3.66 | 0.00051605 | -0.0027121 | 0.26 | 0.25996 | 0.26 | 0.99968 | -0.0060204 | 0.99975 | -0.0046016 | 30.879
69 | -0.20379 | -0.098698 | 0.20379 | 0.098124 | 1.4056e-06 | -0.00057409 | 0.0065774 | 0.0065702 | 0.0065774 | 0.99377 | -0.074421 | 0.99378 | -0.074481 | 2.9897
70 | -0.20379 | -0.098124 | 0.20381 | 0.090469 | 1.845e-05 | -0.0076546 | 0.0065702 | 0.0064767 | 0.0065702 | 0.99378 | -0.074481 | 0.99386 | -0.075191 | 2.9864
71 | -0.57557 | -0.27043 | 0.57563 | 0.26732 | 6.0201e-05 | -0.0031061 | 0.018471 | 0.018433 | 0.018471 | 0.99386 | -0.075191 | 0.99396 | -0.076029 | 8.3959
72 | 0.37176 | 0.17996 | -0.37176 | -0.18005 | 7.4557e-07 | -9.1284e-05 | 0.011997 | 0.011998 | 0.011998 | 0.99386 | -0.075191 | 0.99386 | -0.075173 | 5.4536
73 | 1.0026 | 0.46846 | -1.002 | -0.46847 | 0.00061556 | -9.9019e-06 | 0.032113 | 0.032118 | 0.032118 | 0.99479 | -0.07295 | 0.99414 | -0.077541 | 15.2943
74 | 0.55328 | 0.25633 | -0.55306 | -0.25666 | 0.00022225 | -0.00033109 | 0.017695 | 0.017701 | 0.017701 | 0.99479 | -0.07295 | 0.99436 | -0.076033 | 8.4289
75 | -1.744 | -0.8159 | 1.744 | 0.81582 | 1.5816e-05 | -8.4977e-05 | 0.055873 | 0.055872 | 0.055873 | 0.99479 | -0.07295 | 0.9948 | -0.073023 | 25.397
76 | 0.65261 | 0.29927 | -0.65259 | -0.30015 | 2.1906e-05 | -0.00088389 | 0.020848 | 0.020859 | 0.020859 | 0.99414 | -0.077541 | 0.99411 | -0.077283 | 9.4812
77 | 0.20337 | 0.087298 | -0.20337 | -0.087351 | 1.2262e-07 | -5.2491e-05 | 0.0064251 | 0.0064257 | 0.0064257 | 0.99436 | -0.076033 | 0.99436 | -0.076029 | 2.9208
78 | -1.744 | -0.81582 | 1.7451 | 0.8098 | 0.0011189 | -0.0060245 | 0.055872 | 0.055794 | 0.055872 | 0.9948 | -0.073023 | 0.99539 | -0.078134 | 25.3965
79 | -0.65248 | -0.30434 | 0.65259 | 0.30015 | 0.00010411 | -0.0041875 | 0.02091 | 0.020859 | 0.02091 | 0.99396 | -0.076029 | 0.99411 | -0.077283 | 9.5046
80 | 0.07686 | 0.037015 | -0.076859 | -0.037225 | 7.2981e-08 | -0.00020989 | 0.0024776 | 0.0024803 | 0.0024803 | 0.99396 | -0.076029 | 0.99396 | -0.076021 | 1.1274
81 | 0.17946 | 0.086865 | -0.17945 | -0.086913 | 2.5163e-06 | -4.8292e-05 | 0.0057848 | 0.0057854 | 0.0057854 | 0.99493 | -0.075808 | 0.99492 | -0.0759 | 2.755
82 | -0.17946 | -0.086865 | 0.17948 | 0.086487 | 1.9658e-05 | -0.0003777 | 0.0057848 | 0.0057798 | 0.0057848 | 0.99493 | -0.075808 | 0.99505 | -0.075078 | 2.7547
83 | -0.31192 | -0.15063 | 0.31192 | 0.15037 | 1.4896e-06 | -0.00026085 | 0.010049 | 0.010046 | 0.010049 | 0.99505 | -0.075078 | 0.99505 | -0.075119 | 4.5678
84 | -0.20335 | -0.098401 | 0.20337 | 0.087351 | 2.6349e-05 | -0.01105 | 0.0065591 | 0.0064257 | 0.0065591 | 0.99424 | -0.075046 | 0.99436 | -0.076029 | 2.9814
85 | 0.20335 | 0.098401 | -0.20335 | -0.098485 | 2.0572e-07 | -8.4457e-05 | 0.0065591 | 0.0065601 | 0.0065601 | 0.99424 | -0.075046 | 0.99424 | -0.075037 | 2.9819
86 | -0.31192 | -0.15037 | 0.31195 | 0.14451 | 3.3215e-05 | -0.0058619 | 0.010046 | 0.009973 | 0.010046 | 0.99505 | -0.075119 | 0.99515 | -0.075997 | 4.5663
87 | 0.31195 | 0.14432 | -0.31195 | -0.14451 | 1.0482e-06 | -0.00018639 | 0.0099707 | 0.009973 | 0.009973 | 0.99515 | -0.076023 | 0.99515 | -0.075997 | 4.5332
88 | -0.70347 | -0.33394 | 0.7035 | 0.33298 | 2.7913e-05 | -0.00096116 | 0.022589 | 0.022577 | 0.022589 | 0.99515 | -0.076023 | 0.99519 | -0.076353 | 10.2677
89 | -0.7035 | -0.33298 | 0.70365 | 0.32764 | 0.00015447 | -0.0053391 | 0.022577 | 0.02251 | 0.022577 | 0.99519 | -0.076353 | 0.99539 | -0.078134 | 10.2622
90 | 0.085544 | 0.040594 | -0.085544 | -0.041431 | 3.5739e-07 | -0.00083656 | 0.002746 | 0.0027565 | 0.0027565 | 0.99539 | -0.078134 | 0.99539 | -0.078099 | 1.253
91 | -0.37628 | -0.18224 | 0.37629 | 0.18171 | 4.4853e-06 | -0.00052785 | 0.012192 | 0.012185 | 0.012192 | 0.98994 | -0.048072 | 0.98995 | -0.048175 | 5.5417
92 | 0.13239 | 0.063946 | -0.13238 | -0.064117 | 4.8624e-06 | -0.00017077 | 0.004286 | 0.0042882 | 0.0042882 | 0.99025 | -0.052751 | 0.99022 | -0.052995 | 2.042
93 | 0.071659 | 0.031335 | -0.071658 | -0.034706 | 1.0203e-06 | -0.0033703 | 0.0022819 | 0.0023231 | 0.0023231 | 0.98941 | -0.049846 | 0.98939 | -0.049736 | 1.0559
94 | 0.58317 | 0.27465 | -0.58307 | -0.27959 | 0.00010082 | -0.0049431 | 0.018807 | 0.01887 | 0.01887 | 0.98941 | -0.049846 | 0.98925 | -0.048403 | 8.5771
95 | 0.25043 | 0.1205 | -0.25043 | -0.12129 | 2.9561e-06 | -0.00078479 | 0.0081099 | 0.0081199 | 0.0081199 | 0.98925 | -0.048403 | 0.98924 | -0.048301 | 3.6908
96 | 0.33264 | 0.15909 | -0.33263 | -0.16041 | 8.7592e-06 | -0.0013195 | 0.01076 | 0.010777 | 0.010777 | 0.98925 | -0.048403 | 0.98922 | -0.048178 | 4.8984
97 | -0.3271 | -0.15842 | 0.32711 | 0.15837 | 9.2675e-06 | -4.786e-05 | 0.010624 | 0.010623 | 0.010624 | 0.98758 | -0.022403 | 0.98761 | -0.022216 | 5.0589
98 | 0.11714 | 0.056694 | -0.11714 | -0.056733 | 8.9207e-07 | -3.9726e-05 | 0.0038039 | 0.0038044 | 0.0038044 | 0.98761 | -0.022216 | 0.9876 | -0.022266 | 1.8116
99 | -0.44687 | -0.21643 | 0.44688 | 0.21589 | 6.5508e-06 | -0.00054054 | 0.014515 | 0.014508 | 0.014515 | 0.98747 | -0.021144 | 0.98749 | -0.021271 | 6.5979
100 | -0.44688 | -0.21589 | 0.44691 | 0.21353 | 2.8578e-05 | -0.0023643 | 0.014508 | 0.014478 | 0.014508 | 0.98749 | -0.021271 | 0.98755 | -0.021819 | 6.5947
101 | 0.95299 | 0.42524 | -0.95288 | -0.42723 | 0.00010829 | -0.0019958 | 0.030505 | 0.030529 | 0.030529 | 0.98755 | -0.021819 | 0.98744 | -0.021001 | 13.8768
102 | -1.3999 | -0.63876 | 1.4 | 0.63768 | 0.00013019 | -0.0010842 | 0.04498 | 0.044966 | 0.04498 | 0.98755 | -0.021819 | 0.98763 | -0.022521 | 20.4454
103 | -1.1517 | -0.5578 | 1.1518 | 0.55714 | 5.1147e-05 | -0.00065456 | 0.036952 | 0.036943 | 0.036952 | 0.99971 | -0.0042153 | 0.99975 | -0.0046016 | 16.7962
104 | 1.2569 | 0.60704 | -1.2569 | -0.6074 | 3.3774e-05 | -0.00036158 | 0.040305 | 0.040309 | 0.040309 | 0.99975 | -0.0046016 | 0.99973 | -0.0043689 | 18.3225
105 | -10.6344 | -4.8242 | 10.6352 | 4.822 | 0.00078969 | -0.0021741 | 0.33718 | 0.33715 | 0.33718 | 0.99975 | -0.0046016 | 0.99984 | -0.0029625 | 40.0454
106 | 0.5042 | 0.24376 | -0.50419 | -0.24419 | 6.3329e-06 | -0.00043085 | 0.016171 | 0.016177 | 0.016177 | 0.99973 | -0.0043689 | 0.99972 | -0.0042597 | 7.353
107 | 0.75271 | 0.36364 | -0.75268 | -0.36451 | 2.8607e-05 | -0.00086871 | 0.024138 | 0.024149 | 0.024149 | 0.99973 | -0.0043689 | 0.99969 | -0.0040387 | 10.977
108 | -10.6352 | -4.822 | 10.6363 | 4.819 | 0.0010764 | -0.0029652 | 0.33715 | 0.3371 | 0.33715 | 0.99984 | -0.0029625 | 0.99996 | -0.00072664 | 40.0413
109 | 0.75268 | 0.36451 | -0.75268 | -0.36454 | 9.7865e-07 | -2.9704e-05 | 0.024149 | 0.02415 | 0.02415 | 0.99969 | -0.0040387 | 0.99969 | -0.0040274 | 10.9771
110 | -12.7133 | -5.825 | 12.7137 | 5.8243 | 0.00042418 | -0.00069723 | 0.4037 | 0.40369 | 0.4037 | 0.99996 | -0.00072664 | 1 | 0 | 47.9459
111 | 5.603 | 2.6529 | -5.6026 | -2.6578 | 0.00040315 | -0.0048831 | 0.17896 | 0.17902 | 0.17902 | 1 | 0 | 0.99992 | -0.0014951 | 21.2619
112 | 0.14225 | 0.068714 | -0.14225 | -0.068897 | 2.2206e-07 | -0.0001827 | 0.0046102 | 0.0046126 | 0.0046126 | 0.98921 | -0.04809 | 0.98921 | -0.048076 | 2.0966
113 | -0.33263 | -0.16092 | 0.33263 | 0.16041 | 3.3913e-06 | -0.00050976 | 0.010783 | 0.010777 | 0.010783 | 0.98921 | -0.04809 | 0.98922 | -0.048178 | 4.9014

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 18.8878 | 8.7575

## res_load
| p_mw | q_mvar
0 | 0.22346 | 0.10822
1 | 0.15171 | 0.073475
2 | 0.22807 | 0.11046
3 | 0.089846 | 0.043515
4 | 0.27234 | 0.1319
5 | 0.36082 | 0.17476
6 | 0.29296 | 0.14188
7 | 0.087691 | 0.042471
8 | 0.19997 | 0.096851
9 | 0.21537 | 0.10431
10 | 0.12372 | 0.059922
11 | 0.13393 | 0.064866
12 | 0.11513 | 0.055759
13 | 0.31436 | 0.15225
14 | 0.078969 | 0.038246
15 | 0.24008 | 0.11628
16 | 0.23428 | 0.11346
17 | 0.39261 | 0.19015
18 | 0.20847 | 0.10097
19 | 0.19127 | 0.092637
20 | 0.15585 | 0.075483
21 | 0.28452 | 0.1378
22 | 0.24739 | 0.11982
23 | 0.26221 | 0.127
24 | 0.11735 | 0.056835
25 | 0.2337 | 0.11319
26 | 0.16524 | 0.080028
27 | 0.20379 | 0.098698
28 | 0.18813 | 0.091115
29 | 0.34936 | 0.16921
30 | 0.34969 | 0.16936
31 | 0.37176 | 0.18005
32 | 0.076859 | 0.037225
33 | 0.17945 | 0.086913
34 | 0.13244 | 0.064144
35 | 0.20335 | 0.098485
36 | 0.39151 | 0.18962
37 | 0.085544 | 0.041431
38 | 0.37628 | 0.18224
39 | 0.13843 | 0.067043
40 | 0.13238 | 0.064117
41 | 0.1358 | 0.065769
42 | 0.071658 | 0.034706
43 | 0.3271 | 0.15842
44 | 0.11714 | 0.056733
45 | 0.44687 | 0.21643
46 | 0.66899 | 0.32401
47 | 1.1517 | 0.5578
48 | 0.50419 | 0.24419
49 | 2.077 | 1.0059
50 | 0.75268 | 0.36454
51 | 0.55711 | 0.26982
52 | 0.32442 | 0.15712
53 | 2.2682 | 1.0985
54 | 0.19037 | 0.092201
55 | 0.14225 | 0.068897
56 | 0.25043 | 0.12129

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1