## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_439_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_439_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_439_0_node_192 | 20 | n |  | TRUE
3 | bus_MV_439_0_node_264 | 20 | n |  | TRUE
4 | bus_MV_439_0_node_189 | 20 | n |  | TRUE
5 | bus_MV_439_0_node_20 | 20 | n |  | TRUE
6 | bus_MV_439_0_node_12 | 20 | n |  | TRUE
7 | bus_MV_439_0_node_19 | 20 | n |  | TRUE
8 | bus_MV_439_0_node_2 | 20 | n |  | TRUE
9 | bus_MV_439_0_node_269 | 20 | n |  | TRUE
10 | bus_MV_439_0_node_29 | 20 | n |  | TRUE
11 | bus_MV_439_0_node_3 | 20 | n |  | TRUE
12 | bus_MV_439_0_node_5 | 20 | n |  | TRUE
13 | bus_MV_439_0_node_4 | 20 | n |  | TRUE
14 | bus_MV_439_0_node_6 | 20 | n |  | TRUE
15 | bus_MV_439_0_node_7 | 20 | n |  | TRUE
16 | bus_MV_439_0_node_8 | 20 | n |  | TRUE
17 | bus_MV_439_0_node_11 | 20 | n |  | TRUE
18 | bus_MV_439_0_node_10 | 20 | n |  | TRUE
19 | bus_MV_439_0_node_9 | 20 | n |  | TRUE
20 | bus_MV_439_0_node_18 | 20 | n |  | TRUE
21 | bus_MV_439_0_node_214 | 20 | n |  | TRUE
22 | bus_MV_439_0_node_254 | 20 | n |  | TRUE
23 | bus_MV_439_0_node_17 | 20 | n |  | TRUE
24 | bus_MV_439_0_node_22 | 20 | n |  | TRUE
25 | bus_MV_439_0_node_21 | 20 | n |  | TRUE
26 | bus_MV_439_0_node_215 | 20 | n |  | TRUE
27 | bus_MV_439_0_node_213 | 20 | n |  | TRUE
28 | bus_MV_439_0_node_263 | 20 | n |  | TRUE
29 | bus_MV_439_0_node_27 | 20 | n |  | TRUE
30 | bus_MV_439_0_node_28 | 20 | n |  | TRUE
31 | bus_MV_439_0_node_30 | 20 | n |  | TRUE
32 | bus_MV_439_0_node_32 | 20 | n |  | TRUE
33 | bus_MV_439_0_node_271 | 20 | n |  | TRUE
34 | bus_MV_439_0_node_13 | 20 | n |  | TRUE
35 | bus_MV_439_0_node_14 | 20 | n |  | TRUE
36 | bus_MV_439_0_node_15 | 20 | n |  | TRUE
37 | bus_MV_439_0_node_16 | 20 | n |  | TRUE
38 | bus_MV_439_0_node_185 | 20 | n |  | TRUE
39 | bus_MV_439_0_node_183 | 20 | n |  | TRUE
40 | bus_MV_439_0_node_212 | 20 | n |  | TRUE
41 | bus_MV_439_0_node_174 | 20 | n |  | TRUE
42 | bus_MV_439_0_node_175 | 20 | n |  | TRUE
43 | bus_MV_439_0_node_173 | 20 | n |  | TRUE
44 | bus_MV_439_0_node_176 | 20 | n |  | TRUE
45 | bus_MV_439_0_node_177 | 20 | n |  | TRUE
46 | bus_MV_439_0_node_178 | 20 | n |  | TRUE
47 | bus_MV_439_0_node_179 | 20 | n |  | TRUE
48 | bus_MV_439_0_node_201 | 20 | n |  | TRUE
49 | bus_MV_439_0_node_203 | 20 | n |  | TRUE
50 | bus_MV_439_0_node_205 | 20 | n |  | TRUE
51 | bus_MV_439_0_node_187 | 20 | n |  | TRUE
52 | bus_MV_439_0_node_188 | 20 | n |  | TRUE
53 | bus_MV_439_0_node_190 | 20 | n |  | TRUE
54 | bus_MV_439_0_node_191 | 20 | n |  | TRUE
55 | bus_MV_439_0_node_245 | 20 | n |  | TRUE
56 | bus_MV_439_0_node_23 | 20 | n |  | TRUE
57 | bus_MV_439_0_node_24 | 20 | n |  | TRUE
58 | bus_MV_439_0_node_25 | 20 | n |  | TRUE
59 | bus_MV_439_0_node_26 | 20 | n |  | TRUE
60 | bus_MV_439_0_node_217 | 20 | n |  | TRUE
61 | bus_MV_439_0_node_216 | 20 | n |  | TRUE
62 | bus_MV_439_0_node_218 | 20 | n |  | TRUE
63 | bus_MV_439_0_node_31 | 20 | n |  | TRUE
64 | bus_MV_439_0_node_33 | 20 | n |  | TRUE
65 | bus_MV_439_0_node_34 | 20 | n |  | TRUE
66 | bus_MV_439_0_node_35 | 20 | n |  | TRUE
67 | bus_MV_439_0_node_219 | 20 | n |  | TRUE
68 | bus_MV_439_0_node_277 | 20 | n |  | TRUE
69 | bus_MV_439_0_node_220 | 20 | n |  | TRUE
70 | bus_MV_439_0_node_36 | 20 | n |  | TRUE
71 | bus_MV_439_0_node_37 | 20 | n |  | TRUE
72 | bus_MV_439_0_node_38 | 20 | n |  | TRUE
73 | bus_MV_439_0_node_169 | 20 | n |  | TRUE
74 | bus_MV_439_0_node_170 | 20 | n |  | TRUE
75 | bus_MV_439_0_node_258 | 20 | n |  | TRUE
76 | bus_MV_439_0_node_39 | 20 | n |  | TRUE
77 | bus_MV_439_0_node_40 | 20 | n |  | TRUE
78 | bus_MV_439_0_node_42 | 20 | n |  | TRUE
79 | bus_MV_439_0_node_180 | 20 | n |  | TRUE
80 | bus_MV_439_0_node_181 | 20 | n |  | TRUE
81 | bus_MV_439_0_node_44 | 20 | n |  | TRUE
82 | bus_MV_439_0_node_41 | 20 | n |  | TRUE
83 | bus_MV_439_0_node_272 | 20 | n |  | TRUE
84 | bus_MV_439_0_node_43 | 20 | n |  | TRUE
85 | bus_MV_439_0_node_46 | 20 | n |  | TRUE
86 | bus_MV_439_0_node_45 | 20 | n |  | TRUE
87 | bus_MV_439_0_node_186 | 20 | n |  | TRUE
88 | bus_MV_439_0_node_172 | 20 | n |  | TRUE
89 | bus_MV_439_0_node_160 | 20 | n |  | TRUE
90 | bus_MV_439_0_node_184 | 20 | n |  | TRUE
91 | bus_MV_439_0_node_76 | 20 | n |  | TRUE
92 | bus_MV_439_0_node_77 | 20 | n |  | TRUE
93 | bus_MV_439_0_node_182 | 20 | n |  | TRUE
94 | bus_MV_439_0_node_128 | 20 | n |  | TRUE
95 | bus_MV_439_0_node_129 | 20 | n |  | TRUE
96 | bus_MV_439_0_node_130 | 20 | n |  | TRUE
97 | bus_MV_439_0_node_240 | 20 | n |  | TRUE
98 | bus_MV_439_0_node_242 | 20 | n |  | TRUE
99 | bus_MV_439_0_node_239 | 20 | n |  | TRUE
100 | bus_MV_439_0_node_247 | 20 | n |  | TRUE
101 | bus_MV_439_0_node_246 | 20 | n |  | TRUE
102 | bus_MV_439_0_node_139 | 20 | n |  | TRUE
103 | bus_MV_439_0_node_156 | 20 | n |  | TRUE
104 | bus_MV_439_0_node_141 | 20 | n |  | TRUE
105 | bus_MV_439_0_node_131 | 20 | n |  | TRUE
106 | bus_MV_439_0_node_132 | 20 | n |  | TRUE
107 | bus_MV_439_0_node_133 | 20 | n |  | TRUE
108 | bus_MV_439_0_node_142 | 20 | n |  | TRUE
109 | bus_MV_439_0_node_138 | 20 | n |  | TRUE
110 | bus_MV_439_0_node_136 | 20 | n |  | TRUE
111 | bus_MV_439_0_node_200 | 20 | n |  | TRUE
112 | bus_MV_439_0_node_268 | 20 | n |  | TRUE
113 | bus_MV_439_0_node_198 | 20 | n |  | TRUE
114 | bus_MV_439_0_node_134 | 20 | n |  | TRUE
115 | bus_MV_439_0_node_135 | 20 | n |  | TRUE
116 | bus_MV_439_0_node_137 | 20 | n |  | TRUE
117 | bus_MV_439_0_node_229 | 20 | n |  | TRUE
118 | bus_MV_439_0_node_140 | 20 | n |  | TRUE
119 | bus_MV_439_0_node_143 | 20 | n |  | TRUE
120 | bus_MV_439_0_node_145 | 20 | n |  | TRUE
121 | bus_MV_439_0_node_144 | 20 | n |  | TRUE
122 | bus_MV_439_0_node_147 | 20 | n |  | TRUE
123 | bus_MV_439_0_node_146 | 20 | n |  | TRUE
124 | bus_MV_439_0_node_157 | 20 | n |  | TRUE
125 | bus_MV_439_0_node_257 | 20 | n |  | TRUE
126 | bus_MV_439_0_node_158 | 20 | n |  | TRUE
127 | bus_MV_439_0_node_159 | 20 | n |  | TRUE
128 | bus_MV_439_0_node_148 | 20 | n |  | TRUE
129 | bus_MV_439_0_node_149 | 20 | n |  | TRUE
130 | bus_MV_439_0_node_150 | 20 | n |  | TRUE
131 | bus_MV_439_0_node_152 | 20 | n |  | TRUE
132 | bus_MV_439_0_node_153 | 20 | n |  | TRUE
133 | bus_MV_439_0_node_154 | 20 | n |  | TRUE
134 | bus_MV_439_0_node_151 | 20 | n |  | TRUE
135 | bus_MV_439_0_node_230 | 20 | n |  | TRUE
136 | bus_MV_439_0_node_155 | 20 | n |  | TRUE
137 | bus_MV_439_0_node_234 | 20 | n |  | TRUE
138 | bus_MV_439_0_node_171 | 20 | n |  | TRUE
139 | bus_MV_439_0_node_231 | 20 | n |  | TRUE
140 | bus_MV_439_0_node_164 | 20 | n |  | TRUE
141 | bus_MV_439_0_node_161 | 20 | n |  | TRUE
142 | bus_MV_439_0_node_162 | 20 | n |  | TRUE
143 | bus_MV_439_0_node_163 | 20 | n |  | TRUE
144 | bus_MV_439_0_node_249 | 20 | n |  | TRUE
145 | bus_MV_439_0_node_167 | 20 | n |  | TRUE
146 | bus_MV_439_0_node_250 | 20 | n |  | TRUE
147 | bus_MV_439_0_node_165 | 20 | n |  | TRUE
148 | bus_MV_439_0_node_210 | 20 | n |  | TRUE
149 | bus_MV_439_0_node_208 | 20 | n |  | TRUE
150 | bus_MV_439_0_node_193 | 20 | n |  | TRUE
151 | bus_MV_439_0_node_194 | 20 | n |  | TRUE
152 | bus_MV_439_0_node_207 | 20 | n |  | TRUE
153 | bus_MV_439_0_node_195 | 20 | n |  | TRUE
154 | bus_MV_439_0_node_206 | 20 | n |  | TRUE
155 | bus_MV_439_0_node_197 | 20 | n |  | TRUE
156 | bus_MV_439_0_node_244 | 20 | n |  | TRUE
157 | bus_MV_439_0_node_196 | 20 | n |  | TRUE
158 | bus_MV_439_0_node_211 | 20 | n |  | TRUE
159 | bus_MV_439_0_node_248 | 20 | n |  | TRUE
160 | bus_MV_439_0_node_209 | 20 | n |  | TRUE
161 | bus_MV_439_0_node_232 | 20 | n |  | TRUE
162 | bus_MV_439_0_node_233 | 20 | n |  | TRUE
163 | bus_MV_439_0_node_238 | 20 | n |  | TRUE
164 | bus_MV_439_0_node_237 | 20 | n |  | TRUE
165 | bus_MV_439_0_node_235 | 20 | n |  | TRUE
166 | bus_MV_439_0_node_236 | 20 | n |  | TRUE
167 | bus_MV_439_0_node_241 | 20 | n |  | TRUE
168 | bus_MV_439_0_node_243 | 20 | n |  | TRUE
169 | bus_HV_439_0_node_173 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_439_0_load_0 | 0 | 0.13915 | 0.067395 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_439_0_load_264 | 3 | 0.90313 | 0.4374 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_439_0_load_19 | 7 | 0.20583 | 0.099689 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_439_0_load_2 | 8 | 0.34628 | 0.16771 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_439_0_load_269 | 9 | 0.45913 | 0.22237 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_439_0_load_3 | 11 | 0.37001 | 0.17921 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_439_0_load_5 | 12 | 0.071857 | 0.034802 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_439_0_load_18 | 20 | 0.12161 | 0.058899 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_439_0_load_214 | 21 | 0.33707 | 0.16325 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_439_0_load_254 | 22 | 0.32462 | 0.15722 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_439_0_load_17 | 23 | 0.17965 | 0.087009 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_439_0_load_22 | 24 | 0.2215 | 0.10728 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_439_0_load_21 | 25 | 0.1903 | 0.092164 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_439_0_load_215 | 26 | 0.068684 | 0.033265 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_439_0_load_263 | 28 | 0.16206 | 0.078489 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_439_0_load_27 | 29 | 0.32311 | 0.15649 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_439_0_load_271 | 33 | 0.12288 | 0.059513 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_439_0_load_13 | 34 | 0.20606 | 0.099801 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_439_0_load_185 | 38 | 0.11539 | 0.055887 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_439_0_load_183 | 39 | 0.15548 | 0.075303 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_439_0_load_212 | 40 | 0.08082 | 0.039143 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_439_0_load_174 | 41 | 0.12842 | 0.062195 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_439_0_load_173 | 43 | 0.16378 | 0.07932 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_439_0_load_179 | 47 | 0.1337 | 0.064755 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_439_0_load_201 | 48 | 0.14516 | 0.070305 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_439_0_load_187 | 51 | 0.1647 | 0.079767 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_439_0_load_245 | 55 | 0.072358 | 0.035045 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_439_0_load_23 | 56 | 0.28503 | 0.13805 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_439_0_load_24 | 57 | 0.17279 | 0.083686 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_439_0_load_25 | 58 | 0.091892 | 0.044505 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_439_0_load_217 | 60 | 0.15397 | 0.074571 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_439_0_load_216 | 61 | 0.093369 | 0.045221 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_439_0_load_31 | 63 | 0.26693 | 0.12928 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_439_0_load_219 | 67 | 0.092643 | 0.044869 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_439_0_load_277 | 68 | 0.14201 | 0.06878 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_439_0_load_36 | 70 | 0.15683 | 0.075954 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_439_0_load_169 | 73 | 0.12157 | 0.058879 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_439_0_load_258 | 75 | 0.086108 | 0.041704 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_439_0_load_39 | 76 | 0.066577 | 0.032245 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_439_0_load_180 | 79 | 0.090347 | 0.043757 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_439_0_load_44 | 81 | 0.078711 | 0.038122 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_439_0_load_272 | 83 | 0.11726 | 0.056792 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_439_0_load_45 | 86 | 0.053379 | 0.025853 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_439_0_load_186 | 87 | 0.052841 | 0.025592 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_439_0_load_172 | 88 | 0.13346 | 0.064636 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_439_0_load_184 | 90 | 0.10614 | 0.051404 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_439_0_load_76 | 91 | 0.0959 | 0.046447 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_439_0_load_128 | 94 | 0.11218 | 0.054333 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_439_0_load_242 | 98 | 0.12938 | 0.062663 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_439_0_load_239 | 99 | 0.78515 | 0.38027 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_439_0_load_247 | 100 | 0.15509 | 0.075113 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_439_0_load_246 | 101 | 0.11502 | 0.055707 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_439_0_load_139 | 102 | 0.15759 | 0.076326 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_439_0_load_131 | 105 | 0.11013 | 0.053337 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_439_0_load_142 | 108 | 0.057711 | 0.027951 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_439_0_load_138 | 109 | 0.10169 | 0.049251 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_439_0_load_268 | 112 | 0.14208 | 0.068813 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_439_0_load_134 | 114 | 0.060138 | 0.029126 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_439_0_load_229 | 117 | 0.12101 | 0.058609 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_439_0_load_143 | 119 | 0.08456 | 0.040954 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_439_0_load_157 | 124 | 0.10589 | 0.051287 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_439_0_load_257 | 125 | 0.12877 | 0.062365 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_439_0_load_148 | 128 | 0.079892 | 0.038693 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_439_0_load_151 | 134 | 0.10698 | 0.051811 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_439_0_load_230 | 135 | 0.11345 | 0.054944 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_439_0_load_234 | 137 | 0.094326 | 0.045684 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_439_0_load_171 | 138 | 0.16478 | 0.079804 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_439_0_load_231 | 139 | 0.27291 | 0.13218 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_439_0_load_161 | 141 | 0.1131 | 0.054779 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_439_0_load_249 | 144 | 0.12637 | 0.061204 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_439_0_load_250 | 146 | 0.094446 | 0.045742 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_439_0_load_165 | 147 | 0.10241 | 0.0496 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_439_0_load_210 | 148 | 0.12888 | 0.062421 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_439_0_load_208 | 149 | 0.1317 | 0.063787 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_439_0_load_193 | 150 | 0.12333 | 0.059732 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_439_0_load_194 | 151 | 0.10831 | 0.052459 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_439_0_load_206 | 154 | 0.15558 | 0.07535 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_439_0_load_197 | 155 | 0.072836 | 0.035276 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_439_0_load_196 | 157 | 0.095486 | 0.046246 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_439_0_load_248 | 159 | 0.14343 | 0.069467 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_439_0_load_232 | 161 | 0.10564 | 0.051162 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_439_0_load_233 | 162 | 0.18859 | 0.09134 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_439_0_load_238 | 163 | 0.13628 | 0.066002 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_439_0_load_236 | 166 | 0.1047 | 0.050708 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_439_0_load_241 | 167 | 0.10338 | 0.050069 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_439_0_load_243 | 168 | 0.14741 | 0.071394 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_439_0_line_0 |  | 0 | 1 | 0.004497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_439_0_line_1 |  | 1 | 2 | 1.0941 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_439_0_line_2 |  | 2 | 3 | 0.053626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_439_0_line_3 |  | 2 | 4 | 0.1521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_439_0_line_4 |  | 4 | 54 | 0.12535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_439_0_line_5 |  | 4 | 51 | 0.022181 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_439_0_line_6 |  | 5 | 6 | 0.83884 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_439_0_line_7 |  | 5 | 7 | 0.062837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_439_0_line_8 |  | 6 | 26 | 0.029328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_439_0_line_9 |  | 6 | 10 | 1.8618 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
10 | MV_439_0_line_10 |  | 6 | 18 | 0.99459 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
11 | MV_439_0_line_11 |  | 8 | 9 | 1.9192 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_439_0_line_12 |  | 9 | 10 | 0.10285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_439_0_line_13 |  | 10 | 30 | 0.26425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_439_0_line_14 |  | 11 | 12 | 0.022539 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_439_0_line_15 |  | 11 | 13 | 0.061085 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_439_0_line_16 |  | 13 | 14 | 0.078848 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
17 | MV_439_0_line_17 |  | 13 | 15 | 0.15533 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
18 | MV_439_0_line_18 |  | 14 | 16 | 0.53162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_439_0_line_19 |  | 14 | 17 | 0.5764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_439_0_line_20 |  | 14 | 18 | 0.76283 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
21 | MV_439_0_line_21 |  | 14 | 19 | 0.7086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_439_0_line_22 |  | 14 | 20 | 0.046693 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_439_0_line_23 |  | 15 | 21 | 0.015734 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
24 | MV_439_0_line_24 |  | 16 | 22 | 0.035437 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_439_0_line_25 |  | 17 | 25 | 0.060475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_439_0_line_26 |  | 18 | 24 | 0.062602 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_439_0_line_27 |  | 19 | 23 | 0.021035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_439_0_line_28 |  | 21 | 27 | 0.026255 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
29 | MV_439_0_line_29 |  | 23 | 28 | 1.1236 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_439_0_line_30 |  | 27 | 37 | 0.019728 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
31 | MV_439_0_line_31 |  | 28 | 54 | 0.04585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_439_0_line_32 |  | 29 | 30 | 0.003616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_439_0_line_33 |  | 30 | 31 | 0.91629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_439_0_line_34 |  | 31 | 32 | 0.68776 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_439_0_line_35 |  | 31 | 33 | 0.062122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_439_0_line_36 |  | 32 | 63 | 0.005026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_439_0_line_37 |  | 34 | 35 | 0.010131 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
38 | MV_439_0_line_38 |  | 34 | 36 | 0.087428 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
39 | MV_439_0_line_39 |  | 35 | 37 | 0.63245 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
40 | MV_439_0_line_40 |  | 36 | 38 | 1.2455 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
41 | MV_439_0_line_41 |  | 36 | 39 | 1.4971 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_439_0_line_42 |  | 37 | 40 | 0.033122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_439_0_line_43 |  | 38 | 46 | 0.11277 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
44 | MV_439_0_line_44 |  | 39 | 90 | 0.12225 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_439_0_line_45 |  | 41 | 42 | 0.044328 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
46 | MV_439_0_line_46 |  | 41 | 43 | 0.25595 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
47 | MV_439_0_line_47 |  | 42 | 44 | 0.21942 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
48 | MV_439_0_line_48 |  | 42 | 45 | 0.22235 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
49 | MV_439_0_line_49 |  | 44 | 46 | 0.22449 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
50 | MV_439_0_line_50 |  | 44 | 47 | 0.049241 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_439_0_line_51 |  | 45 | 148 | 0.031584 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
52 | MV_439_0_line_52 |  | 48 | 49 | 0.052045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_439_0_line_53 |  | 49 | 50 | 0.17973 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_439_0_line_54 |  | 50 | 148 | 0.041501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_439_0_line_55 |  | 51 | 52 | 0.001612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_439_0_line_56 |  | 52 | 53 | 0.022905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_439_0_line_57 |  | 53 | 55 | 0.09891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_439_0_line_58 |  | 56 | 57 | 0.053522 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_439_0_line_59 |  | 57 | 58 | 0.0043099 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_439_0_line_60 |  | 58 | 59 | 0.024078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_439_0_line_61 |  | 59 | 60 | 0.0082529 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_439_0_line_62 |  | 59 | 61 | 0.02581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_439_0_line_63 |  | 60 | 62 | 0.017146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_439_0_line_64 |  | 62 | 69 | 0.0373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_439_0_line_65 |  | 63 | 64 | 0.011701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_439_0_line_66 |  | 64 | 65 | 0.34372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_439_0_line_67 |  | 65 | 66 | 0.36627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_439_0_line_68 |  | 65 | 67 | 0.060659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_439_0_line_69 |  | 66 | 68 | 0.02894 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_439_0_line_70 |  | 67 | 69 | 0.057126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_439_0_line_71 |  | 70 | 71 | 0.070405 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_439_0_line_72 |  | 71 | 72 | 0.58484 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_439_0_line_73 |  | 71 | 73 | 2.3708 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_439_0_line_74 |  | 72 | 75 | 0.02456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_439_0_line_75 |  | 73 | 74 | 0.034128 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_439_0_line_76 |  | 74 | 147 | 0.31173 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_439_0_line_77 |  | 76 | 77 | 0.028575 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_439_0_line_78 |  | 77 | 78 | 0.73891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_439_0_line_79 |  | 78 | 84 | 1.3296 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_439_0_line_80 |  | 78 | 81 | 0.12929 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_439_0_line_81 |  | 78 | 82 | 1.1086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_439_0_line_82 |  | 79 | 80 | 0.031991 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_439_0_line_83 |  | 79 | 81 | 0.9663 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_439_0_line_84 |  | 80 | 93 | 1.2729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_439_0_line_85 |  | 80 | 92 | 1.5727 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_439_0_line_86 |  | 82 | 83 | 0.099437 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
87 | MV_439_0_line_87 |  | 84 | 85 | 1.0657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_439_0_line_88 |  | 84 | 86 | 0.1001 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_439_0_line_89 |  | 85 | 87 | 0.014306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_439_0_line_90 |  | 88 | 89 | 0.06209 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_439_0_line_91 |  | 89 | 127 | 0.33647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_439_0_line_92 |  | 90 | 93 | 0.12272 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
93 | MV_439_0_line_93 |  | 91 | 92 | 0.021347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_439_0_line_94 |  | 94 | 95 | 0.046611 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_439_0_line_95 |  | 95 | 96 | 0.49587 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_439_0_line_96 |  | 96 | 100 | 0.016439 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_439_0_line_97 |  | 97 | 98 | 0.11095 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_439_0_line_98 |  | 97 | 99 | 0.028755 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_439_0_line_99 |  | 98 | 168 | 0.10042 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_439_0_line_100 |  | 98 | 167 | 0.00096238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_439_0_line_101 |  | 99 | 166 | 0.023924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_439_0_line_102 |  | 100 | 104 | 0.044421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_439_0_line_103 |  | 101 | 102 | 1.293 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
104 | MV_439_0_line_104 |  | 101 | 103 | 0.057601 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_439_0_line_105 |  | 102 | 118 | 0.056829 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_439_0_line_106 |  | 103 | 111 | 1.1847 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
107 | MV_439_0_line_107 |  | 103 | 131 | 0.33553 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_439_0_line_108 |  | 103 | 136 | 0.24651 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_439_0_line_109 |  | 104 | 118 | 0.35087 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_439_0_line_110 |  | 104 | 116 | 0.076177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_439_0_line_111 |  | 105 | 106 | 0.047215 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_439_0_line_112 |  | 106 | 107 | 0.83974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_439_0_line_113 |  | 106 | 108 | 1.0472 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_439_0_line_114 |  | 107 | 109 | 0.16278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_439_0_line_115 |  | 109 | 110 | 0.042242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_439_0_line_116 |  | 110 | 115 | 0.94656 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_439_0_line_117 |  | 111 | 112 | 0.061803 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_439_0_line_118 |  | 111 | 113 | 1.3098 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
119 | MV_439_0_line_119 |  | 113 | 155 | 0.13692 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
120 | MV_439_0_line_120 |  | 114 | 115 | 0.061126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_439_0_line_121 |  | 115 | 116 | 0.23173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_439_0_line_122 |  | 116 | 117 | 0.019524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_439_0_line_123 |  | 119 | 120 | 0.00464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_439_0_line_124 |  | 119 | 121 | 0.1475 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
125 | MV_439_0_line_125 |  | 120 | 122 | 0.11232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_439_0_line_126 |  | 121 | 123 | 0.13566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_439_0_line_127 |  | 122 | 125 | 0.065296 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
128 | MV_439_0_line_128 |  | 123 | 124 | 0.037841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_439_0_line_129 |  | 124 | 126 | 0.053805 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
130 | MV_439_0_line_130 |  | 125 | 138 | 0.62723 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
131 | MV_439_0_line_131 |  | 125 | 132 | 0.03252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_439_0_line_132 |  | 126 | 127 | 0.30975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_439_0_line_133 |  | 127 | 140 | 0.36405 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_439_0_line_134 |  | 127 | 141 | 0.032008 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
135 | MV_439_0_line_135 |  | 128 | 129 | 0.094606 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_439_0_line_136 |  | 129 | 130 | 0.083919 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_439_0_line_137 |  | 130 | 134 | 0.076515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_439_0_line_138 |  | 131 | 132 | 0.24245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_439_0_line_139 |  | 131 | 133 | 0.1232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_439_0_line_140 |  | 131 | 134 | 0.084566 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_439_0_line_141 |  | 133 | 135 | 0.13291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_439_0_line_142 |  | 135 | 139 | 0.0045838 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_439_0_line_143 |  | 136 | 137 | 0.068404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_439_0_line_144 |  | 138 | 142 | 0.077899 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_439_0_line_145 |  | 139 | 161 | 0.024242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_439_0_line_146 |  | 140 | 146 | 0.008718 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_439_0_line_147 |  | 142 | 143 | 0.77379 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_439_0_line_148 |  | 143 | 144 | 0.063553 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_439_0_line_149 |  | 143 | 145 | 0.51386 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_439_0_line_150 |  | 145 | 147 | 0.029912 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_439_0_line_151 |  | 148 | 149 | 0.086052 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
152 | MV_439_0_line_152 |  | 149 | 160 | 0.01273 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
153 | MV_439_0_line_153 |  | 150 | 151 | 0.0206 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
154 | MV_439_0_line_154 |  | 150 | 152 | 0.17748 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
155 | MV_439_0_line_155 |  | 151 | 153 | 0.036584 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_439_0_line_156 |  | 152 | 154 | 0.051187 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_439_0_line_157 |  | 153 | 157 | 0.045803 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_439_0_line_158 |  | 155 | 156 | 1.3491 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
159 | MV_439_0_line_159 |  | 156 | 158 | 0.18503 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
160 | MV_439_0_line_160 |  | 156 | 157 | 0.04618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_439_0_line_161 |  | 158 | 159 | 0.037987 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
162 | MV_439_0_line_162 |  | 158 | 160 | 0.12849 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
163 | MV_439_0_line_163 |  | 161 | 162 | 0.014926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_439_0_line_164 |  | 162 | 163 | 0.033989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_439_0_line_165 |  | 163 | 164 | 0.07748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_439_0_line_166 |  | 164 | 165 | 0.22417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_439_0_line_167 |  | 165 | 166 | 0.10422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_439_0_trafo_173 | 25 MVA 110/20 kV | 169 | 43 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2717769.9036 | 1271145.7192
1 | 2717769.0779 | 1271150.1401
2 | 2718322.941 | 1272093.6914
3 | 2718304.0057 | 1272143.8801
4 | 2718434.5964 | 1272122.3558
5 | 2716955.2614 | 1272736.9979
6 | 2716896.7582 | 1273159.4464
7 | 2716958.3051 | 1272799.7598
8 | 2715481.3232 | 1270770.8813
9 | 2715045.1756 | 1272639.8419
10 | 2715090.716 | 1272707.079
11 | 2717627.9838 | 1273684.093
12 | 2717605.6 | 1273686.738
13 | 2717656.2917 | 1273629.9631
14 | 2717637.6929 | 1273603.8241
15 | 2717790.0351 | 1273696.6243
16 | 2717410.6933 | 1273258.1339
17 | 2717414.5158 | 1273761.7815
18 | 2717036.8652 | 1273539.0683
19 | 2717732.4086 | 1273161.6409
20 | 2717679.0322 | 1273581.9613
21 | 2717803.4925 | 1273704.8448
22 | 2717446.0535 | 1273260.4727
23 | 2717753.4212 | 1273163.3837
24 | 2717049.4849 | 1273477.7514
25 | 2717379.611 | 1273811.166
26 | 2716916.9408 | 1273138.8702
27 | 2717827.8038 | 1273714.9392
28 | 2718369.2547 | 1272223.5492
29 | 2714908.4313 | 1272768.173
30 | 2714911.9255 | 1272769.1418
31 | 2714384.4402 | 1272680.9761
32 | 2713998.859 | 1272785.5137
33 | 2714336.3363 | 1272641.9538
34 | 2718351.2983 | 1273954.9196
35 | 2718353.2802 | 1273944.9835
36 | 2718435.1215 | 1273980.4797
37 | 2717846.0727 | 1273722.5219
38 | 2719611.8447 | 1273572.1718
39 | 2719268.1128 | 1275224.4105
40 | 2717859.7288 | 1273692.3461
41 | 2719682.1798 | 1273237.1217
42 | 2719677.119 | 1273281.1597
43 | 2719490.6486 | 1273067.3418
44 | 2719687.4517 | 1273368.0492
45 | 2719773.2136 | 1273134.918
46 | 2719628.2511 | 1273460.846
47 | 2719639.8435 | 1273355.4727
48 | 2719924.4149 | 1273220.744
49 | 2719874.5623 | 1273234.5444
50 | 2719818.7841 | 1273099.7547
51 | 2718452.6573 | 1272109.4062
52 | 2718453.9776 | 1272108.4763
53 | 2718474.847 | 1272099.9205
54 | 2718332.8691 | 1272195.5055
55 | 2718531.9729 | 1272179.9692
56 | 2713667.7486 | 1272837.6662
57 | 2713719.2355 | 1272852.2839
58 | 2713723.3815 | 1272853.461
59 | 2713746.5442 | 1272860.0371
60 | 2713748.6663 | 1272852.0617
61 | 2713740.0491 | 1272885.0168
62 | 2713754.8606 | 1272836.4205
63 | 2714000.7544 | 1272780.8572
64 | 2713989.8711 | 1272776.4765
65 | 2713826.5911 | 1272948.9152
66 | 2713641.1626 | 1273225.1033
67 | 2713808.0035 | 1272891.1748
68 | 2713669.889 | 1273221.5976
69 | 2713790.828 | 1272836.6915
70 | 2725953.3099 | 1273374.4669
71 | 2725904.1124 | 1273324.1034
72 | 2726399.6772 | 1273325.3598
73 | 2723883.0856 | 1272084.7836
74 | 2723860.5008 | 1272110.1223
75 | 2726424.2995 | 1273324.6085
76 | 2721676.058 | 1275058.6265
77 | 2721659.579 | 1275040.1584
78 | 2721409.9058 | 1275264.3491
79 | 2720326.5769 | 1275399.9794
80 | 2720309.3991 | 1275425.9312
81 | 2721281.4337 | 1275251.7405
82 | 2721739.4685 | 1275778.9969
83 | 2721832.8577 | 1275813.1449
84 | 2722266.1526 | 1275207.6711
85 | 2722220.9371 | 1274289.8877
86 | 2722251.084 | 1275306.6295
87 | 2722234.3019 | 1274284.8152
88 | 2722252.2189 | 1272764.0596
89 | 2722260.0327 | 1272702.4754
90 | 2719383.2878 | 1275183.4232
91 | 2720570.705 | 1276983.2185
92 | 2720549.5156 | 1276980.1493
93 | 2719380.5708 | 1275306.1153
94 | 2721887.1788 | 1269854.4972
95 | 2721840.585 | 1269855.7595
96 | 2721720.5762 | 1269965.0191
97 | 2722535.7769 | 1271347.6023
98 | 2722646.1046 | 1271335.8469
99 | 2722509.5202 | 1271359.3254
100 | 2721704.5202 | 1269968.7584
101 | 2722065.1166 | 1271480.5678
102 | 2721931.5915 | 1270194.5258
103 | 2722012.228 | 1271503.3849
104 | 2721664.2596 | 1269985.6001
105 | 2720743.2196 | 1268417.408
106 | 2720701.3615 | 1268439.484
107 | 2720847.6842 | 1269137.1094
108 | 2719738.2083 | 1268850.483
109 | 2721000.299 | 1269193.273
110 | 2721042.2005 | 1269199.348
111 | 2720956.4324 | 1271542.8594
112 | 2720898.9538 | 1271565.57
113 | 2719989.7678 | 1271438.523
114 | 2721430.2046 | 1269939.253
115 | 2721470.7012 | 1269893.3658
116 | 2721625.0134 | 1270045.6358
117 | 2721616.9585 | 1270063.4211
118 | 2721932.5848 | 1270137.7052
119 | 2722199.1688 | 1272069.8292
120 | 2722203.4715 | 1272068.061
121 | 2722255.421 | 1272206.1864
122 | 2722166.6706 | 1271966.7503
123 | 2722317.8654 | 1272306.4725
124 | 2722332.0646 | 1272341.5658
125 | 2722141.7134 | 1271906.4116
126 | 2722352.2239 | 1272391.4519
127 | 2722495.7082 | 1272522.4593
128 | 2721763.6762 | 1271765.4749
129 | 2721850.3131 | 1271727.4711
130 | 2721907.6311 | 1271757.4484
131 | 2722060.7203 | 1271734.5448
132 | 2722129.2738 | 1271876.3488
133 | 2722106.9357 | 1271644.695
134 | 2721982.5024 | 1271766.6918
135 | 2722220.1915 | 1271576.4352
136 | 2722170.5995 | 1271511.3551
137 | 2722233.0852 | 1271483.5235
138 | 2722665.1295 | 1272252.0252
139 | 2722224.5863 | 1271575.1517
140 | 2722645.3237 | 1272703.1105
141 | 2722496.8722 | 1272554.4465
142 | 2722731.8365 | 1272211.7962
143 | 2723150.8545 | 1272280.0831
144 | 2723139.9249 | 1272342.6912
145 | 2723531.6107 | 1272050.2776
146 | 2722637.2639 | 1272706.4907
147 | 2723557.6431 | 1272036.2981
148 | 2719778.1931 | 1273104.5577
149 | 2719766.6849 | 1273019.2791
150 | 2720075.3537 | 1272892.0421
151 | 2720073.4061 | 1272871.5344
152 | 2720139.5003 | 1273057.5217
153 | 2720069.6736 | 1272835.1409
154 | 2720144.8124 | 1273108.4322
155 | 2719865.1058 | 1271493.4419
156 | 2719977.9245 | 1272837.7672
157 | 2720023.9282 | 1272833.9769
158 | 2719818.9817 | 1272918.5474
159 | 2719838.4575 | 1272951.1616
160 | 2719769.1202 | 1273006.7837
161 | 2722248.2022 | 1271569.678
162 | 2722262.7432 | 1271566.3076
163 | 2722295.8545 | 1271558.633
164 | 2722371.3334 | 1271541.1384
165 | 2722392.5089 | 1271411.5685
166 | 2722487.6745 | 1271369.0791
167 | 2722646.6237 | 1271336.6573
168 | 2722716.8805 | 1271264.608
169 | 2719490.6486 | 1273067.3418

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98622 | -0.27445 | 0.13915 | 0.067395
1 | 0.98622 | -0.27446 | 0 | 0
2 | 0.98652 | -0.2725 | 0 | 0
3 | 0.98646 | -0.27191 | 0.90313 | 0.4374
4 | 0.98672 | -0.2744 | 0 | 0
5 | 0.99036 | -0.28981 | 0 | 0
6 | 0.99058 | -0.2913 | 0 | 0
7 | 0.99035 | -0.28965 | 0.20583 | 0.099689
8 | 0.9868 | -0.38089 | 0.34628 | 0.16771
9 | 0.9881 | -0.37247 | 0.45913 | 0.22237
10 | 0.98821 | -0.37346 | 0 | 0
11 | 0.99172 | -0.26742 | 0.37001 | 0.17921
12 | 0.99172 | -0.2674 | 0.071857 | 0.034802
13 | 0.99178 | -0.26708 | 0 | 0
14 | 0.99169 | -0.2689 | 0 | 0
15 | 0.99197 | -0.26322 | 0 | 0
16 | 0.99147 | -0.26702 | 0 | 0
17 | 0.99155 | -0.26788 | 0 | 0
18 | 0.99119 | -0.27924 | 0 | 0
19 | 0.99021 | -0.25593 | 0 | 0
20 | 0.99168 | -0.26884 | 0.12161 | 0.058899
21 | 0.99199 | -0.26283 | 0.33707 | 0.16325
22 | 0.99144 | -0.26716 | 0.32462 | 0.15722
23 | 0.99017 | -0.25553 | 0.17965 | 0.087009
24 | 0.99116 | -0.27941 | 0.2215 | 0.10728
25 | 0.99153 | -0.26774 | 0.1903 | 0.092164
26 | 0.99058 | -0.29128 | 0.068684 | 0.033265
27 | 0.99202 | -0.26214 | 0 | 0
28 | 0.98701 | -0.27697 | 0.16206 | 0.078489
29 | 0.98762 | -0.3689 | 0.32311 | 0.15649
30 | 0.98762 | -0.36892 | 0 | 0
31 | 0.98595 | -0.35594 | 0 | 0
32 | 0.9848 | -0.3463 | 0 | 0
33 | 0.98594 | -0.35584 | 0.12288 | 0.059513
34 | 0.9929 | -0.24443 | 0.20606 | 0.099801
35 | 0.99289 | -0.2447 | 0 | 0
36 | 0.99302 | -0.242 | 0 | 0
37 | 0.99205 | -0.26162 | 0 | 0
38 | 0.99733 | -0.082413 | 0.11539 | 0.055887
39 | 0.99083 | -0.27496 | 0.15548 | 0.075303
40 | 0.99205 | -0.26159 | 0.08082 | 0.039143
41 | 0.99833 | -0.061608 | 0.12842 | 0.062195
42 | 0.9982 | -0.064254 | 0 | 0
43 | 1 | 0 | -13.7297 | -5.7465
44 | 0.99785 | -0.0715 | 0 | 0
45 | 0.99791 | -0.07015 | 0 | 0
46 | 0.9975 | -0.078771 | 0 | 0
47 | 0.99784 | -0.07158 | 0.1337 | 0.064755
48 | 0.99782 | -0.070566 | 0.14516 | 0.070305
49 | 0.99783 | -0.070654 | 0 | 0
50 | 0.99787 | -0.070929 | 0 | 0
51 | 0.98672 | -0.27434 | 0.1647 | 0.079767
52 | 0.98672 | -0.27434 | 0 | 0
53 | 0.98671 | -0.27433 | 0 | 0
54 | 0.98693 | -0.27628 | 0 | 0
55 | 0.98671 | -0.27425 | 0.072358 | 0.035045
56 | 0.98408 | -0.34034 | 0.28503 | 0.13805
57 | 0.98411 | -0.34015 | 0.17279 | 0.083686
58 | 0.98411 | -0.34017 | 0.091892 | 0.044505
59 | 0.98413 | -0.34033 | 0 | 0
60 | 0.98414 | -0.3404 | 0.15397 | 0.074571
61 | 0.98413 | -0.3403 | 0.093369 | 0.045221
62 | 0.98415 | -0.34056 | 0 | 0
63 | 0.98479 | -0.34623 | 0.26693 | 0.12928
64 | 0.98478 | -0.34609 | 0 | 0
65 | 0.98432 | -0.34212 | 0 | 0
66 | 0.98425 | -0.34158 | 0 | 0
67 | 0.98425 | -0.34148 | 0.092643 | 0.044869
68 | 0.98425 | -0.34163 | 0.14201 | 0.06878
69 | 0.98419 | -0.34093 | 0 | 0
70 | 0.98411 | -0.27833 | 0.15683 | 0.075954
71 | 0.98413 | -0.27819 | 0 | 0
72 | 0.98407 | -0.27785 | 0 | 0
73 | 0.98523 | -0.26778 | 0.12157 | 0.058879
74 | 0.98524 | -0.2679 | 0 | 0
75 | 0.98406 | -0.27783 | 0.086108 | 0.041704
76 | 0.98898 | -0.29461 | 0.066577 | 0.032245
77 | 0.98898 | -0.29463 | 0 | 0
78 | 0.98904 | -0.29479 | 0 | 0
79 | 0.98969 | -0.28126 | 0.090347 | 0.043757
80 | 0.98971 | -0.28122 | 0 | 0
81 | 0.98909 | -0.29439 | 0.078711 | 0.038122
82 | 0.98888 | -0.29414 | 0 | 0
83 | 0.98886 | -0.29428 | 0.11726 | 0.056792
84 | 0.98888 | -0.2966 | 0 | 0
85 | 0.98881 | -0.2968 | 0 | 0
86 | 0.98887 | -0.29667 | 0.053379 | 0.025853
87 | 0.98881 | -0.29679 | 0.052841 | 0.025592
88 | 0.98675 | -0.26182 | 0.13346 | 0.064636
89 | 0.98676 | -0.26192 | 0 | 0
90 | 0.99068 | -0.27742 | 0.10614 | 0.051404
91 | 0.98941 | -0.28325 | 0.0959 | 0.046447
92 | 0.98942 | -0.28328 | 0 | 0
93 | 0.99057 | -0.27972 | 0 | 0
94 | 0.98672 | -0.30116 | 0.11218 | 0.054333
95 | 0.98673 | -0.30109 | 0 | 0
96 | 0.9868 | -0.30159 | 0 | 0
97 | 0.98629 | -0.25109 | 0 | 0
98 | 0.98621 | -0.25162 | 0.12938 | 0.062663
99 | 0.98631 | -0.25122 | 0.78515 | 0.38027
100 | 0.9868 | -0.3016 | 0.15509 | 0.075113
101 | 0.98933 | -0.2792 | 0.11502 | 0.055707
102 | 0.98721 | -0.30219 | 0.15759 | 0.076326
103 | 0.98944 | -0.2781 | 0 | 0
104 | 0.98681 | -0.30171 | 0 | 0
105 | 0.98613 | -0.29934 | 0.11013 | 0.053337
106 | 0.98613 | -0.2994 | 0 | 0
107 | 0.98631 | -0.30047 | 0 | 0
108 | 0.98602 | -0.30021 | 0.057711 | 0.027951
109 | 0.98635 | -0.30055 | 0.10169 | 0.049251
110 | 0.98636 | -0.30062 | 0 | 0
111 | 0.99248 | -0.23941 | 0 | 0
112 | 0.99246 | -0.23951 | 0.14208 | 0.068813
113 | 0.99386 | -0.21109 | 0 | 0
114 | 0.98667 | -0.30138 | 0.060138 | 0.029126
115 | 0.98668 | -0.30143 | 0 | 0
116 | 0.98677 | -0.30157 | 0 | 0
117 | 0.98677 | -0.30154 | 0.12101 | 0.058609
118 | 0.98713 | -0.30308 | 0 | 0
119 | 0.98721 | -0.26231 | 0.08456 | 0.040954
120 | 0.98722 | -0.26234 | 0 | 0
121 | 0.98709 | -0.26351 | 0 | 0
122 | 0.98729 | -0.26284 | 0 | 0
123 | 0.98701 | -0.26301 | 0 | 0
124 | 0.98699 | -0.26287 | 0.10589 | 0.051287
125 | 0.98736 | -0.26223 | 0.12877 | 0.062365
126 | 0.98695 | -0.26321 | 0 | 0
127 | 0.98682 | -0.26235 | 0 | 0
128 | 0.98779 | -0.26565 | 0.079892 | 0.038693
129 | 0.98781 | -0.26555 | 0 | 0
130 | 0.98781 | -0.26563 | 0 | 0
131 | 0.98785 | -0.26547 | 0 | 0
132 | 0.98742 | -0.26262 | 0 | 0
133 | 0.98752 | -0.26245 | 0 | 0
134 | 0.98782 | -0.26569 | 0.10698 | 0.051811
135 | 0.98717 | -0.25917 | 0.11345 | 0.054944
136 | 0.98941 | -0.27788 | 0 | 0
137 | 0.9894 | -0.27781 | 0.094326 | 0.045684
138 | 0.98645 | -0.27091 | 0.16478 | 0.079804
139 | 0.98715 | -0.25906 | 0.27291 | 0.13218
140 | 0.98678 | -0.26204 | 0 | 0
141 | 0.98681 | -0.2624 | 0.1131 | 0.054779
142 | 0.98637 | -0.27182 | 0 | 0
143 | 0.98578 | -0.26826 | 0 | 0
144 | 0.98577 | -0.26816 | 0.12637 | 0.061204
145 | 0.98548 | -0.26613 | 0 | 0
146 | 0.98678 | -0.26203 | 0.094446 | 0.045742
147 | 0.98546 | -0.266 | 0.10241 | 0.0496
148 | 0.99787 | -0.070985 | 0.12888 | 0.062421
149 | 0.99763 | -0.07975 | 0.1317 | 0.063787
150 | 0.99717 | -0.087168 | 0.12333 | 0.059732
151 | 0.99718 | -0.087095 | 0.10831 | 0.052459
152 | 0.99711 | -0.087523 | 0 | 0
153 | 0.9972 | -0.087261 | 0 | 0
154 | 0.9971 | -0.087429 | 0.15558 | 0.07535
155 | 0.99401 | -0.20806 | 0.072836 | 0.035276
156 | 0.99725 | -0.087723 | 0 | 0
157 | 0.99722 | -0.087466 | 0.095486 | 0.046246
158 | 0.99746 | -0.083253 | 0 | 0
159 | 0.99745 | -0.083319 | 0.14343 | 0.069467
160 | 0.99762 | -0.080067 | 0 | 0
161 | 0.9871 | -0.25858 | 0.10564 | 0.051162
162 | 0.98707 | -0.2583 | 0.18859 | 0.09134
163 | 0.98701 | -0.25773 | 0.13628 | 0.066002
164 | 0.98688 | -0.25658 | 0 | 0
165 | 0.98651 | -0.25317 | 0 | 0
166 | 0.98634 | -0.25157 | 0.1047 | 0.050708
167 | 0.98621 | -0.25162 | 0.10338 | 0.050069
168 | 0.98618 | -0.2518 | 0.14741 | 0.071394
169 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13915 | -0.067395 | 0.13915 | 0.06729 | 1.2294e-07 | -0.0001044 | 0.0045257 | 0.0045244 | 0.0045257 | 0.98622 | -0.27445 | 0.98622 | -0.27446 | 2.0571
1 | -0.13915 | -0.06729 | 0.13919 | 0.066045 | 3.9761e-05 | -0.0012459 | 0.0045244 | 0.0045083 | 0.0045244 | 0.98622 | -0.27446 | 0.98652 | -0.2725 | 2.1545
2 | 0.90319 | 0.43618 | -0.90313 | -0.4374 | 6.1701e-05 | -0.0012277 | 0.02935 | 0.029365 | 0.029365 | 0.98652 | -0.2725 | 0.98646 | -0.27191 | 13.3479
3 | -1.0424 | -0.50222 | 1.0426 | 0.49875 | 0.00023246 | -0.003466 | 0.033858 | 0.033813 | 0.033858 | 0.98652 | -0.2725 | 0.98672 | -0.2744 | 15.3899
4 | -1.2797 | -0.61018 | 1.28 | 0.60735 | 0.00028761 | -0.0028291 | 0.041476 | 0.04144 | 0.041476 | 0.98672 | -0.2744 | 0.98693 | -0.27628 | 18.8528
5 | 0.23706 | 0.11143 | -0.23706 | -0.11194 | 1.7404e-06 | -0.00051511 | 0.0076633 | 0.0076697 | 0.0076697 | 0.98672 | -0.2744 | 0.98672 | -0.27434 | 3.4862
6 | -0.20584 | -0.098218 | 0.20588 | 0.078584 | 4.7746e-05 | -0.019634 | 0.0066478 | 0.0064221 | 0.0066478 | 0.99036 | -0.28981 | 0.99058 | -0.2913 | 3.0217
7 | 0.20584 | 0.098218 | -0.20583 | -0.099689 | 3.7176e-06 | -0.0014704 | 0.0066478 | 0.0066664 | 0.0066664 | 0.99036 | -0.28981 | 0.99035 | -0.28965 | 3.0302
8 | 0.068684 | 0.032578 | -0.068684 | -0.033265 | 1.929e-07 | -0.00068706 | 0.0022153 | 0.002224 | 0.002224 | 0.99058 | -0.2913 | 0.99058 | -0.29128 | 1.0109
9 | 2.5611 | 1.167 | -2.5566 | -1.1652 | 0.0044668 | 0.001749 | 0.082017 | 0.082074 | 0.082074 | 0.99058 | -0.2913 | 0.98821 | -0.37346 | 10.0091
10 | -2.8356 | -1.2781 | 2.8371 | 1.2049 | 0.0014809 | -0.073252 | 0.090642 | 0.089771 | 0.090642 | 0.99058 | -0.2913 | 0.99119 | -0.27924 | 10.7651
11 | -0.34628 | -0.16771 | 0.34671 | 0.16575 | 0.00043211 | -0.0019633 | 0.011256 | 0.011227 | 0.011256 | 0.9868 | -0.38089 | 0.9881 | -0.37247 | 5.3598
12 | -0.80585 | -0.38812 | 0.80594 | 0.38575 | 9.365e-05 | -0.0023701 | 0.026131 | 0.026101 | 0.026131 | 0.9881 | -0.37247 | 0.98821 | -0.37346 | 11.8778
13 | 1.7506 | 0.77948 | -1.7495 | -0.78531 | 0.001107 | -0.0058293 | 0.05598 | 0.056054 | 0.056054 | 0.98821 | -0.37346 | 0.98762 | -0.36892 | 25.4789
14 | 0.071857 | 0.034273 | -0.071857 | -0.034802 | 1.6205e-07 | -0.00052924 | 0.0023174 | 0.002324 | 0.002324 | 0.99172 | -0.26742 | 0.99172 | -0.2674 | 1.0564
15 | -0.44187 | -0.21348 | 0.44189 | 0.21342 | 2.2206e-05 | -5.7816e-05 | 0.014285 | 0.014284 | 0.014285 | 0.99172 | -0.26742 | 0.99178 | -0.26708 | 6.8022
16 | 5.3258 | 2.2871 | -5.3254 | -2.2927 | 0.00041085 | -0.0055479 | 0.16871 | 0.16877 | 0.16877 | 0.99178 | -0.26708 | 0.99169 | -0.2689 | 20.0445
17 | -5.7677 | -2.5006 | 5.7686 | 2.4897 | 0.00095102 | -0.010803 | 0.18298 | 0.18284 | 0.18298 | 0.99178 | -0.26708 | 0.99197 | -0.26322 | 21.7313
18 | 0.32471 | 0.14473 | -0.32463 | -0.15718 | 7.7112e-05 | -0.012457 | 0.010348 | 0.010502 | 0.010502 | 0.99169 | -0.2689 | 0.99147 | -0.26702 | 4.7734
19 | 0.19033 | 0.077222 | -0.1903 | -0.090746 | 2.8219e-05 | -0.013524 | 0.005979 | 0.006138 | 0.006138 | 0.99169 | -0.2689 | 0.99155 | -0.26788 | 2.79
20 | 3.0599 | 1.256 | -3.0586 | -1.3121 | 0.0013028 | -0.056093 | 0.096284 | 0.09693 | 0.09693 | 0.99169 | -0.2689 | 0.99119 | -0.27924 | 11.5119
21 | 1.6288 | 0.75692 | -1.6262 | -0.77277 | 0.0025961 | -0.015844 | 0.052283 | 0.052489 | 0.052489 | 0.99169 | -0.2689 | 0.99021 | -0.25593 | 23.8588
22 | 0.12161 | 0.057803 | -0.12161 | -0.058899 | 9.6103e-07 | -0.0010961 | 0.0039196 | 0.0039334 | 0.0039334 | 0.99169 | -0.2689 | 0.99168 | -0.26884 | 1.7879
23 | -5.7686 | -2.4897 | 5.7687 | 2.4887 | 9.6253e-05 | -0.0010946 | 0.18284 | 0.18283 | 0.18284 | 0.99197 | -0.26322 | 0.99199 | -0.26283 | 21.7153
24 | 0.32463 | 0.15718 | -0.32462 | -0.15722 | 6.9635e-06 | -3.7224e-05 | 0.010502 | 0.010502 | 0.010502 | 0.99147 | -0.26702 | 0.99144 | -0.26716 | 5.001
25 | 0.1903 | 0.090746 | -0.1903 | -0.092164 | 3.0505e-06 | -0.0014187 | 0.006138 | 0.0061559 | 0.0061559 | 0.99155 | -0.26788 | 0.99153 | -0.26774 | 2.7981
26 | 0.22151 | 0.10721 | -0.2215 | -0.10728 | 5.7303e-06 | -6.9832e-05 | 0.0071672 | 0.0071681 | 0.0071681 | 0.99119 | -0.27924 | 0.99116 | -0.27941 | 3.4134
27 | 1.6262 | 0.77277 | -1.6261 | -0.77324 | 7.7378e-05 | -0.00046948 | 0.052489 | 0.052495 | 0.052495 | 0.99021 | -0.25593 | 0.99017 | -0.25553 | 23.8616
28 | -6.1058 | -2.6519 | 6.106 | 2.6501 | 0.00018028 | -0.0018085 | 0.19372 | 0.19369 | 0.19372 | 0.99199 | -0.26283 | 0.99202 | -0.26214 | 23.0069
29 | 1.4465 | 0.68623 | -1.4421 | -0.68481 | 0.0043631 | 0.001422 | 0.046676 | 0.046693 | 0.046693 | 0.99017 | -0.25553 | 0.98701 | -0.27697 | 22.2345
30 | -6.106 | -2.6501 | 6.1061 | 2.6487 | 0.00013544 | -0.001359 | 0.19369 | 0.19368 | 0.19369 | 0.99202 | -0.26214 | 0.99205 | -0.26162 | 23.0041
31 | 1.2801 | 0.60632 | -1.28 | -0.60735 | 0.00010508 | -0.0010352 | 0.041426 | 0.04144 | 0.04144 | 0.98701 | -0.27697 | 0.98693 | -0.27628 | 18.8362
32 | -0.32311 | -0.15649 | 0.32311 | 0.15641 | 5.3151e-07 | -8.4053e-05 | 0.010494 | 0.010493 | 0.010494 | 0.98762 | -0.3689 | 0.98762 | -0.36892 | 4.7699
33 | 1.4264 | 0.62891 | -1.4239 | -0.64945 | 0.002554 | -0.020545 | 0.045566 | 0.045821 | 0.045821 | 0.98762 | -0.36892 | 0.98595 | -0.35594 | 20.8279
34 | 1.301 | 0.59138 | -1.2994 | -0.60685 | 0.001615 | -0.015465 | 0.041842 | 0.042038 | 0.042038 | 0.98595 | -0.35594 | 0.9848 | -0.3463 | 19.1082
35 | 0.12288 | 0.058071 | -0.12288 | -0.059513 | 1.3192e-06 | -0.0014414 | 0.0039793 | 0.0039975 | 0.0039975 | 0.98595 | -0.35594 | 0.98594 | -0.35584 | 1.8171
36 | 1.2994 | 0.60685 | -1.2994 | -0.60696 | 1.1858e-05 | -0.00011286 | 0.042038 | 0.042039 | 0.042039 | 0.9848 | -0.3463 | 0.98479 | -0.34623 | 19.1088
37 | 6.1914 | 2.6429 | -6.1914 | -2.6436 | 7.1024e-05 | -0.00069788 | 0.19572 | 0.19573 | 0.19573 | 0.9929 | -0.24443 | 0.99289 | -0.2447 | 23.2461
38 | -6.3975 | -2.7427 | 6.3982 | 2.7367 | 0.000655 | -0.0059848 | 0.20237 | 0.2023 | 0.20237 | 0.9929 | -0.24443 | 0.99302 | -0.242 | 24.0348
39 | 6.1914 | 2.6436 | -6.1869 | -2.6871 | 0.0044464 | -0.043514 | 0.19573 | 0.19628 | 0.19628 | 0.99289 | -0.2447 | 0.99205 | -0.26162 | 23.3111
40 | -7.2174 | -2.9943 | 7.2403 | 3.0242 | 0.022901 | 0.029964 | 0.22715 | 0.22712 | 0.22715 | 0.99302 | -0.242 | 0.99733 | -0.082413 | 27.7014
41 | 0.81923 | 0.25758 | -0.81756 | -0.25829 | 0.0016634 | -0.00071657 | 0.024965 | 0.02498 | 0.02498 | 0.99302 | -0.242 | 0.99083 | -0.27496 | 11.8952
42 | 0.08082 | 0.038365 | -0.08082 | -0.039143 | 3.008e-07 | -0.00077821 | 0.0026033 | 0.0026131 | 0.0026131 | 0.99205 | -0.26162 | 0.99205 | -0.26159 | 1.1878
43 | -7.3557 | -3.0801 | 7.3568 | 3.0726 | 0.0010991 | -0.0075629 | 0.23082 | 0.23073 | 0.23082 | 0.99733 | -0.082413 | 0.9975 | -0.078771 | 27.4135
44 | 0.66208 | 0.18299 | -0.66199 | -0.18308 | 8.7242e-05 | -8.8612e-05 | 0.020013 | 0.020014 | 0.020014 | 0.99083 | -0.27496 | 0.99068 | -0.27742 | 9.5304
45 | 13.5705 | 5.6501 | -13.569 | -5.6521 | 0.0014658 | -0.0020295 | 0.42506 | 0.42509 | 0.42509 | 0.99833 | -0.061608 | 0.9982 | -0.064254 | 50.4862
46 | -13.6989 | -5.7123 | 13.7157 | 5.736 | 0.016802 | 0.023664 | 0.42918 | 0.42917 | 0.42918 | 0.99833 | -0.061608 | 1 | 0 | 52.3385
47 | 7.4949 | 3.1075 | -7.4927 | -3.1222 | 0.0022124 | -0.014667 | 0.23464 | 0.23483 | 0.23483 | 0.9982 | -0.064254 | 0.99785 | -0.0715 | 27.8891
48 | 6.0742 | 2.5446 | -6.0727 | -2.5602 | 0.0014774 | -0.015566 | 0.19045 | 0.19064 | 0.19064 | 0.9982 | -0.064254 | 0.99791 | -0.07015 | 22.6417
49 | 7.359 | 3.0575 | -7.3568 | -3.0726 | 0.0021852 | -0.015066 | 0.23054 | 0.23073 | 0.23073 | 0.99785 | -0.0715 | 0.9975 | -0.078771 | 27.4021
50 | 0.1337 | 0.064698 | -0.1337 | -0.064755 | 1.6203e-06 | -5.7517e-05 | 0.0042971 | 0.0042978 | 0.0042978 | 0.99785 | -0.0715 | 0.99784 | -0.07158 | 2.0466
51 | 6.0727 | 2.5602 | -6.0725 | -2.5624 | 0.0002101 | -0.0022101 | 0.19064 | 0.19067 | 0.19067 | 0.99791 | -0.07015 | 0.99787 | -0.070985 | 22.6449
52 | -0.14516 | -0.070305 | 0.14516 | 0.069068 | 1.5078e-06 | -0.0012368 | 0.0046662 | 0.0046507 | 0.0046662 | 0.99782 | -0.070566 | 0.99783 | -0.070654 | 2.121
53 | -0.14516 | -0.069068 | 0.14517 | 0.064797 | 5.1313e-06 | -0.0042712 | 0.0046507 | 0.004599 | 0.0046507 | 0.99783 | -0.070654 | 0.99787 | -0.070929 | 2.114
54 | -0.14517 | -0.064797 | 0.14517 | 0.063811 | 1.1689e-06 | -0.00098632 | 0.004599 | 0.0045874 | 0.004599 | 0.99787 | -0.070929 | 0.99787 | -0.070985 | 2.0905
55 | 0.072359 | 0.032176 | -0.072359 | -0.032213 | 1.1553e-08 | -3.7469e-05 | 0.0023168 | 0.0023172 | 0.0023172 | 0.98672 | -0.27434 | 0.98672 | -0.27434 | 1.0533
56 | 0.072359 | 0.032213 | -0.072359 | -0.032746 | 1.6465e-07 | -0.0005324 | 0.0023172 | 0.0023236 | 0.0023236 | 0.98672 | -0.27434 | 0.98671 | -0.27433 | 1.0562
57 | 0.072359 | 0.032746 | -0.072358 | -0.035045 | 7.216e-07 | -0.002299 | 0.0023236 | 0.0023522 | 0.0023522 | 0.98671 | -0.27433 | 0.98671 | -0.27425 | 1.0692
58 | -0.28503 | -0.13805 | 0.28504 | 0.13799 | 8.2298e-06 | -5.6723e-05 | 0.0092903 | 0.0092895 | 0.0092903 | 0.98408 | -0.34034 | 0.98411 | -0.34015 | 4.424
59 | -0.45783 | -0.22168 | 0.45783 | 0.22158 | 1.2809e-06 | -9.9279e-05 | 0.014921 | 0.01492 | 0.014921 | 0.98411 | -0.34015 | 0.98411 | -0.34017 | 6.7824
60 | -0.54972 | -0.26608 | 0.54973 | 0.26553 | 1.0313e-05 | -0.00055372 | 0.017915 | 0.017908 | 0.017915 | 0.98411 | -0.34017 | 0.98413 | -0.34033 | 8.1432
61 | -0.6431 | -0.31015 | 0.64311 | 0.30996 | 4.832e-06 | -0.00018941 | 0.020943 | 0.020941 | 0.020943 | 0.98413 | -0.34033 | 0.98414 | -0.3404 | 9.5197
62 | 0.093369 | 0.044624 | -0.093369 | -0.045221 | 3.1829e-07 | -0.00059675 | 0.0030355 | 0.0030431 | 0.0030431 | 0.98413 | -0.34033 | 0.98413 | -0.3403 | 1.3832
63 | -0.79708 | -0.38453 | 0.79709 | 0.38414 | 1.5422e-05 | -0.00039193 | 0.025959 | 0.025954 | 0.025959 | 0.98414 | -0.3404 | 0.98415 | -0.34056 | 11.7996
64 | -0.79709 | -0.38414 | 0.79713 | 0.38329 | 3.3529e-05 | -0.00085267 | 0.025954 | 0.025943 | 0.025954 | 0.98415 | -0.34056 | 0.98419 | -0.34093 | 11.7973
65 | 1.0324 | 0.47768 | -1.0324 | -0.47794 | 1.7372e-05 | -0.00026578 | 0.033347 | 0.03335 | 0.03335 | 0.98479 | -0.34623 | 0.98478 | -0.34609 | 15.159
66 | 1.0324 | 0.47794 | -1.0319 | -0.48575 | 0.00051186 | -0.0078032 | 0.03335 | 0.033449 | 0.033449 | 0.98478 | -0.34609 | 0.98432 | -0.34212 | 15.2039
67 | 0.14202 | 0.060278 | -0.14201 | -0.068747 | 1.0233e-05 | -0.0084693 | 0.0045248 | 0.0046276 | 0.0046276 | 0.98432 | -0.34212 | 0.98425 | -0.34158 | 2.1034
68 | 0.88989 | 0.42547 | -0.88982 | -0.42685 | 6.7806e-05 | -0.001383 | 0.028928 | 0.028945 | 0.028945 | 0.98432 | -0.34212 | 0.98425 | -0.34148 | 13.157
69 | 0.14201 | 0.068747 | -0.14201 | -0.06878 | 1.1043e-06 | -3.2777e-05 | 0.0046276 | 0.004628 | 0.004628 | 0.98425 | -0.34158 | 0.98425 | -0.34163 | 2.2038
70 | 0.79718 | 0.38198 | -0.79713 | -0.38329 | 5.1296e-05 | -0.001306 | 0.025926 | 0.025943 | 0.025943 | 0.98425 | -0.34148 | 0.98419 | -0.34093 | 11.7923
71 | -0.15683 | -0.075954 | 0.15683 | 0.075875 | 3.2767e-06 | -7.9349e-05 | 0.0051114 | 0.0051104 | 0.0051114 | 0.98411 | -0.27833 | 0.98413 | -0.27819 | 2.434
72 | 0.086114 | 0.027615 | -0.086108 | -0.041136 | 5.7756e-06 | -0.013521 | 0.0026527 | 0.0027994 | 0.0027994 | 0.98413 | -0.27819 | 0.98407 | -0.27785 | 1.2725
73 | -0.24294 | -0.10349 | 0.2432 | 0.1009 | 0.00025241 | -0.002586 | 0.0077459 | 0.0077147 | 0.0077459 | 0.98413 | -0.27819 | 0.98523 | -0.26778 | 3.6885
74 | 0.086108 | 0.041136 | -0.086108 | -0.041704 | 2.5761e-07 | -0.00056778 | 0.0027994 | 0.0028066 | 0.0028066 | 0.98407 | -0.27785 | 0.98406 | -0.27783 | 1.2757
75 | -0.36476 | -0.15978 | 0.36477 | 0.15899 | 6.198e-06 | -0.00078912 | 0.011668 | 0.011659 | 0.011668 | 0.98523 | -0.26778 | 0.98524 | -0.2679 | 5.3037
76 | -0.36477 | -0.15899 | 0.36485 | 0.15868 | 7.5468e-05 | -0.00031405 | 0.011659 | 0.011655 | 0.011659 | 0.98524 | -0.2679 | 0.98546 | -0.266 | 5.5518
77 | -0.066577 | -0.032245 | 0.066577 | 0.031578 | 1.7717e-07 | -0.00066726 | 0.0021593 | 0.0021508 | 0.0021593 | 0.98898 | -0.29461 | 0.98898 | -0.29463 | 0.98148
78 | -0.066577 | -0.031578 | 0.066582 | 0.014322 | 4.168e-06 | -0.017256 | 0.0021508 | 0.0019878 | 0.0021508 | 0.98898 | -0.29463 | 0.98904 | -0.29479 | 0.97766
79 | 0.10624 | -0.0049278 | -0.10622 | -0.026115 | 1.7237e-05 | -0.031043 | 0.0031042 | 0.0031933 | 0.0031933 | 0.98904 | -0.29479 | 0.98888 | -0.2966 | 1.4515
80 | -0.29011 | -0.04019 | 0.29012 | 0.037173 | 1.2595e-05 | -0.0030162 | 0.0085483 | 0.0085366 | 0.0085483 | 0.98904 | -0.29479 | 0.98909 | -0.29439 | 3.8856
81 | 0.11728 | 0.030795 | -0.11726 | -0.056678 | 1.9755e-05 | -0.025882 | 0.0035392 | 0.003802 | 0.003802 | 0.98904 | -0.29479 | 0.98888 | -0.29414 | 1.7282
82 | -0.45939 | -0.11805 | 0.45939 | 0.11731 | 8.1712e-06 | -0.00074574 | 0.013835 | 0.013829 | 0.013835 | 0.98969 | -0.28126 | 0.98971 | -0.28122 | 6.2886
83 | 0.36904 | 0.074296 | -0.36883 | -0.075295 | 0.00020769 | -0.00099913 | 0.01098 | 0.010987 | 0.010987 | 0.98969 | -0.28126 | 0.98909 | -0.29439 | 5.2318
84 | -0.55532 | -0.16143 | 0.5558 | 0.13178 | 0.00047687 | -0.029653 | 0.016868 | 0.016646 | 0.016868 | 0.98971 | -0.28122 | 0.99057 | -0.27972 | 7.6673
85 | 0.095927 | 0.044126 | -0.095901 | -0.045948 | 2.6773e-05 | -0.0018217 | 0.0030798 | 0.0031026 | 0.0031026 | 0.98971 | -0.28122 | 0.98942 | -0.28328 | 1.4774
86 | 0.11726 | 0.056678 | -0.11726 | -0.056792 | 2.562e-06 | -0.00011448 | 0.003802 | 0.0038035 | 0.0038035 | 0.98888 | -0.29414 | 0.98886 | -0.29428 | 1.8112
87 | 0.052845 | 0.00037853 | -0.052841 | -0.025258 | 3.585e-06 | -0.02488 | 0.0015427 | 0.0017098 | 0.0017098 | 0.98888 | -0.2966 | 0.98881 | -0.2968 | 0.77719
88 | 0.05338 | 0.025736 | -0.053379 | -0.025853 | 5.3419e-07 | -0.00011652 | 0.0017299 | 0.0017314 | 0.0017314 | 0.98888 | -0.2966 | 0.98887 | -0.29667 | 0.82448
89 | 0.052841 | 0.025258 | -0.052841 | -0.025592 | 5.597e-08 | -0.00033395 | 0.0017098 | 0.0017141 | 0.0017141 | 0.98881 | -0.2968 | 0.98881 | -0.29679 | 0.77912
90 | -0.13346 | -0.064636 | 0.13346 | 0.063193 | 1.5533e-06 | -0.001443 | 0.0043381 | 0.0043198 | 0.0043381 | 0.98675 | -0.26182 | 0.98676 | -0.26192 | 1.9718
91 | -0.13346 | -0.063193 | 0.13347 | 0.055372 | 8.198e-06 | -0.0078203 | 0.0043198 | 0.004227 | 0.0043198 | 0.98676 | -0.26192 | 0.98682 | -0.26235 | 1.9636
92 | 0.55586 | 0.13167 | -0.5558 | -0.13178 | 6.0586e-05 | -0.00010582 | 0.016645 | 0.016646 | 0.016646 | 0.99068 | -0.27742 | 0.99057 | -0.27972 | 7.9268
93 | -0.0959 | -0.046447 | 0.095901 | 0.045948 | 2.7489e-07 | -0.00049887 | 0.0031089 | 0.0031026 | 0.0031089 | 0.98941 | -0.28325 | 0.98942 | -0.28328 | 1.4131
94 | -0.11218 | -0.054333 | 0.11219 | 0.05428 | 1.1042e-06 | -5.3485e-05 | 0.0036468 | 0.0036461 | 0.0036468 | 0.98672 | -0.30116 | 0.98673 | -0.30109 | 1.7366
95 | -0.11219 | -0.05428 | 0.11219 | 0.042754 | 8.4646e-06 | -0.011526 | 0.0036461 | 0.0035123 | 0.0036461 | 0.98673 | -0.30109 | 0.9868 | -0.30159 | 1.6573
96 | -0.11219 | -0.042754 | 0.11219 | 0.042372 | 2.7042e-07 | -0.00038212 | 0.0035123 | 0.0035084 | 0.0035123 | 0.9868 | -0.30159 | 0.9868 | -0.3016 | 1.5965
97 | 0.38021 | 0.18388 | -0.38018 | -0.18399 | 3.021e-05 | -0.00010992 | 0.012361 | 0.012363 | 0.012363 | 0.98629 | -0.25109 | 0.98621 | -0.25162 | 5.8871
98 | -0.38021 | -0.18388 | 0.38021 | 0.18321 | 5.8616e-06 | -0.00066613 | 0.012361 | 0.012353 | 0.012361 | 0.98629 | -0.25109 | 0.98631 | -0.25122 | 5.6188
99 | 0.14741 | 0.071279 | -0.14741 | -0.071394 | 4.1114e-06 | -0.00011402 | 0.0047929 | 0.0047944 | 0.0047944 | 0.98621 | -0.25162 | 0.98618 | -0.2518 | 2.283
100 | 0.10338 | 0.050047 | -0.10338 | -0.050069 | 1.4656e-08 | -2.2344e-05 | 0.003362 | 0.0033623 | 0.0033623 | 0.98621 | -0.25162 | 0.98621 | -0.25162 | 1.5283
101 | -1.1654 | -0.56348 | 1.1654 | 0.56294 | 4.5835e-05 | -0.00054211 | 0.037886 | 0.037879 | 0.037886 | 0.98631 | -0.25122 | 0.98634 | -0.25157 | 17.2209
102 | -0.26728 | -0.11748 | 0.26729 | 0.11645 | 4.3199e-06 | -0.0010315 | 0.008541 | 0.0085289 | 0.008541 | 0.9868 | -0.3016 | 0.98681 | -0.30171 | 3.8823
103 | 0.87778 | 0.34497 | -0.87604 | -0.34538 | 0.0017456 | -0.00041412 | 0.02752 | 0.027536 | 0.027536 | 0.98933 | -0.2792 | 0.98721 | -0.30219 | 13.1122
104 | -0.9928 | -0.40068 | 0.9929 | 0.40067 | 0.00010015 | -4.5814e-06 | 0.031239 | 0.031238 | 0.031239 | 0.98933 | -0.2792 | 0.98944 | -0.2781 | 14.8757
105 | 0.71844 | 0.26906 | -0.71839 | -0.26909 | 5.0957e-05 | -3.4195e-05 | 0.022433 | 0.022434 | 0.022434 | 0.98721 | -0.30219 | 0.98713 | -0.30308 | 10.6829
106 | -4.791 | -2.1109 | 4.8043 | 2.0807 | 0.01331 | -0.030239 | 0.15275 | 0.15228 | 0.15275 | 0.98944 | -0.2781 | 0.99248 | -0.23941 | 42.1953
107 | 3.7038 | 1.6719 | -3.6975 | -1.6779 | 0.0063013 | -0.005961 | 0.11856 | 0.11865 | 0.11865 | 0.98944 | -0.2781 | 0.98785 | -0.26547 | 53.9336
108 | 0.09433 | 0.038325 | -0.094327 | -0.044086 | 2.9682e-06 | -0.0057609 | 0.0029706 | 0.0030379 | 0.0030379 | 0.98944 | -0.2781 | 0.98941 | -0.27788 | 1.3809
109 | -0.71816 | -0.27718 | 0.71839 | 0.26909 | 0.00023663 | -0.0080905 | 0.022519 | 0.022434 | 0.022519 | 0.98681 | -0.30171 | 0.98713 | -0.30308 | 10.2358
110 | 0.45087 | 0.16073 | -0.45085 | -0.16249 | 1.9964e-05 | -0.0017652 | 0.014002 | 0.01402 | 0.01402 | 0.98681 | -0.30171 | 0.98677 | -0.30157 | 6.3727
111 | -0.11013 | -0.053337 | 0.11013 | 0.052241 | 8.0561e-07 | -0.001096 | 0.003582 | 0.0035681 | 0.003582 | 0.98613 | -0.29934 | 0.98613 | -0.2994 | 1.6282
112 | -0.16784 | -0.07898 | 0.16788 | 0.059488 | 3.1668e-05 | -0.019492 | 0.0054302 | 0.0052128 | 0.0054302 | 0.98613 | -0.2994 | 0.98631 | -0.30047 | 2.4683
113 | 0.057717 | 0.026739 | -0.057711 | -0.027951 | 6.5219e-06 | -0.0012115 | 0.0018621 | 0.0018773 | 0.0018773 | 0.98613 | -0.2994 | 0.98602 | -0.30021 | 0.89397
114 | -0.16788 | -0.059488 | 0.16788 | 0.055709 | 5.8638e-06 | -0.0037793 | 0.0052128 | 0.0051769 | 0.0052128 | 0.98631 | -0.30047 | 0.98635 | -0.30055 | 2.3695
115 | -0.26957 | -0.10496 | 0.26958 | 0.10398 | 4.0374e-06 | -0.00098004 | 0.0084665 | 0.0084562 | 0.0084665 | 0.98635 | -0.30055 | 0.98636 | -0.30062 | 3.8484
116 | -0.26958 | -0.10398 | 0.26966 | 0.082011 | 8.8016e-05 | -0.021969 | 0.0084562 | 0.0082464 | 0.0084562 | 0.98636 | -0.30062 | 0.98668 | -0.30143 | 3.8437
117 | 0.14208 | 0.068741 | -0.14208 | -0.068813 | 2.3213e-06 | -7.1219e-05 | 0.0045909 | 0.0045918 | 0.0045918 | 0.99248 | -0.23941 | 0.99246 | -0.23951 | 2.1866
118 | -4.9464 | -2.1494 | 4.9522 | 2.0561 | 0.0058559 | -0.093336 | 0.15687 | 0.15575 | 0.15687 | 0.99248 | -0.23941 | 0.99386 | -0.21109 | 18.6305
119 | -4.9522 | -2.0561 | 4.9529 | 2.0463 | 0.00060737 | -0.0097775 | 0.15575 | 0.15563 | 0.15575 | 0.99386 | -0.21109 | 0.99401 | -0.20806 | 18.4972
120 | -0.060138 | -0.029126 | 0.060139 | 0.027706 | 3.0903e-07 | -0.0014207 | 0.001955 | 0.0019372 | 0.001955 | 0.98667 | -0.30138 | 0.98668 | -0.30143 | 0.88863
121 | -0.3298 | -0.10972 | 0.32983 | 0.10434 | 3.1837e-05 | -0.0053775 | 0.010169 | 0.01012 | 0.010169 | 0.98668 | -0.30143 | 0.98677 | -0.30157 | 4.6223
122 | 0.12101 | 0.058156 | -0.12101 | -0.058609 | 4.0271e-07 | -0.00045379 | 0.0039278 | 0.0039335 | 0.0039335 | 0.98677 | -0.30157 | 0.98677 | -0.30154 | 1.788
123 | -0.53163 | -0.22803 | 0.53164 | 0.22792 | 1.7723e-06 | -0.00010744 | 0.016915 | 0.016914 | 0.016915 | 0.98721 | -0.26231 | 0.98722 | -0.26234 | 7.6888
124 | 0.44707 | 0.18707 | -0.44702 | -0.18721 | 5.2787e-05 | -0.00013853 | 0.014171 | 0.014173 | 0.014173 | 0.98721 | -0.26231 | 0.98709 | -0.26351 | 6.7492
125 | -0.53164 | -0.22792 | 0.53168 | 0.22532 | 4.2822e-05 | -0.0026012 | 0.016914 | 0.016884 | 0.016914 | 0.98722 | -0.26234 | 0.98729 | -0.26284 | 7.6882
126 | 0.44702 | 0.18721 | -0.44699 | -0.19036 | 3.6474e-05 | -0.0031449 | 0.014173 | 0.014209 | 0.014209 | 0.98709 | -0.26351 | 0.98701 | -0.26301 | 6.4588
127 | -0.53168 | -0.22532 | 0.53171 | 0.22526 | 3.3164e-05 | -5.5215e-05 | 0.016884 | 0.016883 | 0.016884 | 0.98729 | -0.26284 | 0.98736 | -0.26223 | 8.0401
128 | 0.44699 | 0.19036 | -0.44697 | -0.19123 | 1.0207e-05 | -0.00087713 | 0.014209 | 0.014219 | 0.014219 | 0.98701 | -0.26301 | 0.98699 | -0.26287 | 6.4634
129 | 0.34108 | 0.13995 | -0.34107 | -0.14 | 1.1147e-05 | -5.5588e-05 | 0.010783 | 0.010784 | 0.010784 | 0.98699 | -0.26287 | 0.98695 | -0.26321 | 5.1351
130 | 0.75963 | 0.31701 | -0.75898 | -0.31733 | 0.00064745 | -0.00032376 | 0.024066 | 0.024074 | 0.024074 | 0.98736 | -0.26223 | 0.98645 | -0.27091 | 11.4638
131 | -1.4201 | -0.60464 | 1.4202 | 0.60391 | 8.8392e-05 | -0.00073077 | 0.045127 | 0.045118 | 0.045127 | 0.98736 | -0.26223 | 0.98742 | -0.26262 | 20.5121
132 | 0.34107 | 0.14 | -0.34102 | -0.14719 | 4.8449e-05 | -0.0071886 | 0.010784 | 0.010865 | 0.010865 | 0.98695 | -0.26321 | 0.98682 | -0.26235 | 4.9389
133 | 0.09445 | 0.037077 | -0.094446 | -0.04554 | 4.4199e-06 | -0.0084629 | 0.0029682 | 0.0030674 | 0.0030674 | 0.98682 | -0.26235 | 0.98678 | -0.26204 | 1.3943
134 | 0.11311 | 0.054742 | -0.1131 | -0.054779 | 7.7066e-07 | -3.6728e-05 | 0.0036758 | 0.0036763 | 0.0036763 | 0.98682 | -0.26235 | 0.98681 | -0.2624 | 1.7506
135 | -0.079892 | -0.038693 | 0.079893 | 0.038584 | 1.1338e-06 | -0.00010949 | 0.0025942 | 0.0025928 | 0.0025942 | 0.98779 | -0.26565 | 0.98781 | -0.26555 | 1.2353
136 | -0.079893 | -0.038584 | 0.079893 | 0.036629 | 7.4602e-07 | -0.0019549 | 0.0025928 | 0.0025685 | 0.0025928 | 0.98781 | -0.26555 | 0.98781 | -0.26563 | 1.1785
137 | -0.079893 | -0.036629 | 0.079894 | 0.034846 | 6.6824e-07 | -0.0017824 | 0.0025685 | 0.0025472 | 0.0025685 | 0.98781 | -0.26563 | 0.98782 | -0.26569 | 1.1675
138 | 1.4209 | 0.59846 | -1.4202 | -0.60391 | 0.00065792 | -0.0054513 | 0.045054 | 0.045118 | 0.045118 | 0.98785 | -0.26547 | 0.98742 | -0.26262 | 20.5082
139 | 2.0897 | 0.99288 | -2.089 | -0.99553 | 0.0007522 | -0.0026464 | 0.067609 | 0.067645 | 0.067645 | 0.98785 | -0.26547 | 0.98752 | -0.26245 | 30.7479
140 | 0.18687 | 0.086562 | -0.18687 | -0.086657 | 5.4585e-06 | -9.5096e-05 | 0.0060184 | 0.0060196 | 0.0060196 | 0.98785 | -0.26547 | 0.98782 | -0.26569 | 2.8665
141 | 2.089 | 0.99553 | -2.0882 | -0.99838 | 0.00081239 | -0.0028526 | 0.067645 | 0.067684 | 0.067684 | 0.98752 | -0.26245 | 0.98717 | -0.25917 | 30.7657
142 | 1.9747 | 0.94344 | -1.9747 | -0.94354 | 2.5064e-05 | -9.9217e-05 | 0.063998 | 0.064 | 0.064 | 0.98717 | -0.25917 | 0.98715 | -0.25906 | 29.0908
143 | 0.094327 | 0.044086 | -0.094326 | -0.045684 | 8.483e-07 | -0.0015985 | 0.0030379 | 0.0030579 | 0.0030579 | 0.98941 | -0.27788 | 0.9894 | -0.27781 | 1.39
144 | 0.59421 | 0.23753 | -0.59416 | -0.23759 | 4.8675e-05 | -5.9997e-05 | 0.018727 | 0.018728 | 0.018728 | 0.98645 | -0.27091 | 0.98637 | -0.27182 | 8.9179
145 | 1.7018 | 0.81136 | -1.7017 | -0.81189 | 9.8382e-05 | -0.00053481 | 0.055132 | 0.055139 | 0.055139 | 0.98715 | -0.25906 | 0.9871 | -0.25858 | 25.0634
146 | 0.094446 | 0.04554 | -0.094446 | -0.045742 | 1.096e-07 | -0.00020265 | 0.0030674 | 0.0030699 | 0.0030699 | 0.98678 | -0.26204 | 0.98678 | -0.26203 | 1.3954
147 | 0.59416 | 0.23759 | -0.59379 | -0.25544 | 0.00036615 | -0.017856 | 0.018728 | 0.018929 | 0.018929 | 0.98637 | -0.27182 | 0.98578 | -0.26826 | 8.6042
148 | 0.12637 | 0.05973 | -0.12637 | -0.061204 | 1.4279e-06 | -0.0014741 | 0.0040932 | 0.0041118 | 0.0041118 | 0.98578 | -0.26826 | 0.98577 | -0.26816 | 1.869
149 | 0.46742 | 0.19571 | -0.46727 | -0.20759 | 0.00015246 | -0.011874 | 0.014839 | 0.014978 | 0.014978 | 0.98578 | -0.26826 | 0.98548 | -0.26613 | 6.808
150 | 0.46727 | 0.20759 | -0.46726 | -0.20828 | 8.9629e-06 | -0.00069092 | 0.014978 | 0.014986 | 0.014986 | 0.98548 | -0.26613 | 0.98546 | -0.266 | 6.8117
151 | 5.7984 | 2.4362 | -5.7974 | -2.4349 | 0.0010153 | 0.0012482 | 0.18195 | 0.18195 | 0.18195 | 0.99787 | -0.070985 | 0.99763 | -0.07975 | 22.1889
152 | 5.6657 | 2.3711 | -5.6656 | -2.372 | 7.3584e-05 | -0.00090045 | 0.17772 | 0.17773 | 0.17773 | 0.99763 | -0.07975 | 0.99762 | -0.080067 | 21.1082
153 | -0.27892 | -0.13366 | 0.27892 | 0.13364 | 2.9425e-06 | -2.2611e-05 | 0.0089539 | 0.0089536 | 0.0089539 | 0.99717 | -0.087168 | 0.99718 | -0.087095 | 4.2638
154 | 0.15559 | 0.07393 | -0.15558 | -0.074136 | 7.8679e-06 | -0.00020574 | 0.0049868 | 0.0049895 | 0.0049895 | 0.99717 | -0.087168 | 0.99711 | -0.087523 | 2.3759
155 | -0.38724 | -0.1861 | 0.38724 | 0.18523 | 7.5486e-06 | -0.00086635 | 0.012438 | 0.012427 | 0.012438 | 0.99718 | -0.087095 | 0.9972 | -0.087261 | 5.6534
156 | 0.15558 | 0.074136 | -0.15558 | -0.07535 | 1.7064e-06 | -0.0012146 | 0.0049895 | 0.0050047 | 0.0050047 | 0.99711 | -0.087523 | 0.9971 | -0.087429 | 2.2749
157 | -0.38724 | -0.18523 | 0.38725 | 0.18415 | 9.4321e-06 | -0.0010847 | 0.012427 | 0.012413 | 0.012427 | 0.9972 | -0.087261 | 0.99722 | -0.087466 | 5.6485
158 | -5.0257 | -2.0816 | 5.0377 | 2.0955 | 0.011997 | 0.013907 | 0.15798 | 0.15794 | 0.15798 | 0.99401 | -0.20806 | 0.99725 | -0.087723 | 19.2656
159 | -5.5204 | -2.3248 | 5.5215 | 2.3117 | 0.0010171 | -0.013128 | 0.17339 | 0.17324 | 0.17339 | 0.99725 | -0.087723 | 0.99746 | -0.083253 | 20.593
160 | 0.48275 | 0.2293 | -0.48274 | -0.23039 | 1.4768e-05 | -0.0010921 | 0.015471 | 0.015484 | 0.015484 | 0.99725 | -0.087723 | 0.99722 | -0.087466 | 7.0383
161 | 0.14343 | 0.069423 | -0.14343 | -0.069467 | 1.4396e-06 | -4.4217e-05 | 0.0046118 | 0.0046123 | 0.0046123 | 0.99746 | -0.083253 | 0.99745 | -0.083319 | 2.1963
162 | -5.6649 | -2.3811 | 5.6656 | 2.372 | 0.0007432 | -0.0090864 | 0.17784 | 0.17773 | 0.17784 | 0.99746 | -0.083253 | 0.99762 | -0.080067 | 21.1212
163 | 1.596 | 0.76073 | -1.596 | -0.76106 | 5.3281e-05 | -0.00033143 | 0.051707 | 0.051711 | 0.051711 | 0.9871 | -0.25858 | 0.98707 | -0.2583 | 23.5051
164 | 1.4074 | 0.66972 | -1.4073 | -0.67049 | 9.4302e-05 | -0.00076266 | 0.045583 | 0.045593 | 0.045593 | 0.98707 | -0.2583 | 0.98701 | -0.25773 | 20.724
165 | 1.271 | 0.60448 | -1.2709 | -0.60623 | 0.00017537 | -0.0017499 | 0.041164 | 0.041187 | 0.041187 | 0.98701 | -0.25773 | 0.98688 | -0.25658 | 18.7214
166 | 1.2709 | 0.60623 | -1.2703 | -0.61129 | 0.00050847 | -0.00506 | 0.041187 | 0.041253 | 0.041253 | 0.98688 | -0.25658 | 0.98651 | -0.25317 | 18.7513
167 | 1.2703 | 0.61129 | -1.2701 | -0.61365 | 0.00023696 | -0.002351 | 0.041253 | 0.041284 | 0.041284 | 0.98651 | -0.25317 | 0.98634 | -0.25157 | 18.7653

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 13.8935 | 5.8258

## res_load
| p_mw | q_mvar
0 | 0.13915 | 0.067395
1 | 0.90313 | 0.4374
2 | 0.20583 | 0.099689
3 | 0.34628 | 0.16771
4 | 0.45913 | 0.22237
5 | 0.37001 | 0.17921
6 | 0.071857 | 0.034802
7 | 0.12161 | 0.058899
8 | 0.33707 | 0.16325
9 | 0.32462 | 0.15722
10 | 0.17965 | 0.087009
11 | 0.2215 | 0.10728
12 | 0.1903 | 0.092164
13 | 0.068684 | 0.033265
14 | 0.16206 | 0.078489
15 | 0.32311 | 0.15649
16 | 0.12288 | 0.059513
17 | 0.20606 | 0.099801
18 | 0.11539 | 0.055887
19 | 0.15548 | 0.075303
20 | 0.08082 | 0.039143
21 | 0.12842 | 0.062195
22 | 0.16378 | 0.07932
23 | 0.1337 | 0.064755
24 | 0.14516 | 0.070305
25 | 0.1647 | 0.079767
26 | 0.072358 | 0.035045
27 | 0.28503 | 0.13805
28 | 0.17279 | 0.083686
29 | 0.091892 | 0.044505
30 | 0.15397 | 0.074571
31 | 0.093369 | 0.045221
32 | 0.26693 | 0.12928
33 | 0.092643 | 0.044869
34 | 0.14201 | 0.06878
35 | 0.15683 | 0.075954
36 | 0.12157 | 0.058879
37 | 0.086108 | 0.041704
38 | 0.066577 | 0.032245
39 | 0.090347 | 0.043757
40 | 0.078711 | 0.038122
41 | 0.11726 | 0.056792
42 | 0.053379 | 0.025853
43 | 0.052841 | 0.025592
44 | 0.13346 | 0.064636
45 | 0.10614 | 0.051404
46 | 0.0959 | 0.046447
47 | 0.11218 | 0.054333
48 | 0.12938 | 0.062663
49 | 0.78515 | 0.38027
50 | 0.15509 | 0.075113
51 | 0.11502 | 0.055707
52 | 0.15759 | 0.076326
53 | 0.11013 | 0.053337
54 | 0.057711 | 0.027951
55 | 0.10169 | 0.049251
56 | 0.14208 | 0.068813
57 | 0.060138 | 0.029126
58 | 0.12101 | 0.058609
59 | 0.08456 | 0.040954
60 | 0.10589 | 0.051287
61 | 0.12877 | 0.062365
62 | 0.079892 | 0.038693
63 | 0.10698 | 0.051811
64 | 0.11345 | 0.054944
65 | 0.094326 | 0.045684
66 | 0.16478 | 0.079804
67 | 0.27291 | 0.13218
68 | 0.1131 | 0.054779
69 | 0.12637 | 0.061204
70 | 0.094446 | 0.045742
71 | 0.10241 | 0.0496
72 | 0.12888 | 0.062421
73 | 0.1317 | 0.063787
74 | 0.12333 | 0.059732
75 | 0.10831 | 0.052459
76 | 0.15558 | 0.07535
77 | 0.072836 | 0.035276
78 | 0.095486 | 0.046246
79 | 0.14343 | 0.069467
80 | 0.10564 | 0.051162
81 | 0.18859 | 0.09134
82 | 0.13628 | 0.066002
83 | 0.1047 | 0.050708
84 | 0.10338 | 0.050069
85 | 0.14741 | 0.071394

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1