## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_439_1_node_47 | 20 | n |  | TRUE
1 | bus_MV_439_1_node_48 | 20 | n |  | TRUE
2 | bus_MV_439_1_node_49 | 20 | n |  | TRUE
3 | bus_MV_439_1_node_50 | 20 | n |  | TRUE
4 | bus_MV_439_1_node_253 | 20 | n |  | TRUE
5 | bus_MV_439_1_node_51 | 20 | n |  | TRUE
6 | bus_MV_439_1_node_265 | 20 | n |  | TRUE
7 | bus_MV_439_1_node_266 | 20 | n |  | TRUE
8 | bus_MV_439_1_node_52 | 20 | n |  | TRUE
9 | bus_MV_439_1_node_53 | 20 | n |  | TRUE
10 | bus_MV_439_1_node_55 | 20 | n |  | TRUE
11 | bus_MV_439_1_node_54 | 20 | n |  | TRUE
12 | bus_MV_439_1_node_56 | 20 | n |  | TRUE
13 | bus_MV_439_1_node_109 | 20 | n |  | TRUE
14 | bus_MV_439_1_node_57 | 20 | n |  | TRUE
15 | bus_MV_439_1_node_58 | 20 | n |  | TRUE
16 | bus_MV_439_1_node_59 | 20 | n |  | TRUE
17 | bus_MV_439_1_node_60 | 20 | n |  | TRUE
18 | bus_MV_439_1_node_61 | 20 | n |  | TRUE
19 | bus_MV_439_1_node_62 | 20 | n |  | TRUE
20 | bus_MV_439_1_node_222 | 20 | n |  | TRUE
21 | bus_MV_439_1_node_64 | 20 | n |  | TRUE
22 | bus_MV_439_1_node_65 | 20 | n |  | TRUE
23 | bus_MV_439_1_node_252 | 20 | n |  | TRUE
24 | bus_MV_439_1_node_74 | 20 | n |  | TRUE
25 | bus_MV_439_1_node_69 | 20 | n |  | TRUE
26 | bus_MV_439_1_node_66 | 20 | n |  | TRUE
27 | bus_MV_439_1_node_67 | 20 | n |  | TRUE
28 | bus_MV_439_1_node_68 | 20 | n |  | TRUE
29 | bus_MV_439_1_node_270 | 20 | n |  | TRUE
30 | bus_MV_439_1_node_224 | 20 | n |  | TRUE
31 | bus_MV_439_1_node_71 | 20 | n |  | TRUE
32 | bus_MV_439_1_node_72 | 20 | n |  | TRUE
33 | bus_MV_439_1_node_73 | 20 | n |  | TRUE
34 | bus_MV_439_1_node_221 | 20 | n |  | TRUE
35 | bus_MV_439_1_node_75 | 20 | n |  | TRUE
36 | bus_MV_439_1_node_78 | 20 | n |  | TRUE
37 | bus_MV_439_1_node_79 | 20 | n |  | TRUE
38 | bus_MV_439_1_node_80 | 20 | n |  | TRUE
39 | bus_MV_439_1_node_82 | 20 | n |  | TRUE
40 | bus_MV_439_1_node_275 | 20 | n |  | TRUE
41 | bus_MV_439_1_node_81 | 20 | n |  | TRUE
42 | bus_MV_439_1_node_120 | 20 | n |  | TRUE
43 | bus_MV_439_1_node_117 | 20 | n |  | TRUE
44 | bus_MV_439_1_node_256 | 20 | n |  | TRUE
45 | bus_MV_439_1_node_83 | 20 | n |  | TRUE
46 | bus_MV_439_1_node_86 | 20 | n |  | TRUE
47 | bus_MV_439_1_node_87 | 20 | n |  | TRUE
48 | bus_MV_439_1_node_255 | 20 | n |  | TRUE
49 | bus_MV_439_1_node_121 | 20 | n |  | TRUE
50 | bus_MV_439_1_node_85 | 20 | n |  | TRUE
51 | bus_MV_439_1_node_101 | 20 | n |  | TRUE
52 | bus_MV_439_1_node_103 | 20 | n |  | TRUE
53 | bus_MV_439_1_node_127 | 20 | n |  | TRUE
54 | bus_MV_439_1_node_119 | 20 | n |  | TRUE
55 | bus_MV_439_1_node_88 | 20 | n |  | TRUE
56 | bus_MV_439_1_node_89 | 20 | n |  | TRUE
57 | bus_MV_439_1_node_90 | 20 | n |  | TRUE
58 | bus_MV_439_1_node_102 | 20 | n |  | TRUE
59 | bus_MV_439_1_node_91 | 20 | n |  | TRUE
60 | bus_MV_439_1_node_93 | 20 | n |  | TRUE
61 | bus_MV_439_1_node_94 | 20 | n |  | TRUE
62 | bus_MV_439_1_node_92 | 20 | n |  | TRUE
63 | bus_MV_439_1_node_95 | 20 | n |  | TRUE
64 | bus_MV_439_1_node_97 | 20 | n |  | TRUE
65 | bus_MV_439_1_node_98 | 20 | n |  | TRUE
66 | bus_MV_439_1_node_96 | 20 | n |  | TRUE
67 | bus_MV_439_1_node_106 | 20 | n |  | TRUE
68 | bus_MV_439_1_node_100 | 20 | n |  | TRUE
69 | bus_MV_439_1_node_107 | 20 | n |  | TRUE
70 | bus_MV_439_1_node_262 | 20 | n |  | TRUE
71 | bus_MV_439_1_node_99 | 20 | n |  | TRUE
72 | bus_MV_439_1_node_125 | 20 | n |  | TRUE
73 | bus_MV_439_1_node_118 | 20 | n |  | TRUE
74 | bus_MV_439_1_node_104 | 20 | n |  | TRUE
75 | bus_MV_439_1_node_105 | 20 | n |  | TRUE
76 | bus_MV_439_1_node_111 | 20 | n |  | TRUE
77 | bus_MV_439_1_node_110 | 20 | n |  | TRUE
78 | bus_MV_439_1_node_108 | 20 | n |  | TRUE
79 | bus_MV_439_1_node_112 | 20 | n |  | TRUE
80 | bus_MV_439_1_node_113 | 20 | n |  | TRUE
81 | bus_MV_439_1_node_126 | 20 | n |  | TRUE
82 | bus_MV_439_1_node_267 | 20 | n |  | TRUE
83 | bus_MV_439_1_node_114 | 20 | n |  | TRUE
84 | bus_MV_439_1_node_115 | 20 | n |  | TRUE
85 | bus_MV_439_1_node_273 | 20 | n |  | TRUE
86 | bus_MV_439_1_node_226 | 20 | n |  | TRUE
87 | bus_MV_439_1_node_122 | 20 | n |  | TRUE
88 | bus_MV_439_1_node_123 | 20 | n |  | TRUE
89 | bus_MV_439_1_node_259 | 20 | n |  | TRUE
90 | bus_MV_439_1_node_278 | 20 | n |  | TRUE
91 | bus_MV_439_1_node_223 | 20 | n |  | TRUE
92 | bus_MV_439_1_node_276 | 20 | n |  | TRUE
93 | bus_MV_439_1_node_227 | 20 | n |  | TRUE
94 | bus_MV_439_1_node_228 | 20 | n |  | TRUE
95 | bus_MV_439_1_node_251 | 20 | n |  | TRUE
96 | bus_MV_439_1_node_260 | 20 | n |  | TRUE
97 | bus_MV_439_1_node_274 | 20 | n |  | TRUE
98 | bus_HV_439_1_node_251 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_439_1_load_47 | 0 | 0.10596 | 0.051316 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_439_1_load_253 | 4 | 0.13317 | 0.064498 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_439_1_load_265 | 6 | 0.098901 | 0.0479 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_439_1_load_266 | 7 | 0.084709 | 0.041026 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_439_1_load_52 | 8 | 0.14096 | 0.068268 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_439_1_load_55 | 10 | 0.12457 | 0.06033 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_439_1_load_56 | 12 | 0.15904 | 0.077025 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_439_1_load_109 | 13 | 0.078171 | 0.03786 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_439_1_load_59 | 16 | 0.12989 | 0.06291 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_439_1_load_62 | 19 | 0.15687 | 0.075976 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_439_1_load_64 | 21 | 0.066633 | 0.032272 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_439_1_load_252 | 23 | 0.065449 | 0.031698 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_439_1_load_74 | 24 | 0.14749 | 0.071431 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_439_1_load_69 | 25 | 0.14066 | 0.068124 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_439_1_load_66 | 26 | 0.14099 | 0.068287 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_439_1_load_270 | 29 | 0.14446 | 0.069963 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_439_1_load_224 | 30 | 0.6887 | 0.33355 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_439_1_load_71 | 31 | 0.056532 | 0.02738 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_439_1_load_221 | 34 | 0.083639 | 0.040508 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_439_1_load_78 | 36 | 0.096839 | 0.046901 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_439_1_load_275 | 40 | 0.15536 | 0.075247 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_439_1_load_120 | 42 | 0.12552 | 0.06079 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_439_1_load_256 | 44 | 0.16137 | 0.078155 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_439_1_load_255 | 48 | 0.13363 | 0.064719 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_439_1_load_121 | 49 | 0.11344 | 0.054942 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_439_1_load_101 | 51 | 0.1414 | 0.068483 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_439_1_load_127 | 53 | 0.14798 | 0.071672 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_439_1_load_119 | 54 | 0.07791 | 0.037734 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_439_1_load_88 | 55 | 0.065289 | 0.031621 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_439_1_load_102 | 58 | 0.13445 | 0.065117 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_439_1_load_91 | 59 | 0.069878 | 0.033843 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_439_1_load_106 | 67 | 0.10122 | 0.049024 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_439_1_load_100 | 68 | 0.075949 | 0.036784 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_439_1_load_262 | 70 | 0.15732 | 0.076194 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_439_1_load_125 | 72 | 0.1076 | 0.052112 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_439_1_load_118 | 73 | 0.10539 | 0.051041 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_439_1_load_111 | 76 | 0.071616 | 0.034685 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_439_1_load_110 | 77 | 0.11867 | 0.057475 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_439_1_load_126 | 81 | 0.16119 | 0.078066 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_439_1_load_267 | 82 | 0.098778 | 0.04784 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_439_1_load_114 | 83 | 0.094626 | 0.045829 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_439_1_load_226 | 86 | 0.69054 | 0.33444 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_439_1_load_259 | 89 | 0.14881 | 0.072072 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_439_1_load_278 | 90 | 0.11857 | 0.057427 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_439_1_load_276 | 92 | 0.40001 | 0.19373 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_439_1_load_274 | 97 | 0.14252 | 0.069025 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 95 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_439_1_line_0 |  | 0 | 1 | 0.034002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_439_1_line_1 |  | 1 | 2 | 0.36001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_439_1_line_2 |  | 1 | 3 | 1.1126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_439_1_line_3 |  | 2 | 4 | 0.004965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_439_1_line_4 |  | 3 | 5 | 0.40957 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_439_1_line_5 |  | 3 | 6 | 0.04731 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_439_1_line_6 |  | 4 | 15 | 0.023826 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_439_1_line_7 |  | 5 | 7 | 0.028456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_439_1_line_8 |  | 8 | 9 | 0.009568 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_439_1_line_9 |  | 8 | 10 | 0.18795 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_439_1_line_10 |  | 9 | 11 | 0.035528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_439_1_line_11 |  | 10 | 13 | 2.2272 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_439_1_line_12 |  | 11 | 12 | 0.032657 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_439_1_line_13 |  | 12 | 14 | 0.04064 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_439_1_line_14 |  | 13 | 77 | 0.077553 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_439_1_line_15 |  | 13 | 78 | 0.093596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_439_1_line_16 |  | 14 | 15 | 0.18051 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_439_1_line_17 |  | 16 | 17 | 0.089299 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_439_1_line_18 |  | 17 | 18 | 0.15887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_439_1_line_19 |  | 18 | 19 | 0.019265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_439_1_line_20 |  | 19 | 20 | 0.50125 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_439_1_line_21 |  | 20 | 91 | 0.98834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_439_1_line_22 |  | 20 | 34 | 0.068982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_439_1_line_23 |  | 21 | 22 | 0.040239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_439_1_line_24 |  | 21 | 23 | 1.254 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_439_1_line_25 |  | 21 | 24 | 1.3543 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_439_1_line_26 |  | 22 | 25 | 1.2349 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_439_1_line_27 |  | 23 | 95 | 0.12977 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_439_1_line_28 |  | 24 | 35 | 0.006008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_439_1_line_29 |  | 26 | 27 | 0.16003 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_439_1_line_30 |  | 27 | 28 | 0.17168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_439_1_line_31 |  | 27 | 29 | 1.6926 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_439_1_line_32 |  | 28 | 30 | 0.042921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_439_1_line_33 |  | 29 | 33 | 0.015863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_439_1_line_34 |  | 31 | 32 | 0.13218 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_439_1_line_35 |  | 32 | 33 | 0.35355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_439_1_line_36 |  | 32 | 34 | 1.5669 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_439_1_line_37 |  | 33 | 35 | 0.36621 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_439_1_line_38 |  | 36 | 37 | 0.016718 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
39 | MV_439_1_line_39 |  | 36 | 38 | 0.07293 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
40 | MV_439_1_line_40 |  | 37 | 39 | 0.21316 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
41 | MV_439_1_line_41 |  | 38 | 40 | 0.075429 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
42 | MV_439_1_line_42 |  | 39 | 43 | 0.24722 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
43 | MV_439_1_line_43 |  | 39 | 44 | 0.071199 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_439_1_line_44 |  | 39 | 41 | 0.2543 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_439_1_line_45 |  | 40 | 95 | 1.5639 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
46 | MV_439_1_line_46 |  | 41 | 42 | 0.095041 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_439_1_line_47 |  | 42 | 84 | 0.33268 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_439_1_line_48 |  | 43 | 86 | 0.053562 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
49 | MV_439_1_line_49 |  | 45 | 46 | 0.35242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_439_1_line_50 |  | 45 | 47 | 0.21148 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_439_1_line_51 |  | 45 | 48 | 0.32093 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
52 | MV_439_1_line_52 |  | 45 | 49 | 0.061346 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
53 | MV_439_1_line_53 |  | 46 | 53 | 0.037945 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_439_1_line_54 |  | 47 | 54 | 0.032045 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_439_1_line_55 |  | 48 | 94 | 0.005356 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
56 | MV_439_1_line_56 |  | 49 | 87 | 0.005236 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
57 | MV_439_1_line_57 |  | 50 | 51 | 0.09629 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_439_1_line_58 |  | 50 | 52 | 0.21693 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_439_1_line_59 |  | 52 | 74 | 0.18714 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_439_1_line_60 |  | 52 | 58 | 0.059389 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_439_1_line_61 |  | 55 | 56 | 0.083531 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_439_1_line_62 |  | 56 | 57 | 0.1828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_439_1_line_63 |  | 57 | 58 | 0.060856 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_439_1_line_64 |  | 59 | 60 | 0.023633 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
65 | MV_439_1_line_65 |  | 59 | 61 | 0.026292 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_439_1_line_66 |  | 59 | 62 | 0.053513 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
67 | MV_439_1_line_67 |  | 60 | 64 | 0.07664 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
68 | MV_439_1_line_68 |  | 61 | 65 | 0.09008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_439_1_line_69 |  | 62 | 63 | 0.063711 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
70 | MV_439_1_line_70 |  | 63 | 66 | 0.22121 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
71 | MV_439_1_line_71 |  | 63 | 67 | 0.059789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_439_1_line_72 |  | 64 | 70 | 0.018942 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
73 | MV_439_1_line_73 |  | 65 | 71 | 0.10618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_439_1_line_74 |  | 65 | 72 | 0.052756 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_439_1_line_75 |  | 66 | 68 | 0.004264 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_439_1_line_76 |  | 66 | 69 | 0.12796 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
77 | MV_439_1_line_77 |  | 69 | 78 | 0.24161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_439_1_line_78 |  | 70 | 96 | 0.061927 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
79 | MV_439_1_line_79 |  | 71 | 73 | 0.022688 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_439_1_line_80 |  | 74 | 75 | 0.28114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_439_1_line_81 |  | 74 | 76 | 0.003957 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_439_1_line_82 |  | 75 | 77 | 0.12378 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_439_1_line_83 |  | 79 | 80 | 0.21134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_439_1_line_84 |  | 79 | 81 | 0.039276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_439_1_line_85 |  | 80 | 82 | 0.019574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_439_1_line_86 |  | 82 | 90 | 0.18068 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
87 | MV_439_1_line_87 |  | 83 | 84 | 0.024852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_439_1_line_88 |  | 83 | 85 | 0.76586 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_439_1_line_89 |  | 85 | 97 | 0.050375 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_439_1_line_90 |  | 86 | 93 | 0.037168 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
91 | MV_439_1_line_91 |  | 87 | 88 | 0.18207 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
92 | MV_439_1_line_92 |  | 88 | 89 | 0.021327 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
93 | MV_439_1_line_93 |  | 88 | 90 | 0.15143 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_439_1_line_94 |  | 89 | 96 | 0.003466 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
95 | MV_439_1_line_95 |  | 91 | 92 | 0.038554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_439_1_line_96 |  | 93 | 94 | 0.1285 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_439_1_trafo_251 | 25 MVA 110/20 kV | 98 | 95 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2719007.1087 | 1281318.0813
1 | 2719007.2255 | 1281352.0825
2 | 2718799.9185 | 1281539.1013
3 | 2719851.5304 | 1281481.2624
4 | 2718796.0031 | 1281542.1697
5 | 2719580.9876 | 1281376.4586
6 | 2719897.1024 | 1281468.0764
7 | 2719582.6796 | 1281404.8643
8 | 2718601.2603 | 1281643.0558
9 | 2718610.5895 | 1281645.3012
10 | 2718488.0219 | 1281493.0482
11 | 2718645.6081 | 1281651.6451
12 | 2718678.0139 | 1281655.69
13 | 2716430.2075 | 1280641.0879
14 | 2718689.329 | 1281616.7809
15 | 2718782.8756 | 1281522.2864
16 | 2712681.5091 | 1275965.3172
17 | 2712704.1593 | 1275878.9381
18 | 2712770.7887 | 1275736.6373
19 | 2712789.4792 | 1275741.4099
20 | 2713266.0252 | 1275896.8443
21 | 2716598.0015 | 1277158.574
22 | 2716638.3608 | 1277158.9609
23 | 2716528.4735 | 1278410.6602
24 | 2715256.1904 | 1276975.2091
25 | 2717873.2492 | 1277163.9615
26 | 2716062.2954 | 1275343.5881
27 | 2715903.062 | 1275327.6334
28 | 2715857.6919 | 1275216.5298
29 | 2714976.1281 | 1276743.8329
30 | 2715816.8106 | 1275203.4571
31 | 2714778.5761 | 1276800.5313
32 | 2714653.027 | 1276764.0982
33 | 2714963.3738 | 1276753.3154
34 | 2713325.2103 | 1275932.2786
35 | 2715253.5294 | 1276969.8189
36 | 2715612.8028 | 1279880.4967
37 | 2715599.214 | 1279890.2839
38 | 2715684.9294 | 1279889.5084
39 | 2715445.7419 | 1279974.2336
40 | 2715759.7108 | 1279879.6443
41 | 2715323.2701 | 1279768.1793
42 | 2715236.7557 | 1279728.8341
43 | 2715390.7039 | 1280215.2475
44 | 2715374.5576 | 1279972.7726
45 | 2715739.8616 | 1280445.2375
46 | 2715774.7386 | 1280146.8994
47 | 2715843.6102 | 1280393.5041
48 | 2715432.3951 | 1280353.2698
49 | 2715786.546 | 1280485.0355
50 | 2715977.9169 | 1280193.2681
51 | 2715943.5022 | 1280283.1976
52 | 2716190.8347 | 1280234.798
53 | 2715740.685 | 1280130.1616
54 | 2715865.7409 | 1280370.3283
55 | 2716483.2784 | 1280187.6785
56 | 2716403.9972 | 1280213.9821
57 | 2716261.1031 | 1280145.0657
58 | 2716240.4934 | 1280202.2239
59 | 2715993.2353 | 1280752.3694
60 | 2715996.0247 | 1280731.6494
61 | 2715981.9867 | 1280776.1482
62 | 2716042.7645 | 1280772.6295
63 | 2716095.659 | 1280787.5513
64 | 2715948.8976 | 1280676.3486
65 | 2715936.3213 | 1280852.3437
66 | 2716158.5907 | 1280937.6867
67 | 2716152.7201 | 1280805.6475
68 | 2716159.7493 | 1280941.7911
69 | 2716270.8933 | 1280876.3426
70 | 2715936.7203 | 1280661.8067
71 | 2715975.8177 | 1280894.8935
72 | 2715903.89 | 1280810.7339
73 | 2715993.4226 | 1280909.2039
74 | 2716163.7067 | 1280403.8771
75 | 2716272.4964 | 1280535.8889
76 | 2716160.6537 | 1280401.3479
77 | 2716390.0101 | 1280574.7657
78 | 2716372.3716 | 1280709.3324
79 | 2716148.1491 | 1280617.9596
80 | 2716063.0732 | 1280478.4875
81 | 2716183.2964 | 1280600.4317
82 | 2716047.2263 | 1280490.042
83 | 2714924.4806 | 1279565.2643
84 | 2714948.6814 | 1279562.4425
85 | 2714160.7408 | 1279508.3108
86 | 2715435.4965 | 1280236.9179
87 | 2715784.0811 | 1280489.6581
88 | 2715886.4946 | 1280607.3797
89 | 2715881.087 | 1280627.926
90 | 2715869.6131 | 1280456.8963
91 | 2713716.5868 | 1275181.6474
92 | 2713746.4187 | 1275174.9161
93 | 2715469.5913 | 1280251.7145
94 | 2715432.2069 | 1280347.9167
95 | 2716406.9331 | 1278455.9026
96 | 2715884.5167 | 1280628.4939
97 | 2714134.2668 | 1279549.5366
98 | 2716406.9331 | 1278455.9026

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98183 | -0.35937 | 0.10596 | 0.051316
1 | 0.98183 | -0.35942 | 0 | 0
2 | 0.98196 | -0.35972 | 0 | 0
3 | 0.98158 | -0.35864 | 0 | 0
4 | 0.98197 | -0.35972 | 0.13317 | 0.064498
5 | 0.98153 | -0.35836 | 0 | 0
6 | 0.98157 | -0.35859 | 0.098901 | 0.0479
7 | 0.98153 | -0.35833 | 0.084709 | 0.041026
8 | 0.98217 | -0.35973 | 0.14096 | 0.068268
9 | 0.98216 | -0.3597 | 0 | 0
10 | 0.98243 | -0.35717 | 0.12457 | 0.06033
11 | 0.98214 | -0.35956 | 0 | 0
12 | 0.9821 | -0.35995 | 0.15904 | 0.077025
13 | 0.98604 | -0.32312 | 0.078171 | 0.03786
14 | 0.98208 | -0.35987 | 0 | 0
15 | 0.98198 | -0.3595 | 0 | 0
16 | 0.98535 | -0.087551 | 0.12989 | 0.06291
17 | 0.98538 | -0.087406 | 0 | 0
18 | 0.9854 | -0.08764 | 0 | 0
19 | 0.98541 | -0.087666 | 0.15687 | 0.075976
20 | 0.98569 | -0.085679 | 0 | 0
21 | 0.9944 | -0.036887 | 0.066633 | 0.032272
22 | 0.9944 | -0.036823 | 0 | 0
23 | 0.99963 | 0.0029649 | 0.065449 | 0.031698
24 | 0.9893 | -0.076463 | 0.14749 | 0.071431
25 | 0.99406 | -0.039024 | 0.14066 | 0.068124
26 | 0.98563 | -0.088002 | 0.14099 | 0.068287
27 | 0.98568 | -0.08772 | 0 | 0
28 | 0.98552 | -0.086297 | 0 | 0
29 | 0.98842 | -0.069387 | 0.14446 | 0.069963
30 | 0.98549 | -0.085934 | 0.6887 | 0.33355
31 | 0.98806 | -0.066801 | 0.056532 | 0.02738
32 | 0.98807 | -0.06688 | 0 | 0
33 | 0.98844 | -0.069569 | 0 | 0
34 | 0.98575 | -0.086129 | 0.083639 | 0.040508
35 | 0.98929 | -0.076354 | 0 | 0
36 | 0.99109 | -0.23079 | 0.096839 | 0.046901
37 | 0.99106 | -0.23126 | 0 | 0
38 | 0.99127 | -0.22871 | 0 | 0
39 | 0.99056 | -0.23722 | 0 | 0
40 | 0.99166 | -0.21843 | 0.15536 | 0.075247
41 | 0.99044 | -0.23623 | 0 | 0
42 | 0.9904 | -0.23583 | 0.12552 | 0.06079
43 | 0.98947 | -0.26623 | 0 | 0
44 | 0.99054 | -0.23736 | 0.16137 | 0.078155
45 | 0.98797 | -0.30091 | 0 | 0
46 | 0.98791 | -0.30039 | 0 | 0
47 | 0.98795 | -0.30074 | 0 | 0
48 | 0.98908 | -0.27108 | 0.13363 | 0.064719
49 | 0.98778 | -0.30617 | 0.11344 | 0.054942
50 | 0.98557 | -0.3231 | 0 | 0
51 | 0.98554 | -0.32327 | 0.1414 | 0.068483
52 | 0.98563 | -0.32272 | 0 | 0
53 | 0.9879 | -0.30032 | 0.14798 | 0.071672
54 | 0.98795 | -0.30077 | 0.07791 | 0.037734
55 | 0.98557 | -0.32282 | 0.065289 | 0.031621
56 | 0.98558 | -0.32275 | 0 | 0
57 | 0.9856 | -0.32287 | 0 | 0
58 | 0.9856 | -0.3229 | 0.13445 | 0.065117
59 | 0.98721 | -0.31552 | 0.069878 | 0.033843
60 | 0.98724 | -0.31521 | 0 | 0
61 | 0.98721 | -0.31546 | 0 | 0
62 | 0.98711 | -0.31834 | 0 | 0
63 | 0.98706 | -0.31908 | 0 | 0
64 | 0.98732 | -0.31418 | 0 | 0
65 | 0.98718 | -0.31525 | 0 | 0
66 | 0.98687 | -0.32147 | 0 | 0
67 | 0.98705 | -0.31901 | 0.10122 | 0.049024
68 | 0.98687 | -0.32146 | 0.075949 | 0.036784
69 | 0.98666 | -0.32748 | 0 | 0
70 | 0.98734 | -0.31393 | 0.15732 | 0.076194
71 | 0.98717 | -0.31513 | 0 | 0
72 | 0.98717 | -0.31532 | 0.1076 | 0.052112
73 | 0.98716 | -0.3151 | 0.10539 | 0.051041
74 | 0.98571 | -0.3234 | 0 | 0
75 | 0.98586 | -0.32458 | 0 | 0
76 | 0.98571 | -0.3234 | 0.071616 | 0.034685
77 | 0.98596 | -0.32375 | 0.11867 | 0.057475
78 | 0.98621 | -0.32436 | 0 | 0
79 | 0.98727 | -0.31054 | 0 | 0
80 | 0.98731 | -0.31091 | 0 | 0
81 | 0.98726 | -0.31046 | 0.16119 | 0.078066
82 | 0.98731 | -0.31094 | 0.098778 | 0.04784
83 | 0.99024 | -0.23682 | 0.094626 | 0.045829
84 | 0.99025 | -0.23689 | 0 | 0
85 | 0.99003 | -0.23827 | 0 | 0
86 | 0.98936 | -0.26755 | 0.69054 | 0.33444
87 | 0.98777 | -0.30626 | 0 | 0
88 | 0.98752 | -0.30946 | 0 | 0
89 | 0.98749 | -0.30978 | 0.14881 | 0.072072
90 | 0.9874 | -0.31026 | 0.11857 | 0.057427
91 | 0.98518 | -0.081609 | 0 | 0
92 | 0.98516 | -0.08142 | 0.40001 | 0.19373
93 | 0.9893 | -0.26832 | 0 | 0
94 | 0.98908 | -0.27097 | 0 | 0
95 | 1 | 0 | -6.8529 | -3.1236
96 | 0.98749 | -0.30983 | 0 | 0
97 | 0.99002 | -0.23819 | 0.14252 | 0.069025
98 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.10596 | -0.051316 | 0.10596 | 0.050534 | 5.4229e-07 | -0.00078244 | 0.0034614 | 0.0034514 | 0.0034614 | 0.98183 | -0.35937 | 0.98183 | -0.35942 | 1.5734
1 | -0.28962 | -0.10271 | 0.28966 | 0.094433 | 3.8886e-05 | -0.0082758 | 0.0090349 | 0.0089564 | 0.0090349 | 0.98183 | -0.35942 | 0.98196 | -0.35972 | 4.1068
2 | 0.18366 | 0.052175 | -0.18361 | -0.077763 | 4.8736e-05 | -0.025588 | 0.0056137 | 0.0058643 | 0.0058643 | 0.98183 | -0.35942 | 0.98158 | -0.35864 | 2.6656
3 | -0.28966 | -0.094433 | 0.28966 | 0.094319 | 5.3166e-07 | -0.00011415 | 0.0089564 | 0.0089554 | 0.0089564 | 0.98196 | -0.35972 | 0.98197 | -0.35972 | 4.0711
4 | 0.084713 | 0.030952 | -0.084709 | -0.040372 | 3.9952e-06 | -0.0094203 | 0.0026524 | 0.0027598 | 0.0027598 | 0.98158 | -0.35864 | 0.98153 | -0.35836 | 1.2545
5 | 0.098902 | 0.046812 | -0.098901 | -0.0479 | 6.5684e-07 | -0.0010881 | 0.003218 | 0.0032318 | 0.0032318 | 0.98158 | -0.35864 | 0.98157 | -0.35859 | 1.469
6 | -0.42283 | -0.15882 | 0.42284 | 0.15879 | 7.4843e-06 | -2.274e-05 | 0.013278 | 0.013278 | 0.013278 | 0.98197 | -0.35972 | 0.98198 | -0.3595 | 6.3229
7 | 0.084709 | 0.040372 | -0.084709 | -0.041026 | 2.9022e-07 | -0.00065447 | 0.0027598 | 0.0027682 | 0.0027682 | 0.98153 | -0.35836 | 0.98153 | -0.35833 | 1.2583
8 | 0.58197 | 0.22968 | -0.58196 | -0.2299 | 4.3198e-06 | -0.00021909 | 0.018389 | 0.018391 | 0.018391 | 0.98217 | -0.35973 | 0.98216 | -0.3597 | 8.3597
9 | -0.72292 | -0.29795 | 0.7231 | 0.29785 | 0.00017685 | -0.00010573 | 0.022982 | 0.022979 | 0.022982 | 0.98217 | -0.35973 | 0.98243 | -0.35717 | 10.9437
10 | 0.58196 | 0.2299 | -0.58195 | -0.23072 | 1.605e-05 | -0.0008135 | 0.018391 | 0.0184 | 0.0184 | 0.98216 | -0.3597 | 0.98214 | -0.35956 | 8.3637
11 | -0.84766 | -0.35818 | 0.85056 | 0.35742 | 0.0028982 | -0.00076031 | 0.02704 | 0.027011 | 0.02704 | 0.98243 | -0.35717 | 0.98604 | -0.32312 | 12.8761
12 | 0.58195 | 0.23072 | -0.58193 | -0.23074 | 1.97e-05 | -2.5265e-05 | 0.0184 | 0.018401 | 0.018401 | 0.98214 | -0.35956 | 0.9821 | -0.35995 | 8.7621
13 | 0.42289 | 0.15372 | -0.42288 | -0.15465 | 9.4973e-06 | -0.00093306 | 0.013226 | 0.013235 | 0.013235 | 0.9821 | -0.35995 | 0.98208 | -0.35987 | 6.0161
14 | 0.53162 | 0.2401 | -0.53158 | -0.24017 | 4.0301e-05 | -6.4765e-05 | 0.017078 | 0.017079 | 0.017079 | 0.98604 | -0.32312 | 0.98596 | -0.32375 | 8.1327
15 | -1.4604 | -0.63538 | 1.4606 | 0.63328 | 0.00027148 | -0.0020926 | 0.046625 | 0.0466 | 0.046625 | 0.98604 | -0.32312 | 0.98621 | -0.32436 | 21.1932
16 | 0.42288 | 0.15465 | -0.42284 | -0.15879 | 4.235e-05 | -0.0041439 | 0.013235 | 0.013278 | 0.013278 | 0.98208 | -0.35987 | 0.98198 | -0.3595 | 6.0354
17 | -0.12989 | -0.06291 | 0.1299 | 0.062808 | 2.8436e-06 | -0.00010173 | 0.0042283 | 0.0042269 | 0.0042283 | 0.98535 | -0.087551 | 0.98538 | -0.087406 | 2.0135
18 | -0.1299 | -0.062808 | 0.1299 | 0.059126 | 3.748e-06 | -0.0036821 | 0.0042269 | 0.0041811 | 0.0042269 | 0.98538 | -0.087406 | 0.9854 | -0.08764 | 1.9213
19 | -0.1299 | -0.059126 | 0.1299 | 0.05868 | 4.4902e-07 | -0.00044651 | 0.0041811 | 0.0041757 | 0.0041811 | 0.9854 | -0.08764 | 0.98541 | -0.087666 | 1.9005
20 | -0.28677 | -0.13466 | 0.28685 | 0.13412 | 7.6868e-05 | -0.00053308 | 0.009281 | 0.0092738 | 0.009281 | 0.98541 | -0.087666 | 0.98569 | -0.085679 | 4.4195
21 | 0.40024 | 0.16999 | -0.40002 | -0.19284 | 0.00021855 | -0.02285 | 0.012735 | 0.013012 | 0.013012 | 0.98569 | -0.085679 | 0.98518 | -0.081609 | 5.9147
22 | -0.68709 | -0.30412 | 0.68713 | 0.30253 | 4.4556e-05 | -0.0015871 | 0.022006 | 0.021987 | 0.022006 | 0.98569 | -0.085679 | 0.98575 | -0.086129 | 10.0025
23 | 0.14071 | 0.065746 | -0.1407 | -0.066695 | 1.0948e-06 | -0.0009497 | 0.0045086 | 0.0045203 | 0.0045203 | 0.9944 | -0.036887 | 0.9944 | -0.036823 | 2.0547
24 | -2.1718 | -0.98975 | 2.1825 | 0.99498 | 0.010723 | 0.0052283 | 0.069286 | 0.069268 | 0.069286 | 0.9944 | -0.036887 | 0.99963 | 0.0029649 | 32.9932
25 | 1.9645 | 0.89173 | -1.955 | -0.88739 | 0.0094672 | 0.0043394 | 0.062629 | 0.062648 | 0.062648 | 0.9944 | -0.036887 | 0.9893 | -0.076463 | 29.8323
26 | 0.1407 | 0.066695 | -0.14066 | -0.068124 | 4.5139e-05 | -0.001429 | 0.0045203 | 0.0045386 | 0.0045386 | 0.9944 | -0.036823 | 0.99406 | -0.039024 | 2.1612
27 | -2.248 | -1.0267 | 2.2489 | 1.0238 | 0.0008819 | -0.0028356 | 0.071367 | 0.07133 | 0.071367 | 0.99963 | 0.0029649 | 1 | 0 | 32.4397
28 | 1.8075 | 0.81596 | -1.8075 | -0.81609 | 2.6859e-05 | -0.00013243 | 0.057868 | 0.057869 | 0.057869 | 0.9893 | -0.076463 | 0.98929 | -0.076354 | 26.3042
29 | -0.14099 | -0.068287 | 0.141 | 0.068105 | 5.9996e-06 | -0.00018185 | 0.0045883 | 0.004586 | 0.0045883 | 0.98563 | -0.088002 | 0.98568 | -0.08772 | 2.1849
30 | 0.68884 | 0.32862 | -0.68873 | -0.33256 | 0.00011476 | -0.0039477 | 0.022352 | 0.022403 | 0.022403 | 0.98568 | -0.08772 | 0.98552 | -0.086297 | 10.183
31 | -0.82984 | -0.39672 | 0.83203 | 0.39612 | 0.0021863 | -0.00059917 | 0.026938 | 0.026913 | 0.026938 | 0.98568 | -0.08772 | 0.98842 | -0.069387 | 12.8277
32 | 0.68873 | 0.33256 | -0.6887 | -0.33355 | 2.8773e-05 | -0.00098675 | 0.022403 | 0.022415 | 0.022415 | 0.98552 | -0.086297 | 0.98549 | -0.085934 | 10.1888
33 | -0.97648 | -0.46609 | 0.9765 | 0.46572 | 2.1145e-05 | -0.00036376 | 0.031601 | 0.031596 | 0.031601 | 0.98842 | -0.069387 | 0.98844 | -0.069569 | 14.364
34 | -0.056532 | -0.02738 | 0.056533 | 0.024299 | 5.8194e-07 | -0.0030809 | 0.0018352 | 0.0017978 | 0.0018352 | 0.98806 | -0.066801 | 0.98807 | -0.06688 | 0.83417
35 | -0.82901 | -0.36658 | 0.82934 | 0.35843 | 0.00032981 | -0.0081466 | 0.026483 | 0.026386 | 0.026483 | 0.98807 | -0.06688 | 0.98844 | -0.069569 | 12.0375
36 | 0.77247 | 0.34228 | -0.77077 | -0.34304 | 0.0017026 | -0.00075542 | 0.024685 | 0.024707 | 0.024707 | 0.98807 | -0.06688 | 0.98575 | -0.086129 | 11.765
37 | -1.8058 | -0.82416 | 1.8075 | 0.81609 | 0.0016401 | -0.0080635 | 0.057972 | 0.057869 | 0.057972 | 0.98844 | -0.069569 | 0.98929 | -0.076354 | 26.3511
38 | 4.3053 | 1.9347 | -4.3051 | -1.9352 | 0.00015263 | -0.00045242 | 0.13748 | 0.13749 | 0.13749 | 0.99109 | -0.23079 | 0.99106 | -0.23126 | 37.9798
39 | -4.4021 | -1.9816 | 4.4028 | 1.9797 | 0.00069633 | -0.001952 | 0.14061 | 0.14058 | 0.14061 | 0.99109 | -0.23079 | 0.99127 | -0.22871 | 38.8433
40 | 4.3051 | 1.9352 | -4.3032 | -1.9409 | 0.0019473 | -0.0057637 | 0.13749 | 0.13757 | 0.13757 | 0.99106 | -0.23126 | 0.99056 | -0.23722 | 38.0035
41 | -4.4028 | -1.9797 | 4.4042 | 1.9811 | 0.0013685 | 0.0014721 | 0.14058 | 0.14058 | 0.14058 | 0.99127 | -0.22871 | 0.99166 | -0.21843 | 40.1667
42 | 3.779 | 1.6984 | -3.7757 | -1.6949 | 0.0033087 | 0.0034799 | 0.12074 | 0.12075 | 0.12075 | 0.99056 | -0.23722 | 0.98947 | -0.26623 | 34.4987
43 | 0.16137 | 0.078074 | -0.16137 | -0.078155 | 3.4631e-06 | -8.123e-05 | 0.0052243 | 0.0052254 | 0.0052254 | 0.99056 | -0.23722 | 0.99054 | -0.23736 | 2.4883
44 | 0.36279 | 0.16447 | -0.36274 | -0.17042 | 4.6033e-05 | -0.0059431 | 0.011608 | 0.011681 | 0.011681 | 0.99056 | -0.23722 | 0.99044 | -0.23623 | 5.3096
45 | -4.5596 | -2.0564 | 4.59 | 2.0892 | 0.030434 | 0.032861 | 0.14561 | 0.14558 | 0.14561 | 0.99166 | -0.21843 | 1 | 0 | 41.6016
46 | 0.36274 | 0.17042 | -0.36273 | -0.17264 | 1.7354e-05 | -0.0022208 | 0.011681 | 0.011709 | 0.011709 | 0.99044 | -0.23623 | 0.9904 | -0.23583 | 5.3222
47 | 0.23721 | 0.11185 | -0.23718 | -0.11222 | 3.4657e-05 | -0.00036779 | 0.0076441 | 0.007649 | 0.007649 | 0.9904 | -0.23583 | 0.99025 | -0.23689 | 3.6424
48 | 3.7757 | 1.6949 | -3.7753 | -1.6964 | 0.00037724 | -0.0015247 | 0.12075 | 0.12077 | 0.12077 | 0.98947 | -0.26623 | 0.98936 | -0.26755 | 33.361
49 | 0.148 | 0.062579 | -0.14799 | -0.070788 | 1.0584e-05 | -0.0082095 | 0.004695 | 0.0047935 | 0.0047935 | 0.98797 | -0.30091 | 0.98791 | -0.30039 | 2.1789
50 | 0.077912 | 0.032768 | -0.07791 | -0.037696 | 1.7624e-06 | -0.0049281 | 0.0024697 | 0.002529 | 0.002529 | 0.98797 | -0.30091 | 0.98795 | -0.30074 | 1.1495
51 | -2.9478 | -1.2998 | 2.9504 | 1.3024 | 0.0026104 | 0.0025917 | 0.094132 | 0.094128 | 0.094132 | 0.98797 | -0.30091 | 0.98908 | -0.27108 | 26.895
52 | 2.7219 | 1.2045 | -2.7214 | -1.2041 | 0.00042595 | 0.00041197 | 0.086969 | 0.08697 | 0.08697 | 0.98797 | -0.30091 | 0.98778 | -0.30617 | 24.8485
53 | 0.14799 | 0.070788 | -0.14798 | -0.071672 | 1.1667e-06 | -0.00088384 | 0.0047935 | 0.0048048 | 0.0048048 | 0.98791 | -0.30039 | 0.9879 | -0.30032 | 2.184
54 | 0.07791 | 0.037696 | -0.07791 | -0.037734 | 3.6523e-07 | -3.711e-05 | 0.002529 | 0.0025295 | 0.0025295 | 0.98795 | -0.30074 | 0.98795 | -0.30077 | 1.2045
55 | -3.084 | -1.3671 | 3.084 | 1.367 | 2.5078e-05 | -0.00016153 | 0.098459 | 0.098457 | 0.098459 | 0.98908 | -0.27108 | 0.98908 | -0.27097 | 27.1985
56 | 2.608 | 1.1491 | -2.608 | -1.1493 | 1.7544e-05 | -0.00016251 | 0.083288 | 0.08329 | 0.08329 | 0.98778 | -0.30617 | 0.98777 | -0.30626 | 23.0084
57 | 0.1414 | 0.068373 | -0.1414 | -0.068483 | 3.6321e-06 | -0.00010938 | 0.0046005 | 0.0046019 | 0.0046019 | 0.98557 | -0.3231 | 0.98554 | -0.32327 | 2.1914
58 | -0.1414 | -0.068373 | 0.14141 | 0.068127 | 8.1745e-06 | -0.00024645 | 0.0046005 | 0.0045973 | 0.0046005 | 0.98557 | -0.3231 | 0.98563 | -0.32272 | 2.1907
59 | -0.34116 | -0.15905 | 0.34119 | 0.15472 | 3.0218e-05 | -0.0043321 | 0.011025 | 0.010971 | 0.011025 | 0.98563 | -0.32272 | 0.98571 | -0.3234 | 5.0111
60 | 0.19975 | 0.090925 | -0.19974 | -0.090991 | 4.3725e-06 | -6.6135e-05 | 0.0064279 | 0.0064287 | 0.0064287 | 0.98563 | -0.32272 | 0.9856 | -0.3229 | 3.0613
61 | -0.065289 | -0.031621 | 0.06529 | 0.031524 | 6.7153e-07 | -9.6443e-05 | 0.0021248 | 0.0021236 | 0.0021248 | 0.98557 | -0.32282 | 0.98558 | -0.32275 | 1.0118
62 | -0.06529 | -0.031524 | 0.065291 | 0.027285 | 1.0734e-06 | -0.0042393 | 0.0021236 | 0.0020726 | 0.0021236 | 0.98558 | -0.32275 | 0.9856 | -0.32287 | 0.96526
63 | -0.065291 | -0.027285 | 0.065291 | 0.025874 | 3.4634e-07 | -0.0014114 | 0.0020726 | 0.002057 | 0.0020726 | 0.9856 | -0.32287 | 0.9856 | -0.3229 | 0.94209
64 | -1.9221 | -0.83438 | 1.9221 | 0.83362 | 4.2847e-05 | -0.00075904 | 0.061272 | 0.061263 | 0.061272 | 0.98721 | -0.31552 | 0.98724 | -0.31521 | 16.926
65 | 0.21299 | 0.097389 | -0.21299 | -0.098 | 1.648e-06 | -0.00061131 | 0.0068484 | 0.0068559 | 0.0068559 | 0.98721 | -0.31552 | 0.98721 | -0.31546 | 3.1163
66 | 1.6392 | 0.70314 | -1.6391 | -0.70306 | 0.00013364 | 8.7323e-05 | 0.052157 | 0.052158 | 0.052158 | 0.98721 | -0.31552 | 0.98711 | -0.31834 | 14.9022
67 | -1.9221 | -0.83362 | 1.9223 | 0.83115 | 0.00013886 | -0.0024619 | 0.061263 | 0.061233 | 0.061263 | 0.98724 | -0.31521 | 0.98732 | -0.31418 | 16.9234
68 | 0.21299 | 0.098 | -0.21299 | -0.10009 | 5.6737e-06 | -0.0020944 | 0.0068559 | 0.0068817 | 0.0068817 | 0.98721 | -0.31546 | 0.98718 | -0.31525 | 3.1281
69 | 1.6391 | 0.70306 | -1.639 | -0.70513 | 8.3754e-05 | -0.0020687 | 0.052158 | 0.052182 | 0.052182 | 0.98711 | -0.31834 | 0.98706 | -0.31908 | 14.415
70 | 1.5378 | 0.65749 | -1.5375 | -0.6647 | 0.00025606 | -0.0072062 | 0.048912 | 0.048998 | 0.048998 | 0.98706 | -0.31908 | 0.98687 | -0.32147 | 13.5353
71 | 0.10122 | 0.047633 | -0.10122 | -0.049024 | 8.5897e-07 | -0.0013905 | 0.0032718 | 0.0032893 | 0.0032893 | 0.98706 | -0.31908 | 0.98705 | -0.31901 | 1.4951
72 | -1.9223 | -0.83115 | 1.9223 | 0.83055 | 3.43e-05 | -0.00060854 | 0.061233 | 0.061226 | 0.061233 | 0.98732 | -0.31418 | 0.98734 | -0.31393 | 16.9152
73 | 0.10539 | 0.048043 | -0.10539 | -0.050513 | 1.6406e-06 | -0.00247 | 0.0033869 | 0.0034175 | 0.0034175 | 0.98718 | -0.31525 | 0.98717 | -0.31513 | 1.5534
74 | 0.1076 | 0.052051 | -0.1076 | -0.052112 | 1.1486e-06 | -6.0656e-05 | 0.0034953 | 0.0034961 | 0.0034961 | 0.98718 | -0.31525 | 0.98717 | -0.31532 | 1.6648
75 | 0.075949 | 0.036685 | -0.075949 | -0.036784 | 3.4677e-08 | -9.9142e-05 | 0.0024672 | 0.0024685 | 0.0024685 | 0.98687 | -0.32147 | 0.98687 | -0.32146 | 1.122
76 | 1.4616 | 0.62801 | -1.4613 | -0.62788 | 0.00025437 | 0.00013437 | 0.046533 | 0.046535 | 0.046535 | 0.98687 | -0.32147 | 0.98666 | -0.32748 | 13.2956
77 | 1.4613 | 0.62788 | -1.4606 | -0.63328 | 0.00069944 | -0.0054057 | 0.046535 | 0.0466 | 0.0466 | 0.98666 | -0.32748 | 0.98621 | -0.32436 | 21.1817
78 | -2.0796 | -0.90674 | 2.0799 | 0.90695 | 0.00025013 | 0.00021022 | 0.066332 | 0.066331 | 0.066332 | 0.98734 | -0.31393 | 0.98749 | -0.30983 | 18.952
79 | 0.10539 | 0.050513 | -0.10539 | -0.051041 | 3.5445e-07 | -0.00052779 | 0.0034175 | 0.0034242 | 0.0034242 | 0.98717 | -0.31513 | 0.98716 | -0.3151 | 1.5565
80 | -0.4128 | -0.18931 | 0.41287 | 0.18281 | 6.5998e-05 | -0.0065035 | 0.0133 | 0.013222 | 0.0133 | 0.98571 | -0.3234 | 0.98586 | -0.32458 | 6.0455
81 | 0.071616 | 0.034593 | -0.071616 | -0.034685 | 2.8642e-08 | -9.1788e-05 | 0.0023292 | 0.0023304 | 0.0023304 | 0.98571 | -0.3234 | 0.98571 | -0.3234 | 1.0593
82 | -0.41287 | -0.18281 | 0.41291 | 0.18269 | 3.8547e-05 | -0.00011949 | 0.013222 | 0.01322 | 0.013222 | 0.98586 | -0.32458 | 0.98596 | -0.32375 | 6.296
83 | -0.16119 | -0.077152 | 0.1612 | 0.072236 | 7.6131e-06 | -0.0049163 | 0.0052252 | 0.0051647 | 0.0052252 | 0.98727 | -0.31054 | 0.98731 | -0.31091 | 2.3751
84 | 0.16119 | 0.077152 | -0.16119 | -0.078066 | 1.4347e-06 | -0.00091359 | 0.0052252 | 0.0052368 | 0.0052368 | 0.98727 | -0.31054 | 0.98726 | -0.31046 | 2.3804
85 | -0.1612 | -0.072236 | 0.1612 | 0.071781 | 6.9631e-07 | -0.00045536 | 0.0051647 | 0.0051593 | 0.0051647 | 0.98731 | -0.31091 | 0.98731 | -0.31094 | 2.3476
86 | -0.25997 | -0.11962 | 0.26 | 0.11942 | 2.2531e-05 | -0.00019616 | 0.0083673 | 0.0083647 | 0.0083673 | 0.98731 | -0.31094 | 0.9874 | -0.31026 | 3.9844
87 | -0.23717 | -0.1128 | 0.23718 | 0.11222 | 1.943e-06 | -0.00058127 | 0.0076563 | 0.007649 | 0.0076563 | 0.99024 | -0.23682 | 0.99025 | -0.23689 | 3.4801
88 | 0.14255 | 0.066968 | -0.14252 | -0.067847 | 2.8835e-05 | -0.00087827 | 0.0045913 | 0.0046025 | 0.0046025 | 0.99024 | -0.23682 | 0.99003 | -0.23827 | 2.1917
89 | 0.14252 | 0.067847 | -0.14252 | -0.069025 | 1.4292e-06 | -0.0011785 | 0.0046025 | 0.0046174 | 0.0046174 | 0.99003 | -0.23827 | 0.99002 | -0.23819 | 2.0988
90 | 3.0848 | 1.362 | -3.0846 | -1.3631 | 0.00017381 | -0.0011217 | 0.098391 | 0.098406 | 0.098406 | 0.98936 | -0.26755 | 0.9893 | -0.26832 | 27.1839
91 | 2.608 | 1.1493 | -2.6074 | -1.1549 | 0.0006106 | -0.0056491 | 0.08329 | 0.083362 | 0.083362 | 0.98777 | -0.30626 | 0.98752 | -0.30946 | 23.0283
92 | 2.2288 | 0.97824 | -2.2287 | -0.97891 | 5.2155e-05 | -0.00067557 | 0.071151 | 0.07116 | 0.07116 | 0.98752 | -0.30946 | 0.98749 | -0.30978 | 19.6574
93 | 0.37861 | 0.1767 | -0.37857 | -0.17685 | 4.0254e-05 | -0.00015106 | 0.012214 | 0.012216 | 0.012216 | 0.98752 | -0.30946 | 0.9874 | -0.31026 | 5.8171
94 | 2.0799 | 0.90684 | -2.0799 | -0.90695 | 7.3655e-06 | -0.0001106 | 0.06633 | 0.066331 | 0.066331 | 0.98749 | -0.30978 | 0.98749 | -0.30983 | 18.3235
95 | 0.40002 | 0.19284 | -0.40001 | -0.19373 | 8.7224e-06 | -0.00089083 | 0.013012 | 0.013024 | 0.013024 | 0.98518 | -0.081609 | 0.98516 | -0.08142 | 5.9198
96 | 3.0846 | 1.3631 | -3.084 | -1.367 | 0.00060135 | -0.0038767 | 0.098406 | 0.098457 | 0.098457 | 0.9893 | -0.26832 | 0.98908 | -0.27097 | 27.1979

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 6.8529 | 3.1236

## res_load
| p_mw | q_mvar
0 | 0.10596 | 0.051316
1 | 0.13317 | 0.064498
2 | 0.098901 | 0.0479
3 | 0.084709 | 0.041026
4 | 0.14096 | 0.068268
5 | 0.12457 | 0.06033
6 | 0.15904 | 0.077025
7 | 0.078171 | 0.03786
8 | 0.12989 | 0.06291
9 | 0.15687 | 0.075976
10 | 0.066633 | 0.032272
11 | 0.065449 | 0.031698
12 | 0.14749 | 0.071431
13 | 0.14066 | 0.068124
14 | 0.14099 | 0.068287
15 | 0.14446 | 0.069963
16 | 0.6887 | 0.33355
17 | 0.056532 | 0.02738
18 | 0.083639 | 0.040508
19 | 0.096839 | 0.046901
20 | 0.15536 | 0.075247
21 | 0.12552 | 0.06079
22 | 0.16137 | 0.078155
23 | 0.13363 | 0.064719
24 | 0.11344 | 0.054942
25 | 0.1414 | 0.068483
26 | 0.14798 | 0.071672
27 | 0.07791 | 0.037734
28 | 0.065289 | 0.031621
29 | 0.13445 | 0.065117
30 | 0.069878 | 0.033843
31 | 0.10122 | 0.049024
32 | 0.075949 | 0.036784
33 | 0.15732 | 0.076194
34 | 0.1076 | 0.052112
35 | 0.10539 | 0.051041
36 | 0.071616 | 0.034685
37 | 0.11867 | 0.057475
38 | 0.16119 | 0.078066
39 | 0.098778 | 0.04784
40 | 0.094626 | 0.045829
41 | 0.69054 | 0.33444
42 | 0.14881 | 0.072072
43 | 0.11857 | 0.057427
44 | 0.40001 | 0.19373
45 | 0.14252 | 0.069025

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1