## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_440_1_node_128 | 20 | n |  | TRUE
1 | bus_MV_440_1_node_127 | 20 | n |  | TRUE
2 | bus_MV_440_1_node_132 | 20 | n |  | TRUE
3 | bus_MV_440_1_node_129 | 20 | n |  | TRUE
4 | bus_MV_440_1_node_135 | 20 | n |  | TRUE
5 | bus_MV_440_1_node_131 | 20 | n |  | TRUE
6 | bus_MV_440_1_node_130 | 20 | n |  | TRUE
7 | bus_MV_440_1_node_184 | 20 | n |  | TRUE
8 | bus_MV_440_1_node_183 | 20 | n |  | TRUE
9 | bus_MV_440_1_node_194 | 20 | n |  | TRUE
10 | bus_MV_440_1_node_227 | 20 | n |  | TRUE
11 | bus_MV_440_1_node_133 | 20 | n |  | TRUE
12 | bus_MV_440_1_node_134 | 20 | n |  | TRUE
13 | bus_MV_440_1_node_191 | 20 | n |  | TRUE
14 | bus_MV_440_1_node_141 | 20 | n |  | TRUE
15 | bus_MV_440_1_node_136 | 20 | n |  | TRUE
16 | bus_MV_440_1_node_185 | 20 | n |  | TRUE
17 | bus_MV_440_1_node_186 | 20 | n |  | TRUE
18 | bus_MV_440_1_node_137 | 20 | n |  | TRUE
19 | bus_MV_440_1_node_138 | 20 | n |  | TRUE
20 | bus_MV_440_1_node_139 | 20 | n |  | TRUE
21 | bus_MV_440_1_node_140 | 20 | n |  | TRUE
22 | bus_MV_440_1_node_180 | 20 | n |  | TRUE
23 | bus_MV_440_1_node_142 | 20 | n |  | TRUE
24 | bus_MV_440_1_node_123 | 20 | n |  | TRUE
25 | bus_MV_440_1_node_143 | 20 | n |  | TRUE
26 | bus_MV_440_1_node_144 | 20 | n |  | TRUE
27 | bus_MV_440_1_node_125 | 20 | n |  | TRUE
28 | bus_MV_440_1_node_145 | 20 | n |  | TRUE
29 | bus_MV_440_1_node_113 | 20 | n |  | TRUE
30 | bus_MV_440_1_node_146 | 20 | n |  | TRUE
31 | bus_MV_440_1_node_147 | 20 | n |  | TRUE
32 | bus_MV_440_1_node_148 | 20 | n |  | TRUE
33 | bus_MV_440_1_node_189 | 20 | n |  | TRUE
34 | bus_MV_440_1_node_210 | 20 | n |  | TRUE
35 | bus_MV_440_1_node_211 | 20 | n |  | TRUE
36 | bus_MV_440_1_node_150 | 20 | n |  | TRUE
37 | bus_MV_440_1_node_116 | 20 | n |  | TRUE
38 | bus_MV_440_1_node_151 | 20 | n |  | TRUE
39 | bus_MV_440_1_node_152 | 20 | n |  | TRUE
40 | bus_MV_440_1_node_117 | 20 | n |  | TRUE
41 | bus_MV_440_1_node_153 | 20 | n |  | TRUE
42 | bus_MV_440_1_node_120 | 20 | n |  | TRUE
43 | bus_MV_440_1_node_154 | 20 | n |  | TRUE
44 | bus_MV_440_1_node_200 | 20 | n |  | TRUE
45 | bus_MV_440_1_node_181 | 20 | n |  | TRUE
46 | bus_MV_440_1_node_182 | 20 | n |  | TRUE
47 | bus_MV_440_1_node_212 | 20 | n |  | TRUE
48 | bus_MV_440_1_node_193 | 20 | n |  | TRUE
49 | bus_MV_440_1_node_221 | 20 | n |  | TRUE
50 | bus_MV_440_1_node_201 | 20 | n |  | TRUE
51 | bus_MV_440_1_node_187 | 20 | n |  | TRUE
52 | bus_MV_440_1_node_122 | 20 | n |  | TRUE
53 | bus_MV_440_1_node_188 | 20 | n |  | TRUE
54 | bus_MV_440_1_node_190 | 20 | n |  | TRUE
55 | bus_MV_440_1_node_192 | 20 | n |  | TRUE
56 | bus_MV_440_1_node_195 | 20 | n |  | TRUE
57 | bus_MV_440_1_node_196 | 20 | n |  | TRUE
58 | bus_MV_440_1_node_197 | 20 | n |  | TRUE
59 | bus_MV_440_1_node_198 | 20 | n |  | TRUE
60 | bus_MV_440_1_node_226 | 20 | n |  | TRUE
61 | bus_MV_440_1_node_223 | 20 | n |  | TRUE
62 | bus_MV_440_1_node_199 | 20 | n |  | TRUE
63 | bus_MV_440_1_node_118 | 20 | n |  | TRUE
64 | bus_MV_440_1_node_124 | 20 | n |  | TRUE
65 | bus_MV_440_1_node_203 | 20 | n |  | TRUE
66 | bus_MV_440_1_node_225 | 20 | n |  | TRUE
67 | bus_MV_440_1_node_215 | 20 | n |  | TRUE
68 | bus_MV_440_1_node_119 | 20 | n |  | TRUE
69 | bus_MV_440_1_node_224 | 20 | n |  | TRUE
70 | bus_MV_440_1_node_126 | 20 | n |  | TRUE
71 | bus_MV_440_1_node_115 | 20 | n |  | TRUE
72 | bus_HV_440_1_node_115 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_440_1_load_127 | 1 | 0.24065 | 0.11655 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_440_1_load_135 | 4 | 0.073037 | 0.035374 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_440_1_load_183 | 8 | 0.33271 | 0.16114 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_440_1_load_194 | 9 | 0.097683 | 0.04731 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_440_1_load_227 | 10 | 0.29954 | 0.14507 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_440_1_load_191 | 13 | 0.091247 | 0.044193 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_440_1_load_141 | 14 | 0.32533 | 0.15756 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_440_1_load_137 | 18 | 0.27292 | 0.13218 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_440_1_load_180 | 22 | 0.25869 | 0.12529 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_440_1_load_143 | 25 | 0.30342 | 0.14695 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_440_1_load_144 | 26 | 0.37832 | 0.18323 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_440_1_load_145 | 28 | 0.19643 | 0.095137 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_440_1_load_113 | 29 | 0.32284 | 0.15636 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_440_1_load_189 | 33 | 0.068309 | 0.033084 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_440_1_load_210 | 34 | 0.39207 | 0.18989 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_440_1_load_150 | 36 | 0.24226 | 0.11733 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_440_1_load_151 | 38 | 0.24871 | 0.12045 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_440_1_load_152 | 39 | 0.34446 | 0.16683 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_440_1_load_200 | 44 | 0.15754 | 0.076301 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_440_1_load_212 | 47 | 0.34934 | 0.16919 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_440_1_load_193 | 48 | 0.10986 | 0.053206 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_440_1_load_221 | 49 | 0.36926 | 0.17884 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_440_1_load_201 | 50 | 0.34996 | 0.1695 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_440_1_load_187 | 51 | 0.074887 | 0.036269 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_440_1_load_188 | 53 | 0.40698 | 0.19711 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_440_1_load_190 | 54 | 0.20489 | 0.099234 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_440_1_load_192 | 55 | 0.072288 | 0.035011 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_440_1_load_195 | 56 | 0.18804 | 0.091073 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_440_1_load_196 | 57 | 0.14633 | 0.070869 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_440_1_load_226 | 60 | 0.073047 | 0.035378 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_440_1_load_199 | 62 | 0.19625 | 0.09505 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_440_1_load_203 | 65 | 0.31614 | 0.15311 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_440_1_load_225 | 66 | 0.10883 | 0.052711 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_440_1_load_215 | 67 | 0.10711 | 0.051878 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_440_1_load_224 | 69 | 0.20981 | 0.10162 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 71 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_440_1_line_0 |  | 0 | 1 | 0.034849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_440_1_line_1 |  | 0 | 2 | 0.52597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_440_1_line_2 |  | 2 | 10 | 0.012718 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_440_1_line_3 |  | 2 | 11 | 0.14705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_440_1_line_4 |  | 2 | 12 | 0.58709 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_440_1_line_5 |  | 2 | 5 | 0.22141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_440_1_line_6 |  | 2 | 6 | 0.092913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_440_1_line_7 |  | 3 | 4 | 0.012526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_440_1_line_8 |  | 3 | 5 | 0.10378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_440_1_line_9 |  | 4 | 15 | 0.047999 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_440_1_line_10 |  | 5 | 9 | 0.012591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_440_1_line_11 |  | 6 | 7 | 0.20316 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_440_1_line_12 |  | 6 | 8 | 0.017735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_440_1_line_13 |  | 7 | 48 | 0.07764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_440_1_line_14 |  | 8 | 20 | 0.013786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_440_1_line_15 |  | 9 | 56 | 0.032564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_440_1_line_16 |  | 11 | 13 | 0.0099288 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_440_1_line_17 |  | 12 | 14 | 0.019627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_440_1_line_18 |  | 13 | 55 | 0.0038493 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_440_1_line_19 |  | 14 | 23 | 0.013638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_440_1_line_20 |  | 15 | 16 | 0.13402 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_440_1_line_21 |  | 15 | 17 | 0.38134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_440_1_line_22 |  | 16 | 49 | 0.01496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_440_1_line_23 |  | 17 | 50 | 0.0123 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_440_1_line_24 |  | 18 | 19 | 0.009726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_440_1_line_25 |  | 19 | 20 | 0.01771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_440_1_line_26 |  | 20 | 21 | 0.071932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_440_1_line_27 |  | 21 | 22 | 0.032528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_440_1_line_28 |  | 22 | 45 | 0.0046137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_440_1_line_29 |  | 23 | 24 | 0.19253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_440_1_line_30 |  | 24 | 70 | 0.2553 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_440_1_line_31 |  | 24 | 25 | 0.023608 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_440_1_line_32 |  | 26 | 27 | 0.004696 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_440_1_line_33 |  | 27 | 64 | 0.41957 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_440_1_line_34 |  | 27 | 71 | 0.43974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_440_1_line_35 |  | 28 | 29 | 0.47173 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_440_1_line_36 |  | 28 | 30 | 0.015217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_440_1_line_37 |  | 29 | 71 | 0.004747 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_440_1_line_38 |  | 29 | 65 | 0.2232 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_440_1_line_39 |  | 30 | 31 | 0.35983 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_440_1_line_40 |  | 30 | 32 | 0.22124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_440_1_line_41 |  | 31 | 33 | 0.059183 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_440_1_line_42 |  | 32 | 34 | 0.005626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_440_1_line_43 |  | 32 | 35 | 0.36542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_440_1_line_44 |  | 35 | 66 | 0.010498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_440_1_line_45 |  | 36 | 37 | 0.039341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_440_1_line_46 |  | 36 | 38 | 0.056386 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_440_1_line_47 |  | 37 | 68 | 0.53127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_440_1_line_48 |  | 37 | 39 | 0.2989 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_440_1_line_49 |  | 39 | 40 | 0.13048 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_440_1_line_50 |  | 39 | 41 | 0.060869 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_440_1_line_51 |  | 40 | 54 | 0.028526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_440_1_line_52 |  | 41 | 42 | 0.14884 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_440_1_line_53 |  | 41 | 43 | 0.36471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_440_1_line_54 |  | 42 | 53 | 0.0040115 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_440_1_line_55 |  | 43 | 44 | 0.017923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_440_1_line_56 |  | 44 | 64 | 0.0776 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_440_1_line_57 |  | 45 | 46 | 0.14464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_440_1_line_58 |  | 46 | 47 | 0.010858 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_440_1_line_59 |  | 47 | 61 | 0.034425 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_440_1_line_60 |  | 51 | 52 | 0.057165 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_440_1_line_61 |  | 52 | 71 | 0.51583 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_440_1_line_62 |  | 57 | 58 | 0.0041865 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_440_1_line_63 |  | 58 | 59 | 0.12827 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_440_1_line_64 |  | 59 | 60 | 0.003954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_440_1_line_65 |  | 59 | 61 | 0.007631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_440_1_line_66 |  | 62 | 63 | 0.026338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_440_1_line_67 |  | 63 | 68 | 0.13319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_440_1_line_68 |  | 67 | 68 | 0.05492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_440_1_line_69 |  | 69 | 70 | 0.020954 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_440_1_line_70 |  | 70 | 71 | 0.42949 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_440_1_trafo_115 | 25 MVA 110/20 kV | 72 | 71 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2709657.7301 | 1268117.941
1 | 2709681.152 | 1268143.8093
2 | 2709693.5664 | 1268246.7183
3 | 2709606.7289 | 1268166.8374
4 | 2709594.4988 | 1268169.5434
5 | 2709645.8192 | 1268241.6389
6 | 2709643.7782 | 1268316.2772
7 | 2709556.0696 | 1268345.8429
8 | 2709632.0979 | 1268329.6222
9 | 2709637.6613 | 1268251.2292
10 | 2709683.7962 | 1268238.541
11 | 2709677.2651 | 1268299.5507
12 | 2709876.0004 | 1268362.5976
13 | 2709684.866 | 1268305.9388
14 | 2709863.4558 | 1268377.722
15 | 2709548.4409 | 1268173.5625
16 | 2709508.9216 | 1268120.9842
17 | 2709407.3988 | 1267954.6034
18 | 2709643.082 | 1268341.1971
19 | 2709638.3993 | 1268349.7288
20 | 2709623.4644 | 1268340.3658
21 | 2709634.236 | 1268397.5821
22 | 2709656.6959 | 1268421.1108
23 | 2709857.7857 | 1268389.9384
24 | 2709993.0145 | 1268410.7611
25 | 2709976.1592 | 1268427.3396
26 | 2709695.3157 | 1268807.2955
27 | 2709696.4883 | 1268811.8435
28 | 2710420.791 | 1268984.3079
29 | 2710007.3678 | 1268757.1198
30 | 2710428.074 | 1268971.2103
31 | 2710439.8975 | 1269264.6108
32 | 2710583.4174 | 1269098.4272
33 | 2710411.4061 | 1269218.2633
34 | 2710587.2951 | 1269094.3407
35 | 2710825.4554 | 1269303.1198
36 | 2710235.5109 | 1269367.0615
37 | 2710198.769 | 1269352.7524
38 | 2710288.8291 | 1269385.408
39 | 2709938.1434 | 1269206.4174
40 | 2710068.4468 | 1269213.2787
41 | 2709907.6689 | 1269259.0925
42 | 2710048.7972 | 1269306.372
43 | 2709708.5424 | 1269164.4866
44 | 2709719.7647 | 1269150.5296
45 | 2709659.8816 | 1268424.4481
46 | 2709729.1819 | 1268466.6714
47 | 2709736.523 | 1268474.6925
48 | 2709544.5529 | 1268308.1691
49 | 2709521.275 | 1268112.4946
50 | 2709412.0964 | 1267943.2361
51 | 2709858.2806 | 1268897.3947
52 | 2709860.5683 | 1268951.97
53 | 2710047.8718 | 1269310.2753
54 | 2710066.0063 | 1269237.8534
55 | 2709687.8109 | 1268308.4177
56 | 2709645.2898 | 1268275.8255
57 | 2709840.6406 | 1268582.0018
58 | 2709837.7141 | 1268579.0081
59 | 2709771.314 | 1268497.9256
60 | 2709774.0841 | 1268495.0969
61 | 2709766.0573 | 1268492.3787
62 | 2710430.4188 | 1269543.1686
63 | 2710451.429 | 1269559.0515
64 | 2709756.2007 | 1269084.4684
65 | 2710213.6806 | 1268842.2834
66 | 2710835.8062 | 1269305.049
67 | 2710453.9968 | 1269690.1036
68 | 2710484.267 | 1269649.5339
69 | 2710041.334 | 1268568.8098
70 | 2710021.3011 | 1268574.9533
71 | 2710004.6009 | 1268760.9827
72 | 2710004.6009 | 1268760.9827

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99406 | 0.030818 | 0 | 0
1 | 0.99405 | 0.030919 | 0.24065 | 0.11655
2 | 0.99422 | 0.029524 | 0 | 0
3 | 0.99381 | 0.033022 | 0 | 0
4 | 0.9938 | 0.033131 | 0.073037 | 0.035374
5 | 0.99392 | 0.032127 | 0 | 0
6 | 0.99404 | 0.031147 | 0 | 0
7 | 0.99401 | 0.031362 | 0 | 0
8 | 0.99401 | 0.031442 | 0.33271 | 0.16114
9 | 0.99391 | 0.03217 | 0.097683 | 0.04731
10 | 0.99422 | 0.02957 | 0.29954 | 0.14507
11 | 0.99419 | 0.029796 | 0 | 0
12 | 0.99671 | 0.0084828 | 0 | 0
13 | 0.99419 | 0.029815 | 0.091247 | 0.044193
14 | 0.99679 | 0.0077902 | 0.32533 | 0.15756
15 | 0.99376 | 0.033508 | 0 | 0
16 | 0.99369 | 0.034091 | 0 | 0
17 | 0.99359 | 0.035014 | 0 | 0
18 | 0.99398 | 0.031707 | 0.27292 | 0.13218
19 | 0.99398 | 0.031675 | 0 | 0
20 | 0.99399 | 0.031617 | 0 | 0
21 | 0.99391 | 0.032296 | 0 | 0
22 | 0.99388 | 0.032607 | 0.25869 | 0.12529
23 | 0.99685 | 0.007256 | 0 | 0
24 | 0.99775 | -0.00024837 | 0 | 0
25 | 0.99774 | -0.00016271 | 0.30342 | 0.14695
26 | 0.99872 | 0.010728 | 0.37832 | 0.18323
27 | 0.99872 | 0.010706 | 0 | 0
28 | 0.9993 | -0.0053007 | 0.19643 | 0.095137
29 | 0.99999 | 7.2078e-05 | 0.32284 | 0.15636
30 | 0.99929 | -0.0052208 | 0 | 0
31 | 0.99926 | -0.0050572 | 0 | 0
32 | 0.99915 | -0.0040585 | 0 | 0
33 | 0.99926 | -0.0050114 | 0.068309 | 0.033084
34 | 0.99915 | -0.0040321 | 0.39207 | 0.18989
35 | 0.9991 | -0.0036894 | 0 | 0
36 | 0.99608 | 0.026128 | 0.24226 | 0.11733
37 | 0.99611 | 0.025897 | 0 | 0
38 | 0.99605 | 0.025958 | 0.24871 | 0.12045
39 | 0.99656 | 0.02927 | 0.34446 | 0.16683
40 | 0.99651 | 0.028937 | 0 | 0
41 | 0.99667 | 0.028365 | 0 | 0
42 | 0.99655 | 0.027626 | 0 | 0
43 | 0.99748 | 0.021284 | 0 | 0
44 | 0.99752 | 0.020941 | 0.15754 | 0.076301
45 | 0.99387 | 0.032636 | 0 | 0
46 | 0.99377 | 0.033582 | 0 | 0
47 | 0.99376 | 0.033654 | 0.34934 | 0.16919
48 | 0.994 | 0.031461 | 0.10986 | 0.053206
49 | 0.99369 | 0.034158 | 0.36926 | 0.17884
50 | 0.99358 | 0.034962 | 0.34996 | 0.1695
51 | 0.99995 | 0.00026357 | 0.074887 | 0.036269
52 | 0.99995 | 0.00021483 | 0 | 0
53 | 0.99655 | 0.027645 | 0.40698 | 0.19711
54 | 0.9965 | 0.029006 | 0.20489 | 0.099234
55 | 0.99419 | 0.029819 | 0.072288 | 0.035011
56 | 0.99391 | 0.032243 | 0.18804 | 0.091073
57 | 0.99372 | 0.033792 | 0.14633 | 0.070869
58 | 0.99372 | 0.033785 | 0 | 0
59 | 0.99374 | 0.033571 | 0 | 0
60 | 0.99374 | 0.033574 | 0.073047 | 0.035378
61 | 0.99375 | 0.033552 | 0 | 0
62 | 0.99586 | 0.027811 | 0.19625 | 0.09505
63 | 0.99587 | 0.027749 | 0 | 0
64 | 0.99771 | 0.019317 | 0 | 0
65 | 0.99986 | -0.00078324 | 0.31614 | 0.15311
66 | 0.9991 | -0.0036757 | 0.10883 | 0.052711
67 | 0.99589 | 0.027521 | 0.10711 | 0.051878
68 | 0.9959 | 0.027453 | 0 | 0
69 | 0.99903 | -0.011065 | 0.20981 | 0.10162
70 | 0.99903 | -0.011012 | 0 | 0
71 | 1 | 0 | -7.975 | -3.6692
72 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.24065 | 0.11573 | -0.24065 | -0.11655 | 2.8013e-06 | -0.00082137 | 0.0077545 | 0.0077649 | 0.0077649 | 0.99406 | 0.030818 | 0.99405 | 0.030919 | 3.5295
1 | -0.24065 | -0.11573 | 0.24069 | 0.10333 | 4.1396e-05 | -0.012399 | 0.0077545 | 0.0076053 | 0.0077545 | 0.99406 | 0.030818 | 0.99422 | 0.029524 | 3.5248
2 | 0.29954 | 0.14478 | -0.29954 | -0.14507 | 1.585e-06 | -0.00029969 | 0.0096599 | 0.0096637 | 0.0096637 | 0.99422 | 0.029524 | 0.99422 | 0.02957 | 4.3926
3 | 0.16354 | 0.07541 | -0.16354 | -0.078879 | 5.4113e-06 | -0.0034688 | 0.005229 | 0.0052719 | 0.0052719 | 0.99422 | 0.029524 | 0.99419 | 0.029796 | 2.3963
4 | -3.3258 | -1.5506 | 3.3347 | 1.5394 | 0.0088832 | -0.011256 | 0.10655 | 0.10638 | 0.10655 | 0.99422 | 0.029524 | 0.99671 | 0.0084828 | 48.43
5 | 1.0786 | 0.49959 | -1.0782 | -0.50471 | 0.00035273 | -0.0051192 | 0.034513 | 0.034577 | 0.034577 | 0.99422 | 0.029524 | 0.99392 | 0.032127 | 15.7168
6 | 1.5435 | 0.72755 | -1.5432 | -0.72965 | 0.00030463 | -0.0021021 | 0.049544 | 0.049571 | 0.049571 | 0.99422 | 0.029524 | 0.99404 | 0.031147 | 22.5324
7 | 0.7924 | 0.36981 | -0.79239 | -0.3701 | 1.079e-05 | -0.00029218 | 0.0254 | 0.025404 | 0.025404 | 0.99381 | 0.033022 | 0.9938 | 0.033131 | 11.5472
8 | -0.7924 | -0.36981 | 0.79249 | 0.36739 | 8.9283e-05 | -0.0024211 | 0.0254 | 0.02537 | 0.0254 | 0.99381 | 0.033022 | 0.99392 | 0.032127 | 11.5456
9 | 0.71935 | 0.33473 | -0.71932 | -0.33585 | 3.4056e-05 | -0.0011217 | 0.023047 | 0.023061 | 0.023061 | 0.9938 | 0.033131 | 0.99376 | 0.033508 | 10.4822
10 | 0.28573 | 0.13732 | -0.28573 | -0.13762 | 1.4255e-06 | -0.00029655 | 0.0092073 | 0.0092111 | 0.0092111 | 0.99392 | 0.032127 | 0.99391 | 0.03217 | 4.1869
11 | 0.10986 | 0.046583 | -0.10986 | -0.051375 | 3.3095e-06 | -0.004792 | 0.0034654 | 0.0035221 | 0.0035221 | 0.99404 | 0.031147 | 0.99401 | 0.031362 | 1.6009
12 | 1.4333 | 0.68306 | -1.4332 | -0.68347 | 5.0341e-05 | -0.00040346 | 0.046109 | 0.046114 | 0.046114 | 0.99404 | 0.031147 | 0.99401 | 0.031442 | 20.961
13 | 0.10986 | 0.051375 | -0.10986 | -0.053206 | 1.2941e-06 | -0.0018312 | 0.0035221 | 0.0035449 | 0.0035449 | 0.99401 | 0.031362 | 0.994 | 0.031461 | 1.6113
14 | 1.1005 | 0.52233 | -1.1005 | -0.52265 | 2.3038e-05 | -0.00031839 | 0.035378 | 0.035382 | 0.035382 | 0.99401 | 0.031442 | 0.99399 | 0.031617 | 16.0829
15 | 0.18804 | 0.090305 | -0.18804 | -0.091073 | 1.5983e-06 | -0.00076758 | 0.0060587 | 0.0060684 | 0.0060684 | 0.99391 | 0.03217 | 0.99391 | 0.032243 | 2.7584
16 | 0.16354 | 0.078879 | -0.16354 | -0.079113 | 3.6859e-07 | -0.00023421 | 0.0052719 | 0.0052749 | 0.0052749 | 0.99419 | 0.029796 | 0.99419 | 0.029815 | 2.3977
17 | -3.3347 | -1.5394 | 3.335 | 1.539 | 0.00029649 | -0.00037763 | 0.10638 | 0.10637 | 0.10638 | 0.99671 | 0.0084828 | 0.99679 | 0.0077902 | 48.353
18 | 0.072288 | 0.03492 | -0.072288 | -0.035011 | 2.7933e-08 | -9.0834e-05 | 0.0023311 | 0.0023322 | 0.0023322 | 0.99419 | 0.029815 | 0.99419 | 0.029819 | 1.0601
19 | -3.6603 | -1.6966 | 3.6606 | 1.6963 | 0.00024853 | -0.00024983 | 0.11684 | 0.11683 | 0.11684 | 0.99679 | 0.0077902 | 0.99685 | 0.007256 | 53.1081
20 | 0.36929 | 0.17534 | -0.36926 | -0.17849 | 2.5315e-05 | -0.0031523 | 0.011875 | 0.011915 | 0.011915 | 0.99376 | 0.033508 | 0.99369 | 0.034091 | 5.4158
21 | 0.35003 | 0.16051 | -0.34997 | -0.16948 | 6.433e-05 | -0.0089709 | 0.011186 | 0.011297 | 0.011297 | 0.99376 | 0.033508 | 0.99359 | 0.035014 | 5.1352
22 | 0.36926 | 0.17849 | -0.36926 | -0.17884 | 2.8363e-06 | -0.00035185 | 0.011915 | 0.011919 | 0.011919 | 0.99369 | 0.034091 | 0.99369 | 0.034158 | 5.4179
23 | 0.34997 | 0.16948 | -0.34996 | -0.1695 | 2.7971e-06 | -1.2744e-05 | 0.011297 | 0.011298 | 0.011298 | 0.99359 | 0.035014 | 0.99358 | 0.034962 | 5.3798
24 | -0.27292 | -0.13218 | 0.27292 | 0.13195 | 1.0068e-06 | -0.00022913 | 0.008807 | 0.0088041 | 0.008807 | 0.99398 | 0.031707 | 0.99398 | 0.031675 | 4.0032
25 | -0.27292 | -0.13195 | 0.27292 | 0.13154 | 1.8315e-06 | -0.00041722 | 0.0088041 | 0.0087988 | 0.0088041 | 0.99398 | 0.031675 | 0.99399 | 0.031617 | 4.0019
26 | 0.82759 | 0.39111 | -0.82752 | -0.39279 | 6.7917e-05 | -0.0016766 | 0.026584 | 0.026605 | 0.026605 | 0.99399 | 0.031617 | 0.99391 | 0.032296 | 12.0931
27 | 0.82752 | 0.39279 | -0.82749 | -0.39354 | 3.0748e-05 | -0.00075806 | 0.026605 | 0.026614 | 0.026614 | 0.99391 | 0.032296 | 0.99388 | 0.032607 | 12.0974
28 | 0.56879 | 0.26825 | -0.56879 | -0.26836 | 2.0552e-06 | -0.0001082 | 0.018266 | 0.018267 | 0.018267 | 0.99388 | 0.032607 | 0.99387 | 0.032636 | 8.3033
29 | -3.6606 | -1.6963 | 3.6641 | 1.6928 | 0.0035067 | -0.0035318 | 0.11683 | 0.11678 | 0.11683 | 0.99685 | 0.007256 | 0.99775 | -0.00024837 | 53.1063
30 | -3.9675 | -1.8392 | 3.973 | 1.8347 | 0.0054529 | -0.0044585 | 0.12652 | 0.12645 | 0.12652 | 0.99775 | -0.00024837 | 0.99903 | -0.011012 | 57.511
31 | 0.30342 | 0.14639 | -0.30342 | -0.14695 | 2.9965e-06 | -0.00056024 | 0.0097472 | 0.0097543 | 0.0097543 | 0.99775 | -0.00024837 | 0.99774 | -0.00016271 | 4.4338
32 | -0.37832 | -0.18323 | 0.37832 | 0.18312 | 9.2539e-07 | -0.00011156 | 0.01215 | 0.012149 | 0.01215 | 0.99872 | 0.010728 | 0.99872 | 0.010706 | 5.5228
33 | 1.9129 | 0.88325 | -1.9108 | -0.89262 | 0.0020816 | -0.0093645 | 0.060902 | 0.061023 | 0.061023 | 0.99872 | 0.010706 | 0.99771 | 0.019317 | 27.7378
34 | -2.2912 | -1.0664 | 2.2944 | 1.0568 | 0.0031271 | -0.0095583 | 0.073049 | 0.072921 | 0.073049 | 0.99872 | 0.010706 | 1 | 0 | 33.2039
35 | -0.76574 | -0.34612 | 0.76623 | 0.34587 | 0.00049515 | -0.00025262 | 0.024275 | 0.024268 | 0.024275 | 0.9993 | -0.0053007 | 0.99999 | 7.2078e-05 | 11.5596
36 | 0.5693 | 0.25099 | -0.5693 | -0.25135 | 6.5639e-06 | -0.00036087 | 0.017973 | 0.017977 | 0.017977 | 0.9993 | -0.0053007 | 0.99929 | -0.0052208 | 8.1715
37 | -1.4052 | -0.6551 | 1.4053 | 0.65499 | 1.2695e-05 | -0.00010957 | 0.044758 | 0.044757 | 0.044758 | 0.99999 | 7.2078e-05 | 1 | 0 | 20.3445
38 | 0.31618 | 0.15287 | -0.31614 | -0.15311 | 4.0888e-05 | -0.0002408 | 0.010138 | 0.010142 | 0.010142 | 0.99999 | 7.2078e-05 | 0.99986 | -0.00078324 | 4.8293
39 | 0.068312 | 0.023094 | -0.06831 | -0.031673 | 2.1713e-06 | -0.0085784 | 0.0020831 | 0.0021752 | 0.0021752 | 0.99929 | -0.0052208 | 0.99926 | -0.0050572 | 0.98872
40 | 0.50098 | 0.22825 | -0.50091 | -0.23351 | 7.5004e-05 | -0.005252 | 0.015904 | 0.015968 | 0.015968 | 0.99929 | -0.0052208 | 0.99915 | -0.0040585 | 7.258
41 | 0.06831 | 0.031673 | -0.068309 | -0.033084 | 3.7681e-07 | -0.0014109 | 0.0021752 | 0.0021927 | 0.0021927 | 0.99926 | -0.0050572 | 0.99926 | -0.0050114 | 0.99666
42 | 0.39207 | 0.18975 | -0.39207 | -0.18989 | 1.1897e-06 | -0.00013375 | 0.012585 | 0.012586 | 0.012586 | 0.99915 | -0.0040585 | 0.99915 | -0.0040321 | 5.721
43 | 0.10884 | 0.043753 | -0.10884 | -0.052461 | 5.7665e-06 | -0.0087078 | 0.0033892 | 0.0034909 | 0.0034909 | 0.99915 | -0.0040585 | 0.9991 | -0.0036894 | 1.5868
44 | 0.10884 | 0.052461 | -0.10883 | -0.052711 | 1.7094e-07 | -0.00025015 | 0.0034909 | 0.003494 | 0.003494 | 0.9991 | -0.0036894 | 0.9991 | -0.0036757 | 1.5882
45 | -0.49097 | -0.23772 | 0.49099 | 0.2368 | 1.3117e-05 | -0.00092809 | 0.015809 | 0.015797 | 0.015809 | 0.99608 | 0.026128 | 0.99611 | 0.025897 | 7.186
46 | 0.24871 | 0.12039 | -0.24871 | -0.12045 | 6.4432e-06 | -6.275e-05 | 0.008008 | 0.0080088 | 0.0080088 | 0.99608 | 0.026128 | 0.99605 | 0.025958 | 3.8137
47 | 0.30344 | 0.12929 | -0.30338 | -0.14185 | 6.5797e-05 | -0.012564 | 0.0095589 | 0.0097076 | 0.0097076 | 0.99611 | 0.025897 | 0.9959 | 0.027453 | 4.4126
48 | -0.79443 | -0.36608 | 0.79477 | 0.36594 | 0.00034216 | -0.00013989 | 0.02535 | 0.025345 | 0.02535 | 0.99611 | 0.025897 | 0.99656 | 0.02927 | 12.0713
49 | 0.2049 | 0.09841 | -0.20489 | -0.098558 | 1.0083e-05 | -0.00014838 | 0.0065846 | 0.0065865 | 0.0065865 | 0.99656 | 0.02927 | 0.99651 | 0.028937 | 3.1364
50 | -1.3441 | -0.63118 | 1.3443 | 0.62979 | 0.00015029 | -0.0013989 | 0.043015 | 0.042997 | 0.043015 | 0.99656 | 0.02927 | 0.99667 | 0.028365 | 19.5522
51 | 0.20489 | 0.098558 | -0.20489 | -0.099234 | 1.6542e-06 | -0.00067584 | 0.0065865 | 0.006595 | 0.006595 | 0.99651 | 0.028937 | 0.9965 | 0.029006 | 2.9977
52 | 0.40703 | 0.19687 | -0.40698 | -0.19702 | 4.5487e-05 | -0.00014799 | 0.013096 | 0.013098 | 0.013098 | 0.99667 | 0.028365 | 0.99655 | 0.027626 | 6.2372
53 | -1.7513 | -0.82665 | 1.7528 | 0.81845 | 0.001529 | -0.0082034 | 0.056092 | 0.055986 | 0.056092 | 0.99667 | 0.028365 | 0.99748 | 0.021284 | 25.4965
54 | 0.40698 | 0.19702 | -0.40698 | -0.19711 | 9.1884e-07 | -9.4847e-05 | 0.013098 | 0.013099 | 0.013099 | 0.99655 | 0.027626 | 0.99655 | 0.027645 | 5.9542
55 | -1.7528 | -0.81845 | 1.7529 | 0.81805 | 7.4992e-05 | -0.00040356 | 0.055986 | 0.055981 | 0.055986 | 0.99748 | 0.021284 | 0.99752 | 0.020941 | 25.4481
56 | -1.9105 | -0.89435 | 1.9108 | 0.89262 | 0.00038592 | -0.0017295 | 0.061046 | 0.061023 | 0.061046 | 0.99752 | 0.020941 | 0.99771 | 0.019317 | 27.7481
57 | 0.56879 | 0.26836 | -0.56873 | -0.27175 | 6.4583e-05 | -0.0033917 | 0.018267 | 0.01831 | 0.01831 | 0.99387 | 0.032636 | 0.99377 | 0.033582 | 8.3226
58 | 0.56873 | 0.27175 | -0.56872 | -0.27201 | 4.8604e-06 | -0.00025458 | 0.01831 | 0.018313 | 0.018313 | 0.99377 | 0.033582 | 0.99376 | 0.033654 | 8.3241
59 | 0.21938 | 0.10281 | -0.21938 | -0.10285 | 3.0382e-06 | -3.8682e-05 | 0.0070379 | 0.0070384 | 0.0070384 | 0.99376 | 0.033654 | 0.99375 | 0.033552 | 3.3516
60 | -0.074887 | -0.036269 | 0.074887 | 0.034905 | 4.3724e-07 | -0.0013646 | 0.0024021 | 0.0023852 | 0.0024021 | 0.99995 | 0.00026357 | 0.99995 | 0.00021483 | 1.0919
61 | -0.074887 | -0.034905 | 0.074891 | 0.02259 | 3.6929e-06 | -0.012314 | 0.0023852 | 0.0022581 | 0.0023852 | 0.99995 | 0.00021483 | 1 | 0 | 1.0842
62 | -0.14633 | -0.070869 | 0.14633 | 0.07077 | 1.2466e-07 | -9.8669e-05 | 0.0047231 | 0.0047218 | 0.0047231 | 0.99372 | 0.033792 | 0.99372 | 0.033785 | 2.1468
63 | -0.14633 | -0.07077 | 0.14633 | 0.067747 | 3.7873e-06 | -0.0030232 | 0.0047218 | 0.0046842 | 0.0047218 | 0.99372 | 0.033785 | 0.99374 | 0.033571 | 2.1463
64 | 0.073047 | 0.035285 | -0.073047 | -0.035378 | 2.9323e-08 | -9.322e-05 | 0.0023566 | 0.0023577 | 0.0023577 | 0.99374 | 0.033571 | 0.99374 | 0.033574 | 1.0717
65 | -0.21938 | -0.10303 | 0.21938 | 0.10285 | 5.0483e-07 | -0.00017978 | 0.0070406 | 0.0070384 | 0.0070406 | 0.99374 | 0.033571 | 0.99375 | 0.033552 | 3.2003
66 | -0.19625 | -0.09505 | 0.19626 | 0.094427 | 1.4031e-06 | -0.00062324 | 0.006321 | 0.0063131 | 0.006321 | 0.99586 | 0.027811 | 0.99587 | 0.027749 | 2.8732
67 | -0.19626 | -0.094427 | 0.19626 | 0.091275 | 7.0427e-06 | -0.0031519 | 0.0063131 | 0.006274 | 0.0063131 | 0.99587 | 0.027749 | 0.9959 | 0.027453 | 2.8696
68 | -0.10711 | -0.051878 | 0.10712 | 0.050578 | 8.6847e-07 | -0.0013003 | 0.0034499 | 0.0034336 | 0.0034499 | 0.99589 | 0.027521 | 0.9959 | 0.027453 | 1.5681
69 | -0.20981 | -0.10162 | 0.20982 | 0.10159 | 1.694e-06 | -2.3905e-05 | 0.0067363 | 0.006736 | 0.0067363 | 0.99903 | -0.011065 | 0.99903 | -0.011012 | 3.2078
70 | -4.1828 | -1.9363 | 4.1864 | 1.9243 | 0.0036748 | -0.01205 | 0.13319 | 0.13301 | 0.13319 | 0.99903 | -0.011012 | 1 | 0 | 36.7915

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 7.975 | 3.6692

## res_load
| p_mw | q_mvar
0 | 0.24065 | 0.11655
1 | 0.073037 | 0.035374
2 | 0.33271 | 0.16114
3 | 0.097683 | 0.04731
4 | 0.29954 | 0.14507
5 | 0.091247 | 0.044193
6 | 0.32533 | 0.15756
7 | 0.27292 | 0.13218
8 | 0.25869 | 0.12529
9 | 0.30342 | 0.14695
10 | 0.37832 | 0.18323
11 | 0.19643 | 0.095137
12 | 0.32284 | 0.15636
13 | 0.068309 | 0.033084
14 | 0.39207 | 0.18989
15 | 0.24226 | 0.11733
16 | 0.24871 | 0.12045
17 | 0.34446 | 0.16683
18 | 0.15754 | 0.076301
19 | 0.34934 | 0.16919
20 | 0.10986 | 0.053206
21 | 0.36926 | 0.17884
22 | 0.34996 | 0.1695
23 | 0.074887 | 0.036269
24 | 0.40698 | 0.19711
25 | 0.20489 | 0.099234
26 | 0.072288 | 0.035011
27 | 0.18804 | 0.091073
28 | 0.14633 | 0.070869
29 | 0.073047 | 0.035378
30 | 0.19625 | 0.09505
31 | 0.31614 | 0.15311
32 | 0.10883 | 0.052711
33 | 0.10711 | 0.051878
34 | 0.20981 | 0.10162

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1