## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_446_1_node_4 | 20 | n |  | TRUE
1 | bus_MV_446_1_node_5 | 20 | n |  | TRUE
2 | bus_MV_446_1_node_176 | 20 | n |  | TRUE
3 | bus_MV_446_1_node_46 | 20 | n |  | TRUE
4 | bus_MV_446_1_node_173 | 20 | n |  | TRUE
5 | bus_MV_446_1_node_51 | 20 | n |  | TRUE
6 | bus_MV_446_1_node_167 | 20 | n |  | TRUE
7 | bus_MV_446_1_node_180 | 20 | n |  | TRUE
8 | bus_MV_446_1_node_142 | 20 | n |  | TRUE
9 | bus_MV_446_1_node_160 | 20 | n |  | TRUE
10 | bus_MV_446_1_node_9 | 20 | n |  | TRUE
11 | bus_MV_446_1_node_170 | 20 | n |  | TRUE
12 | bus_MV_446_1_node_18 | 20 | n |  | TRUE
13 | bus_MV_446_1_node_141 | 20 | n |  | TRUE
14 | bus_MV_446_1_node_19 | 20 | n |  | TRUE
15 | bus_MV_446_1_node_12 | 20 | n |  | TRUE
16 | bus_MV_446_1_node_13 | 20 | n |  | TRUE
17 | bus_MV_446_1_node_35 | 20 | n |  | TRUE
18 | bus_MV_446_1_node_14 | 20 | n |  | TRUE
19 | bus_MV_446_1_node_17 | 20 | n |  | TRUE
20 | bus_MV_446_1_node_36 | 20 | n |  | TRUE
21 | bus_MV_446_1_node_16 | 20 | n |  | TRUE
22 | bus_MV_446_1_node_34 | 20 | n |  | TRUE
23 | bus_MV_446_1_node_23 | 20 | n |  | TRUE
24 | bus_MV_446_1_node_25 | 20 | n |  | TRUE
25 | bus_MV_446_1_node_21 | 20 | n |  | TRUE
26 | bus_MV_446_1_node_20 | 20 | n |  | TRUE
27 | bus_MV_446_1_node_26 | 20 | n |  | TRUE
28 | bus_MV_446_1_node_24 | 20 | n |  | TRUE
29 | bus_MV_446_1_node_143 | 20 | n |  | TRUE
30 | bus_MV_446_1_node_32 | 20 | n |  | TRUE
31 | bus_MV_446_1_node_27 | 20 | n |  | TRUE
32 | bus_MV_446_1_node_28 | 20 | n |  | TRUE
33 | bus_MV_446_1_node_30 | 20 | n |  | TRUE
34 | bus_MV_446_1_node_29 | 20 | n |  | TRUE
35 | bus_MV_446_1_node_125 | 20 | n |  | TRUE
36 | bus_MV_446_1_node_133 | 20 | n |  | TRUE
37 | bus_MV_446_1_node_31 | 20 | n |  | TRUE
38 | bus_MV_446_1_node_126 | 20 | n |  | TRUE
39 | bus_MV_446_1_node_127 | 20 | n |  | TRUE
40 | bus_MV_446_1_node_48 | 20 | n |  | TRUE
41 | bus_MV_446_1_node_47 | 20 | n |  | TRUE
42 | bus_MV_446_1_node_49 | 20 | n |  | TRUE
43 | bus_MV_446_1_node_50 | 20 | n |  | TRUE
44 | bus_MV_446_1_node_53 | 20 | n |  | TRUE
45 | bus_MV_446_1_node_58 | 20 | n |  | TRUE
46 | bus_MV_446_1_node_56 | 20 | n |  | TRUE
47 | bus_MV_446_1_node_57 | 20 | n |  | TRUE
48 | bus_MV_446_1_node_54 | 20 | n |  | TRUE
49 | bus_MV_446_1_node_74 | 20 | n |  | TRUE
50 | bus_MV_446_1_node_70 | 20 | n |  | TRUE
51 | bus_MV_446_1_node_89 | 20 | n |  | TRUE
52 | bus_MV_446_1_node_52 | 20 | n |  | TRUE
53 | bus_MV_446_1_node_55 | 20 | n |  | TRUE
54 | bus_MV_446_1_node_175 | 20 | n |  | TRUE
55 | bus_MV_446_1_node_75 | 20 | n |  | TRUE
56 | bus_MV_446_1_node_90 | 20 | n |  | TRUE
57 | bus_MV_446_1_node_71 | 20 | n |  | TRUE
58 | bus_MV_446_1_node_69 | 20 | n |  | TRUE
59 | bus_MV_446_1_node_59 | 20 | n |  | TRUE
60 | bus_MV_446_1_node_60 | 20 | n |  | TRUE
61 | bus_MV_446_1_node_62 | 20 | n |  | TRUE
62 | bus_MV_446_1_node_63 | 20 | n |  | TRUE
63 | bus_MV_446_1_node_67 | 20 | n |  | TRUE
64 | bus_MV_446_1_node_68 | 20 | n |  | TRUE
65 | bus_MV_446_1_node_66 | 20 | n |  | TRUE
66 | bus_MV_446_1_node_65 | 20 | n |  | TRUE
67 | bus_MV_446_1_node_64 | 20 | n |  | TRUE
68 | bus_MV_446_1_node_109 | 20 | n |  | TRUE
69 | bus_MV_446_1_node_92 | 20 | n |  | TRUE
70 | bus_MV_446_1_node_91 | 20 | n |  | TRUE
71 | bus_MV_446_1_node_93 | 20 | n |  | TRUE
72 | bus_MV_446_1_node_95 | 20 | n |  | TRUE
73 | bus_MV_446_1_node_94 | 20 | n |  | TRUE
74 | bus_MV_446_1_node_168 | 20 | n |  | TRUE
75 | bus_MV_446_1_node_174 | 20 | n |  | TRUE
76 | bus_MV_446_1_node_103 | 20 | n |  | TRUE
77 | bus_MV_446_1_node_159 | 20 | n |  | TRUE
78 | bus_MV_446_1_node_72 | 20 | n |  | TRUE
79 | bus_MV_446_1_node_157 | 20 | n |  | TRUE
80 | bus_MV_446_1_node_172 | 20 | n |  | TRUE
81 | bus_MV_446_1_node_73 | 20 | n |  | TRUE
82 | bus_MV_446_1_node_110 | 20 | n |  | TRUE
83 | bus_MV_446_1_node_113 | 20 | n |  | TRUE
84 | bus_MV_446_1_node_114 | 20 | n |  | TRUE
85 | bus_MV_446_1_node_107 | 20 | n |  | TRUE
86 | bus_MV_446_1_node_105 | 20 | n |  | TRUE
87 | bus_MV_446_1_node_106 | 20 | n |  | TRUE
88 | bus_MV_446_1_node_158 | 20 | n |  | TRUE
89 | bus_MV_446_1_node_102 | 20 | n |  | TRUE
90 | bus_MV_446_1_node_104 | 20 | n |  | TRUE
91 | bus_MV_446_1_node_108 | 20 | n |  | TRUE
92 | bus_MV_446_1_node_177 | 20 | n |  | TRUE
93 | bus_MV_446_1_node_120 | 20 | n |  | TRUE
94 | bus_MV_446_1_node_121 | 20 | n |  | TRUE
95 | bus_MV_446_1_node_132 | 20 | n |  | TRUE
96 | bus_MV_446_1_node_111 | 20 | n |  | TRUE
97 | bus_MV_446_1_node_112 | 20 | n |  | TRUE
98 | bus_MV_446_1_node_119 | 20 | n |  | TRUE
99 | bus_MV_446_1_node_131 | 20 | n |  | TRUE
100 | bus_MV_446_1_node_128 | 20 | n |  | TRUE
101 | bus_MV_446_1_node_130 | 20 | n |  | TRUE
102 | bus_MV_446_1_node_129 | 20 | n |  | TRUE
103 | bus_MV_446_1_node_161 | 20 | n |  | TRUE
104 | bus_MV_446_1_node_169 | 20 | n |  | TRUE
105 | bus_MV_446_1_node_171 | 20 | n |  | TRUE
106 | bus_MV_446_1_node_138 | 20 | n |  | TRUE
107 | bus_MV_446_1_node_139 | 20 | n |  | TRUE
108 | bus_MV_446_1_node_162 | 20 | n |  | TRUE
109 | bus_MV_446_1_node_179 | 20 | n |  | TRUE
110 | bus_MV_446_1_node_134 | 20 | n |  | TRUE
111 | bus_MV_446_1_node_135 | 20 | n |  | TRUE
112 | bus_MV_446_1_node_137 | 20 | n |  | TRUE
113 | bus_MV_446_1_node_140 | 20 | n |  | TRUE
114 | bus_HV_446_1_node_91 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_446_1_load_4 | 0 | 0.063258 | 0.030637 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_446_1_load_176 | 2 | 0.16374 | 0.079304 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_446_1_load_46 | 3 | 0.14767 | 0.071518 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_446_1_load_173 | 4 | 0.14669 | 0.071044 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_446_1_load_167 | 6 | 0.40508 | 0.19619 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_446_1_load_180 | 7 | 0.10356 | 0.050155 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_446_1_load_142 | 8 | 0.096168 | 0.046576 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_446_1_load_160 | 9 | 0.25431 | 0.12317 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_446_1_load_170 | 11 | 0.13318 | 0.064503 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_446_1_load_18 | 12 | 0.13827 | 0.066969 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_446_1_load_12 | 15 | 0.15287 | 0.07404 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_446_1_load_35 | 17 | 0.13746 | 0.066576 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_446_1_load_36 | 20 | 0.11183 | 0.054161 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_446_1_load_34 | 22 | 0.15288 | 0.074042 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_446_1_load_23 | 23 | 0.1221 | 0.059138 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_446_1_load_25 | 24 | 0.053953 | 0.02613 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_446_1_load_26 | 27 | 0.081729 | 0.039583 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_446_1_load_24 | 28 | 0.10277 | 0.049775 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_446_1_load_143 | 29 | 0.092618 | 0.044857 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_446_1_load_30 | 33 | 0.092477 | 0.044789 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_446_1_load_125 | 35 | 0.39074 | 0.18924 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_446_1_load_133 | 36 | 0.29972 | 0.14516 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_446_1_load_47 | 41 | 0.36735 | 0.17792 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_446_1_load_58 | 45 | 0.40627 | 0.19676 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_446_1_load_57 | 47 | 0.18076 | 0.087544 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_446_1_load_89 | 51 | 0.26523 | 0.12846 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_446_1_load_52 | 52 | 0.19993 | 0.096829 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_446_1_load_55 | 53 | 0.18006 | 0.087209 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_446_1_load_175 | 54 | 0.2678 | 0.1297 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_446_1_load_90 | 56 | 0.35179 | 0.17038 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_446_1_load_69 | 58 | 0.33937 | 0.16437 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_446_1_load_59 | 59 | 0.112 | 0.054242 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_446_1_load_66 | 65 | 0.293 | 0.1419 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_446_1_load_65 | 66 | 0.1656 | 0.080204 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_446_1_load_109 | 68 | 0.35773 | 0.17325 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_446_1_load_91 | 70 | 0.23549 | 0.11405 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_446_1_load_168 | 74 | 0.09635 | 0.046665 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_446_1_load_174 | 75 | 0.37068 | 0.17953 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_446_1_load_159 | 77 | 0.091147 | 0.044145 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_446_1_load_157 | 79 | 0.29585 | 0.14329 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_446_1_load_172 | 80 | 0.20145 | 0.097567 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_446_1_load_110 | 82 | 0.13898 | 0.067309 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_446_1_load_114 | 84 | 0.34472 | 0.16695 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_446_1_load_158 | 88 | 0.43916 | 0.2127 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_446_1_load_102 | 89 | 0.19752 | 0.095666 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_446_1_load_104 | 90 | 0.081787 | 0.039611 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_446_1_load_177 | 92 | 0.19968 | 0.096709 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_446_1_load_132 | 95 | 0.33655 | 0.163 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_446_1_load_111 | 96 | 0.19425 | 0.094078 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_446_1_load_131 | 99 | 0.41272 | 0.19989 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_446_1_load_128 | 100 | 0.38745 | 0.18765 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_446_1_load_129 | 102 | 0.34912 | 0.16909 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_446_1_load_161 | 103 | 0.22265 | 0.10784 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_446_1_load_171 | 105 | 0.29176 | 0.14131 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_446_1_load_179 | 109 | 0.067074 | 0.032485 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_446_1_load_134 | 110 | 0.33097 | 0.1603 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_446_1_load_137 | 112 | 0.39905 | 0.19327 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 70 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_446_1_line_0 |  | 0 | 1 | 0.11498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_446_1_line_1 |  | 1 | 2 | 2.2766 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_446_1_line_2 |  | 1 | 3 | 1.7476 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_446_1_line_3 |  | 3 | 5 | 1.7945 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_446_1_line_4 |  | 4 | 5 | 0.10532 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_446_1_line_5 |  | 5 | 40 | 1.1316 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_446_1_line_6 |  | 6 | 7 | 0.31591 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
7 | MV_446_1_line_7 |  | 6 | 8 | 0.15875 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_446_1_line_8 |  | 6 | 9 | 0.26773 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
9 | MV_446_1_line_9 |  | 7 | 113 | 0.015724 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
10 | MV_446_1_line_10 |  | 8 | 112 | 0.03991 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_446_1_line_11 |  | 9 | 107 | 0.007679 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_446_1_line_12 |  | 10 | 11 | 0.067874 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
13 | MV_446_1_line_13 |  | 10 | 12 | 0.66088 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
14 | MV_446_1_line_14 |  | 11 | 13 | 0.15234 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
15 | MV_446_1_line_15 |  | 12 | 14 | 0.059473 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
16 | MV_446_1_line_16 |  | 13 | 113 | 0.25722 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
17 | MV_446_1_line_17 |  | 14 | 25 | 1.0971 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
18 | MV_446_1_line_18 |  | 14 | 24 | 0.33488 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_446_1_line_19 |  | 15 | 16 | 0.041912 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_446_1_line_20 |  | 16 | 17 | 0.25813 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_446_1_line_21 |  | 17 | 18 | 0.20938 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_446_1_line_22 |  | 17 | 19 | 0.39863 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_446_1_line_23 |  | 18 | 20 | 0.15942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_446_1_line_24 |  | 19 | 23 | 0.092565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_446_1_line_25 |  | 19 | 21 | 0.22827 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_446_1_line_26 |  | 20 | 24 | 0.24794 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_446_1_line_27 |  | 21 | 22 | 0.014597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_446_1_line_28 |  | 25 | 28 | 0.058633 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_446_1_line_29 |  | 25 | 26 | 0.25479 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
30 | MV_446_1_line_30 |  | 26 | 27 | 0.093692 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
31 | MV_446_1_line_31 |  | 27 | 29 | 0.1215 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
32 | MV_446_1_line_32 |  | 29 | 30 | 0.13156 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
33 | MV_446_1_line_33 |  | 30 | 37 | 0.061695 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
34 | MV_446_1_line_34 |  | 31 | 32 | 0.34487 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_446_1_line_35 |  | 31 | 33 | 0.068107 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
36 | MV_446_1_line_36 |  | 32 | 34 | 0.086078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_446_1_line_37 |  | 32 | 35 | 0.022164 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
38 | MV_446_1_line_38 |  | 33 | 37 | 0.099324 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
39 | MV_446_1_line_39 |  | 34 | 36 | 0.01745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_446_1_line_40 |  | 35 | 38 | 0.021234 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
41 | MV_446_1_line_41 |  | 38 | 39 | 0.063618 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
42 | MV_446_1_line_42 |  | 39 | 104 | 0.032601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_446_1_line_43 |  | 39 | 74 | 0.029867 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
44 | MV_446_1_line_44 |  | 40 | 42 | 0.57907 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_446_1_line_45 |  | 40 | 41 | 0.083823 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_446_1_line_46 |  | 42 | 43 | 0.75141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_446_1_line_47 |  | 42 | 44 | 0.66061 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_446_1_line_48 |  | 42 | 45 | 0.014257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_446_1_line_49 |  | 43 | 46 | 0.62811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_446_1_line_50 |  | 43 | 47 | 0.055375 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_446_1_line_51 |  | 44 | 52 | 0.039601 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_446_1_line_52 |  | 44 | 48 | 0.54692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_446_1_line_53 |  | 46 | 53 | 0.031121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_446_1_line_54 |  | 48 | 49 | 0.48843 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_446_1_line_55 |  | 48 | 50 | 0.43022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_446_1_line_56 |  | 48 | 51 | 0.004309 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_446_1_line_57 |  | 49 | 54 | 0.006389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_446_1_line_58 |  | 49 | 55 | 0.44806 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_446_1_line_59 |  | 50 | 57 | 0.31971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_446_1_line_60 |  | 50 | 58 | 0.042898 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_446_1_line_61 |  | 54 | 69 | 0.036373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_446_1_line_62 |  | 55 | 56 | 0.075868 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_446_1_line_63 |  | 57 | 78 | 0.20382 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_446_1_line_64 |  | 57 | 79 | 0.044276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_446_1_line_65 |  | 59 | 60 | 0.056339 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_446_1_line_66 |  | 60 | 61 | 0.14605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_446_1_line_67 |  | 60 | 62 | 0.18319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_446_1_line_68 |  | 61 | 66 | 0.087175 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_446_1_line_69 |  | 62 | 65 | 0.011968 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_446_1_line_70 |  | 63 | 64 | 0.35695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_446_1_line_71 |  | 63 | 65 | 0.06388 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_446_1_line_72 |  | 64 | 69 | 0.36619 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
73 | MV_446_1_line_73 |  | 64 | 70 | 0.0027548 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
74 | MV_446_1_line_74 |  | 66 | 67 | 0.14761 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_446_1_line_75 |  | 67 | 68 | 0.18367 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_446_1_line_76 |  | 69 | 71 | 0.44009 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_446_1_line_77 |  | 69 | 72 | 0.52801 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_446_1_line_78 |  | 71 | 73 | 0.40497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_446_1_line_79 |  | 71 | 74 | 0.022943 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
80 | MV_446_1_line_80 |  | 72 | 76 | 0.19054 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_446_1_line_81 |  | 72 | 77 | 0.033396 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_446_1_line_82 |  | 73 | 75 | 0.049437 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_446_1_line_83 |  | 76 | 86 | 0.2416 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_446_1_line_84 |  | 76 | 87 | 0.13351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_446_1_line_85 |  | 78 | 80 | 0.044435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_446_1_line_86 |  | 78 | 81 | 0.24659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_446_1_line_87 |  | 79 | 83 | 0.042486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_446_1_line_88 |  | 81 | 82 | 0.005232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_446_1_line_89 |  | 83 | 97 | 0.23817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_446_1_line_90 |  | 84 | 85 | 0.00992 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_446_1_line_91 |  | 85 | 86 | 0.29836 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_446_1_line_92 |  | 86 | 92 | 0.033357 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
93 | MV_446_1_line_93 |  | 87 | 88 | 0.024046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_446_1_line_94 |  | 89 | 90 | 0.013501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_446_1_line_95 |  | 90 | 91 | 0.070133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_446_1_line_96 |  | 91 | 93 | 0.60766 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_446_1_line_97 |  | 93 | 94 | 0.30434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_446_1_line_98 |  | 93 | 95 | 0.066086 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_446_1_line_99 |  | 94 | 101 | 0.97916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_446_1_line_100 |  | 94 | 102 | 0.058487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_446_1_line_101 |  | 94 | 98 | 0.37678 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_446_1_line_102 |  | 96 | 97 | 0.083296 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
103 | MV_446_1_line_103 |  | 98 | 99 | 0.16822 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_446_1_line_104 |  | 98 | 100 | 0.10499 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_446_1_line_105 |  | 101 | 103 | 0.28574 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_446_1_line_106 |  | 103 | 108 | 0.066045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_446_1_line_107 |  | 104 | 105 | 0.033731 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_446_1_line_108 |  | 106 | 107 | 0.28403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_446_1_line_109 |  | 106 | 108 | 0.031916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_446_1_line_110 |  | 106 | 109 | 0.006185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_446_1_line_111 |  | 110 | 111 | 0.027972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_446_1_line_112 |  | 111 | 112 | 0.060964 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_446_1_trafo_91 | 25 MVA 110/20 kV | 114 | 70 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2615028.4959 | 1219073.9837
1 | 2614966.5332 | 1218978.6069
2 | 2615477.0056 | 1216759.9262
3 | 2613303.9517 | 1218440.0154
4 | 2612684.8881 | 1216730.2525
5 | 2612598.3429 | 1216790.0705
6 | 2609927.5041 | 1213946.4421
7 | 2609914.3632 | 1213630.8017
8 | 2610079.2291 | 1213899.7274
9 | 2610176.8612 | 1214043.9244
10 | 2609786.3239 | 1213280.9285
11 | 2609823.1302 | 1213337.9984
12 | 2610438.2071 | 1213172.266
13 | 2609909.9384 | 1213463.3337
14 | 2610484.7503 | 1213209.2901
15 | 2610819.632 | 1212649.9045
16 | 2610836.5863 | 1212675.694
17 | 2610627.9689 | 1212827.7059
18 | 2610836.0028 | 1212851.4136
19 | 2610956.2292 | 1212601.5475
20 | 2610774.1411 | 1212998.2956
21 | 2610808.9142 | 1212455.5653
22 | 2610821.8486 | 1212448.7292
23 | 2611040.3001 | 1212640.0048
24 | 2610817.9933 | 1213242.3225
25 | 2610924.7747 | 1214054.6836
26 | 2610891.4496 | 1214284.3189
27 | 2610977.4555 | 1214322.0525
28 | 2610901.3063 | 1214105.236
29 | 2611086.6862 | 1214268.8491
30 | 2611117.8814 | 1214359.599
31 | 2610939.5695 | 1214408.1873
32 | 2610851.2354 | 1214608.3619
33 | 2611005.2036 | 1214426.3732
34 | 2610771.293 | 1214579.0235
35 | 2610866.6147 | 1214624.2987
36 | 2610754.4298 | 1214574.5354
37 | 2611104.2387 | 1214418.8071
38 | 2610878.1558 | 1214642.0074
39 | 2610835.5806 | 1214685.9662
40 | 2612196.9693 | 1216057.4683
41 | 2612126.0971 | 1216102.2276
42 | 2611938.2906 | 1215923.6937
43 | 2612486.3065 | 1215740.5403
44 | 2611840.7426 | 1215440.7601
45 | 2611935.5549 | 1215909.7026
46 | 2612819.7487 | 1215683.8458
47 | 2612534.0843 | 1215712.5464
48 | 2611448.0784 | 1215200.0946
49 | 2611166.7018 | 1214911.6454
50 | 2611115.9177 | 1215123.4596
51 | 2611445.6342 | 1215203.6475
52 | 2611871.5205 | 1215465.6796
53 | 2612850.7794 | 1215680.4993
54 | 2611163.6976 | 1214906.0033
55 | 2611534.6777 | 1214877.4895
56 | 2611610.6991 | 1214880.727
57 | 2611055.3119 | 1215359.9255
58 | 2611135.7134 | 1215086.72
59 | 2611465.485 | 1214234.2497
60 | 2611439.849 | 1214284.4178
61 | 2611540.8583 | 1214381.0659
62 | 2611431.0438 | 1214433.4183
63 | 2611396.3467 | 1214500.8681
64 | 2611121.8224 | 1214707.6914
65 | 2611425.753 | 1214444.1587
66 | 2611607.5537 | 1214324.9297
67 | 2611641.2861 | 1214181.2253
68 | 2611787.1916 | 1214069.6698
69 | 2611129.0692 | 1214894.5658
70 | 2611119.9048 | 1214709.6692
71 | 2610872.7606 | 1214723.4658
72 | 2610980.1579 | 1215126.8335
73 | 2610955.0781 | 1215014.1129
74 | 2610856.7201 | 1214707.0618
75 | 2611000.5002 | 1214994.5962
76 | 2610861.6977 | 1215246.4743
77 | 2610951.2741 | 1215110.0708
78 | 2611210.5177 | 1215333.2876
79 | 2611017.5324 | 1215383.0149
80 | 2611251.8552 | 1215316.689
81 | 2611202.5307 | 1215454.6301
82 | 2611204.6782 | 1215459.4035
83 | 2610981.2804 | 1215405.1706
84 | 2610478.4389 | 1215564.0719
85 | 2610484.7998 | 1215556.4454
86 | 2610691.4834 | 1215373.1177
87 | 2610882.8774 | 1215295.3959
88 | 2610895.8427 | 1215275.1659
89 | 2610785.8884 | 1215195.3419
90 | 2610775.0567 | 1215187.2827
91 | 2610719.2722 | 1215144.7828
92 | 2610703.8394 | 1215342.1334
93 | 2610477.6026 | 1215017.3393
94 | 2610330.5151 | 1214961.2192
95 | 2610525.7112 | 1215062.6491
96 | 2610869.4379 | 1215588.2593
97 | 2610946.8428 | 1215619.0286
98 | 2610505.2943 | 1214866.6361
99 | 2610623.5576 | 1214746.8212
100 | 2610485.3058 | 1214763.5652
101 | 2610033.6926 | 1214370.427
102 | 2610347.9548 | 1214905.5735
103 | 2610242.6056 | 1214175.4852
104 | 2610814.8569 | 1214711.1764
105 | 2610821.6925 | 1214744.2073
106 | 2610313.9589 | 1214141.3733
107 | 2610181.2616 | 1214050.2176
108 | 2610295.5734 | 1214136.3944
109 | 2610312.6251 | 1214135.3342
110 | 2610145.0577 | 1213821.2814
111 | 2610162.5881 | 1213842.9583
112 | 2610112.7691 | 1213878.0967
113 | 2609902.751 | 1213621.0548
114 | 2611119.9048 | 1214709.6692

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99071 | 0.010375 | 0.063258 | 0.030637
1 | 0.99072 | 0.010297 | 0 | 0
2 | 0.99 | 0.0054408 | 0.16374 | 0.079304
3 | 0.99149 | 0.016143 | 0.14767 | 0.071518
4 | 0.99277 | 0.025888 | 0.14669 | 0.071044
5 | 0.99279 | 0.025709 | 0 | 0
6 | 0.9883 | -0.23611 | 0.40508 | 0.19619
7 | 0.98962 | -0.20194 | 0.10356 | 0.050155
8 | 0.98804 | -0.23777 | 0.096168 | 0.046576
9 | 0.98757 | -0.25534 | 0.25431 | 0.12317
10 | 0.99061 | -0.19069 | 0 | 0
11 | 0.99047 | -0.19229 | 0.13318 | 0.064503
12 | 0.99357 | -0.1145 | 0.13827 | 0.066969
13 | 0.99017 | -0.19576 | 0 | 0
14 | 0.99385 | -0.10743 | 0 | 0
15 | 0.99262 | -0.11427 | 0.15287 | 0.07404
16 | 0.99263 | -0.11435 | 0 | 0
17 | 0.99271 | -0.11384 | 0.13746 | 0.066576
18 | 0.99293 | -0.11221 | 0 | 0
19 | 0.9925 | -0.11546 | 0 | 0
20 | 0.99305 | -0.11319 | 0.11183 | 0.054161
21 | 0.99245 | -0.11508 | 0 | 0
22 | 0.99245 | -0.11506 | 0.15288 | 0.074042
23 | 0.99248 | -0.11533 | 0.1221 | 0.059138
24 | 0.99337 | -0.11083 | 0.053953 | 0.02613
25 | 0.99662 | -0.075597 | 0 | 0
26 | 0.99688 | -0.070629 | 0 | 0
27 | 0.99698 | -0.068792 | 0.081729 | 0.039583
28 | 0.99661 | -0.075527 | 0.10277 | 0.049775
29 | 0.99727 | -0.058705 | 0.092618 | 0.044857
30 | 0.99741 | -0.05603 | 0 | 0
31 | 0.99789 | -0.040484 | 0 | 0
32 | 0.99827 | -0.033294 | 0 | 0
33 | 0.99772 | -0.046356 | 0.092477 | 0.044789
34 | 0.99824 | -0.032992 | 0 | 0
35 | 0.99829 | -0.032804 | 0.39074 | 0.18924
36 | 0.99823 | -0.03293 | 0.29972 | 0.14516
37 | 0.99748 | -0.054773 | 0 | 0
38 | 0.99832 | -0.032302 | 0 | 0
39 | 0.9984 | -0.030798 | 0 | 0
40 | 0.99353 | 0.020387 | 0 | 0
41 | 0.99347 | 0.020009 | 0.36735 | 0.17792
42 | 0.99419 | 0.015847 | 0 | 0
43 | 0.99384 | 0.017944 | 0 | 0
44 | 0.99557 | 0.0066083 | 0 | 0
45 | 0.99418 | 0.015917 | 0.40627 | 0.19676
46 | 0.9937 | 0.018984 | 0 | 0
47 | 0.99383 | 0.017821 | 0.18076 | 0.087544
48 | 0.99685 | -0.0018347 | 0 | 0
49 | 0.99888 | -0.016184 | 0 | 0
50 | 0.99621 | 0.0033088 | 0 | 0
51 | 0.99685 | -0.001821 | 0.26523 | 0.12846
52 | 0.99555 | 0.0065117 | 0.19993 | 0.096829
53 | 0.99369 | 0.019051 | 0.18006 | 0.087209
54 | 0.99891 | -0.01639 | 0.2678 | 0.1297
55 | 0.99868 | -0.014498 | 0 | 0
56 | 0.99864 | -0.014182 | 0.35179 | 0.17038
57 | 0.99587 | 0.0060299 | 0 | 0
58 | 0.99619 | 0.0034829 | 0.33937 | 0.16437
59 | 0.99929 | 0.0040935 | 0.112 | 0.054242
60 | 0.9993 | 0.00417 | 0 | 0
61 | 0.9992 | 0.0050653 | 0 | 0
62 | 0.99945 | 0.0028483 | 0 | 0
63 | 0.99957 | 0.0035288 | 0 | 0
64 | 0.99999 | -0.00014229 | 0 | 0
65 | 0.99946 | 0.0027637 | 0.293 | 0.1419
66 | 0.99911 | 0.0045098 | 0.1656 | 0.080204
67 | 0.99901 | 0.0038666 | 0 | 0
68 | 0.99889 | 0.0030693 | 0.35773 | 0.17325
69 | 0.99909 | -0.017683 | 0 | 0
70 | 1 | 0 | -12.4711 | -5.5351
71 | 0.99847 | -0.02948 | 0 | 0
72 | 0.99837 | -0.011837 | 0 | 0
73 | 0.99828 | -0.027804 | 0 | 0
74 | 0.99844 | -0.030057 | 0.09635 | 0.046665
75 | 0.99824 | -0.028027 | 0.37068 | 0.17953
76 | 0.99813 | -0.0098202 | 0 | 0
77 | 0.99836 | -0.011801 | 0.091147 | 0.044145
78 | 0.99578 | 0.0067435 | 0 | 0
79 | 0.99584 | 0.006271 | 0.29585 | 0.14329
80 | 0.99577 | 0.00685 | 0.20145 | 0.097567
81 | 0.99574 | 0.0071087 | 0 | 0
82 | 0.99574 | 0.0071175 | 0.13898 | 0.067309
83 | 0.99583 | 0.0063535 | 0 | 0
84 | 0.99783 | -0.0071944 | 0.34472 | 0.16695
85 | 0.99783 | -0.0072354 | 0 | 0
86 | 0.99796 | -0.0083988 | 0 | 0
87 | 0.99806 | -0.0091345 | 0 | 0
88 | 0.99804 | -0.0090081 | 0.43916 | 0.2127
89 | 0.98286 | -0.23287 | 0.19752 | 0.095666
90 | 0.98286 | -0.2329 | 0.081787 | 0.039611
91 | 0.98289 | -0.23314 | 0 | 0
92 | 0.99795 | -0.0084797 | 0.19968 | 0.096709
93 | 0.98311 | -0.23488 | 0 | 0
94 | 0.98335 | -0.23681 | 0 | 0
95 | 0.98306 | -0.23516 | 0.33655 | 0.163
96 | 0.99574 | 0.0066695 | 0.19425 | 0.094078
97 | 0.99578 | 0.006867 | 0 | 0
98 | 0.98296 | -0.23329 | 0 | 0
99 | 0.98287 | -0.23245 | 0.41272 | 0.19989
100 | 0.98288 | -0.2338 | 0.38745 | 0.18765
101 | 0.98557 | -0.25503 | 0 | 0
102 | 0.98332 | -0.23656 | 0.34912 | 0.16909
103 | 0.98655 | -0.24723 | 0.22265 | 0.10784
104 | 0.99839 | -0.030685 | 0 | 0
105 | 0.99837 | -0.030804 | 0.29176 | 0.14131
106 | 0.9868 | -0.24923 | 0 | 0
107 | 0.98754 | -0.25518 | 0 | 0
108 | 0.98671 | -0.24858 | 0 | 0
109 | 0.9868 | -0.24922 | 0.067074 | 0.032485
110 | 0.98794 | -0.23778 | 0.33097 | 0.1603
111 | 0.98796 | -0.23789 | 0 | 0
112 | 0.98798 | -0.23814 | 0.39905 | 0.19327
113 | 0.98966 | -0.20158 | 0 | 0
114 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.063258 | -0.030637 | 0.063259 | 0.027943 | 6.3333e-07 | -0.0026945 | 0.002048 | 0.002015 | 0.002048 | 0.99071 | 0.010375 | 0.99072 | 0.010297 | 0.93092
1 | 0.16385 | 0.076709 | -0.16374 | -0.079304 | 0.00011344 | -0.0025947 | 0.0052717 | 0.0053051 | 0.0053051 | 0.99072 | 0.010297 | 0.99 | 0.0054408 | 2.5262
2 | -0.22711 | -0.10465 | 0.22728 | 0.10271 | 0.00016475 | -0.0019462 | 0.0072863 | 0.0072616 | 0.0072863 | 0.99072 | 0.010297 | 0.99149 | 0.016143 | 3.4697
3 | -0.37494 | -0.17422 | 0.37541 | 0.1724 | 0.0004623 | -0.0018191 | 0.012038 | 0.012012 | 0.012038 | 0.99149 | 0.016143 | 0.99279 | 0.025709 | 5.7322
4 | -0.14669 | -0.071044 | 0.14669 | 0.068566 | 3.1374e-06 | -0.0024776 | 0.0047393 | 0.0047083 | 0.0047393 | 0.99277 | 0.025888 | 0.99279 | 0.025709 | 2.1542
5 | -0.5221 | -0.24097 | 0.52251 | 0.21444 | 0.00041435 | -0.026526 | 0.01672 | 0.016411 | 0.01672 | 0.99279 | 0.025709 | 0.99353 | 0.020387 | 7.6001
6 | -3.5509 | -1.6477 | 3.5547 | 1.6516 | 0.0037914 | 0.0039483 | 0.11434 | 0.11434 | 0.11434 | 0.9883 | -0.23611 | 0.98962 | -0.20194 | 32.669
7 | 0.82644 | 0.39799 | -0.82624 | -0.39805 | 0.00020307 | -5.7865e-05 | 0.026793 | 0.026796 | 0.026796 | 0.9883 | -0.23611 | 0.98804 | -0.23777 | 12.7598
8 | 2.3194 | 1.0535 | -2.318 | -1.0523 | 0.0013609 | 0.0012282 | 0.074408 | 0.074412 | 0.074412 | 0.9883 | -0.23611 | 0.98757 | -0.25534 | 21.2606
9 | -3.6582 | -1.7018 | 3.6583 | 1.7013 | 0.00010519 | -0.00045187 | 0.11769 | 0.11769 | 0.11769 | 0.98962 | -0.20194 | 0.98966 | -0.20158 | 32.5118
10 | 0.73007 | 0.35147 | -0.73003 | -0.3515 | 3.9853e-05 | -2.1547e-05 | 0.023674 | 0.023674 | 0.023674 | 0.98804 | -0.23777 | 0.98798 | -0.23814 | 11.2735
11 | 2.0637 | 0.9291 | -2.0636 | -0.92926 | 4.4867e-05 | -0.0001655 | 0.066155 | 0.066157 | 0.066157 | 0.98757 | -0.25534 | 0.98754 | -0.25518 | 30.0716
12 | 3.7947 | 1.7521 | -3.7943 | -1.754 | 0.00048647 | -0.0019311 | 0.1218 | 0.12183 | 0.12183 | 0.99061 | -0.19069 | 0.99047 | -0.19229 | 33.6545
13 | -3.7947 | -1.7521 | 3.8037 | 1.7616 | 0.0089998 | 0.0094765 | 0.1218 | 0.12179 | 0.1218 | 0.99061 | -0.19069 | 0.99357 | -0.1145 | 34.8004
14 | 3.6611 | 1.6895 | -3.6601 | -1.6939 | 0.0010167 | -0.0043866 | 0.11752 | 0.11758 | 0.11758 | 0.99047 | -0.19229 | 0.99017 | -0.19576 | 32.4806
15 | -3.942 | -1.8286 | 3.9429 | 1.8295 | 0.00087027 | 0.00092161 | 0.12625 | 0.12625 | 0.12625 | 0.99357 | -0.1145 | 0.99385 | -0.10743 | 36.0728
16 | 3.6601 | 1.6939 | -3.6583 | -1.7013 | 0.0017191 | -0.0073977 | 0.11758 | 0.11769 | 0.11769 | 0.99017 | -0.19576 | 0.98966 | -0.20158 | 32.51
17 | -4.6748 | -2.1697 | 4.6866 | 2.141 | 0.011839 | -0.028677 | 0.1497 | 0.14925 | 0.1497 | 0.99385 | -0.10743 | 0.99662 | -0.075597 | 41.3529
18 | 0.7319 | 0.34023 | -0.73158 | -0.34042 | 0.00032799 | -0.00018924 | 0.023444 | 0.023449 | 0.023449 | 0.99385 | -0.10743 | 0.99337 | -0.11083 | 11.166
19 | -0.15287 | -0.07404 | 0.15287 | 0.073054 | 1.3619e-06 | -0.00098559 | 0.0049398 | 0.0049274 | 0.0049398 | 0.99262 | -0.11427 | 0.99263 | -0.11435 | 2.2454
20 | -0.15287 | -0.073054 | 0.15289 | 0.072757 | 1.1158e-05 | -0.00029666 | 0.0049274 | 0.0049236 | 0.0049274 | 0.99263 | -0.11435 | 0.99271 | -0.11384 | 2.3464
21 | -0.56539 | -0.26419 | 0.56552 | 0.26402 | 0.00012284 | -0.00016944 | 0.018148 | 0.018145 | 0.018148 | 0.99271 | -0.11384 | 0.99293 | -0.11221 | 8.6418
22 | 0.27505 | 0.12486 | -0.27499 | -0.12529 | 5.4834e-05 | -0.00043452 | 0.0087838 | 0.0087895 | 0.0087895 | 0.99271 | -0.11384 | 0.9925 | -0.11546 | 4.1855
23 | -0.56552 | -0.26402 | 0.56559 | 0.26029 | 6.989e-05 | -0.0037323 | 0.018145 | 0.018099 | 0.018145 | 0.99293 | -0.11221 | 0.99305 | -0.11319 | 8.2476
24 | 0.12211 | 0.056962 | -0.1221 | -0.059138 | 1.911e-06 | -0.0021764 | 0.003919 | 0.0039462 | 0.0039462 | 0.9925 | -0.11546 | 0.99248 | -0.11533 | 1.7937
25 | 0.15289 | 0.068333 | -0.15288 | -0.073699 | 7.3262e-06 | -0.0053663 | 0.0048708 | 0.0049365 | 0.0049365 | 0.9925 | -0.11546 | 0.99245 | -0.11508 | 2.2439
26 | -0.67742 | -0.31445 | 0.67762 | 0.31429 | 0.00020818 | -0.00016159 | 0.02171 | 0.021707 | 0.02171 | 0.99305 | -0.11319 | 0.99337 | -0.11083 | 10.3383
27 | 0.15288 | 0.073699 | -0.15288 | -0.074042 | 4.7531e-07 | -0.00034314 | 0.0049365 | 0.0049409 | 0.0049409 | 0.99245 | -0.11508 | 0.99245 | -0.11506 | 2.2459
28 | 0.10277 | 0.048384 | -0.10277 | -0.049775 | 8.5184e-07 | -0.0013902 | 0.0032903 | 0.0033076 | 0.0033076 | 0.99662 | -0.075597 | 0.99661 | -0.075527 | 1.5035
29 | -4.7894 | -2.1894 | 4.7905 | 2.1711 | 0.0010832 | -0.018346 | 0.15254 | 0.1523 | 0.15254 | 0.99662 | -0.075597 | 0.99688 | -0.070629 | 18.1158
30 | -4.7905 | -2.1711 | 4.7909 | 2.1643 | 0.00039749 | -0.0067496 | 0.1523 | 0.15222 | 0.1523 | 0.99688 | -0.070629 | 0.99698 | -0.068792 | 18.0883
31 | -4.8726 | -2.2039 | 4.8737 | 2.2051 | 0.0010383 | 0.0011905 | 0.15485 | 0.15484 | 0.15485 | 0.99698 | -0.068792 | 0.99727 | -0.058705 | 18.8838
32 | -4.9663 | -2.25 | 4.9669 | 2.2405 | 0.00059922 | -0.0094484 | 0.15782 | 0.1577 | 0.15782 | 0.99727 | -0.058705 | 0.99741 | -0.05603 | 18.7436
33 | -4.9669 | -2.2405 | 4.9671 | 2.2361 | 0.00028068 | -0.004432 | 0.1577 | 0.15765 | 0.1577 | 0.99741 | -0.05603 | 0.99748 | -0.054773 | 18.7294
34 | -5.0611 | -2.2826 | 5.0628 | 2.2579 | 0.0016249 | -0.024757 | 0.16061 | 0.1603 | 0.16061 | 0.99789 | -0.040484 | 0.99827 | -0.033294 | 19.0751
35 | 5.0611 | 2.2826 | -5.0605 | -2.2819 | 0.00062617 | 0.00073105 | 0.16061 | 0.16061 | 0.16061 | 0.99789 | -0.040484 | 0.99772 | -0.046356 | 19.5872
36 | 0.29973 | 0.1427 | -0.29972 | -0.14475 | 1.0618e-05 | -0.0020449 | 0.0095997 | 0.0096253 | 0.0096253 | 0.99827 | -0.033294 | 0.99824 | -0.032992 | 4.3752
37 | -5.3625 | -2.4006 | 5.3626 | 2.399 | 0.00011707 | -0.0015801 | 0.1699 | 0.16988 | 0.1699 | 0.99827 | -0.033294 | 0.99829 | -0.032804 | 20.178
38 | 4.968 | 2.2371 | -4.9671 | -2.2361 | 0.00087973 | 0.0010178 | 0.15764 | 0.15765 | 0.15765 | 0.99772 | -0.046356 | 0.99748 | -0.054773 | 19.2251
39 | 0.29972 | 0.14475 | -0.29972 | -0.14516 | 2.1595e-06 | -0.00041453 | 0.0096253 | 0.0096306 | 0.0096306 | 0.99824 | -0.032992 | 0.99823 | -0.03293 | 4.3775
40 | -5.7533 | -2.5882 | 5.7535 | 2.5867 | 0.00012931 | -0.0014982 | 0.18243 | 0.18241 | 0.18243 | 0.99829 | -0.032804 | 0.99832 | -0.032302 | 21.666
41 | -5.7535 | -2.5867 | 5.7539 | 2.5822 | 0.00038725 | -0.0044892 | 0.18241 | 0.18235 | 0.18241 | 0.99832 | -0.032302 | 0.9984 | -0.030798 | 21.6638
42 | 0.29177 | 0.1405 | -0.29177 | -0.14127 | 3.8197e-06 | -0.00077475 | 0.0093633 | 0.0093731 | 0.0093731 | 0.9984 | -0.030798 | 0.99839 | -0.030685 | 4.2605
43 | -6.0456 | -2.7227 | 6.0458 | 2.7206 | 0.00020086 | -0.0020904 | 0.19171 | 0.19168 | 0.19171 | 0.9984 | -0.030798 | 0.99844 | -0.030057 | 22.7686
44 | -0.88988 | -0.39227 | 0.8905 | 0.3788 | 0.00061377 | -0.013475 | 0.028257 | 0.028099 | 0.028257 | 0.99353 | 0.020387 | 0.99419 | 0.015847 | 12.8439
45 | 0.36737 | 0.17783 | -0.36735 | -0.17792 | 2.1005e-05 | -8.5615e-05 | 0.011859 | 0.01186 | 0.01186 | 0.99353 | 0.020387 | 0.99347 | 0.020009 | 5.6477
46 | 0.36098 | 0.14147 | -0.36085 | -0.15915 | 0.00012932 | -0.017688 | 0.011258 | 0.011456 | 0.011456 | 0.99419 | 0.015847 | 0.99384 | 0.017944 | 5.2071
47 | -1.6577 | -0.7167 | 1.6602 | 0.7018 | 0.002417 | -0.014895 | 0.052441 | 0.052263 | 0.052441 | 0.99419 | 0.015847 | 0.99557 | 0.0066083 | 23.8367
48 | 0.40627 | 0.19643 | -0.40627 | -0.19676 | 3.2689e-06 | -0.00033548 | 0.013103 | 0.013107 | 0.013107 | 0.99419 | 0.015847 | 0.99418 | 0.015917 | 5.9579
49 | 0.18009 | 0.071673 | -0.18007 | -0.086476 | 2.7369e-05 | -0.014803 | 0.0056301 | 0.005803 | 0.005803 | 0.99384 | 0.017944 | 0.9937 | 0.018984 | 2.6377
50 | 0.18076 | 0.08748 | -0.18076 | -0.087544 | 3.3572e-06 | -6.3191e-05 | 0.0058329 | 0.0058337 | 0.0058337 | 0.99384 | 0.017944 | 0.99383 | 0.017821 | 2.778
51 | 0.19993 | 0.096784 | -0.19993 | -0.096829 | 2.9272e-06 | -4.5024e-05 | 0.0064407 | 0.0064413 | 0.0064413 | 0.99557 | 0.0066083 | 0.99555 | 0.0065117 | 3.0673
52 | -1.8601 | -0.79858 | 1.8626 | 0.78637 | 0.0025092 | -0.012215 | 0.058696 | 0.058549 | 0.058696 | 0.99557 | 0.0066083 | 0.99685 | -0.0018347 | 26.68
53 | 0.18007 | 0.086476 | -0.18006 | -0.087209 | 1.4013e-06 | -0.0007333 | 0.005803 | 0.0058122 | 0.0058122 | 0.9937 | 0.018984 | 0.99369 | 0.019051 | 2.6419
54 | -3.2989 | -1.4433 | 3.306 | 1.4337 | 0.0070809 | -0.0095117 | 0.10427 | 0.10414 | 0.10427 | 0.99685 | -0.0018347 | 0.99888 | -0.016184 | 47.3977
55 | 1.1711 | 0.52853 | -1.1703 | -0.5385 | 0.0007977 | -0.0099641 | 0.037207 | 0.037329 | 0.037329 | 0.99685 | -0.0018347 | 0.99621 | 0.0033088 | 16.9679
56 | 0.26523 | 0.12835 | -0.26523 | -0.12846 | 4.1888e-07 | -0.00010211 | 0.0085328 | 0.0085341 | 0.0085341 | 0.99685 | -0.0018347 | 0.99685 | -0.001821 | 3.8791
57 | -3.6579 | -1.5917 | 3.658 | 1.5916 | 0.00011336 | -0.00011858 | 0.11529 | 0.11528 | 0.11529 | 0.99888 | -0.016184 | 0.99891 | -0.01639 | 52.403
58 | 0.35188 | 0.15793 | -0.35181 | -0.16858 | 7.5177e-05 | -0.01065 | 0.011147 | 0.011276 | 0.011276 | 0.99888 | -0.016184 | 0.99868 | -0.014498 | 5.1257
59 | 0.8309 | 0.37515 | -0.8306 | -0.38263 | 0.00029889 | -0.0074846 | 0.026417 | 0.026509 | 0.026509 | 0.99621 | 0.0033088 | 0.99587 | 0.0060299 | 12.0493
60 | 0.33938 | 0.16335 | -0.33937 | -0.16437 | 6.8299e-06 | -0.0010144 | 0.010914 | 0.010927 | 0.010927 | 0.99621 | 0.0033088 | 0.99619 | 0.0034829 | 4.9668
61 | -3.9258 | -1.7213 | 3.9265 | 1.7206 | 0.00074509 | -0.00064569 | 0.12388 | 0.12387 | 0.12388 | 0.99891 | -0.01639 | 0.99909 | -0.017683 | 56.3079
62 | 0.35181 | 0.16858 | -0.35179 | -0.17038 | 1.2905e-05 | -0.0018028 | 0.011276 | 0.011299 | 0.011299 | 0.99868 | -0.014498 | 0.99864 | -0.014182 | 5.136
63 | 0.34047 | 0.15305 | -0.34043 | -0.15786 | 3.2028e-05 | -0.0048164 | 0.01082 | 0.010879 | 0.010879 | 0.99587 | 0.0060299 | 0.99578 | 0.0067435 | 4.9448
64 | 0.49013 | 0.22958 | -0.49011 | -0.23063 | 1.4561e-05 | -0.0010441 | 0.015689 | 0.015702 | 0.015702 | 0.99587 | 0.0060299 | 0.99584 | 0.006271 | 7.1372
65 | -0.112 | -0.054242 | 0.112 | 0.054176 | 1.2969e-06 | -6.635e-05 | 0.0035948 | 0.003594 | 0.0035948 | 0.99929 | 0.0040935 | 0.9993 | 0.00417 | 1.7118
66 | 0.5235 | 0.24957 | -0.52345 | -0.25304 | 5.4866e-05 | -0.0034656 | 0.016753 | 0.016797 | 0.016797 | 0.9993 | 0.00417 | 0.9992 | 0.0050653 | 7.635
67 | -0.6355 | -0.30375 | 0.6356 | 0.29941 | 0.00010098 | -0.0043384 | 0.020347 | 0.020293 | 0.020347 | 0.9993 | 0.00417 | 0.99945 | 0.0028483 | 9.2488
68 | 0.52345 | 0.25304 | -0.5234 | -0.25311 | 4.3825e-05 | -7.6445e-05 | 0.016797 | 0.016798 | 0.016798 | 0.9992 | 0.0050653 | 0.99911 | 0.0045098 | 7.9992
69 | -0.6356 | -0.29941 | 0.63561 | 0.29912 | 6.5786e-06 | -0.00028349 | 0.020293 | 0.02029 | 0.020293 | 0.99945 | 0.0028483 | 0.99946 | 0.0027637 | 9.2242
70 | -0.9287 | -0.44102 | 0.92912 | 0.43262 | 0.00041862 | -0.0083948 | 0.029691 | 0.029587 | 0.029691 | 0.99957 | 0.0035288 | 0.99999 | -0.00014229 | 13.4961
71 | 0.9287 | 0.44102 | -0.9286 | -0.44103 | 0.00010034 | -1.3337e-05 | 0.029691 | 0.029692 | 0.029692 | 0.99957 | 0.0035288 | 0.99946 | 0.0027637 | 14.1392
72 | 11.5279 | 5.0921 | -11.519 | -5.1119 | 0.0088775 | -0.019803 | 0.36381 | 0.36413 | 0.36413 | 0.99999 | -0.00014229 | 0.99909 | -0.017683 | 43.2461
73 | -12.457 | -5.5247 | 12.4571 | 5.5246 | 7.8016e-05 | -0.00013886 | 0.39339 | 0.39338 | 0.39339 | 0.99999 | -0.00014229 | 1 | 0 | 46.7205
74 | 0.3578 | 0.17291 | -0.35777 | -0.17306 | 3.4679e-05 | -0.00015417 | 0.011482 | 0.011484 | 0.011484 | 0.99911 | 0.0045098 | 0.99901 | 0.0038666 | 5.4686
75 | 0.35777 | 0.17306 | -0.35773 | -0.17325 | 4.3168e-05 | -0.00019176 | 0.011484 | 0.011487 | 0.011487 | 0.99901 | 0.0038666 | 0.99889 | 0.0030693 | 5.4699
76 | 6.5165 | 2.9052 | -6.5131 | -2.9356 | 0.0034293 | -0.030394 | 0.20615 | 0.20655 | 0.20655 | 0.99909 | -0.017683 | 0.99847 | -0.02948 | 24.5307
77 | 1.076 | 0.48612 | -1.0752 | -0.49845 | 0.000824 | -0.01233 | 0.034115 | 0.034266 | 0.034266 | 0.99909 | -0.017683 | 0.99837 | -0.011837 | 15.5755
78 | 0.37077 | 0.16986 | -0.37069 | -0.17948 | 7.5914e-05 | -0.0096152 | 0.011791 | 0.01191 | 0.01191 | 0.99847 | -0.02948 | 0.99828 | -0.027804 | 5.4135
79 | 6.1423 | 2.7657 | -6.1422 | -2.7673 | 0.00015927 | -0.0016013 | 0.19476 | 0.19478 | 0.19478 | 0.99847 | -0.02948 | 0.99844 | -0.030057 | 23.1329
80 | 0.984 | 0.4551 | -0.98375 | -0.45956 | 0.00025041 | -0.0044593 | 0.031348 | 0.031403 | 0.031403 | 0.99837 | -0.011837 | 0.99813 | -0.0098202 | 14.2741
81 | 0.091147 | 0.04335 | -0.091147 | -0.044145 | 3.81e-07 | -0.00079464 | 0.0029184 | 0.0029283 | 0.0029283 | 0.99837 | -0.011837 | 0.99836 | -0.011801 | 1.3311
82 | 0.37069 | 0.17948 | -0.37068 | -0.17953 | 1.2495e-05 | -5.0987e-05 | 0.01191 | 0.011911 | 0.011911 | 0.99828 | -0.027804 | 0.99824 | -0.028027 | 5.6717
83 | 0.54455 | 0.25059 | -0.54445 | -0.25631 | 9.7333e-05 | -0.0057171 | 0.017337 | 0.017407 | 0.017407 | 0.99813 | -0.0098202 | 0.99796 | -0.0083988 | 7.9122
84 | 0.43921 | 0.20896 | -0.43917 | -0.21213 | 3.5368e-05 | -0.0031651 | 0.014067 | 0.014107 | 0.014107 | 0.99813 | -0.0098202 | 0.99806 | -0.0091345 | 6.4121
85 | 0.20145 | 0.096516 | -0.20145 | -0.097567 | 2.4927e-06 | -0.0010513 | 0.0064757 | 0.006489 | 0.006489 | 0.99578 | 0.0067435 | 0.99577 | 0.00685 | 2.9495
86 | 0.13898 | 0.061349 | -0.13898 | -0.067185 | 6.4866e-06 | -0.0058359 | 0.0044041 | 0.0044751 | 0.0044751 | 0.99578 | 0.0067435 | 0.99574 | 0.0071087 | 2.0342
87 | 0.19427 | 0.087342 | -0.19426 | -0.088347 | 2.1665e-06 | -0.0010053 | 0.0061744 | 0.0061864 | 0.0061864 | 0.99584 | 0.006271 | 0.99583 | 0.0063535 | 2.812
88 | 0.13898 | 0.067185 | -0.13898 | -0.067309 | 1.3995e-07 | -0.00012382 | 0.0044751 | 0.0044767 | 0.0044767 | 0.99574 | 0.0071087 | 0.99574 | 0.0071175 | 2.0349
89 | 0.19426 | 0.088347 | -0.19425 | -0.093983 | 1.2304e-05 | -0.0056354 | 0.0061864 | 0.0062558 | 0.0062558 | 0.99583 | 0.0063535 | 0.99578 | 0.006867 | 2.8436
90 | -0.34472 | -0.16695 | 0.34472 | 0.16672 | 1.6256e-06 | -0.00023534 | 0.011081 | 0.011078 | 0.011081 | 0.99783 | -0.0071944 | 0.99783 | -0.0072354 | 5.0368
91 | -0.34472 | -0.16672 | 0.34477 | 0.15964 | 4.8491e-05 | -0.0070795 | 0.011078 | 0.01099 | 0.011078 | 0.99783 | -0.0072354 | 0.99796 | -0.0083988 | 5.0354
92 | 0.19968 | 0.096671 | -0.19968 | -0.096709 | 2.4478e-06 | -3.8126e-05 | 0.0064174 | 0.0064179 | 0.0064179 | 0.99796 | -0.0083988 | 0.99795 | -0.0084797 | 3.0561
93 | 0.43917 | 0.21213 | -0.43916 | -0.2127 | 6.3915e-06 | -0.00057 | 0.014107 | 0.014114 | 0.014114 | 0.99806 | -0.0091345 | 0.99804 | -0.0090081 | 6.4154
94 | -0.19752 | -0.095666 | 0.19753 | 0.095354 | 7.4846e-07 | -0.00031117 | 0.0064461 | 0.0064421 | 0.0064461 | 0.98286 | -0.23287 | 0.98286 | -0.2329 | 2.93
95 | -0.27931 | -0.13497 | 0.27932 | 0.13335 | 7.7547e-06 | -0.0016153 | 0.0091112 | 0.0090906 | 0.0091112 | 0.98286 | -0.2329 | 0.98289 | -0.23314 | 4.1414
96 | -0.27932 | -0.13335 | 0.27939 | 0.11935 | 6.5765e-05 | -0.014 | 0.0090906 | 0.008921 | 0.0090906 | 0.98289 | -0.23314 | 0.98311 | -0.23488 | 4.1321
97 | -0.61595 | -0.28228 | 0.61611 | 0.27531 | 0.00016013 | -0.0069772 | 0.019895 | 0.01981 | 0.019895 | 0.98311 | -0.23488 | 0.98335 | -0.23681 | 9.0434
98 | 0.33657 | 0.16293 | -0.33655 | -0.163 | 1.4197e-05 | -6.7356e-05 | 0.01098 | 0.010981 | 0.010981 | 0.98311 | -0.23488 | 0.98306 | -0.23516 | 5.229
99 | -1.7658 | -0.81802 | 1.7701 | 0.79662 | 0.0042458 | -0.021398 | 0.05713 | 0.056854 | 0.05713 | 0.98335 | -0.23681 | 0.98557 | -0.25503 | 25.9683
100 | 0.34913 | 0.16774 | -0.34912 | -0.16909 | 1.0111e-05 | -0.0013473 | 0.011371 | 0.011388 | 0.011388 | 0.98335 | -0.23681 | 0.98332 | -0.23656 | 5.1764
101 | 0.80058 | 0.37497 | -0.80024 | -0.38357 | 0.0003402 | -0.0085947 | 0.025952 | 0.026061 | 0.026061 | 0.98335 | -0.23681 | 0.98296 | -0.23329 | 11.8461
102 | -0.19425 | -0.094078 | 0.19425 | 0.093983 | 5.8092e-06 | -9.4959e-05 | 0.0062571 | 0.0062558 | 0.0062571 | 0.99574 | 0.0066695 | 0.99578 | 0.006867 | 2.9796
103 | 0.41276 | 0.19602 | -0.41272 | -0.19989 | 4.0589e-05 | -0.0038684 | 0.013419 | 0.013469 | 0.013469 | 0.98296 | -0.23329 | 0.98287 | -0.23245 | 6.1221
104 | 0.38748 | 0.18755 | -0.38745 | -0.18765 | 2.9902e-05 | -0.00010236 | 0.012642 | 0.012644 | 0.012644 | 0.98296 | -0.23329 | 0.98288 | -0.2338 | 6.0209
105 | -1.7701 | -0.79662 | 1.7717 | 0.79732 | 0.0016455 | 0.00069902 | 0.056854 | 0.05685 | 0.056854 | 0.98557 | -0.25503 | 0.98655 | -0.24723 | 27.0735
106 | -1.9944 | -0.90516 | 1.9947 | 0.90373 | 0.00036202 | -0.0014276 | 0.064087 | 0.064068 | 0.064087 | 0.98655 | -0.24723 | 0.98671 | -0.24858 | 29.1304
107 | 0.29177 | 0.14127 | -0.29176 | -0.14131 | 5.2802e-06 | -3.683e-05 | 0.0093731 | 0.0093736 | 0.0093736 | 0.99839 | -0.030685 | 0.99837 | -0.030804 | 4.4636
108 | -2.062 | -0.93538 | 2.0636 | 0.92926 | 0.0016616 | -0.0061158 | 0.066237 | 0.066157 | 0.066237 | 0.9868 | -0.24923 | 0.98754 | -0.25518 | 30.1077
109 | 1.9949 | 0.90304 | -1.9947 | -0.90373 | 0.00017487 | -0.0006901 | 0.064059 | 0.064068 | 0.064068 | 0.9868 | -0.24923 | 0.98671 | -0.24858 | 29.1219
110 | 0.067074 | 0.032341 | -0.067074 | -0.032485 | 3.9223e-08 | -0.00014379 | 0.0021783 | 0.0021802 | 0.0021802 | 0.9868 | -0.24923 | 0.9868 | -0.24922 | 0.99099
111 | -0.33097 | -0.1603 | 0.33097 | 0.15964 | 4.3083e-06 | -0.00065058 | 0.010745 | 0.010737 | 0.010745 | 0.98794 | -0.23778 | 0.98796 | -0.23789 | 4.8843
112 | -0.33097 | -0.15964 | 0.33098 | 0.15823 | 9.367e-06 | -0.001418 | 0.010737 | 0.010719 | 0.010737 | 0.98796 | -0.23789 | 0.98798 | -0.23814 | 4.8805

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 12.7066 | 5.6491

## res_load
| p_mw | q_mvar
0 | 0.063258 | 0.030637
1 | 0.16374 | 0.079304
2 | 0.14767 | 0.071518
3 | 0.14669 | 0.071044
4 | 0.40508 | 0.19619
5 | 0.10356 | 0.050155
6 | 0.096168 | 0.046576
7 | 0.25431 | 0.12317
8 | 0.13318 | 0.064503
9 | 0.13827 | 0.066969
10 | 0.15287 | 0.07404
11 | 0.13746 | 0.066576
12 | 0.11183 | 0.054161
13 | 0.15288 | 0.074042
14 | 0.1221 | 0.059138
15 | 0.053953 | 0.02613
16 | 0.081729 | 0.039583
17 | 0.10277 | 0.049775
18 | 0.092618 | 0.044857
19 | 0.092477 | 0.044789
20 | 0.39074 | 0.18924
21 | 0.29972 | 0.14516
22 | 0.36735 | 0.17792
23 | 0.40627 | 0.19676
24 | 0.18076 | 0.087544
25 | 0.26523 | 0.12846
26 | 0.19993 | 0.096829
27 | 0.18006 | 0.087209
28 | 0.2678 | 0.1297
29 | 0.35179 | 0.17038
30 | 0.33937 | 0.16437
31 | 0.112 | 0.054242
32 | 0.293 | 0.1419
33 | 0.1656 | 0.080204
34 | 0.35773 | 0.17325
35 | 0.23549 | 0.11405
36 | 0.09635 | 0.046665
37 | 0.37068 | 0.17953
38 | 0.091147 | 0.044145
39 | 0.29585 | 0.14329
40 | 0.20145 | 0.097567
41 | 0.13898 | 0.067309
42 | 0.34472 | 0.16695
43 | 0.43916 | 0.2127
44 | 0.19752 | 0.095666
45 | 0.081787 | 0.039611
46 | 0.19968 | 0.096709
47 | 0.33655 | 0.163
48 | 0.19425 | 0.094078
49 | 0.41272 | 0.19989
50 | 0.38745 | 0.18765
51 | 0.34912 | 0.16909
52 | 0.22265 | 0.10784
53 | 0.29176 | 0.14131
54 | 0.067074 | 0.032485
55 | 0.33097 | 0.1603
56 | 0.39905 | 0.19327

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1