## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_447_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_447_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_447_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_447_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_447_0_node_7 | 20 | n |  | TRUE
5 | bus_MV_447_0_node_63 | 20 | n |  | TRUE
6 | bus_MV_447_0_node_4 | 20 | n |  | TRUE
7 | bus_MV_447_0_node_6 | 20 | n |  | TRUE
8 | bus_MV_447_0_node_9 | 20 | n |  | TRUE
9 | bus_MV_447_0_node_11 | 20 | n |  | TRUE
10 | bus_MV_447_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_447_0_node_72 | 20 | n |  | TRUE
12 | bus_MV_447_0_node_15 | 20 | n |  | TRUE
13 | bus_MV_447_0_node_62 | 20 | n |  | TRUE
14 | bus_MV_447_0_node_8 | 20 | n |  | TRUE
15 | bus_MV_447_0_node_61 | 20 | n |  | TRUE
16 | bus_MV_447_0_node_60 | 20 | n |  | TRUE
17 | bus_MV_447_0_node_14 | 20 | n |  | TRUE
18 | bus_MV_447_0_node_16 | 20 | n |  | TRUE
19 | bus_MV_447_0_node_10 | 20 | n |  | TRUE
20 | bus_MV_447_0_node_12 | 20 | n |  | TRUE
21 | bus_MV_447_0_node_71 | 20 | n |  | TRUE
22 | bus_MV_447_0_node_13 | 20 | n |  | TRUE
23 | bus_MV_447_0_node_20 | 20 | n |  | TRUE
24 | bus_MV_447_0_node_22 | 20 | n |  | TRUE
25 | bus_MV_447_0_node_17 | 20 | n |  | TRUE
26 | bus_MV_447_0_node_18 | 20 | n |  | TRUE
27 | bus_MV_447_0_node_58 | 20 | n |  | TRUE
28 | bus_MV_447_0_node_23 | 20 | n |  | TRUE
29 | bus_MV_447_0_node_44 | 20 | n |  | TRUE
30 | bus_MV_447_0_node_46 | 20 | n |  | TRUE
31 | bus_MV_447_0_node_59 | 20 | n |  | TRUE
32 | bus_MV_447_0_node_21 | 20 | n |  | TRUE
33 | bus_MV_447_0_node_51 | 20 | n |  | TRUE
34 | bus_MV_447_0_node_45 | 20 | n |  | TRUE
35 | bus_MV_447_0_node_39 | 20 | n |  | TRUE
36 | bus_MV_447_0_node_43 | 20 | n |  | TRUE
37 | bus_MV_447_0_node_47 | 20 | n |  | TRUE
38 | bus_MV_447_0_node_24 | 20 | n |  | TRUE
39 | bus_MV_447_0_node_26 | 20 | n |  | TRUE
40 | bus_MV_447_0_node_27 | 20 | n |  | TRUE
41 | bus_MV_447_0_node_31 | 20 | n |  | TRUE
42 | bus_MV_447_0_node_73 | 20 | n |  | TRUE
43 | bus_MV_447_0_node_30 | 20 | n |  | TRUE
44 | bus_MV_447_0_node_50 | 20 | n |  | TRUE
45 | bus_MV_447_0_node_28 | 20 | n |  | TRUE
46 | bus_MV_447_0_node_57 | 20 | n |  | TRUE
47 | bus_MV_447_0_node_56 | 20 | n |  | TRUE
48 | bus_MV_447_0_node_29 | 20 | n |  | TRUE
49 | bus_MV_447_0_node_54 | 20 | n |  | TRUE
50 | bus_MV_447_0_node_53 | 20 | n |  | TRUE
51 | bus_MV_447_0_node_52 | 20 | n |  | TRUE
52 | bus_MV_447_0_node_49 | 20 | n |  | TRUE
53 | bus_MV_447_0_node_69 | 20 | n |  | TRUE
54 | bus_MV_447_0_node_76 | 20 | n |  | TRUE
55 | bus_MV_447_0_node_77 | 20 | n |  | TRUE
56 | bus_MV_447_0_node_78 | 20 | n |  | TRUE
57 | bus_MV_447_0_node_48 | 20 | n |  | TRUE
58 | bus_MV_447_0_node_33 | 20 | n |  | TRUE
59 | bus_MV_447_0_node_74 | 20 | n |  | TRUE
60 | bus_MV_447_0_node_32 | 20 | n |  | TRUE
61 | bus_MV_447_0_node_64 | 20 | n |  | TRUE
62 | bus_MV_447_0_node_55 | 20 | n |  | TRUE
63 | bus_MV_447_0_node_34 | 20 | n |  | TRUE
64 | bus_MV_447_0_node_35 | 20 | n |  | TRUE
65 | bus_MV_447_0_node_36 | 20 | n |  | TRUE
66 | bus_MV_447_0_node_75 | 20 | n |  | TRUE
67 | bus_MV_447_0_node_66 | 20 | n |  | TRUE
68 | bus_MV_447_0_node_68 | 20 | n |  | TRUE
69 | bus_MV_447_0_node_37 | 20 | n |  | TRUE
70 | bus_MV_447_0_node_38 | 20 | n |  | TRUE
71 | bus_MV_447_0_node_40 | 20 | n |  | TRUE
72 | bus_MV_447_0_node_70 | 20 | n |  | TRUE
73 | bus_MV_447_0_node_42 | 20 | n |  | TRUE
74 | bus_MV_447_0_node_67 | 20 | n |  | TRUE
75 | bus_MV_447_0_node_80 | 20 | n |  | TRUE
76 | bus_MV_447_0_node_79 | 20 | n |  | TRUE
77 | bus_HV_447_0_node_46 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_447_0_load_0 | 0 | 0.27039 | 0.13095 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_447_0_load_3 | 2 | 0.13193 | 0.063897 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_447_0_load_63 | 5 | 0.23604 | 0.11432 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_447_0_load_4 | 6 | 0.19855 | 0.09616 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_447_0_load_9 | 8 | 0.30318 | 0.14684 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_447_0_load_5 | 10 | 0.053558 | 0.025939 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_447_0_load_72 | 11 | 0.40647 | 0.19686 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_447_0_load_8 | 14 | 0.22835 | 0.1106 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_447_0_load_61 | 15 | 0.36676 | 0.17763 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_447_0_load_16 | 18 | 0.27784 | 0.13457 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_447_0_load_71 | 21 | 0.15527 | 0.075201 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_447_0_load_17 | 25 | 0.21604 | 0.10463 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_447_0_load_18 | 26 | 0.22555 | 0.10924 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_447_0_load_58 | 27 | 0.22103 | 0.10705 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_447_0_load_59 | 31 | 0.26314 | 0.12745 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_447_0_load_51 | 33 | 0.092971 | 0.045028 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_447_0_load_43 | 36 | 0.54496 | 0.26394 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_447_0_load_47 | 37 | 0.057134 | 0.027671 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_447_0_load_24 | 38 | 0.41376 | 0.20039 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_447_0_load_73 | 42 | 0.36764 | 0.17806 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_447_0_load_56 | 47 | 0.075262 | 0.036451 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_447_0_load_53 | 50 | 0.09831 | 0.047614 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_447_0_load_52 | 51 | 0.075498 | 0.036565 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_447_0_load_49 | 52 | 0.098867 | 0.047883 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_447_0_load_69 | 53 | 0.31453 | 0.15233 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_447_0_load_76 | 54 | 0.058256 | 0.028215 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_447_0_load_77 | 55 | 0.18517 | 0.089681 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_447_0_load_78 | 56 | 0.1701 | 0.082385 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_447_0_load_48 | 57 | 0.099147 | 0.048019 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_447_0_load_74 | 59 | 0.38564 | 0.18677 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_447_0_load_64 | 61 | 0.34548 | 0.16732 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_447_0_load_55 | 62 | 0.11318 | 0.054815 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_447_0_load_34 | 63 | 0.29971 | 0.14516 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_447_0_load_75 | 66 | 0.2616 | 0.1267 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_447_0_load_37 | 69 | 2.9817 | 1.4441 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_447_0_load_40 | 71 | 1.1715 | 0.56737 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_447_0_load_70 | 72 | 0.40015 | 0.1938 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_447_0_load_42 | 73 | 0.13399 | 0.064893 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_447_0_load_80 | 75 | 0.10626 | 0.051466 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_447_0_load_79 | 76 | 0.11065 | 0.053592 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_447_0_line_0 |  | 0 | 1 | 0.035326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_447_0_line_1 |  | 0 | 2 | 0.55642 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_447_0_line_2 |  | 1 | 3 | 0.42063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_447_0_line_3 |  | 3 | 6 | 0.038713 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_447_0_line_4 |  | 4 | 5 | 0.014818 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_447_0_line_5 |  | 4 | 6 | 1.9214 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_447_0_line_6 |  | 4 | 7 | 0.81617 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_447_0_line_7 |  | 5 | 13 | 0.067242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_447_0_line_8 |  | 7 | 10 | 0.03739 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_447_0_line_9 |  | 8 | 9 | 0.004038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_447_0_line_10 |  | 9 | 19 | 0.0893 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_447_0_line_11 |  | 10 | 11 | 0.64339 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_447_0_line_12 |  | 11 | 12 | 0.024903 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_447_0_line_13 |  | 12 | 17 | 0.14351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_447_0_line_14 |  | 13 | 16 | 0.27188 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_447_0_line_15 |  | 14 | 15 | 0.21566 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_447_0_line_16 |  | 15 | 16 | 0.006269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_447_0_line_17 |  | 17 | 18 | 0.070111 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_447_0_line_18 |  | 17 | 19 | 0.71727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_447_0_line_19 |  | 19 | 20 | 0.60752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_447_0_line_20 |  | 20 | 21 | 0.031565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_447_0_line_21 |  | 20 | 22 | 0.40171 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_447_0_line_22 |  | 20 | 23 | 0.32136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_447_0_line_23 |  | 20 | 24 | 0.32015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_447_0_line_24 |  | 22 | 25 | 0.040878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_447_0_line_25 |  | 23 | 26 | 0.016047 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_447_0_line_26 |  | 24 | 27 | 0.059842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_447_0_line_27 |  | 24 | 28 | 0.27144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_447_0_line_28 |  | 26 | 32 | 0.12727 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_447_0_line_29 |  | 28 | 29 | 0.622 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
30 | MV_447_0_line_30 |  | 28 | 30 | 0.59745 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
31 | MV_447_0_line_31 |  | 28 | 31 | 0.037813 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_447_0_line_32 |  | 29 | 34 | 0.11787 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_447_0_line_33 |  | 29 | 35 | 0.39197 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
34 | MV_447_0_line_34 |  | 29 | 36 | 0.021612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_447_0_line_35 |  | 30 | 37 | 0.16129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_447_0_line_36 |  | 32 | 33 | 0.041507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_447_0_line_37 |  | 34 | 72 | 0.049362 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_447_0_line_38 |  | 35 | 71 | 0.061236 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_447_0_line_39 |  | 35 | 70 | 0.09404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_447_0_line_40 |  | 36 | 73 | 0.016109 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_447_0_line_41 |  | 37 | 57 | 0.49607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_447_0_line_42 |  | 38 | 39 | 0.025207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_447_0_line_43 |  | 38 | 40 | 0.26734 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_447_0_line_44 |  | 39 | 41 | 0.51784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_447_0_line_45 |  | 40 | 42 | 0.007503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_447_0_line_46 |  | 40 | 43 | 0.21279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_447_0_line_47 |  | 40 | 44 | 0.20744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_447_0_line_48 |  | 41 | 58 | 0.62895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_447_0_line_49 |  | 41 | 59 | 0.042344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_447_0_line_50 |  | 43 | 51 | 0.028165 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_447_0_line_51 |  | 43 | 45 | 0.19153 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_447_0_line_52 |  | 43 | 48 | 0.16679 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_447_0_line_53 |  | 44 | 52 | 0.044307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_447_0_line_54 |  | 45 | 46 | 0.098507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_447_0_line_55 |  | 45 | 47 | 0.032124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_447_0_line_56 |  | 46 | 54 | 0.046741 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_447_0_line_57 |  | 48 | 49 | 0.15055 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_447_0_line_58 |  | 48 | 50 | 0.057497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_447_0_line_59 |  | 49 | 53 | 0.009658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_447_0_line_60 |  | 54 | 55 | 0.049158 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_447_0_line_61 |  | 54 | 56 | 0.050265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_447_0_line_62 |  | 56 | 57 | 0.63854 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_447_0_line_63 |  | 58 | 62 | 0.039341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_447_0_line_64 |  | 58 | 63 | 0.21799 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_447_0_line_65 |  | 58 | 60 | 0.30717 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_447_0_line_66 |  | 60 | 61 | 0.052528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_447_0_line_67 |  | 63 | 64 | 0.043084 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_447_0_line_68 |  | 64 | 65 | 0.49307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_447_0_line_69 |  | 65 | 66 | 0.062435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_447_0_line_70 |  | 66 | 67 | 0.033863 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_447_0_line_71 |  | 67 | 68 | 0.98397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_447_0_line_72 |  | 68 | 76 | 0.020003 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_447_0_line_73 |  | 68 | 74 | 0.30816 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_447_0_line_74 |  | 69 | 70 | 0.073522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_447_0_line_75 |  | 74 | 75 | 0.014362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_447_0_trafo_46 | 25 MVA 110/20 kV | 77 | 30 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2534435.2862 | 1161828.3208
1 | 2534433.6002 | 1161793.2309
2 | 2534533.3777 | 1162376.0312
3 | 2534553.7189 | 1161469.8747
4 | 2536492.1442 | 1161344.9435
5 | 2536502.7443 | 1161355.326
6 | 2534577.0894 | 1161500.737
7 | 2536377.4586 | 1160639.7925
8 | 2535994.6452 | 1159914.8958
9 | 2535998.5281 | 1159916.044
10 | 2536410.1103 | 1160621.4143
11 | 2536274.3378 | 1159992.5083
12 | 2536273.7822 | 1159967.6116
13 | 2536548.6239 | 1161404.1344
14 | 2536940.1095 | 1161417.2056
15 | 2536741.1225 | 1161334.0534
16 | 2536739.4496 | 1161328.0121
17 | 2536352.9576 | 1159966.249
18 | 2536379.9095 | 1159916.6917
19 | 2536022.4135 | 1159829.9977
20 | 2536260.2286 | 1159500.3879
21 | 2536284.3639 | 1159479.965
22 | 2536533.9475 | 1159432.0293
23 | 2536300.6453 | 1159264.0628
24 | 2536010.3784 | 1159529.3386
25 | 2536573.645 | 1159421.8154
26 | 2536306.7351 | 1159249.2122
27 | 2535981.0016 | 1159581.4025
28 | 2535838.1088 | 1159406.309
29 | 2535352.83 | 1159239.8326
30 | 2535677.1724 | 1159006.0105
31 | 2535804.0515 | 1159422.7375
32 | 2536349.0325 | 1159129.1758
33 | 2536318.4568 | 1159120.9698
34 | 2535283.7858 | 1159314.3728
35 | 2535072.302 | 1158966.0747
36 | 2535363.5315 | 1159258.5981
37 | 2535624.0332 | 1158857.3204
38 | 2535925.7578 | 1157476.681
39 | 2535919.3099 | 1157452.3142
40 | 2535872.6203 | 1157738.6917
41 | 2535645.0424 | 1157425.1311
42 | 2535865.4368 | 1157740.9251
43 | 2536017.4641 | 1157745.84
44 | 2535848.5581 | 1157894.9343
45 | 2535940.2417 | 1157808.6641
46 | 2535974.5282 | 1157887.5974
47 | 2535909.0516 | 1157816.3545
48 | 2536056.079 | 1157775.5451
49 | 2536081.6342 | 1157923.9101
50 | 2536111.5086 | 1157763.3109
51 | 2536006.6224 | 1157770.3834
52 | 2535858.6184 | 1157938.0839
53 | 2536091.295 | 1157923.2069
54 | 2535985.7842 | 1157932.9579
55 | 2536033.5624 | 1157944.522
56 | 2535963.2667 | 1157977.8974
57 | 2536054.0292 | 1158609.9559
58 | 2535848.8557 | 1157005.6101
59 | 2535676.953 | 1157427.7352
60 | 2535991.3981 | 1157241.2078
61 | 2536025.5975 | 1157280.7985
62 | 2535810.1918 | 1157012.8793
63 | 2535978.1972 | 1156830.1343
64 | 2536021.2677 | 1156829.075
65 | 2536264.8572 | 1157018.2451
66 | 2536319.8443 | 1157043.3535
67 | 2536342.9353 | 1157068.1224
68 | 2536727.0469 | 1156698.0069
69 | 2534999.6415 | 1158887.1165
70 | 2535071.6315 | 1158872.1858
71 | 2535011.2708 | 1158971.0723
72 | 2535255.778 | 1159355.0193
73 | 2535372.3869 | 1159272.0546
74 | 2536681.3178 | 1156721.9351
75 | 2536667.5763 | 1156717.6331
76 | 2536746.3082 | 1156703.5961
77 | 2535677.1724 | 1159006.0105

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98553 | 0.029992 | 0.27039 | 0.13095
1 | 0.98555 | 0.029819 | 0 | 0
2 | 0.98539 | 0.029063 | 0.13193 | 0.063897
3 | 0.98577 | 0.02791 | 0 | 0
4 | 0.98804 | 0.044548 | 0 | 0
5 | 0.98803 | 0.044691 | 0.23604 | 0.11432
6 | 0.9858 | 0.028142 | 0.19855 | 0.09616
7 | 0.98954 | 0.031907 | 0 | 0
8 | 0.99383 | 0.026657 | 0.30318 | 0.14684
9 | 0.99383 | 0.026642 | 0 | 0
10 | 0.98961 | 0.031353 | 0.053558 | 0.025939
11 | 0.99146 | 0.045543 | 0.40647 | 0.19686
12 | 0.99155 | 0.046216 | 0 | 0
13 | 0.98798 | 0.045148 | 0 | 0
14 | 0.98767 | 0.046502 | 0.22835 | 0.1106
15 | 0.98776 | 0.047114 | 0.36676 | 0.17763
16 | 0.98777 | 0.047069 | 0 | 0
17 | 0.9919 | 0.043315 | 0 | 0
18 | 0.99187 | 0.043548 | 0.27784 | 0.13457
19 | 0.99389 | 0.026975 | 0 | 0
20 | 0.9958 | 0.011581 | 0 | 0
21 | 0.9958 | 0.01164 | 0.15527 | 0.075201
22 | 0.99569 | 0.012481 | 0 | 0
23 | 0.99567 | 0.012707 | 0 | 0
24 | 0.99709 | 0.0014786 | 0 | 0
25 | 0.99568 | 0.012586 | 0.21604 | 0.10463
26 | 0.99567 | 0.012767 | 0.22555 | 0.10924
27 | 0.99708 | 0.001635 | 0.22103 | 0.10705
28 | 0.99826 | -0.0076405 | 0 | 0
29 | 0.99649 | -0.026195 | 0 | 0
30 | 1 | 0 | -12.6262 | -5.807
31 | 0.99824 | -0.0077612 | 0.26314 | 0.12745
32 | 0.99565 | 0.012611 | 0 | 0
33 | 0.99564 | 0.012657 | 0.092971 | 0.045028
34 | 0.99643 | -0.025638 | 0 | 0
35 | 0.99454 | -0.073805 | 0 | 0
36 | 0.99647 | -0.026019 | 0.54496 | 0.26394
37 | 0.99925 | 0.0057581 | 0.057134 | 0.027671
38 | 0.98948 | -0.0018219 | 0.41376 | 0.20039
39 | 0.98942 | -0.0014556 | 0 | 0
40 | 0.99052 | 0.0068164 | 0 | 0
41 | 0.98835 | 0.0062934 | 0 | 0
42 | 0.99052 | 0.00685 | 0.36764 | 0.17806
43 | 0.9912 | 0.0015676 | 0 | 0
44 | 0.9905 | 0.0070198 | 0 | 0
45 | 0.99193 | -0.0041091 | 0 | 0
46 | 0.99232 | -0.0070891 | 0 | 0
47 | 0.99193 | -0.0040805 | 0.075262 | 0.036451
48 | 0.99111 | 0.0023297 | 0 | 0
49 | 0.99105 | 0.002887 | 0 | 0
50 | 0.99111 | 0.002396 | 0.09831 | 0.047614
51 | 0.9912 | 0.0015929 | 0.075498 | 0.036565
52 | 0.99049 | 0.0070717 | 0.098867 | 0.047883
53 | 0.99105 | 0.002924 | 0.31453 | 0.15233
54 | 0.9925 | -0.008497 | 0.058256 | 0.028215
55 | 0.99249 | -0.0083883 | 0.18517 | 0.089681
56 | 0.99271 | -0.010152 | 0.1701 | 0.082385
57 | 0.99699 | 0.02343 | 0.099147 | 0.048019
58 | 0.98736 | 0.013341 | 0 | 0
59 | 0.98833 | 0.006492 | 0.38564 | 0.18677
60 | 0.98723 | 0.014547 | 0 | 0
61 | 0.9872 | 0.014768 | 0.34548 | 0.16732
62 | 0.98736 | 0.013395 | 0.11318 | 0.054815
63 | 0.98704 | 0.0104 | 0.29971 | 0.14516
64 | 0.987 | 0.009979 | 0 | 0
65 | 0.9867 | 0.01165 | 0 | 0
66 | 0.98667 | 0.011888 | 0.2616 | 0.1267
67 | 0.98665 | 0.011705 | 0 | 0
68 | 0.98638 | 0.01308 | 0 | 0
69 | 0.9939 | -0.067779 | 2.9817 | 1.4441
70 | 0.99418 | -0.07043 | 0 | 0
71 | 0.99445 | -0.07294 | 1.1715 | 0.56737
72 | 0.99639 | -0.025878 | 0.40015 | 0.1938
73 | 0.99647 | -0.025993 | 0.13399 | 0.064893
74 | 0.98634 | 0.013404 | 0 | 0
75 | 0.98634 | 0.013422 | 0.10626 | 0.051466
76 | 0.98638 | 0.013107 | 0.11065 | 0.053592
77 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.40234 | -0.19422 | 0.40235 | 0.1934 | 8.0697e-06 | -0.00081684 | 0.013086 | 0.013076 | 0.013086 | 0.98553 | 0.029992 | 0.98555 | 0.029819 | 5.9483
1 | 0.13195 | 0.063264 | -0.13193 | -0.063897 | 1.8248e-05 | -0.00063366 | 0.0042862 | 0.0042944 | 0.0042944 | 0.98553 | 0.029992 | 0.98539 | 0.029063 | 2.045
2 | -0.40235 | -0.1934 | 0.40244 | 0.18367 | 9.5114e-05 | -0.0097289 | 0.013076 | 0.012955 | 0.013076 | 0.98555 | 0.029819 | 0.98577 | 0.02791 | 5.9436
3 | -0.40244 | -0.18367 | 0.40245 | 0.18364 | 1.1575e-05 | -3.766e-05 | 0.012955 | 0.012954 | 0.012955 | 0.98577 | 0.02791 | 0.9858 | 0.028142 | 6.1689
4 | 0.83136 | 0.39397 | -0.83134 | -0.39431 | 1.4294e-05 | -0.00034114 | 0.026879 | 0.026883 | 0.026883 | 0.98804 | 0.044548 | 0.98803 | 0.044691 | 12.2197
5 | 0.60229 | 0.27837 | -0.601 | -0.2798 | 0.0012883 | -0.0014272 | 0.019386 | 0.019413 | 0.019413 | 0.98804 | 0.044548 | 0.9858 | 0.028142 | 9.2443
6 | -1.4336 | -0.67234 | 1.436 | 0.65397 | 0.0023203 | -0.018364 | 0.046264 | 0.046031 | 0.046264 | 0.98804 | 0.044548 | 0.98954 | 0.031907 | 21.0291
7 | 0.5953 | 0.27999 | -0.59527 | -0.28155 | 3.3198e-05 | -0.0015573 | 0.019221 | 0.01924 | 0.01924 | 0.98803 | 0.044691 | 0.98798 | 0.045148 | 8.7456
8 | -1.436 | -0.65397 | 1.4361 | 0.65313 | 0.00010574 | -0.00084285 | 0.046031 | 0.04602 | 0.046031 | 0.98954 | 0.031907 | 0.98961 | 0.031353 | 20.923
9 | -0.30318 | -0.14684 | 0.30318 | 0.14674 | 5.1608e-07 | -9.5073e-05 | 0.009785 | 0.0097838 | 0.009785 | 0.99383 | 0.026657 | 0.99383 | 0.026642 | 4.4477
10 | -0.30318 | -0.14674 | 0.3032 | 0.14665 | 1.5228e-05 | -9.5763e-05 | 0.0097838 | 0.0097824 | 0.0097838 | 0.99383 | 0.026642 | 0.99389 | 0.026975 | 4.6589
11 | -1.4896 | -0.67907 | 1.4922 | 0.67995 | 0.0026138 | 0.0008836 | 0.047755 | 0.047746 | 0.047755 | 0.98961 | 0.031353 | 0.99146 | 0.045543 | 22.7407
12 | -1.8987 | -0.87681 | 1.8989 | 0.87689 | 0.00016452 | 7.3824e-05 | 0.060893 | 0.060893 | 0.060893 | 0.99146 | 0.045543 | 0.99155 | 0.046216 | 28.9968
13 | -1.8989 | -0.87689 | 1.8996 | 0.87373 | 0.00070993 | -0.0031595 | 0.060893 | 0.060852 | 0.060893 | 0.99155 | 0.046216 | 0.9919 | 0.043315 | 27.6786
14 | 0.59527 | 0.28155 | -0.59513 | -0.28784 | 0.00013492 | -0.0062948 | 0.01924 | 0.01932 | 0.01932 | 0.98798 | 0.045148 | 0.98777 | 0.047069 | 8.7819
15 | -0.22835 | -0.1106 | 0.22837 | 0.11036 | 2.1122e-05 | -0.00023794 | 0.0074158 | 0.0074126 | 0.0074158 | 0.98767 | 0.046502 | 0.98776 | 0.047114 | 3.5313
16 | -0.59513 | -0.28799 | 0.59513 | 0.28784 | 3.1243e-06 | -0.00014511 | 0.019322 | 0.01932 | 0.019322 | 0.98776 | 0.047114 | 0.98777 | 0.047069 | 8.7828
17 | 0.27785 | 0.13292 | -0.27784 | -0.13457 | 7.5384e-06 | -0.0016447 | 0.0089641 | 0.0089848 | 0.0089848 | 0.9919 | 0.043315 | 0.99187 | 0.043548 | 4.084
18 | -2.1774 | -1.0066 | 2.1821 | 0.99115 | 0.0046536 | -0.015503 | 0.069815 | 0.06961 | 0.069815 | 0.9919 | 0.043315 | 0.99389 | 0.026975 | 31.7341
19 | -2.4853 | -1.1378 | 2.4904 | 1.1249 | 0.0051008 | -0.012843 | 0.07939 | 0.079218 | 0.07939 | 0.99389 | 0.026975 | 0.9958 | 0.011581 | 36.0866
20 | 0.15527 | 0.074454 | -0.15527 | -0.075201 | 1.0521e-06 | -0.00074702 | 0.0049919 | 0.0050013 | 0.0050013 | 0.9958 | 0.011581 | 0.9958 | 0.01164 | 2.2733
21 | 0.21607 | 0.094163 | -0.21604 | -0.10367 | 2.5449e-05 | -0.0095023 | 0.0068326 | 0.0069473 | 0.0069473 | 0.9958 | 0.011581 | 0.99569 | 0.012481 | 3.1579
22 | 0.31857 | 0.14516 | -0.31853 | -0.15276 | 4.459e-05 | -0.0075943 | 0.010149 | 0.010242 | 0.010242 | 0.9958 | 0.011581 | 0.99567 | 0.012707 | 4.6555
23 | -3.1803 | -1.4387 | 3.1847 | 1.4324 | 0.0043723 | -0.0062927 | 0.10119 | 0.1011 | 0.10119 | 0.9958 | 0.011581 | 0.99709 | 0.0014786 | 45.9951
24 | 0.21604 | 0.10367 | -0.21604 | -0.10463 | 2.6385e-06 | -0.00096683 | 0.0069473 | 0.0069595 | 0.0069595 | 0.99569 | 0.012481 | 0.99568 | 0.012586 | 3.1634
25 | 0.31853 | 0.15276 | -0.31853 | -0.15314 | 2.2483e-06 | -0.00037916 | 0.010242 | 0.010247 | 0.010247 | 0.99567 | 0.012707 | 0.99567 | 0.012767 | 4.6577
26 | 0.22104 | 0.10563 | -0.22103 | -0.10705 | 4.0289e-06 | -0.0014193 | 0.0070926 | 0.0071104 | 0.0071104 | 0.99709 | 0.0014786 | 0.99708 | 0.001635 | 3.232
27 | -3.4057 | -1.5381 | 3.4099 | 1.5329 | 0.0042385 | -0.0051935 | 0.10819 | 0.10811 | 0.10819 | 0.99709 | 0.0014786 | 0.99826 | -0.0076405 | 49.1772
28 | 0.092973 | 0.043896 | -0.092971 | -0.044046 | 2.0162e-06 | -0.00014936 | 0.0029809 | 0.0029828 | 0.0029828 | 0.99567 | 0.012767 | 0.99565 | 0.012611 | 1.4204
29 | 5.2495 | 2.5175 | -5.241 | -2.5325 | 0.0085288 | -0.015029 | 0.16836 | 0.16862 | 0.16862 | 0.99826 | -0.0076405 | 0.99649 | -0.026195 | 46.581
30 | -8.9226 | -4.1778 | 8.9375 | 4.1487 | 0.014961 | -0.029049 | 0.2849 | 0.28445 | 0.2849 | 0.99826 | -0.0076405 | 1 | 0 | 44.6558
31 | 0.26315 | 0.1274 | -0.26314 | -0.12745 | 4.816e-06 | -4.1967e-05 | 0.0084546 | 0.0084552 | 0.0084552 | 0.99826 | -0.0076405 | 0.99824 | -0.0077612 | 4.0263
32 | 0.40019 | 0.19096 | -0.40016 | -0.19375 | 2.6036e-05 | -0.0027867 | 0.012845 | 0.012881 | 0.012881 | 0.99649 | -0.026195 | 0.99643 | -0.025638 | 5.8548
33 | 4.1618 | 2.0136 | -4.1553 | -2.0067 | 0.0064551 | 0.0068951 | 0.13393 | 0.13394 | 0.13394 | 0.99649 | -0.026195 | 0.99454 | -0.073805 | 38.2688
34 | 0.67897 | 0.32794 | -0.67895 | -0.32845 | 1.377e-05 | -0.00050829 | 0.021843 | 0.02185 | 0.02185 | 0.99649 | -0.026195 | 0.99647 | -0.026019 | 9.9317
35 | 3.6746 | 1.6477 | -3.6717 | -1.6507 | 0.0029111 | -0.0029845 | 0.11625 | 0.1163 | 0.1163 | 1 | 0 | 0.99925 | 0.0057581 | 52.8631
36 | 0.092971 | 0.044046 | -0.092971 | -0.045028 | 4.9503e-07 | -0.00098226 | 0.0029828 | 0.0029951 | 0.0029951 | 0.99565 | 0.012611 | 0.99564 | 0.012657 | 1.3614
37 | 0.40016 | 0.19375 | -0.40015 | -0.1938 | 1.4592e-05 | -4.9366e-05 | 0.012881 | 0.012881 | 0.012881 | 0.99643 | -0.025638 | 0.99639 | -0.025878 | 6.134
38 | 1.1716 | 0.56595 | -1.1715 | -0.56737 | 0.00011665 | -0.0014114 | 0.037766 | 0.037784 | 0.037784 | 0.99454 | -0.073805 | 0.99445 | -0.07294 | 17.1747
39 | 2.9838 | 1.4408 | -2.9826 | -1.4426 | 0.0011616 | -0.0018755 | 0.096175 | 0.096203 | 0.096203 | 0.99454 | -0.073805 | 0.99418 | -0.07043 | 43.7286
40 | 0.13399 | 0.064511 | -0.13399 | -0.064893 | 3.9957e-07 | -0.00038179 | 0.0043081 | 0.0043129 | 0.0043129 | 0.99647 | -0.026019 | 0.99647 | -0.025993 | 1.9604
41 | 3.6146 | 1.6231 | -3.6059 | -1.6323 | 0.0086877 | -0.0092227 | 0.11447 | 0.11461 | 0.11461 | 0.99925 | 0.0057581 | 0.99699 | 0.02343 | 52.0936
42 | 1.6263 | 0.70535 | -1.6262 | -0.70591 | 9.002e-05 | -0.00056251 | 0.051718 | 0.051725 | 0.051725 | 0.98948 | -0.0018219 | 0.98942 | -0.0014556 | 23.5112
43 | -2.0401 | -0.90574 | 2.0421 | 0.90669 | 0.0020199 | 0.00095238 | 0.065121 | 0.065117 | 0.065121 | 0.98948 | -0.0018219 | 0.99052 | 0.0068164 | 31.01
44 | 1.6262 | 0.70591 | -1.6244 | -0.71745 | 0.0018546 | -0.011541 | 0.051725 | 0.051866 | 0.051866 | 0.98942 | -0.0014556 | 0.98835 | 0.0062934 | 23.5756
45 | 0.36764 | 0.17788 | -0.36764 | -0.17806 | 1.4193e-06 | -0.00017534 | 0.011903 | 0.011905 | 0.011905 | 0.99052 | 0.0068164 | 0.99052 | 0.00685 | 5.4113
46 | -2.5086 | -1.1266 | 2.5104 | 1.1221 | 0.0018233 | -0.0044473 | 0.080144 | 0.080085 | 0.080144 | 0.99052 | 0.0068164 | 0.9912 | 0.0015676 | 36.4293
47 | 0.09887 | 0.041987 | -0.098867 | -0.046846 | 2.7633e-06 | -0.0048584 | 0.0031305 | 0.0031885 | 0.0031885 | 0.99052 | 0.0068164 | 0.9905 | 0.0070198 | 1.4493
48 | 1.2387 | 0.53167 | -1.2374 | -0.54593 | 0.0013073 | -0.014267 | 0.039373 | 0.039543 | 0.039543 | 0.98835 | 0.0062934 | 0.98736 | 0.013341 | 17.9743
49 | 0.38564 | 0.18579 | -0.38564 | -0.18677 | 8.8454e-06 | -0.00098495 | 0.012503 | 0.012515 | 0.012515 | 0.98835 | 0.0062934 | 0.98833 | 0.006492 | 5.6888
50 | 0.075498 | 0.035905 | -0.075498 | -0.036565 | 2.2366e-07 | -0.00066061 | 0.0024348 | 0.0024431 | 0.0024431 | 0.9912 | 0.0015676 | 0.9912 | 0.0015929 | 1.1105
51 | -2.9988 | -1.349 | 3.0012 | 1.3452 | 0.0023437 | -0.003801 | 0.095767 | 0.095714 | 0.095767 | 0.9912 | 0.0015676 | 0.99193 | -0.0041091 | 43.5305
52 | 0.4129 | 0.19095 | -0.41286 | -0.19485 | 3.9226e-05 | -0.0039004 | 0.013249 | 0.013297 | 0.013297 | 0.9912 | 0.0015676 | 0.99111 | 0.0023297 | 6.0442
53 | 0.098867 | 0.046846 | -0.098867 | -0.047883 | 6.0382e-07 | -0.0010377 | 0.0031885 | 0.0032016 | 0.0032016 | 0.9905 | 0.0070198 | 0.99049 | 0.0070717 | 1.4553
54 | -3.0765 | -1.3809 | 3.0777 | 1.3789 | 0.0012662 | -0.0019395 | 0.098137 | 0.09811 | 0.098137 | 0.99193 | -0.0041091 | 0.99232 | -0.0070891 | 44.6078
55 | 0.075262 | 0.035696 | -0.075262 | -0.036451 | 2.5301e-07 | -0.0007546 | 0.0024242 | 0.0024337 | 0.0024337 | 0.99193 | -0.0041091 | 0.99193 | -0.0040805 | 1.1062
56 | -3.0777 | -1.3789 | 3.0783 | 1.378 | 0.00060054 | -0.00092097 | 0.09811 | 0.098097 | 0.09811 | 0.99232 | -0.0070891 | 0.9925 | -0.008497 | 44.5953
57 | 0.31455 | 0.14858 | -0.31453 | -0.15211 | 2.0725e-05 | -0.0035246 | 0.010132 | 0.010177 | 0.010177 | 0.99111 | 0.0023297 | 0.99105 | 0.002887 | 4.6258
58 | 0.098311 | 0.046265 | -0.09831 | -0.047614 | 7.7283e-07 | -0.0013483 | 0.0031647 | 0.0031816 | 0.0031816 | 0.99111 | 0.0023297 | 0.99111 | 0.002396 | 1.4462
59 | 0.31453 | 0.15211 | -0.31453 | -0.15233 | 1.3357e-06 | -0.00022609 | 0.010177 | 0.01018 | 0.01018 | 0.99105 | 0.002887 | 0.99105 | 0.002924 | 4.6271
60 | 0.18517 | 0.088526 | -0.18517 | -0.089681 | 2.3444e-06 | -0.0011554 | 0.0059697 | 0.0059842 | 0.0059842 | 0.9925 | -0.008497 | 0.99249 | -0.0083883 | 2.7201
61 | -3.3217 | -1.4947 | 3.3225 | 1.4938 | 0.00075312 | -0.00095906 | 0.10595 | 0.10593 | 0.10595 | 0.9925 | -0.008497 | 0.99271 | -0.010152 | 48.1574
62 | -3.4926 | -1.5762 | 3.5067 | 1.5843 | 0.014124 | 0.0080925 | 0.11143 | 0.11142 | 0.11143 | 0.99271 | -0.010152 | 0.99699 | 0.02343 | 53.0601
63 | 0.11318 | 0.053899 | -0.11318 | -0.054815 | 7.0773e-07 | -0.00091551 | 0.0036651 | 0.0036767 | 0.0036767 | 0.98736 | 0.013341 | 0.98736 | 0.013395 | 1.6712
64 | 0.77872 | 0.33306 | -0.77848 | -0.33317 | 0.00023818 | -0.00010443 | 0.024762 | 0.024765 | 0.024765 | 0.98736 | 0.013341 | 0.98704 | 0.0104 | 11.793
65 | 0.34554 | 0.15897 | -0.34549 | -0.1661 | 5.1115e-05 | -0.0071338 | 0.01112 | 0.011209 | 0.011209 | 0.98736 | 0.013341 | 0.98723 | 0.014547 | 5.0952
66 | 0.34549 | 0.1661 | -0.34548 | -0.16732 | 8.8235e-06 | -0.0012197 | 0.011209 | 0.011225 | 0.011225 | 0.98723 | 0.014547 | 0.9872 | 0.014768 | 5.1023
67 | 0.47877 | 0.18801 | -0.47875 | -0.18805 | 1.7372e-05 | -3.9226e-05 | 0.015043 | 0.015044 | 0.015044 | 0.98704 | 0.0104 | 0.987 | 0.009979 | 7.1638
68 | 0.47875 | 0.18805 | -0.4786 | -0.19947 | 0.00015021 | -0.011421 | 0.015044 | 0.01517 | 0.01517 | 0.987 | 0.009979 | 0.9867 | 0.01165 | 6.8953
69 | 0.4786 | 0.19947 | -0.47858 | -0.20092 | 1.9201e-05 | -0.0014456 | 0.01517 | 0.015186 | 0.015186 | 0.9867 | 0.01165 | 0.98667 | 0.011888 | 6.9028
70 | 0.21699 | 0.074219 | -0.21698 | -0.074257 | 2.7163e-06 | -3.7653e-05 | 0.0067096 | 0.00671 | 0.00671 | 0.98667 | 0.011888 | 0.98665 | 0.011705 | 3.1952
71 | 0.21698 | 0.074257 | -0.21692 | -0.097103 | 6.1201e-05 | -0.022846 | 0.00671 | 0.0069555 | 0.0069555 | 0.98665 | 0.011705 | 0.98638 | 0.01308 | 3.1616
72 | 0.11065 | 0.053127 | -0.11065 | -0.053592 | 3.4518e-07 | -0.00046457 | 0.0035923 | 0.0035982 | 0.0035982 | 0.98638 | 0.01308 | 0.98638 | 0.013107 | 1.6356
73 | 0.10627 | 0.043976 | -0.10626 | -0.051132 | 4.776e-06 | -0.0071568 | 0.0033658 | 0.0034514 | 0.0034514 | 0.98638 | 0.01308 | 0.98634 | 0.013404 | 1.5688
74 | -2.9817 | -1.4441 | 2.9826 | 1.4426 | 0.0009086 | -0.001465 | 0.096225 | 0.096203 | 0.096225 | 0.9939 | -0.067779 | 0.99418 | -0.07043 | 43.7385
75 | 0.10626 | 0.051132 | -0.10626 | -0.051466 | 2.2867e-07 | -0.00033354 | 0.0034514 | 0.0034556 | 0.0034556 | 0.98634 | 0.013404 | 0.98634 | 0.013422 | 1.5707

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 12.6262 | 5.807

## res_load
| p_mw | q_mvar
0 | 0.27039 | 0.13095
1 | 0.13193 | 0.063897
2 | 0.23604 | 0.11432
3 | 0.19855 | 0.09616
4 | 0.30318 | 0.14684
5 | 0.053558 | 0.025939
6 | 0.40647 | 0.19686
7 | 0.22835 | 0.1106
8 | 0.36676 | 0.17763
9 | 0.27784 | 0.13457
10 | 0.15527 | 0.075201
11 | 0.21604 | 0.10463
12 | 0.22555 | 0.10924
13 | 0.22103 | 0.10705
14 | 0.26314 | 0.12745
15 | 0.092971 | 0.045028
16 | 0.54496 | 0.26394
17 | 0.057134 | 0.027671
18 | 0.41376 | 0.20039
19 | 0.36764 | 0.17806
20 | 0.075262 | 0.036451
21 | 0.09831 | 0.047614
22 | 0.075498 | 0.036565
23 | 0.098867 | 0.047883
24 | 0.31453 | 0.15233
25 | 0.058256 | 0.028215
26 | 0.18517 | 0.089681
27 | 0.1701 | 0.082385
28 | 0.099147 | 0.048019
29 | 0.38564 | 0.18677
30 | 0.34548 | 0.16732
31 | 0.11318 | 0.054815
32 | 0.29971 | 0.14516
33 | 0.2616 | 0.1267
34 | 2.9817 | 1.4441
35 | 1.1715 | 0.56737
36 | 0.40015 | 0.1938
37 | 0.13399 | 0.064893
38 | 0.10626 | 0.051466
39 | 0.11065 | 0.053592

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1