## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_449_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_449_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_449_0_node_21 | 20 | n |  | TRUE
3 | bus_MV_449_0_node_34 | 20 | n |  | TRUE
4 | bus_MV_449_0_node_2 | 20 | n |  | TRUE
5 | bus_MV_449_0_node_3 | 20 | n |  | TRUE
6 | bus_MV_449_0_node_125 | 20 | n |  | TRUE
7 | bus_MV_449_0_node_4 | 20 | n |  | TRUE
8 | bus_MV_449_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_449_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_449_0_node_8 | 20 | n |  | TRUE
11 | bus_MV_449_0_node_93 | 20 | n |  | TRUE
12 | bus_MV_449_0_node_7 | 20 | n |  | TRUE
13 | bus_MV_449_0_node_9 | 20 | n |  | TRUE
14 | bus_MV_449_0_node_22 | 20 | n |  | TRUE
15 | bus_MV_449_0_node_16 | 20 | n |  | TRUE
16 | bus_MV_449_0_node_12 | 20 | n |  | TRUE
17 | bus_MV_449_0_node_10 | 20 | n |  | TRUE
18 | bus_MV_449_0_node_11 | 20 | n |  | TRUE
19 | bus_MV_449_0_node_90 | 20 | n |  | TRUE
20 | bus_MV_449_0_node_41 | 20 | n |  | TRUE
21 | bus_MV_449_0_node_13 | 20 | n |  | TRUE
22 | bus_MV_449_0_node_14 | 20 | n |  | TRUE
23 | bus_MV_449_0_node_15 | 20 | n |  | TRUE
24 | bus_MV_449_0_node_18 | 20 | n |  | TRUE
25 | bus_MV_449_0_node_20 | 20 | n |  | TRUE
26 | bus_MV_449_0_node_105 | 20 | n |  | TRUE
27 | bus_MV_449_0_node_23 | 20 | n |  | TRUE
28 | bus_MV_449_0_node_24 | 20 | n |  | TRUE
29 | bus_MV_449_0_node_128 | 20 | n |  | TRUE
30 | bus_MV_449_0_node_124 | 20 | n |  | TRUE
31 | bus_MV_449_0_node_39 | 20 | n |  | TRUE
32 | bus_MV_449_0_node_40 | 20 | n |  | TRUE
33 | bus_MV_449_0_node_42 | 20 | n |  | TRUE
34 | bus_MV_449_0_node_123 | 20 | n |  | TRUE
35 | bus_MV_449_0_node_129 | 20 | n |  | TRUE
36 | bus_MV_449_0_node_107 | 20 | n |  | TRUE
37 | bus_MV_449_0_node_119 | 20 | n |  | TRUE
38 | bus_MV_449_0_node_83 | 20 | n |  | TRUE
39 | bus_MV_449_0_node_84 | 20 | n |  | TRUE
40 | bus_MV_449_0_node_85 | 20 | n |  | TRUE
41 | bus_MV_449_0_node_86 | 20 | n |  | TRUE
42 | bus_MV_449_0_node_91 | 20 | n |  | TRUE
43 | bus_MV_449_0_node_87 | 20 | n |  | TRUE
44 | bus_MV_449_0_node_88 | 20 | n |  | TRUE
45 | bus_MV_449_0_node_89 | 20 | n |  | TRUE
46 | bus_MV_449_0_node_92 | 20 | n |  | TRUE
47 | bus_MV_449_0_node_106 | 20 | n |  | TRUE
48 | bus_MV_449_0_node_114 | 20 | n |  | TRUE
49 | bus_MV_449_0_node_115 | 20 | n |  | TRUE
50 | bus_MV_449_0_node_120 | 20 | n |  | TRUE
51 | bus_MV_449_0_node_116 | 20 | n |  | TRUE
52 | bus_MV_449_0_node_117 | 20 | n |  | TRUE
53 | bus_MV_449_0_node_118 | 20 | n |  | TRUE
54 | bus_MV_449_0_node_127 | 20 | n |  | TRUE
55 | bus_MV_449_0_node_121 | 20 | n |  | TRUE
56 | bus_MV_449_0_node_122 | 20 | n |  | TRUE
57 | bus_HV_449_0_node_6 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_449_0_load_0 | 0 | 0.25745 | 0.12469 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_449_0_load_21 | 2 | 0.1497 | 0.072504 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_449_0_load_34 | 3 | 0.35474 | 0.17181 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_449_0_load_2 | 4 | 0.086975 | 0.042124 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_449_0_load_125 | 6 | 0.30731 | 0.14884 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_449_0_load_4 | 7 | 0.39105 | 0.1894 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_449_0_load_93 | 11 | 3.0805 | 1.4919 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_449_0_load_22 | 14 | 0.14526 | 0.070352 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_449_0_load_16 | 15 | 0.37417 | 0.18122 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_449_0_load_12 | 16 | 0.26465 | 0.12818 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_449_0_load_10 | 17 | 0.097519 | 0.047231 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_449_0_load_90 | 19 | 1.298 | 0.62866 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_449_0_load_15 | 23 | 0.084306 | 0.040831 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_449_0_load_105 | 26 | 0.33104 | 0.16033 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_449_0_load_128 | 29 | 0.23308 | 0.11289 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_449_0_load_39 | 31 | 0.15461 | 0.074881 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_449_0_load_123 | 34 | 0.15825 | 0.076646 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_449_0_load_129 | 35 | 0.20627 | 0.099899 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_449_0_load_83 | 38 | 1.4603 | 0.70728 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_449_0_load_86 | 41 | 0.68715 | 0.3328 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_449_0_load_87 | 43 | 0.16899 | 0.081847 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_449_0_load_114 | 48 | 0.052833 | 0.025588 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_449_0_load_120 | 50 | 0.057043 | 0.027627 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_449_0_load_117 | 52 | 0.29415 | 0.14246 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_449_0_load_127 | 54 | 0.25339 | 0.12272 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_449_0_line_0 |  | 0 | 1 | 0.013147 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_449_0_line_1 |  | 0 | 2 | 1.9541 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_449_0_line_2 |  | 1 | 3 | 2.2761 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_449_0_line_3 |  | 3 | 4 | 1.3965 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_449_0_line_4 |  | 4 | 5 | 0.03053 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_449_0_line_5 |  | 5 | 6 | 1.7123 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_449_0_line_6 |  | 6 | 30 | 0.00954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_449_0_line_7 |  | 7 | 8 | 0.010557 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_449_0_line_8 |  | 8 | 9 | 0.28869 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_449_0_line_9 |  | 8 | 10 | 0.41744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_449_0_line_10 |  | 9 | 11 | 0.085027 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
11 | MV_449_0_line_11 |  | 10 | 15 | 0.006528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_449_0_line_12 |  | 10 | 12 | 0.52956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_449_0_line_13 |  | 11 | 46 | 0.078578 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
14 | MV_449_0_line_14 |  | 12 | 13 | 0.11652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_449_0_line_15 |  | 12 | 14 | 0.02808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_449_0_line_16 |  | 13 | 16 | 0.049766 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_449_0_line_17 |  | 14 | 27 | 0.019734 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_449_0_line_18 |  | 15 | 24 | 0.064321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_449_0_line_19 |  | 16 | 21 | 0.048795 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_449_0_line_20 |  | 17 | 18 | 0.097215 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_449_0_line_21 |  | 17 | 19 | 1.1312 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_449_0_line_22 |  | 18 | 20 | 2.334 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_449_0_line_23 |  | 19 | 45 | 0.033971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_449_0_line_24 |  | 20 | 31 | 0.051311 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_449_0_line_25 |  | 21 | 22 | 0.007848 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_449_0_line_26 |  | 22 | 23 | 0.0019399 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_449_0_line_27 |  | 24 | 25 | 0.18648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_449_0_line_28 |  | 25 | 26 | 0.042271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_449_0_line_29 |  | 26 | 47 | 0.029442 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_449_0_line_30 |  | 27 | 28 | 0.27545 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_449_0_line_31 |  | 28 | 29 | 0.015849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_449_0_line_32 |  | 29 | 30 | 0.27205 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_449_0_line_33 |  | 31 | 32 | 0.011394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_449_0_line_34 |  | 32 | 33 | 0.29851 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_449_0_line_35 |  | 33 | 34 | 0.043756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_449_0_line_36 |  | 35 | 36 | 0.13554 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_449_0_line_37 |  | 35 | 37 | 1.5475 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_449_0_line_38 |  | 36 | 47 | 0.4657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_449_0_line_39 |  | 37 | 52 | 0.010784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_449_0_line_40 |  | 38 | 39 | 0.064525 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_449_0_line_41 |  | 39 | 40 | 0.048948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_449_0_line_42 |  | 40 | 41 | 0.076114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_449_0_line_43 |  | 41 | 42 | 0.063245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_449_0_line_44 |  | 42 | 46 | 0.11687 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
45 | MV_449_0_line_45 |  | 42 | 45 | 0.07759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_449_0_line_46 |  | 43 | 44 | 0.092299 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_449_0_line_47 |  | 44 | 45 | 0.011866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_449_0_line_48 |  | 48 | 49 | 0.053017 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_449_0_line_49 |  | 49 | 50 | 0.51631 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_449_0_line_50 |  | 50 | 55 | 0.023682 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_449_0_line_51 |  | 51 | 52 | 0.008646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_449_0_line_52 |  | 51 | 53 | 0.36347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_449_0_line_53 |  | 53 | 54 | 0.014997 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_449_0_line_54 |  | 54 | 56 | 0.10227 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_449_0_line_55 |  | 55 | 56 | 0.56431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_449_0_trafo_6 | 25 MVA 110/20 kV | 57 | 9 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2535841.486 | 1172758.5169
1 | 2535849.6956 | 1172768.8015
2 | 2533962.3825 | 1173294.821
3 | 2535848.5783 | 1175044.8785
4 | 2534541.1267 | 1175535.5223
5 | 2534510.5872 | 1175537.724
6 | 2533713.9099 | 1174022.0749
7 | 2533288.3232 | 1173141.7122
8 | 2533286.4332 | 1173131.3274
9 | 2533219.5183 | 1172851.7927
10 | 2533652.9724 | 1173133.6258
11 | 2533137.7721 | 1172875.1833
12 | 2533672.6682 | 1173479.8142
13 | 2533605.1093 | 1173503.7648
14 | 2533690.8593 | 1173501.047
15 | 2533659.4169 | 1173134.7774
16 | 2533569.6872 | 1173538.2658
17 | 2531886.3559 | 1172876.8338
18 | 2531861.828 | 1172788.0734
19 | 2533015.2096 | 1172804.0517
20 | 2529829.0526 | 1171641.1318
21 | 2533526.409 | 1173560.8029
22 | 2533523.0115 | 1173553.7255
23 | 2533521.3668 | 1173554.7543
24 | 2533646.0781 | 1173071.8674
25 | 2533608.01 | 1172889.3194
26 | 2533598.9787 | 1172848.0295
27 | 2533699.9319 | 1173518.5788
28 | 2533712.8973 | 1173735.1019
29 | 2533698.7852 | 1173742.3955
30 | 2533718.3828 | 1174013.743
31 | 2529789.334 | 1171673.7044
32 | 2529780.1418 | 1171680.4714
33 | 2529595.0841 | 1171779.2319
34 | 2529632.1638 | 1171755.9498
35 | 2533681.5523 | 1172420.8189
36 | 2533601.0578 | 1172529.8716
37 | 2533209.0695 | 1170947.2247
38 | 2533127.8276 | 1172736.9804
39 | 2533189.8876 | 1172719.3149
40 | 2533201.1266 | 1172766.9498
41 | 2533127.8619 | 1172787.5481
42 | 2533066.9922 | 1172804.7011
43 | 2533050.8298 | 1172697.9584
44 | 2533026.1471 | 1172763.3563
45 | 2533019.812 | 1172773.3995
46 | 2533061.5065 | 1172893.4903
47 | 2533592.046 | 1172819.4347
48 | 2533580.7702 | 1169570.5439
49 | 2533588.601 | 1169619.7848
50 | 2533327.2328 | 1170065.0467
51 | 2533202.8814 | 1170928.8055
52 | 2533205.5666 | 1170937.0246
53 | 2533344.9539 | 1170642.0739
54 | 2533337.4506 | 1170629.2168
55 | 2533331.0807 | 1170088.3503
56 | 2533256.4274 | 1170566.8054
57 | 2533219.5183 | 1172851.7927

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98749 | -0.0054943 | 0.25745 | 0.12469
1 | 0.9875 | -0.0055579 | 0 | 0
2 | 0.98692 | -0.0093153 | 0.1497 | 0.072504
3 | 0.98931 | 0.0066787 | 0.35474 | 0.17181
4 | 0.99138 | 0.02052 | 0.086975 | 0.042124
5 | 0.99141 | 0.020218 | 0 | 0
6 | 0.99425 | 0.039307 | 0.30731 | 0.14884
7 | 0.99858 | 0.011641 | 0.39105 | 0.1894
8 | 0.99859 | 0.011591 | 0 | 0
9 | 1 | 0 | -10.9921 | -5.1906
10 | 0.99675 | 0.026676 | 0 | 0
11 | 0.99973 | -0.0046354 | 3.0805 | 1.4919
12 | 0.99548 | 0.037786 | 0 | 0
13 | 0.99543 | 0.038256 | 0 | 0
14 | 0.99543 | 0.038277 | 0.14526 | 0.070352
15 | 0.99674 | 0.02678 | 0.37417 | 0.18122
16 | 0.99541 | 0.038463 | 0.26465 | 0.12818
17 | 0.9982 | -0.014595 | 0.097519 | 0.047231
18 | 0.99816 | -0.014313 | 0 | 0
19 | 0.99908 | -0.007487 | 1.298 | 0.62866
20 | 0.99676 | -0.025377 | 0 | 0
21 | 0.9954 | 0.038411 | 0 | 0
22 | 0.9954 | 0.038419 | 0 | 0
23 | 0.9954 | 0.038421 | 0.084306 | 0.040831
24 | 0.99664 | 0.027521 | 0 | 0
25 | 0.99636 | 0.029706 | 0 | 0
26 | 0.9963 | 0.030209 | 0.33104 | 0.16033
27 | 0.99539 | 0.038589 | 0 | 0
28 | 0.9949 | 0.042998 | 0 | 0
29 | 0.99487 | 0.043255 | 0.23308 | 0.11289
30 | 0.99426 | 0.039179 | 0 | 0
31 | 0.99674 | -0.025213 | 0.15461 | 0.074881
32 | 0.99674 | -0.025198 | 0 | 0
33 | 0.99668 | -0.024716 | 0 | 0
34 | 0.99667 | -0.024634 | 0.15825 | 0.076646
35 | 0.99553 | 0.032587 | 0.20627 | 0.099899
36 | 0.99576 | 0.034329 | 0 | 0
37 | 0.99359 | 0.016679 | 0 | 0
38 | 0.99881 | -0.0048959 | 1.4603 | 0.70728
39 | 0.99893 | -0.0060226 | 0 | 0
40 | 0.99903 | -0.006873 | 0 | 0
41 | 0.99917 | -0.0081876 | 0.68715 | 0.3328
42 | 0.99934 | -0.0097937 | 0 | 0
43 | 0.99913 | -0.0079447 | 0.16899 | 0.081847
44 | 0.99915 | -0.0081252 | 0 | 0
45 | 0.99916 | -0.0081474 | 0 | 0
46 | 0.9996 | -0.0070808 | 0 | 0
47 | 0.99627 | 0.030444 | 0 | 0
48 | 0.99324 | 0.017744 | 0.052833 | 0.025588
49 | 0.99325 | 0.017712 | 0 | 0
50 | 0.9933 | 0.018115 | 0.057043 | 0.027627
51 | 0.99357 | 0.016771 | 0 | 0
52 | 0.99358 | 0.016747 | 0.29415 | 0.14246
53 | 0.99341 | 0.017891 | 0 | 0
54 | 0.9934 | 0.017942 | 0.25339 | 0.12272
55 | 0.9933 | 0.018087 | 0 | 0
56 | 0.99338 | 0.017665 | 0 | 0
57 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.40723 | -0.19497 | 0.40723 | 0.19466 | 3.0566e-06 | -0.00030519 | 0.013199 | 0.013195 | 0.013199 | 0.98749 | -0.0054943 | 0.9875 | -0.0055579 | 5.9994
1 | 0.14978 | 0.070282 | -0.1497 | -0.072504 | 8.1931e-05 | -0.0022222 | 0.0048368 | 0.0048654 | 0.0048654 | 0.98749 | -0.0054943 | 0.98692 | -0.0093153 | 2.3168
2 | -0.40723 | -0.19466 | 0.40794 | 0.19245 | 0.00070426 | -0.0022134 | 0.013195 | 0.013162 | 0.013195 | 0.9875 | -0.0055579 | 0.98931 | 0.0066787 | 6.2833
3 | -0.76268 | -0.36426 | 0.76419 | 0.36357 | 0.0015121 | -0.00068793 | 0.024663 | 0.024642 | 0.024663 | 0.98931 | 0.0066787 | 0.99138 | 0.02052 | 11.7441
4 | -0.85117 | -0.4057 | 0.8512 | 0.40499 | 3.0715e-05 | -0.00070734 | 0.027456 | 0.027447 | 0.027456 | 0.99138 | 0.02052 | 0.99141 | 0.020218 | 12.4801
5 | -0.8512 | -0.40499 | 0.8535 | 0.40441 | 0.0022962 | -0.00057667 | 0.027447 | 0.027422 | 0.027447 | 0.99141 | 0.020218 | 0.99425 | 0.039307 | 13.0701
6 | -1.1608 | -0.55325 | 1.1608 | 0.55303 | 1.7752e-05 | -0.0002199 | 0.037336 | 0.037333 | 0.037336 | 0.99425 | 0.039307 | 0.99426 | 0.039179 | 16.9708
7 | -0.39105 | -0.1894 | 0.39106 | 0.18915 | 2.2231e-06 | -0.00025069 | 0.012561 | 0.012558 | 0.012561 | 0.99858 | 0.011641 | 0.99859 | 0.011591 | 5.7095
8 | -3.8616 | -1.7779 | 3.8675 | 1.7728 | 0.0058171 | -0.0051576 | 0.1229 | 0.12281 | 0.1229 | 0.99859 | 0.011591 | 1 | 0 | 55.8622
9 | 3.4706 | 1.5888 | -3.4638 | -1.5967 | 0.0067925 | -0.0079057 | 0.11034 | 0.11046 | 0.11046 | 0.99859 | 0.011591 | 0.99675 | 0.026676 | 50.2098
10 | 7.1106 | 3.4073 | -7.109 | -3.4091 | 0.0016126 | -0.0017669 | 0.22762 | 0.22766 | 0.22766 | 1 | 0 | 0.99973 | -0.0046354 | 54.0752
11 | 1.5715 | 0.71504 | -1.5714 | -0.71519 | 2.1789e-05 | -0.00014839 | 0.050002 | 0.050003 | 0.050003 | 0.99675 | 0.026676 | 0.99674 | 0.02678 | 22.7288
12 | 1.8923 | 0.88164 | -1.8897 | -0.89342 | 0.002591 | -0.011777 | 0.060461 | 0.060616 | 0.060616 | 0.99675 | 0.026676 | 0.99548 | 0.037786 | 27.5526
13 | 4.0286 | 1.9172 | -4.0281 | -1.9197 | 0.00047744 | -0.0025615 | 0.12883 | 0.12886 | 0.12886 | 0.99973 | -0.0046354 | 0.9996 | -0.0070808 | 30.6089
14 | 0.34899 | 0.16479 | -0.34897 | -0.16754 | 1.9543e-05 | -0.002751 | 0.011192 | 0.011226 | 0.011226 | 0.99548 | 0.037786 | 0.99543 | 0.038256 | 5.1027
15 | 1.5408 | 0.72862 | -1.5407 | -0.72926 | 9.1585e-05 | -0.00063719 | 0.049424 | 0.049432 | 0.049432 | 0.99548 | 0.037786 | 0.99543 | 0.038277 | 22.4692
16 | 0.34897 | 0.16754 | -0.34896 | -0.16872 | 8.3838e-06 | -0.0011749 | 0.011226 | 0.011241 | 0.011241 | 0.99543 | 0.038256 | 0.99541 | 0.038463 | 5.1095
17 | 1.3954 | 0.65891 | -1.3954 | -0.65936 | 5.2768e-05 | -0.0004512 | 0.044752 | 0.044758 | 0.044758 | 0.99543 | 0.038277 | 0.99539 | 0.038589 | 20.3444
18 | 1.1973 | 0.53397 | -1.1971 | -0.53546 | 0.00012384 | -0.0014889 | 0.037967 | 0.037985 | 0.037985 | 0.99674 | 0.02678 | 0.99664 | 0.027521 | 17.266
19 | 0.084306 | 0.040542 | -0.084306 | -0.0406 | 6.4005e-07 | -5.7316e-05 | 0.002713 | 0.0027137 | 0.0027137 | 0.99541 | 0.038463 | 0.9954 | 0.038411 | 1.2922
20 | 0.31331 | 0.1371 | -0.31329 | -0.13941 | 1.2729e-05 | -0.0023089 | 0.0098903 | 0.0099173 | 0.0099173 | 0.9982 | -0.014595 | 0.99816 | -0.014313 | 4.5078
21 | -0.41082 | -0.18433 | 0.41117 | 0.1832 | 0.00034135 | -0.0011329 | 0.013022 | 0.013006 | 0.013022 | 0.9982 | -0.014595 | 0.99908 | -0.007487 | 6.201
22 | 0.31329 | 0.13941 | -0.31288 | -0.14193 | 0.00041035 | -0.0025152 | 0.0099173 | 0.0099501 | 0.0099501 | 0.99816 | -0.014313 | 0.99676 | -0.025377 | 4.7382
23 | -1.7092 | -0.81186 | 1.7093 | 0.81109 | 0.00013554 | -0.00076946 | 0.054673 | 0.054663 | 0.054673 | 0.99908 | -0.007487 | 0.99916 | -0.0081474 | 24.8515
24 | 0.31288 | 0.14193 | -0.31288 | -0.14314 | 6.7918e-06 | -0.0012152 | 0.0099501 | 0.0099648 | 0.0099648 | 0.99676 | -0.025377 | 0.99674 | -0.025213 | 4.5294
25 | 0.084306 | 0.0406 | -0.084306 | -0.040785 | 7.7217e-08 | -0.00018564 | 0.0027137 | 0.002716 | 0.002716 | 0.9954 | 0.038411 | 0.9954 | 0.038419 | 1.2346
26 | 0.084306 | 0.040785 | -0.084306 | -0.040831 | 1.9058e-08 | -4.5887e-05 | 0.002716 | 0.0027166 | 0.0027166 | 0.9954 | 0.038419 | 0.9954 | 0.038421 | 1.2348
27 | 1.1971 | 0.53546 | -1.1968 | -0.53977 | 0.0003597 | -0.0043146 | 0.037985 | 0.038038 | 0.038038 | 0.99664 | 0.027521 | 0.99636 | 0.029706 | 17.2899
28 | 1.1968 | 0.53977 | -1.1967 | -0.54075 | 8.1675e-05 | -0.00097765 | 0.038038 | 0.03805 | 0.03805 | 0.99636 | 0.029706 | 0.9963 | 0.030209 | 17.2953
29 | 0.86566 | 0.38042 | -0.86563 | -0.38111 | 2.9512e-05 | -0.00068899 | 0.027397 | 0.027406 | 0.027406 | 0.9963 | 0.030209 | 0.99627 | 0.030444 | 12.4571
30 | 1.3954 | 0.65936 | -1.3946 | -0.66565 | 0.00073796 | -0.006294 | 0.044758 | 0.044839 | 0.044839 | 0.99539 | 0.038589 | 0.9949 | 0.042998 | 20.3812
31 | 1.3946 | 0.66565 | -1.3946 | -0.66602 | 4.2543e-05 | -0.00036193 | 0.044839 | 0.044843 | 0.044843 | 0.9949 | 0.042998 | 0.99487 | 0.043255 | 20.3833
32 | 1.1615 | 0.55313 | -1.1608 | -0.55303 | 0.0006755 | 0.00010185 | 0.037329 | 0.037333 | 0.037333 | 0.99487 | 0.043255 | 0.99426 | 0.039179 | 17.7775
33 | 0.15827 | 0.068261 | -0.15827 | -0.068531 | 3.7927e-07 | -0.00027016 | 0.0049919 | 0.004995 | 0.004995 | 0.99674 | -0.025213 | 0.99674 | -0.025198 | 2.2704
34 | 0.15827 | 0.068531 | -0.15826 | -0.075609 | 1.0109e-05 | -0.0070775 | 0.004995 | 0.0050799 | 0.0050799 | 0.99674 | -0.025198 | 0.99668 | -0.024716 | 2.3091
35 | 0.15826 | 0.075609 | -0.15825 | -0.076646 | 1.5113e-06 | -0.0010373 | 0.0050799 | 0.005093 | 0.005093 | 0.99668 | -0.024716 | 0.99667 | -0.024634 | 2.315
36 | -0.86498 | -0.39205 | 0.86516 | 0.392 | 0.00018312 | -4.5703e-05 | 0.027538 | 0.027536 | 0.027538 | 0.99553 | 0.032587 | 0.99576 | 0.034329 | 13.1132
37 | 0.65871 | 0.29215 | -0.6575 | -0.29322 | 0.001205 | -0.0010726 | 0.020895 | 0.020917 | 0.020917 | 0.99553 | 0.032587 | 0.99359 | 0.016679 | 9.9603
38 | -0.86516 | -0.392 | 0.86563 | 0.38111 | 0.00046915 | -0.010891 | 0.027536 | 0.027406 | 0.027536 | 0.99576 | 0.034329 | 0.99627 | 0.030444 | 12.5163
39 | 0.6575 | 0.29322 | -0.6575 | -0.29347 | 6.2995e-06 | -0.00025232 | 0.020917 | 0.02092 | 0.02092 | 0.99359 | 0.016679 | 0.99358 | 0.016747 | 9.5089
40 | -1.4603 | -0.70728 | 1.4605 | 0.7058 | 0.00018937 | -0.001481 | 0.046896 | 0.046877 | 0.046896 | 0.99881 | -0.0048959 | 0.99893 | -0.0060226 | 21.3165
41 | -1.4605 | -0.7058 | 1.4607 | 0.70467 | 0.00014355 | -0.0011237 | 0.046877 | 0.046862 | 0.046877 | 0.99893 | -0.0060226 | 0.99903 | -0.006873 | 21.3077
42 | -1.4607 | -0.70467 | 1.4609 | 0.70293 | 0.00022304 | -0.0017479 | 0.046862 | 0.046839 | 0.046862 | 0.99903 | -0.006873 | 0.99917 | -0.0081876 | 21.301
43 | -2.1481 | -1.0357 | 2.1485 | 1.0343 | 0.00040068 | -0.0013889 | 0.068898 | 0.068879 | 0.068898 | 0.99917 | -0.0081876 | 0.99934 | -0.0097937 | 31.3174
44 | -4.0271 | -1.9231 | 4.0281 | 1.9197 | 0.0009377 | -0.0033236 | 0.12891 | 0.12886 | 0.12891 | 0.99934 | -0.0097937 | 0.9996 | -0.0070808 | 35.6114
45 | 1.8787 | 0.88871 | -1.8783 | -0.89045 | 0.00037347 | -0.001739 | 0.060035 | 0.060057 | 0.060057 | 0.99934 | -0.0097937 | 0.99916 | -0.0081474 | 27.2988
46 | -0.16899 | -0.081847 | 0.169 | 0.079648 | 3.6082e-06 | -0.0021989 | 0.0054251 | 0.0053977 | 0.0054251 | 0.99913 | -0.0079447 | 0.99915 | -0.0081252 | 2.466
47 | -0.169 | -0.079648 | 0.169 | 0.079365 | 4.6124e-07 | -0.0002827 | 0.0053977 | 0.0053943 | 0.0053977 | 0.99915 | -0.0081252 | 0.99916 | -0.0081474 | 2.4535
48 | -0.052833 | -0.025588 | 0.052833 | 0.02434 | 2.0414e-07 | -0.0012487 | 0.0017062 | 0.0016906 | 0.0017062 | 0.99324 | 0.017744 | 0.99325 | 0.017712 | 0.77552
49 | -0.052833 | -0.02434 | 0.052836 | 0.023733 | 2.6179e-06 | -0.00060646 | 0.0016906 | 0.0016833 | 0.0016906 | 0.99325 | 0.017712 | 0.9933 | 0.018115 | 0.80507
50 | -0.10988 | -0.05136 | 0.10988 | 0.050802 | 3.9207e-07 | -0.00055777 | 0.0035249 | 0.0035181 | 0.0035249 | 0.9933 | 0.018115 | 0.9933 | 0.018087 | 1.6022
51 | -0.36335 | -0.15121 | 0.36335 | 0.15101 | 1.5088e-06 | -0.00020334 | 0.011435 | 0.011432 | 0.011435 | 0.99357 | 0.016771 | 0.99358 | 0.016747 | 5.1975
52 | 0.36335 | 0.15121 | -0.36328 | -0.15976 | 6.3982e-05 | -0.0085468 | 0.011435 | 0.011532 | 0.011532 | 0.99357 | 0.016771 | 0.99341 | 0.017891 | 5.242
53 | 0.36328 | 0.15976 | -0.36328 | -0.16011 | 2.6637e-06 | -0.00035257 | 0.011532 | 0.011537 | 0.011537 | 0.99341 | 0.017891 | 0.9934 | 0.017942 | 5.2439
54 | 0.10989 | 0.037391 | -0.10989 | -0.03751 | 2.074e-06 | -0.00011919 | 0.0033731 | 0.0033742 | 0.0033742 | 0.9934 | 0.017942 | 0.99338 | 0.017665 | 1.6068
55 | -0.10988 | -0.050802 | 0.10989 | 0.03751 | 8.9227e-06 | -0.013292 | 0.0035181 | 0.0033742 | 0.0035181 | 0.9933 | 0.018087 | 0.99338 | 0.017665 | 1.5991

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 10.9921 | 5.1906

## res_load
| p_mw | q_mvar
0 | 0.25745 | 0.12469
1 | 0.1497 | 0.072504
2 | 0.35474 | 0.17181
3 | 0.086975 | 0.042124
4 | 0.30731 | 0.14884
5 | 0.39105 | 0.1894
6 | 3.0805 | 1.4919
7 | 0.14526 | 0.070352
8 | 0.37417 | 0.18122
9 | 0.26465 | 0.12818
10 | 0.097519 | 0.047231
11 | 1.298 | 0.62866
12 | 0.084306 | 0.040831
13 | 0.33104 | 0.16033
14 | 0.23308 | 0.11289
15 | 0.15461 | 0.074881
16 | 0.15825 | 0.076646
17 | 0.20627 | 0.099899
18 | 1.4603 | 0.70728
19 | 0.68715 | 0.3328
20 | 0.16899 | 0.081847
21 | 0.052833 | 0.025588
22 | 0.057043 | 0.027627
23 | 0.29415 | 0.14246
24 | 0.25339 | 0.12272

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1