## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_449_1_node_30 | 20 | n |  | TRUE
1 | bus_MV_449_1_node_25 | 20 | n |  | TRUE
2 | bus_MV_449_1_node_26 | 20 | n |  | TRUE
3 | bus_MV_449_1_node_27 | 20 | n |  | TRUE
4 | bus_MV_449_1_node_81 | 20 | n |  | TRUE
5 | bus_MV_449_1_node_82 | 20 | n |  | TRUE
6 | bus_MV_449_1_node_28 | 20 | n |  | TRUE
7 | bus_MV_449_1_node_29 | 20 | n |  | TRUE
8 | bus_MV_449_1_node_113 | 20 | n |  | TRUE
9 | bus_MV_449_1_node_31 | 20 | n |  | TRUE
10 | bus_MV_449_1_node_32 | 20 | n |  | TRUE
11 | bus_MV_449_1_node_112 | 20 | n |  | TRUE
12 | bus_MV_449_1_node_33 | 20 | n |  | TRUE
13 | bus_MV_449_1_node_36 | 20 | n |  | TRUE
14 | bus_MV_449_1_node_111 | 20 | n |  | TRUE
15 | bus_MV_449_1_node_53 | 20 | n |  | TRUE
16 | bus_MV_449_1_node_109 | 20 | n |  | TRUE
17 | bus_MV_449_1_node_35 | 20 | n |  | TRUE
18 | bus_MV_449_1_node_37 | 20 | n |  | TRUE
19 | bus_MV_449_1_node_131 | 20 | n |  | TRUE
20 | bus_MV_449_1_node_130 | 20 | n |  | TRUE
21 | bus_MV_449_1_node_43 | 20 | n |  | TRUE
22 | bus_MV_449_1_node_104 | 20 | n |  | TRUE
23 | bus_MV_449_1_node_45 | 20 | n |  | TRUE
24 | bus_MV_449_1_node_72 | 20 | n |  | TRUE
25 | bus_MV_449_1_node_99 | 20 | n |  | TRUE
26 | bus_MV_449_1_node_71 | 20 | n |  | TRUE
27 | bus_MV_449_1_node_98 | 20 | n |  | TRUE
28 | bus_MV_449_1_node_46 | 20 | n |  | TRUE
29 | bus_MV_449_1_node_47 | 20 | n |  | TRUE
30 | bus_MV_449_1_node_77 | 20 | n |  | TRUE
31 | bus_MV_449_1_node_48 | 20 | n |  | TRUE
32 | bus_MV_449_1_node_102 | 20 | n |  | TRUE
33 | bus_MV_449_1_node_78 | 20 | n |  | TRUE
34 | bus_MV_449_1_node_110 | 20 | n |  | TRUE
35 | bus_MV_449_1_node_76 | 20 | n |  | TRUE
36 | bus_MV_449_1_node_52 | 20 | n |  | TRUE
37 | bus_MV_449_1_node_50 | 20 | n |  | TRUE
38 | bus_MV_449_1_node_51 | 20 | n |  | TRUE
39 | bus_MV_449_1_node_54 | 20 | n |  | TRUE
40 | bus_MV_449_1_node_55 | 20 | n |  | TRUE
41 | bus_MV_449_1_node_56 | 20 | n |  | TRUE
42 | bus_MV_449_1_node_57 | 20 | n |  | TRUE
43 | bus_MV_449_1_node_60 | 20 | n |  | TRUE
44 | bus_MV_449_1_node_62 | 20 | n |  | TRUE
45 | bus_MV_449_1_node_58 | 20 | n |  | TRUE
46 | bus_MV_449_1_node_100 | 20 | n |  | TRUE
47 | bus_MV_449_1_node_59 | 20 | n |  | TRUE
48 | bus_MV_449_1_node_95 | 20 | n |  | TRUE
49 | bus_MV_449_1_node_73 | 20 | n |  | TRUE
50 | bus_MV_449_1_node_61 | 20 | n |  | TRUE
51 | bus_MV_449_1_node_97 | 20 | n |  | TRUE
52 | bus_MV_449_1_node_96 | 20 | n |  | TRUE
53 | bus_MV_449_1_node_101 | 20 | n |  | TRUE
54 | bus_MV_449_1_node_74 | 20 | n |  | TRUE
55 | bus_MV_449_1_node_103 | 20 | n |  | TRUE
56 | bus_MV_449_1_node_68 | 20 | n |  | TRUE
57 | bus_MV_449_1_node_63 | 20 | n |  | TRUE
58 | bus_MV_449_1_node_64 | 20 | n |  | TRUE
59 | bus_MV_449_1_node_67 | 20 | n |  | TRUE
60 | bus_MV_449_1_node_65 | 20 | n |  | TRUE
61 | bus_MV_449_1_node_94 | 20 | n |  | TRUE
62 | bus_MV_449_1_node_80 | 20 | n |  | TRUE
63 | bus_MV_449_1_node_79 | 20 | n |  | TRUE
64 | bus_MV_449_1_node_69 | 20 | n |  | TRUE
65 | bus_MV_449_1_node_70 | 20 | n |  | TRUE
66 | bus_MV_449_1_node_75 | 20 | n |  | TRUE
67 | bus_MV_449_1_node_108 | 20 | n |  | TRUE
68 | bus_HV_449_1_node_70 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_449_1_load_30 | 0 | 0.21765 | 0.10541 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_449_1_load_25 | 1 | 0.17416 | 0.084348 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_449_1_load_81 | 4 | 0.082712 | 0.040059 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_449_1_load_28 | 6 | 0.12184 | 0.059012 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_449_1_load_31 | 9 | 0.3537 | 0.1713 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_449_1_load_112 | 11 | 0.21038 | 0.10189 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_449_1_load_111 | 14 | 0.09007 | 0.043623 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_449_1_load_109 | 16 | 0.20934 | 0.10139 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_449_1_load_35 | 17 | 0.12324 | 0.059687 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_449_1_load_37 | 18 | 0.14811 | 0.071735 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_449_1_load_131 | 19 | 0.18846 | 0.091273 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_449_1_load_43 | 21 | 0.34183 | 0.16555 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_449_1_load_104 | 22 | 0.069799 | 0.033805 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_449_1_load_71 | 26 | 0.1873 | 0.090714 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_449_1_load_98 | 27 | 0.51162 | 0.24779 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_449_1_load_46 | 28 | 0.28994 | 0.14042 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_449_1_load_77 | 30 | 0.36129 | 0.17498 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_449_1_load_102 | 32 | 0.094614 | 0.045824 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_449_1_load_110 | 34 | 0.19784 | 0.095819 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_449_1_load_50 | 37 | 0.21599 | 0.10461 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_449_1_load_54 | 39 | 0.22713 | 0.11001 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_449_1_load_60 | 43 | 0.39917 | 0.19333 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_449_1_load_100 | 46 | 0.35767 | 0.17323 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_449_1_load_95 | 48 | 0.4212 | 0.204 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_449_1_load_73 | 49 | 0.30918 | 0.14974 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_449_1_load_96 | 52 | 0.39309 | 0.19038 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_449_1_load_101 | 53 | 0.18628 | 0.09022 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_449_1_load_103 | 55 | 1.6101 | 0.77979 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_449_1_load_63 | 57 | 0.068573 | 0.033211 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_449_1_load_94 | 61 | 0.074542 | 0.036103 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_449_1_load_80 | 62 | 0.39155 | 0.18964 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_449_1_load_69 | 64 | 0.27379 | 0.1326 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_449_1_load_108 | 67 | 0.31238 | 0.15129 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 65 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_449_1_line_0 |  | 0 | 1 | 1.205 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
1 | MV_449_1_line_1 |  | 1 | 2 | 0.020751 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
2 | MV_449_1_line_2 |  | 2 | 3 | 1.1535 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
3 | MV_449_1_line_3 |  | 3 | 4 | 0.05845 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
4 | MV_449_1_line_4 |  | 4 | 5 | 0.024539 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
5 | MV_449_1_line_5 |  | 5 | 20 | 1.2527 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
6 | MV_449_1_line_6 |  | 6 | 7 | 0.027268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_449_1_line_7 |  | 7 | 8 | 1.6694 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_449_1_line_8 |  | 7 | 9 | 1.8995 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
9 | MV_449_1_line_9 |  | 8 | 11 | 0.05936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_449_1_line_10 |  | 9 | 10 | 0.022758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_449_1_line_11 |  | 10 | 12 | 0.55248 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
12 | MV_449_1_line_12 |  | 10 | 13 | 2.7976 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
13 | MV_449_1_line_13 |  | 12 | 16 | 0.029441 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_449_1_line_14 |  | 12 | 14 | 0.79341 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
15 | MV_449_1_line_15 |  | 13 | 17 | 0.012472 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
16 | MV_449_1_line_16 |  | 14 | 15 | 0.066711 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
17 | MV_449_1_line_17 |  | 15 | 38 | 0.85822 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
18 | MV_449_1_line_18 |  | 17 | 18 | 1.5899 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
19 | MV_449_1_line_19 |  | 18 | 19 | 1.2355 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
20 | MV_449_1_line_20 |  | 19 | 20 | 0.034379 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
21 | MV_449_1_line_21 |  | 21 | 22 | 0.087212 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_449_1_line_22 |  | 22 | 23 | 0.049452 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_449_1_line_23 |  | 23 | 24 | 0.61196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_449_1_line_24 |  | 24 | 25 | 0.10298 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
25 | MV_449_1_line_25 |  | 24 | 26 | 0.072582 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
26 | MV_449_1_line_26 |  | 25 | 27 | 0.051644 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_449_1_line_27 |  | 26 | 65 | 0.006466 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
28 | MV_449_1_line_28 |  | 27 | 60 | 0.09499 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_449_1_line_29 |  | 28 | 29 | 0.033821 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_449_1_line_30 |  | 28 | 30 | 0.27906 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_449_1_line_31 |  | 29 | 31 | 0.37691 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
32 | MV_449_1_line_32 |  | 29 | 32 | 0.26315 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
33 | MV_449_1_line_33 |  | 30 | 33 | 0.024099 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_449_1_line_34 |  | 31 | 34 | 0.063618 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
35 | MV_449_1_line_35 |  | 32 | 35 | 0.067102 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
36 | MV_449_1_line_36 |  | 33 | 63 | 0.32594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_449_1_line_37 |  | 34 | 36 | 0.010792 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
38 | MV_449_1_line_38 |  | 35 | 66 | 0.23134 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
39 | MV_449_1_line_39 |  | 36 | 38 | 0.49211 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
40 | MV_449_1_line_40 |  | 37 | 38 | 0.007881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_449_1_line_41 |  | 39 | 40 | 0.014504 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
42 | MV_449_1_line_42 |  | 39 | 41 | 0.024611 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
43 | MV_449_1_line_43 |  | 40 | 42 | 0.042282 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
44 | MV_449_1_line_44 |  | 41 | 43 | 0.063047 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_449_1_line_45 |  | 41 | 44 | 0.056327 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
46 | MV_449_1_line_46 |  | 42 | 45 | 0.13933 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
47 | MV_449_1_line_47 |  | 42 | 46 | 0.028345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_449_1_line_48 |  | 44 | 53 | 0.06272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_449_1_line_49 |  | 44 | 50 | 0.031177 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
50 | MV_449_1_line_50 |  | 45 | 47 | 0.15684 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
51 | MV_449_1_line_51 |  | 45 | 48 | 0.060798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_449_1_line_52 |  | 47 | 49 | 0.022688 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
53 | MV_449_1_line_53 |  | 49 | 54 | 0.006426 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
54 | MV_449_1_line_54 |  | 50 | 51 | 0.24911 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_449_1_line_55 |  | 50 | 52 | 0.062403 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
56 | MV_449_1_line_56 |  | 51 | 55 | 0.08861 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_449_1_line_57 |  | 52 | 56 | 0.06058 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
58 | MV_449_1_line_58 |  | 54 | 66 | 0.36168 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
59 | MV_449_1_line_59 |  | 56 | 59 | 0.34771 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
60 | MV_449_1_line_60 |  | 57 | 58 | 0.15091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_449_1_line_61 |  | 58 | 59 | 0.28668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_449_1_line_62 |  | 59 | 61 | 0.048524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_449_1_line_63 |  | 59 | 60 | 0.45268 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
64 | MV_449_1_line_64 |  | 62 | 63 | 0.036132 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_449_1_line_65 |  | 64 | 65 | 0.14137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_449_1_line_66 |  | 66 | 67 | 0.004352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_449_1_trafo_70 | 25 MVA 110/20 kV | 68 | 65 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2536575.5983 | 1177246.384
1 | 2537761.5868 | 1177459.5587
2 | 2537781.3033 | 1177452.9167
3 | 2538640.7159 | 1177884.1336
4 | 2538696.9185 | 1177869.0716
5 | 2538718.8897 | 1177858.0294
6 | 2542793.105 | 1180202.3441
7 | 2542769.6504 | 1180188.3272
8 | 2543300.0409 | 1178605.4238
9 | 2541213.5147 | 1179099.0044
10 | 2541190.9507 | 1179095.5797
11 | 2543316.0104 | 1178548.252
12 | 2540830.1762 | 1179220.1159
13 | 2541205.7023 | 1176298.0589
14 | 2540163.5787 | 1179650.3944
15 | 2540158.9383 | 1179705.8051
16 | 2540851.8867 | 1179240.0013
17 | 2541194.3611 | 1176292.8007
18 | 2540112.7543 | 1177458.157
19 | 2539166.7212 | 1176663.5621
20 | 2539134.743 | 1176676.4164
21 | 2539243.4383 | 1178982.5678
22 | 2539284.5865 | 1179059.4625
23 | 2539246.3251 | 1179090.788
24 | 2539488.4557 | 1179381.0201
25 | 2539498.7024 | 1179454.4798
26 | 2539552.4079 | 1179412.069
27 | 2539452.4847 | 1179477.5246
28 | 2539537.819 | 1180097.8228
29 | 2539545.5952 | 1180066.0709
30 | 2539271.0956 | 1180015.7552
31 | 2539772.7289 | 1180116.2979
32 | 2539740.0281 | 1179888.7489
33 | 2539247.0075 | 1180017.7341
34 | 2539826.5489 | 1180150.2199
35 | 2539805.1515 | 1179904.9088
36 | 2539835.6894 | 1180155.9979
37 | 2540186.5102 | 1179952.7342
38 | 2540179.9541 | 1179957.1356
39 | 2539449.97 | 1179643.2117
40 | 2539458.1527 | 1179631.2222
41 | 2539436.0814 | 1179663.5525
42 | 2539492.9828 | 1179609.5467
43 | 2539381.9968 | 1179631.2248
44 | 2539401.1519 | 1179694.9792
45 | 2539502.0088 | 1179690.0006
46 | 2539512.4199 | 1179595.4424
47 | 2539631.817 | 1179723.453
48 | 2539467.8028 | 1179740.2637
49 | 2539654.0646 | 1179728.2091
50 | 2539399.2883 | 1179717.633
51 | 2539271.6728 | 1179868.7001
52 | 2539347.6195 | 1179682.6408
53 | 2539387.7893 | 1179650.761
54 | 2539660.3653 | 1179729.5575
55 | 2539359.7642 | 1179859.1244
56 | 2539297.46 | 1179648.6707
57 | 2538931.1047 | 1179698.5255
58 | 2539014.5589 | 1179576.6507
59 | 2539100.3063 | 1179557.3668
60 | 2539367.4758 | 1179519.9111
61 | 2539127.8545 | 1179517.4206
62 | 2539042.4805 | 1180034.6121
63 | 2539075.7514 | 1180035.7184
64 | 2539596.2284 | 1179544.646
65 | 2539553.0295 | 1179418.3885
66 | 2539886.9539 | 1179884.7753
67 | 2539882.733 | 1179885.885
68 | 2539553.0295 | 1179418.3885

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98383 | -0.32188 | 0.21765 | 0.10541
1 | 0.98414 | -0.31401 | 0.17416 | 0.084348
2 | 0.98415 | -0.31396 | 0 | 0
3 | 0.98439 | -0.31077 | 0 | 0
4 | 0.9844 | -0.31058 | 0.082712 | 0.040059
5 | 0.98441 | -0.31049 | 0 | 0
6 | 0.9893 | -0.14603 | 0.12184 | 0.059012
7 | 0.9893 | -0.14607 | 0 | 0
8 | 0.98862 | -0.15075 | 0 | 0
9 | 0.99053 | -0.13745 | 0.3537 | 0.1713
10 | 0.99055 | -0.13763 | 0 | 0
11 | 0.9886 | -0.1506 | 0.21038 | 0.10189
12 | 0.99103 | -0.13166 | 0 | 0
13 | 0.98752 | -0.22133 | 0 | 0
14 | 0.99272 | -0.086191 | 0.09007 | 0.043623
15 | 0.99279 | -0.085343 | 0 | 0
16 | 0.99102 | -0.13173 | 0.20934 | 0.10139
17 | 0.98751 | -0.22142 | 0.12324 | 0.059687
18 | 0.98602 | -0.26317 | 0.14811 | 0.071735
19 | 0.98508 | -0.29014 | 0.18846 | 0.091273
20 | 0.98508 | -0.29028 | 0 | 0
21 | 0.99937 | 0.0013544 | 0.34183 | 0.16555
22 | 0.99943 | 0.0017155 | 0.069799 | 0.033805
23 | 0.99946 | 0.0014739 | 0 | 0
24 | 0.99978 | -0.0012074 | 0 | 0
25 | 0.9995 | -0.002697 | 0 | 0
26 | 0.99998 | -0.00010025 | 0.1873 | 0.090714
27 | 0.99936 | -0.0034407 | 0.51162 | 0.24779
28 | 0.99466 | -0.059774 | 0.28994 | 0.14042
29 | 0.99471 | -0.060179 | 0 | 0
30 | 0.99425 | -0.062564 | 0.36129 | 0.17498
31 | 0.99442 | -0.061973 | 0 | 0
32 | 0.99529 | -0.025623 | 0.094614 | 0.045824
33 | 0.99424 | -0.062464 | 0 | 0
34 | 0.99425 | -0.06668 | 0.19784 | 0.095819
35 | 0.99536 | -0.025193 | 0 | 0
36 | 0.99424 | -0.066842 | 0 | 0
37 | 0.99367 | -0.074109 | 0.21599 | 0.10461
38 | 0.99368 | -0.074129 | 0 | 0
39 | 0.9966 | -0.017939 | 0.22713 | 0.11001
40 | 0.99658 | -0.018069 | 0 | 0
41 | 0.99664 | -0.01771 | 0 | 0
42 | 0.99651 | -0.018449 | 0 | 0
43 | 0.99661 | -0.01741 | 0.39917 | 0.19333
44 | 0.99674 | -0.017158 | 0 | 0
45 | 0.99631 | -0.019628 | 0 | 0
46 | 0.9965 | -0.018327 | 0.35767 | 0.17323
47 | 0.9961 | -0.020853 | 0 | 0
48 | 0.99628 | -0.019322 | 0.4212 | 0.204
49 | 0.99607 | -0.021029 | 0.30918 | 0.14974
50 | 0.9968 | -0.016843 | 0 | 0
51 | 0.99629 | -0.012092 | 0 | 0
52 | 0.99695 | -0.016086 | 0.39309 | 0.19038
53 | 0.99673 | -0.01702 | 0.18628 | 0.09022
54 | 0.99606 | -0.021076 | 0 | 0
55 | 0.99611 | -0.010378 | 1.6101 | 0.77979
56 | 0.9971 | -0.01532 | 0 | 0
57 | 0.99793 | -0.010646 | 0.068573 | 0.033211
58 | 0.99794 | -0.010753 | 0 | 0
59 | 0.99797 | -0.010861 | 0 | 0
60 | 0.99912 | -0.0047461 | 0 | 0
61 | 0.99796 | -0.010819 | 0.074542 | 0.036103
62 | 0.99406 | -0.060848 | 0.39155 | 0.18964
63 | 0.99408 | -0.061018 | 0 | 0
64 | 0.99995 | 0.00044789 | 0.27379 | 0.1326
65 | 1 | 0 | -9.2735 | -4.1486
66 | 0.99562 | -0.023677 | 0 | 0
67 | 0.99562 | -0.02366 | 0.31238 | 0.15129
68 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.21765 | -0.10541 | 0.21771 | 0.10401 | 5.5552e-05 | -0.0014026 | 0.0070959 | 0.0070773 | 0.0070959 | 0.98383 | -0.32188 | 0.98414 | -0.31401 | 2.0274
1 | -0.39186 | -0.18836 | 0.39186 | 0.18767 | 1.629e-06 | -0.00068831 | 0.012753 | 0.012745 | 0.012753 | 0.98414 | -0.31401 | 0.98415 | -0.31396 | 3.523
2 | -0.39186 | -0.18767 | 0.39195 | 0.1494 | 8.7219e-05 | -0.038272 | 0.012745 | 0.012301 | 0.012745 | 0.98415 | -0.31396 | 0.98439 | -0.31077 | 3.5206
3 | -0.39195 | -0.1494 | 0.39196 | 0.14746 | 4.2646e-06 | -0.00194 | 0.012301 | 0.012281 | 0.012301 | 0.98439 | -0.31077 | 0.9844 | -0.31058 | 3.398
4 | -0.47467 | -0.18752 | 0.47467 | 0.1867 | 2.6533e-06 | -0.00081386 | 0.014966 | 0.014958 | 0.014966 | 0.9844 | -0.31058 | 0.98441 | -0.31049 | 4.1344
5 | -0.47467 | -0.1867 | 0.47493 | 0.18547 | 0.000257 | -0.0012325 | 0.014958 | 0.014941 | 0.014958 | 0.98441 | -0.31049 | 0.98508 | -0.29028 | 4.2736
6 | -0.12184 | -0.059012 | 0.12185 | 0.058375 | 5.6694e-07 | -0.00063703 | 0.0039504 | 0.0039424 | 0.0039504 | 0.9893 | -0.14603 | 0.9893 | -0.14607 | 1.7957
7 | 0.21052 | 0.098644 | -0.21038 | -0.10051 | 0.00013737 | -0.0018631 | 0.0067839 | 0.0068082 | 0.0068082 | 0.9893 | -0.14607 | 0.98862 | -0.15075 | 3.242
8 | -0.33237 | -0.15702 | 0.33275 | 0.15504 | 0.00038837 | -0.0019789 | 0.010726 | 0.010699 | 0.010726 | 0.9893 | -0.14607 | 0.99053 | -0.13745 | 5.1077
9 | 0.21038 | 0.10051 | -0.21038 | -0.10189 | 3.6826e-06 | -0.0013841 | 0.0068082 | 0.0068257 | 0.0068257 | 0.98862 | -0.15075 | 0.9886 | -0.1506 | 3.1026
10 | -0.68645 | -0.32634 | 0.68647 | 0.32582 | 1.4903e-05 | -0.00052872 | 0.022151 | 0.022145 | 0.022151 | 0.99053 | -0.13745 | 0.99055 | -0.13763 | 10.0688
11 | -1.625 | -0.72983 | 1.6257 | 0.71175 | 0.0007161 | -0.018086 | 0.051914 | 0.051694 | 0.051914 | 0.99055 | -0.13763 | 0.99103 | -0.13166 | 14.3408
12 | 0.9385 | 0.40402 | -0.93622 | -0.40485 | 0.0022802 | -0.00083075 | 0.029777 | 0.029817 | 0.029817 | 0.99055 | -0.13763 | 0.98752 | -0.22133 | 8.5192
13 | 0.20934 | 0.10136 | -0.20934 | -0.10139 | 2.4079e-06 | -3.301e-05 | 0.006775 | 0.0067755 | 0.0067755 | 0.99103 | -0.13166 | 0.99102 | -0.13173 | 3.2264
14 | -1.835 | -0.8131 | 1.8375 | 0.81497 | 0.0024891 | 0.0018661 | 0.058464 | 0.058453 | 0.058464 | 0.99103 | -0.13166 | 0.99272 | -0.086191 | 16.7041
15 | 0.93622 | 0.40485 | -0.93622 | -0.40526 | 5.3566e-06 | -0.00041336 | 0.029817 | 0.029822 | 0.029822 | 0.98752 | -0.22133 | 0.98751 | -0.22142 | 8.2381
16 | -1.9276 | -0.85859 | 1.9277 | 0.85642 | 0.00012127 | -0.0021674 | 0.061362 | 0.061335 | 0.061362 | 0.99272 | -0.086191 | 0.99279 | -0.085343 | 16.9507
17 | -1.9277 | -0.85642 | 1.9293 | 0.8285 | 0.0015508 | -0.027918 | 0.061335 | 0.060997 | 0.061335 | 0.99279 | -0.085343 | 0.99368 | -0.074129 | 16.9433
18 | 0.81298 | 0.34557 | -0.812 | -0.3464 | 0.00097415 | -0.00083124 | 0.025823 | 0.025846 | 0.025846 | 0.98751 | -0.22142 | 0.98602 | -0.26317 | 7.3845
19 | 0.66389 | 0.27467 | -0.66339 | -0.2756 | 0.0005022 | -0.00093358 | 0.021034 | 0.021051 | 0.021051 | 0.98602 | -0.26317 | 0.98508 | -0.29014 | 6.0146
20 | 0.47493 | 0.18433 | -0.47493 | -0.18547 | 3.7039e-06 | -0.0011418 | 0.014929 | 0.014941 | 0.014941 | 0.98508 | -0.29014 | 0.98508 | -0.29028 | 4.1274
21 | -0.34183 | -0.16555 | 0.34184 | 0.16546 | 1.87e-05 | -9.2277e-05 | 0.010971 | 0.01097 | 0.010971 | 0.99937 | 0.0013544 | 0.99943 | 0.0017155 | 5.2243
22 | -0.41164 | -0.19927 | 0.41166 | 0.19809 | 1.1507e-05 | -0.001176 | 0.01321 | 0.013195 | 0.01321 | 0.99943 | 0.0017155 | 0.99946 | 0.0014739 | 6.0044
23 | -0.41166 | -0.19809 | 0.4118 | 0.18353 | 0.00014031 | -0.014558 | 0.013195 | 0.013018 | 0.013195 | 0.99946 | 0.0014739 | 0.99978 | -0.0012074 | 5.9977
24 | 8.3847 | 3.7385 | -8.3825 | -3.7437 | 0.0022365 | -0.0052061 | 0.26508 | 0.26515 | 0.26515 | 0.99978 | -0.0012074 | 0.9995 | -0.002697 | 41.5598
25 | -8.7965 | -3.922 | 8.7983 | 3.9184 | 0.0017341 | -0.0035828 | 0.27809 | 0.27804 | 0.27809 | 0.99978 | -0.0012074 | 0.99998 | -0.00010025 | 43.5882
26 | 8.3825 | 3.7437 | -8.3814 | -3.7463 | 0.0011221 | -0.0026093 | 0.26515 | 0.26519 | 0.26519 | 0.9995 | -0.002697 | 0.99936 | -0.0034407 | 41.5657
27 | -8.9856 | -4.0092 | 8.9857 | 4.0088 | 0.0001612 | -0.00031549 | 0.28404 | 0.28404 | 0.28404 | 0.99998 | -0.00010025 | 1 | 0 | 44.521
28 | 7.8697 | 3.4985 | -7.8679 | -3.5034 | 0.0018171 | -0.0049361 | 0.24878 | 0.24885 | 0.24885 | 0.99936 | -0.0034407 | 0.99912 | -0.0047461 | 39.0042
29 | -1.0431 | -0.4958 | 1.0432 | 0.49502 | 5.0717e-05 | -0.0007839 | 0.03352 | 0.03351 | 0.03352 | 0.99466 | -0.059774 | 0.99471 | -0.060179 | 15.2365
30 | 0.75321 | 0.35538 | -0.75292 | -0.35553 | 0.00029054 | -0.00014748 | 0.024171 | 0.024175 | 0.024175 | 0.99466 | -0.059774 | 0.99425 | -0.062564 | 11.512
31 | 2.3452 | 0.98974 | -2.3445 | -1.0128 | 0.00063786 | -0.023066 | 0.073873 | 0.07414 | 0.07414 | 0.99471 | -0.060179 | 0.99442 | -0.061973 | 11.6206
32 | -3.3884 | -1.4848 | 3.3895 | 1.4873 | 0.0010828 | 0.0025516 | 0.10736 | 0.10736 | 0.10736 | 0.99471 | -0.060179 | 0.99529 | -0.025623 | 16.6451
33 | 0.39163 | 0.18055 | -0.39163 | -0.18112 | 5.0466e-06 | -0.00056729 | 0.012521 | 0.012528 | 0.012528 | 0.99425 | -0.062564 | 0.99424 | -0.062464 | 5.6945
34 | 2.3445 | 1.0128 | -2.3442 | -1.0125 | 0.00032102 | 0.00028814 | 0.07414 | 0.07414 | 0.07414 | 0.99442 | -0.061973 | 0.99425 | -0.06668 | 21.183
35 | -3.4841 | -1.5331 | 3.4843 | 1.5291 | 0.00025262 | -0.0040346 | 0.1104 | 0.11036 | 0.1104 | 0.99529 | -0.025623 | 0.99536 | -0.025193 | 17.3047
36 | 0.39163 | 0.18112 | -0.39156 | -0.18879 | 6.8809e-05 | -0.0076711 | 0.012528 | 0.012623 | 0.012623 | 0.99424 | -0.062464 | 0.99408 | -0.061018 | 5.7379
37 | 2.1464 | 0.9167 | -2.1463 | -0.91705 | 2.3938e-05 | -0.00034859 | 0.067764 | 0.067769 | 0.067769 | 0.99425 | -0.06668 | 0.99424 | -0.066842 | 18.7206
38 | -3.4843 | -1.5291 | 3.4852 | 1.5152 | 0.00086924 | -0.013915 | 0.11036 | 0.11019 | 0.11036 | 0.99536 | -0.025193 | 0.99562 | -0.023677 | 17.297
39 | 2.1463 | 0.91705 | -2.1453 | -0.93293 | 0.0010947 | -0.015883 | 0.067769 | 0.06796 | 0.06796 | 0.99424 | -0.066842 | 0.99368 | -0.074129 | 18.7736
40 | -0.21599 | -0.10461 | 0.21599 | 0.10442 | 5.1126e-07 | -0.00018564 | 0.0069721 | 0.0069697 | 0.0069721 | 0.99367 | -0.074109 | 0.99368 | -0.074129 | 3.1691
41 | 4.8895 | 2.147 | -4.8894 | -2.1479 | 0.00010724 | -0.00084472 | 0.15468 | 0.15469 | 0.15469 | 0.9966 | -0.017939 | 0.99658 | -0.018069 | 24.2465
42 | -5.1166 | -2.2571 | 5.1168 | 2.2556 | 0.00019953 | -0.0014236 | 0.16199 | 0.16197 | 0.16199 | 0.9966 | -0.017939 | 0.99664 | -0.01771 | 25.3899
43 | 4.8894 | 2.1479 | -4.8891 | -2.1504 | 0.00031271 | -0.0024623 | 0.15469 | 0.15472 | 0.15472 | 0.99658 | -0.018069 | 0.99651 | -0.018449 | 24.2513
44 | 0.39919 | 0.19184 | -0.39917 | -0.19333 | 1.3871e-05 | -0.0014911 | 0.012828 | 0.012847 | 0.012847 | 0.99664 | -0.01771 | 0.99661 | -0.01741 | 5.8396
45 | -5.516 | -2.4475 | 5.5166 | 2.4442 | 0.00053163 | -0.0032164 | 0.17479 | 0.17475 | 0.17479 | 0.99664 | -0.01771 | 0.99674 | -0.017158 | 27.3968
46 | 4.5314 | 1.9778 | -4.5305 | -1.986 | 0.0008838 | -0.0081938 | 0.14323 | 0.14333 | 0.14333 | 0.99651 | -0.018449 | 0.99631 | -0.019628 | 22.4652
47 | 0.35767 | 0.17256 | -0.35767 | -0.17323 | 5.0116e-06 | -0.00067056 | 0.011504 | 0.011512 | 0.011512 | 0.99651 | -0.018449 | 0.9965 | -0.018327 | 5.2329
48 | 0.18628 | 0.088734 | -0.18628 | -0.09022 | 2.9995e-06 | -0.0014869 | 0.005976 | 0.0059946 | 0.0059946 | 0.99674 | -0.017158 | 0.99673 | -0.01702 | 2.7248
49 | -5.7028 | -2.533 | 5.7032 | 2.5312 | 0.00031461 | -0.0017691 | 0.18072 | 0.1807 | 0.18072 | 0.99674 | -0.017158 | 0.9968 | -0.016843 | 28.3266
50 | 4.1093 | 1.7834 | -4.1085 | -1.7928 | 0.00081717 | -0.0093199 | 0.12979 | 0.12991 | 0.12991 | 0.99631 | -0.019628 | 0.9961 | -0.020853 | 20.3618
51 | 0.42121 | 0.20256 | -0.4212 | -0.204 | 1.4905e-05 | -0.0014365 | 0.013542 | 0.01356 | 0.01356 | 0.99631 | -0.019628 | 0.99628 | -0.019322 | 6.1638
52 | 4.1085 | 1.7928 | -4.1084 | -1.7941 | 0.00011833 | -0.0013478 | 0.12991 | 0.12992 | 0.12992 | 0.9961 | -0.020853 | 0.99607 | -0.021029 | 20.3643
53 | 3.7992 | 1.6444 | -3.7992 | -1.6447 | 2.8583e-05 | -0.00038449 | 0.11998 | 0.11998 | 0.11998 | 0.99607 | -0.021029 | 0.99606 | -0.021076 | 18.8059
54 | 1.6113 | 0.77214 | -1.6104 | -0.77779 | 0.00089168 | -0.0056422 | 0.051744 | 0.051818 | 0.051818 | 0.9968 | -0.016843 | 0.99629 | -0.012092 | 23.5538
55 | -7.3144 | -3.3034 | 7.3155 | 3.3 | 0.0010415 | -0.0033099 | 0.23243 | 0.23238 | 0.23243 | 0.9968 | -0.016843 | 0.99695 | -0.016086 | 36.4307
56 | 1.6104 | 0.77779 | -1.6101 | -0.77979 | 0.0003178 | -0.0020053 | 0.051818 | 0.051845 | 0.051845 | 0.99629 | -0.012092 | 0.99611 | -0.010378 | 23.5658
57 | -7.7086 | -3.4904 | 7.7097 | 3.4873 | 0.0011236 | -0.003151 | 0.24502 | 0.24498 | 0.24502 | 0.99695 | -0.016086 | 0.9971 | -0.01532 | 38.4051
58 | 3.7992 | 1.6447 | -3.7976 | -1.6664 | 0.0016123 | -0.021628 | 0.11998 | 0.12024 | 0.12024 | 0.99606 | -0.021076 | 0.99562 | -0.023677 | 18.8468
59 | -7.7097 | -3.4873 | 7.7161 | 3.4692 | 0.0064413 | -0.018112 | 0.24498 | 0.24472 | 0.24498 | 0.9971 | -0.01532 | 0.99797 | -0.010861 | 38.398
60 | -0.068573 | -0.033211 | 0.068574 | 0.029623 | 9.5912e-07 | -0.003588 | 0.002204 | 0.0021608 | 0.002204 | 0.99793 | -0.010646 | 0.99794 | -0.010753 | 1.0018
61 | -0.068574 | -0.029623 | 0.068576 | 0.022807 | 1.726e-06 | -0.0068164 | 0.0021608 | 0.0020905 | 0.0021608 | 0.99794 | -0.010753 | 0.99797 | -0.010861 | 0.98219
62 | 0.074543 | 0.034949 | -0.074542 | -0.036103 | 3.6959e-07 | -0.0011538 | 0.0023815 | 0.0023958 | 0.0023958 | 0.99797 | -0.010861 | 0.99796 | -0.010819 | 1.089
63 | -7.8593 | -3.5269 | 7.8679 | 3.5034 | 0.0086736 | -0.023476 | 0.24918 | 0.24885 | 0.24918 | 0.99797 | -0.010861 | 0.99912 | -0.0047461 | 39.0567
64 | -0.39155 | -0.18964 | 0.39156 | 0.18879 | 7.6929e-06 | -0.00085021 | 0.012634 | 0.012623 | 0.012634 | 0.99406 | -0.060848 | 0.99408 | -0.061018 | 5.7428
65 | -0.27379 | -0.1326 | 0.2738 | 0.12923 | 1.4486e-05 | -0.003371 | 0.0087822 | 0.0087402 | 0.0087822 | 0.99995 | 0.00044789 | 1 | 0 | 3.9919
66 | 0.31238 | 0.15119 | -0.31238 | -0.15129 | 5.8834e-07 | -0.00010283 | 0.010062 | 0.010064 | 0.010064 | 0.99562 | -0.023677 | 0.99562 | -0.02366 | 4.5743

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 9.2735 | 4.1486

## res_load
| p_mw | q_mvar
0 | 0.21765 | 0.10541
1 | 0.17416 | 0.084348
2 | 0.082712 | 0.040059
3 | 0.12184 | 0.059012
4 | 0.3537 | 0.1713
5 | 0.21038 | 0.10189
6 | 0.09007 | 0.043623
7 | 0.20934 | 0.10139
8 | 0.12324 | 0.059687
9 | 0.14811 | 0.071735
10 | 0.18846 | 0.091273
11 | 0.34183 | 0.16555
12 | 0.069799 | 0.033805
13 | 0.1873 | 0.090714
14 | 0.51162 | 0.24779
15 | 0.28994 | 0.14042
16 | 0.36129 | 0.17498
17 | 0.094614 | 0.045824
18 | 0.19784 | 0.095819
19 | 0.21599 | 0.10461
20 | 0.22713 | 0.11001
21 | 0.39917 | 0.19333
22 | 0.35767 | 0.17323
23 | 0.4212 | 0.204
24 | 0.30918 | 0.14974
25 | 0.39309 | 0.19038
26 | 0.18628 | 0.09022
27 | 1.6101 | 0.77979
28 | 0.068573 | 0.033211
29 | 0.074542 | 0.036103
30 | 0.39155 | 0.18964
31 | 0.27379 | 0.1326
32 | 0.31238 | 0.15129

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1