## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_450_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_450_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_450_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_450_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_450_0_node_5 | 20 | n |  | TRUE
5 | bus_MV_450_0_node_6 | 20 | n |  | TRUE
6 | bus_MV_450_0_node_4 | 20 | n |  | TRUE
7 | bus_MV_450_0_node_159 | 20 | n |  | TRUE
8 | bus_MV_450_0_node_80 | 20 | n |  | TRUE
9 | bus_MV_450_0_node_143 | 20 | n |  | TRUE
10 | bus_MV_450_0_node_82 | 20 | n |  | TRUE
11 | bus_MV_450_0_node_79 | 20 | n |  | TRUE
12 | bus_MV_450_0_node_142 | 20 | n |  | TRUE
13 | bus_MV_450_0_node_7 | 20 | n |  | TRUE
14 | bus_MV_450_0_node_8 | 20 | n |  | TRUE
15 | bus_MV_450_0_node_152 | 20 | n |  | TRUE
16 | bus_MV_450_0_node_9 | 20 | n |  | TRUE
17 | bus_MV_450_0_node_151 | 20 | n |  | TRUE
18 | bus_MV_450_0_node_76 | 20 | n |  | TRUE
19 | bus_MV_450_0_node_77 | 20 | n |  | TRUE
20 | bus_MV_450_0_node_11 | 20 | n |  | TRUE
21 | bus_MV_450_0_node_10 | 20 | n |  | TRUE
22 | bus_MV_450_0_node_12 | 20 | n |  | TRUE
23 | bus_MV_450_0_node_145 | 20 | n |  | TRUE
24 | bus_MV_450_0_node_40 | 20 | n |  | TRUE
25 | bus_MV_450_0_node_14 | 20 | n |  | TRUE
26 | bus_MV_450_0_node_17 | 20 | n |  | TRUE
27 | bus_MV_450_0_node_15 | 20 | n |  | TRUE
28 | bus_MV_450_0_node_103 | 20 | n |  | TRUE
29 | bus_MV_450_0_node_104 | 20 | n |  | TRUE
30 | bus_MV_450_0_node_16 | 20 | n |  | TRUE
31 | bus_MV_450_0_node_162 | 20 | n |  | TRUE
32 | bus_MV_450_0_node_128 | 20 | n |  | TRUE
33 | bus_MV_450_0_node_137 | 20 | n |  | TRUE
34 | bus_MV_450_0_node_129 | 20 | n |  | TRUE
35 | bus_MV_450_0_node_146 | 20 | n |  | TRUE
36 | bus_MV_450_0_node_18 | 20 | n |  | TRUE
37 | bus_MV_450_0_node_19 | 20 | n |  | TRUE
38 | bus_MV_450_0_node_20 | 20 | n |  | TRUE
39 | bus_MV_450_0_node_21 | 20 | n |  | TRUE
40 | bus_MV_450_0_node_22 | 20 | n |  | TRUE
41 | bus_MV_450_0_node_157 | 20 | n |  | TRUE
42 | bus_MV_450_0_node_23 | 20 | n |  | TRUE
43 | bus_MV_450_0_node_25 | 20 | n |  | TRUE
44 | bus_MV_450_0_node_26 | 20 | n |  | TRUE
45 | bus_MV_450_0_node_57 | 20 | n |  | TRUE
46 | bus_MV_450_0_node_69 | 20 | n |  | TRUE
47 | bus_MV_450_0_node_161 | 20 | n |  | TRUE
48 | bus_MV_450_0_node_110 | 20 | n |  | TRUE
49 | bus_MV_450_0_node_66 | 20 | n |  | TRUE
50 | bus_MV_450_0_node_108 | 20 | n |  | TRUE
51 | bus_MV_450_0_node_28 | 20 | n |  | TRUE
52 | bus_MV_450_0_node_29 | 20 | n |  | TRUE
53 | bus_MV_450_0_node_30 | 20 | n |  | TRUE
54 | bus_MV_450_0_node_31 | 20 | n |  | TRUE
55 | bus_MV_450_0_node_32 | 20 | n |  | TRUE
56 | bus_MV_450_0_node_33 | 20 | n |  | TRUE
57 | bus_MV_450_0_node_112 | 20 | n |  | TRUE
58 | bus_MV_450_0_node_100 | 20 | n |  | TRUE
59 | bus_MV_450_0_node_98 | 20 | n |  | TRUE
60 | bus_MV_450_0_node_34 | 20 | n |  | TRUE
61 | bus_MV_450_0_node_111 | 20 | n |  | TRUE
62 | bus_MV_450_0_node_102 | 20 | n |  | TRUE
63 | bus_MV_450_0_node_99 | 20 | n |  | TRUE
64 | bus_MV_450_0_node_35 | 20 | n |  | TRUE
65 | bus_MV_450_0_node_37 | 20 | n |  | TRUE
66 | bus_MV_450_0_node_36 | 20 | n |  | TRUE
67 | bus_MV_450_0_node_38 | 20 | n |  | TRUE
68 | bus_MV_450_0_node_39 | 20 | n |  | TRUE
69 | bus_MV_450_0_node_53 | 20 | n |  | TRUE
70 | bus_MV_450_0_node_51 | 20 | n |  | TRUE
71 | bus_MV_450_0_node_41 | 20 | n |  | TRUE
72 | bus_MV_450_0_node_42 | 20 | n |  | TRUE
73 | bus_MV_450_0_node_43 | 20 | n |  | TRUE
74 | bus_MV_450_0_node_60 | 20 | n |  | TRUE
75 | bus_MV_450_0_node_67 | 20 | n |  | TRUE
76 | bus_MV_450_0_node_72 | 20 | n |  | TRUE
77 | bus_MV_450_0_node_65 | 20 | n |  | TRUE
78 | bus_MV_450_0_node_164 | 20 | n |  | TRUE
79 | bus_MV_450_0_node_64 | 20 | n |  | TRUE
80 | bus_MV_450_0_node_61 | 20 | n |  | TRUE
81 | bus_MV_450_0_node_59 | 20 | n |  | TRUE
82 | bus_MV_450_0_node_71 | 20 | n |  | TRUE
83 | bus_MV_450_0_node_70 | 20 | n |  | TRUE
84 | bus_MV_450_0_node_44 | 20 | n |  | TRUE
85 | bus_MV_450_0_node_45 | 20 | n |  | TRUE
86 | bus_MV_450_0_node_46 | 20 | n |  | TRUE
87 | bus_MV_450_0_node_125 | 20 | n |  | TRUE
88 | bus_MV_450_0_node_126 | 20 | n |  | TRUE
89 | bus_MV_450_0_node_127 | 20 | n |  | TRUE
90 | bus_MV_450_0_node_47 | 20 | n |  | TRUE
91 | bus_MV_450_0_node_49 | 20 | n |  | TRUE
92 | bus_MV_450_0_node_55 | 20 | n |  | TRUE
93 | bus_MV_450_0_node_56 | 20 | n |  | TRUE
94 | bus_MV_450_0_node_48 | 20 | n |  | TRUE
95 | bus_MV_450_0_node_50 | 20 | n |  | TRUE
96 | bus_MV_450_0_node_52 | 20 | n |  | TRUE
97 | bus_MV_450_0_node_114 | 20 | n |  | TRUE
98 | bus_MV_450_0_node_54 | 20 | n |  | TRUE
99 | bus_MV_450_0_node_113 | 20 | n |  | TRUE
100 | bus_MV_450_0_node_117 | 20 | n |  | TRUE
101 | bus_MV_450_0_node_116 | 20 | n |  | TRUE
102 | bus_MV_450_0_node_150 | 20 | n |  | TRUE
103 | bus_MV_450_0_node_109 | 20 | n |  | TRUE
104 | bus_MV_450_0_node_124 | 20 | n |  | TRUE
105 | bus_MV_450_0_node_123 | 20 | n |  | TRUE
106 | bus_MV_450_0_node_115 | 20 | n |  | TRUE
107 | bus_MV_450_0_node_118 | 20 | n |  | TRUE
108 | bus_MV_450_0_node_158 | 20 | n |  | TRUE
109 | bus_MV_450_0_node_107 | 20 | n |  | TRUE
110 | bus_MV_450_0_node_134 | 20 | n |  | TRUE
111 | bus_MV_450_0_node_122 | 20 | n |  | TRUE
112 | bus_MV_450_0_node_58 | 20 | n |  | TRUE
113 | bus_MV_450_0_node_155 | 20 | n |  | TRUE
114 | bus_MV_450_0_node_156 | 20 | n |  | TRUE
115 | bus_MV_450_0_node_153 | 20 | n |  | TRUE
116 | bus_MV_450_0_node_135 | 20 | n |  | TRUE
117 | bus_MV_450_0_node_62 | 20 | n |  | TRUE
118 | bus_MV_450_0_node_63 | 20 | n |  | TRUE
119 | bus_MV_450_0_node_136 | 20 | n |  | TRUE
120 | bus_MV_450_0_node_131 | 20 | n |  | TRUE
121 | bus_MV_450_0_node_130 | 20 | n |  | TRUE
122 | bus_MV_450_0_node_73 | 20 | n |  | TRUE
123 | bus_MV_450_0_node_74 | 20 | n |  | TRUE
124 | bus_MV_450_0_node_75 | 20 | n |  | TRUE
125 | bus_MV_450_0_node_85 | 20 | n |  | TRUE
126 | bus_MV_450_0_node_83 | 20 | n |  | TRUE
127 | bus_MV_450_0_node_90 | 20 | n |  | TRUE
128 | bus_MV_450_0_node_84 | 20 | n |  | TRUE
129 | bus_MV_450_0_node_78 | 20 | n |  | TRUE
130 | bus_MV_450_0_node_163 | 20 | n |  | TRUE
131 | bus_MV_450_0_node_139 | 20 | n |  | TRUE
132 | bus_MV_450_0_node_138 | 20 | n |  | TRUE
133 | bus_MV_450_0_node_81 | 20 | n |  | TRUE
134 | bus_MV_450_0_node_86 | 20 | n |  | TRUE
135 | bus_MV_450_0_node_147 | 20 | n |  | TRUE
136 | bus_MV_450_0_node_87 | 20 | n |  | TRUE
137 | bus_MV_450_0_node_88 | 20 | n |  | TRUE
138 | bus_MV_450_0_node_89 | 20 | n |  | TRUE
139 | bus_MV_450_0_node_149 | 20 | n |  | TRUE
140 | bus_MV_450_0_node_105 | 20 | n |  | TRUE
141 | bus_MV_450_0_node_141 | 20 | n |  | TRUE
142 | bus_MV_450_0_node_93 | 20 | n |  | TRUE
143 | bus_MV_450_0_node_95 | 20 | n |  | TRUE
144 | bus_MV_450_0_node_91 | 20 | n |  | TRUE
145 | bus_MV_450_0_node_92 | 20 | n |  | TRUE
146 | bus_MV_450_0_node_94 | 20 | n |  | TRUE
147 | bus_MV_450_0_node_96 | 20 | n |  | TRUE
148 | bus_MV_450_0_node_106 | 20 | n |  | TRUE
149 | bus_MV_450_0_node_97 | 20 | n |  | TRUE
150 | bus_MV_450_0_node_101 | 20 | n |  | TRUE
151 | bus_MV_450_0_node_119 | 20 | n |  | TRUE
152 | bus_MV_450_0_node_120 | 20 | n |  | TRUE
153 | bus_MV_450_0_node_148 | 20 | n |  | TRUE
154 | bus_MV_450_0_node_121 | 20 | n |  | TRUE
155 | bus_MV_450_0_node_132 | 20 | n |  | TRUE
156 | bus_MV_450_0_node_140 | 20 | n |  | TRUE
157 | bus_MV_450_0_node_133 | 20 | n |  | TRUE
158 | bus_MV_450_0_node_154 | 20 | n |  | TRUE
159 | bus_MV_450_0_node_144 | 20 | n |  | TRUE
160 | bus_MV_450_0_node_160 | 20 | n |  | TRUE
161 | bus_HV_450_0_node_108 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_450_0_load_0 | 0 | 0.074046 | 0.035862 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_450_0_load_6 | 5 | 0.34306 | 0.16615 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_450_0_load_159 | 7 | 0.21176 | 0.10256 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_450_0_load_143 | 9 | 0.37804 | 0.18309 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_450_0_load_79 | 11 | 0.076207 | 0.036909 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_450_0_load_7 | 13 | 0.12526 | 0.060667 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_450_0_load_151 | 17 | 0.14168 | 0.068617 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_450_0_load_76 | 18 | 0.21769 | 0.10543 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_450_0_load_10 | 21 | 0.1452 | 0.070324 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_450_0_load_12 | 22 | 0.40882 | 0.198 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_450_0_load_145 | 23 | 0.18204 | 0.088165 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_450_0_load_15 | 27 | 0.35817 | 0.17347 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_450_0_load_103 | 28 | 0.10531 | 0.051003 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_450_0_load_16 | 30 | 0.13868 | 0.067167 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_450_0_load_162 | 31 | 0.3259 | 0.15784 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_450_0_load_137 | 33 | 0.1089 | 0.052743 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_450_0_load_146 | 35 | 0.38132 | 0.18468 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_450_0_load_18 | 36 | 0.32816 | 0.15894 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_450_0_load_22 | 40 | 0.2996 | 0.1451 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_450_0_load_157 | 41 | 0.37589 | 0.18205 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_450_0_load_57 | 45 | 0.29135 | 0.14111 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_450_0_load_69 | 46 | 0.23826 | 0.1154 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_450_0_load_161 | 47 | 0.31732 | 0.15369 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_450_0_load_110 | 48 | 0.097646 | 0.047292 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_450_0_load_28 | 51 | 0.26665 | 0.12914 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_450_0_load_33 | 56 | 1.0171 | 0.4926 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_450_0_load_112 | 57 | 0.11563 | 0.056 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_450_0_load_100 | 58 | 0.29145 | 0.14116 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_450_0_load_98 | 59 | 0.19601 | 0.094933 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_450_0_load_34 | 60 | 0.13213 | 0.063993 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_450_0_load_111 | 61 | 0.34953 | 0.16929 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_450_0_load_99 | 63 | 0.11568 | 0.056028 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_450_0_load_35 | 64 | 0.13534 | 0.06555 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_450_0_load_39 | 68 | 0.37279 | 0.18055 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_450_0_load_41 | 71 | 0.25982 | 0.12584 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_450_0_load_72 | 76 | 0.25201 | 0.12205 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_450_0_load_164 | 78 | 0.091277 | 0.044208 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_450_0_load_64 | 79 | 0.10016 | 0.048509 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_450_0_load_61 | 80 | 0.4098 | 0.19848 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_450_0_load_70 | 83 | 0.3424 | 0.16583 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_450_0_load_44 | 84 | 0.29623 | 0.14347 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_450_0_load_46 | 86 | 0.11238 | 0.05443 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_450_0_load_126 | 88 | 0.077152 | 0.037366 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_450_0_load_127 | 89 | 0.096941 | 0.046951 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_450_0_load_47 | 90 | 0.36549 | 0.17701 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_450_0_load_114 | 97 | 0.11004 | 0.053295 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_450_0_load_113 | 99 | 0.62201 | 0.30126 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_450_0_load_116 | 101 | 0.16446 | 0.079652 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_450_0_load_150 | 102 | 0.34574 | 0.16745 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_450_0_load_124 | 104 | 0.38663 | 0.18726 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_450_0_load_115 | 106 | 0.20763 | 0.10056 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_450_0_load_158 | 108 | 0.34024 | 0.16479 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_450_0_load_107 | 109 | 0.12875 | 0.062356 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_450_0_load_134 | 110 | 0.076912 | 0.03725 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_450_0_load_122 | 111 | 0.19263 | 0.093295 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_450_0_load_58 | 112 | 0.3662 | 0.17736 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_450_0_load_156 | 114 | 0.40034 | 0.19389 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_450_0_load_135 | 116 | 0.35535 | 0.17211 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_450_0_load_63 | 118 | 0.40817 | 0.19768 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_450_0_load_131 | 120 | 0.07066 | 0.034222 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_450_0_load_130 | 121 | 0.095216 | 0.046115 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_450_0_load_73 | 122 | 0.33969 | 0.16452 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_450_0_load_83 | 126 | 0.11187 | 0.054179 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_450_0_load_90 | 127 | 0.071726 | 0.034739 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_450_0_load_163 | 130 | 0.37896 | 0.18354 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_450_0_load_139 | 131 | 0.18274 | 0.088506 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_450_0_load_81 | 133 | 0.081941 | 0.039686 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_450_0_load_147 | 135 | 0.35029 | 0.16965 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_450_0_load_149 | 139 | 0.13353 | 0.064671 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_450_0_load_105 | 140 | 0.097759 | 0.047347 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_450_0_load_141 | 141 | 0.41398 | 0.2005 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_450_0_load_91 | 144 | 0.07554 | 0.036586 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_450_0_load_92 | 145 | 0.10776 | 0.05219 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_450_0_load_106 | 148 | 0.074063 | 0.035871 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_450_0_load_97 | 149 | 0.18751 | 0.090814 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_450_0_load_101 | 150 | 0.089479 | 0.043337 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_450_0_load_119 | 151 | 0.50804 | 0.24606 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_450_0_load_121 | 154 | 0.40813 | 0.19767 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_450_0_load_132 | 155 | 0.068994 | 0.033415 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_450_0_load_154 | 158 | 0.20528 | 0.099422 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_450_0_load_160 | 160 | 0.071141 | 0.034455 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_450_0_line_0 |  | 0 | 1 | 0.050686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_450_0_line_1 |  | 0 | 2 | 0.10866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_450_0_line_2 |  | 1 | 3 | 0.57891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_450_0_line_3 |  | 2 | 4 | 0.53094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_450_0_line_4 |  | 3 | 5 | 0.007808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_450_0_line_5 |  | 4 | 8 | 1.2815 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
6 | MV_450_0_line_6 |  | 4 | 9 | 0.014754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_450_0_line_7 |  | 4 | 6 | 0.4853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_450_0_line_8 |  | 6 | 7 | 0.014641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_450_0_line_9 |  | 8 | 10 | 0.26587 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
10 | MV_450_0_line_10 |  | 8 | 11 | 0.060858 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_450_0_line_11 |  | 9 | 12 | 0.016757 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_450_0_line_12 |  | 10 | 121 | 0.10518 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_450_0_line_13 |  | 10 | 82 | 0.18854 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
14 | MV_450_0_line_14 |  | 11 | 133 | 0.074476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_450_0_line_15 |  | 12 | 159 | 0.66124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_450_0_line_16 |  | 13 | 14 | 0.15732 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_450_0_line_17 |  | 13 | 15 | 0.71812 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_450_0_line_18 |  | 14 | 16 | 1.2409 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_450_0_line_19 |  | 15 | 17 | 0.031038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_450_0_line_20 |  | 16 | 20 | 0.34736 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_450_0_line_21 |  | 16 | 21 | 0.060948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_450_0_line_22 |  | 17 | 18 | 1.1774 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_450_0_line_23 |  | 18 | 19 | 0.046547 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_450_0_line_24 |  | 19 | 129 | 0.14268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_450_0_line_25 |  | 20 | 22 | 0.051891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_450_0_line_26 |  | 23 | 24 | 0.14856 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_450_0_line_27 |  | 24 | 65 | 0.2971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_450_0_line_28 |  | 25 | 26 | 0.11954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_450_0_line_29 |  | 25 | 27 | 0.01969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_450_0_line_30 |  | 26 | 28 | 0.079185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_450_0_line_31 |  | 26 | 29 | 0.1546 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_450_0_line_32 |  | 27 | 30 | 0.014642 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_450_0_line_33 |  | 28 | 33 | 0.035902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_450_0_line_34 |  | 29 | 34 | 0.1159 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_450_0_line_35 |  | 31 | 32 | 0.11215 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_450_0_line_36 |  | 32 | 34 | 0.13637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_450_0_line_37 |  | 32 | 87 | 0.17976 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_450_0_line_38 |  | 34 | 35 | 0.11473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_450_0_line_39 |  | 36 | 37 | 0.054163 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_450_0_line_40 |  | 37 | 38 | 0.23717 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
41 | MV_450_0_line_41 |  | 37 | 39 | 0.30847 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
42 | MV_450_0_line_42 |  | 38 | 40 | 0.076985 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
43 | MV_450_0_line_43 |  | 39 | 41 | 0.035299 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
44 | MV_450_0_line_44 |  | 40 | 42 | 0.051873 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
45 | MV_450_0_line_45 |  | 42 | 43 | 0.38011 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
46 | MV_450_0_line_46 |  | 42 | 44 | 0.40823 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
47 | MV_450_0_line_47 |  | 43 | 45 | 0.13679 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_450_0_line_48 |  | 43 | 46 | 0.084505 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
49 | MV_450_0_line_49 |  | 44 | 47 | 0.027945 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_450_0_line_50 |  | 44 | 48 | 0.166 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
51 | MV_450_0_line_51 |  | 46 | 49 | 0.14182 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
52 | MV_450_0_line_52 |  | 48 | 50 | 0.23424 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
53 | MV_450_0_line_53 |  | 49 | 74 | 0.39809 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
54 | MV_450_0_line_54 |  | 50 | 109 | 0.063928 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
55 | MV_450_0_line_55 |  | 51 | 52 | 0.0055175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_450_0_line_56 |  | 51 | 53 | 0.032201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_450_0_line_57 |  | 52 | 54 | 0.064309 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
58 | MV_450_0_line_58 |  | 52 | 55 | 0.095279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_450_0_line_59 |  | 53 | 56 | 0.075073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_450_0_line_60 |  | 54 | 57 | 0.009813 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
61 | MV_450_0_line_61 |  | 55 | 58 | 0.0068752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_450_0_line_62 |  | 55 | 59 | 0.024221 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_450_0_line_63 |  | 56 | 60 | 0.073008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_450_0_line_64 |  | 57 | 61 | 0.004893 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
65 | MV_450_0_line_65 |  | 58 | 62 | 0.018464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_450_0_line_66 |  | 59 | 63 | 0.030255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_450_0_line_67 |  | 61 | 99 | 0.03232 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
68 | MV_450_0_line_68 |  | 62 | 137 | 0.032701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_450_0_line_69 |  | 63 | 150 | 0.017565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_450_0_line_70 |  | 64 | 65 | 0.025448 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_450_0_line_71 |  | 64 | 66 | 0.24757 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_450_0_line_72 |  | 66 | 67 | 0.18619 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_450_0_line_73 |  | 67 | 68 | 0.069069 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_450_0_line_74 |  | 68 | 69 | 0.14603 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_450_0_line_75 |  | 69 | 70 | 0.29342 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_450_0_line_76 |  | 70 | 98 | 0.15581 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_450_0_line_77 |  | 70 | 99 | 0.045738 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
78 | MV_450_0_line_78 |  | 70 | 94 | 0.32684 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
79 | MV_450_0_line_79 |  | 71 | 72 | 0.039747 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_450_0_line_80 |  | 72 | 73 | 0.042996 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_450_0_line_81 |  | 73 | 74 | 0.36898 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
82 | MV_450_0_line_82 |  | 73 | 75 | 0.45226 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
83 | MV_450_0_line_83 |  | 73 | 76 | 0.18878 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_450_0_line_84 |  | 74 | 79 | 0.069056 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
85 | MV_450_0_line_85 |  | 74 | 80 | 0.088508 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
86 | MV_450_0_line_86 |  | 74 | 81 | 0.16645 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
87 | MV_450_0_line_87 |  | 74 | 77 | 0.10856 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_450_0_line_88 |  | 75 | 82 | 0.4087 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
89 | MV_450_0_line_89 |  | 75 | 83 | 0.12687 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_450_0_line_90 |  | 77 | 78 | 0.0073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_450_0_line_91 |  | 79 | 116 | 0.062756 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
92 | MV_450_0_line_92 |  | 80 | 117 | 0.036919 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
93 | MV_450_0_line_93 |  | 81 | 112 | 0.13783 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
94 | MV_450_0_line_94 |  | 82 | 120 | 0.085936 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
95 | MV_450_0_line_95 |  | 84 | 85 | 0.051235 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_450_0_line_96 |  | 85 | 86 | 0.036735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_450_0_line_97 |  | 86 | 87 | 0.0934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_450_0_line_98 |  | 87 | 88 | 0.040633 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_450_0_line_99 |  | 87 | 89 | 0.0819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_450_0_line_100 |  | 88 | 92 | 0.047341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_450_0_line_101 |  | 90 | 91 | 0.021258 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_450_0_line_102 |  | 91 | 92 | 0.15899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_450_0_line_103 |  | 91 | 93 | 0.16467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_450_0_line_104 |  | 93 | 104 | 0.03302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_450_0_line_105 |  | 93 | 105 | 0.032862 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_450_0_line_106 |  | 94 | 95 | 0.32491 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
107 | MV_450_0_line_107 |  | 95 | 96 | 0.1141 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
108 | MV_450_0_line_108 |  | 95 | 97 | 0.041931 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_450_0_line_109 |  | 96 | 100 | 0.052638 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
110 | MV_450_0_line_110 |  | 96 | 101 | 0.11118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_450_0_line_111 |  | 97 | 106 | 0.056621 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_450_0_line_112 |  | 98 | 102 | 0.058766 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_450_0_line_113 |  | 98 | 103 | 0.01893 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
114 | MV_450_0_line_114 |  | 100 | 107 | 0.1999 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
115 | MV_450_0_line_115 |  | 100 | 108 | 0.013625 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_450_0_line_116 |  | 103 | 109 | 0.065098 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
117 | MV_450_0_line_117 |  | 104 | 110 | 0.20355 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_450_0_line_118 |  | 105 | 111 | 0.064614 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_450_0_line_119 |  | 107 | 130 | 0.064729 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
120 | MV_450_0_line_120 |  | 110 | 157 | 0.019772 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_450_0_line_121 |  | 113 | 114 | 0.050609 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
122 | MV_450_0_line_122 |  | 113 | 115 | 0.13489 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
123 | MV_450_0_line_123 |  | 115 | 158 | 0.011266 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
124 | MV_450_0_line_124 |  | 116 | 119 | 0.20855 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
125 | MV_450_0_line_125 |  | 117 | 118 | 0.028208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_450_0_line_126 |  | 119 | 158 | 0.064393 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
127 | MV_450_0_line_127 |  | 122 | 123 | 0.035231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_450_0_line_128 |  | 123 | 124 | 0.020948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_450_0_line_129 |  | 124 | 125 | 0.039652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_450_0_line_130 |  | 124 | 126 | 0.03172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_450_0_line_131 |  | 125 | 127 | 0.025118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_450_0_line_132 |  | 126 | 128 | 0.04372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_450_0_line_133 |  | 127 | 142 | 0.029112 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_450_0_line_134 |  | 128 | 134 | 0.24452 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_450_0_line_135 |  | 129 | 131 | 0.041748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_450_0_line_136 |  | 130 | 153 | 0.006166 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
137 | MV_450_0_line_137 |  | 131 | 132 | 0.053041 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_450_0_line_138 |  | 132 | 156 | 0.31625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_450_0_line_139 |  | 134 | 135 | 0.007261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_450_0_line_140 |  | 134 | 136 | 0.41148 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_450_0_line_141 |  | 136 | 137 | 0.082832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_450_0_line_142 |  | 136 | 138 | 0.13156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_450_0_line_143 |  | 136 | 139 | 0.068835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_450_0_line_144 |  | 137 | 140 | 0.015915 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_450_0_line_145 |  | 138 | 141 | 0.023258 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_450_0_line_146 |  | 142 | 143 | 0.34789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_450_0_line_147 |  | 142 | 144 | 0.023599 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_450_0_line_148 |  | 143 | 148 | 0.030273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_450_0_line_149 |  | 144 | 145 | 0.014931 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_450_0_line_150 |  | 145 | 146 | 0.049912 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_450_0_line_151 |  | 146 | 147 | 0.007459 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_450_0_line_152 |  | 147 | 149 | 0.010127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_450_0_line_153 |  | 151 | 152 | 0.060131 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
154 | MV_450_0_line_154 |  | 151 | 153 | 0.1301 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
155 | MV_450_0_line_155 |  | 152 | 154 | 0.11273 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_450_0_line_156 |  | 152 | 155 | 0.16071 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
157 | MV_450_0_line_157 |  | 154 | 156 | 0.033789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_450_0_line_158 |  | 155 | 157 | 0.028303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_450_0_line_159 |  | 159 | 160 | 0.002996 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_450_0_trafo_108 | 25 MVA 110/20 kV | 161 | 50 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2522399.1836 | 1147145.627
1 | 2522418.5199 | 1147098.7622
2 | 2522361.3201 | 1147247.2065
3 | 2521956.0809 | 1147108.9461
4 | 2522233.5986 | 1147524.1467
5 | 2521953.0532 | 1147101.7479
6 | 2522007.2196 | 1147355.1238
7 | 2522007.5061 | 1147340.4895
8 | 2522719.6817 | 1147913.6076
9 | 2522218.8076 | 1147523.7265
10 | 2522847.9508 | 1148070.5179
11 | 2522685.3402 | 1147963.7952
12 | 2522202.005 | 1147523.3656
13 | 2524811.8362 | 1150959.8294
14 | 2524909.5759 | 1151083.1005
15 | 2525300.5374 | 1150433.6432
16 | 2524228.6122 | 1150832.7202
17 | 2525297.3518 | 1150402.7764
18 | 2525306.2199 | 1149225.4568
19 | 2525316.3595 | 1149180.0275
20 | 2524114.8777 | 1150683.1801
21 | 2524264.8444 | 1150881.3915
22 | 2524113.7981 | 1150641.4367
23 | 2523564.727 | 1149375.7798
24 | 2523657.0495 | 1149259.4416
25 | 2524368.0997 | 1149393.9268
26 | 2524276.5747 | 1149318.4019
27 | 2524380.3561 | 1149409.3371
28 | 2524351.0636 | 1149343.4194
29 | 2524155.6049 | 1149222.5489
30 | 2524391.9833 | 1149400.437
31 | 2524397.5753 | 1149125.6822
32 | 2524306.7151 | 1149059.9428
33 | 2524383.3927 | 1149359.032
34 | 2524220.3371 | 1149126.4122
35 | 2524121.4229 | 1149068.8261
36 | 2524171.6159 | 1147930.7928
37 | 2524225.2687 | 1147923.3795
38 | 2524424.252 | 1148053.262
39 | 2523963.8275 | 1147761.3072
40 | 2524387.0603 | 1148120.6896
41 | 2523961.2295 | 1147727.1207
42 | 2524339.193 | 1148100.7021
43 | 2524000.5496 | 1147993.6529
44 | 2524165.8155 | 1148180.3962
45 | 2523959.783 | 1148124.2308
46 | 2523996.8179 | 1147909.2299
47 | 2524151.9833 | 1148204.6954
48 | 2524312.3167 | 1148258.4516
49 | 2523864.1174 | 1147905.5163
50 | 2524161.0934 | 1148408.2626
51 | 2524498.7524 | 1148418.9509
52 | 2524496.843 | 1148422.6933
53 | 2524512.5412 | 1148393.4131
54 | 2524451.6527 | 1148462.7609
55 | 2524570.3347 | 1148366.2063
56 | 2524463.752 | 1148336.3863
57 | 2524443.5771 | 1148468.3357
58 | 2524575.2264 | 1148361.3752
59 | 2524550.3095 | 1148355.2645
60 | 2524414.685 | 1148282.3331
61 | 2524439.5504 | 1148471.1155
62 | 2524588.3661 | 1148348.4036
63 | 2524531.1555 | 1148331.8449
64 | 2523781.0362 | 1148988.1157
65 | 2523803.1735 | 1149000.7758
66 | 2523910.3344 | 1148776.9928
67 | 2523977.821 | 1148605.2424
68 | 2524037.3122 | 1148640.4333
69 | 2524182.7141 | 1148653.9627
70 | 2524375.3127 | 1148515.4607
71 | 2523742.4156 | 1147887.936
72 | 2523705.6399 | 1147872.6045
73 | 2523665.8529 | 1147856.033
74 | 2523651.7716 | 1147697.2437
75 | 2523271.3129 | 1147910.1698
76 | 2523594.4337 | 1148030.7829
77 | 2523562.6064 | 1147694.6851
78 | 2523555.7015 | 1147692.2603
79 | 2523592.5558 | 1147661.7155
80 | 2523738.1884 | 1147716.8703
81 | 2523718.5616 | 1147552.4924
82 | 2522981.9099 | 1148051.5579
83 | 2523377.9083 | 1147978.9619
84 | 2524262.8067 | 1148809.2533
85 | 2524241.7248 | 1148855.9673
86 | 2524275.1848 | 1148871.1283
87 | 2524358.6638 | 1148912.9507
88 | 2524380.8287 | 1148878.8951
89 | 2524429.5295 | 1148954.2281
90 | 2524381.0548 | 1148743.1064
91 | 2524401.9275 | 1148747.4355
92 | 2524406.652 | 1148839.217
93 | 2524527.24 | 1148734.8776
94 | 2524397.7311 | 1148676.2923
95 | 2524597.1502 | 1148587.1731
96 | 2524662.2002 | 1148533.0721
97 | 2524565.1335 | 1148560.1091
98 | 2524281.5781 | 1148492.3708
99 | 2524412.9525 | 1148489.4768
100 | 2524699.797 | 1148496.1251
101 | 2524597.153 | 1148450.807
102 | 2524319.0886 | 1148449.3412
103 | 2524267.4959 | 1148479.7297
104 | 2524556.4847 | 1148750.364
105 | 2524517.2523 | 1148765.6981
106 | 2524522.1581 | 1148523.2431
107 | 2524822.3259 | 1148594.0262
108 | 2524713.0587 | 1148493.0019
109 | 2524217.0751 | 1148439.1304
110 | 2524689.049 | 1148904.8243
111 | 2524485.7809 | 1148821.9032
112 | 2523607.9303 | 1147471.1908
113 | 2523305.9765 | 1147380.8604
114 | 2523316.7923 | 1147331.5279
115 | 2523280.0673 | 1147513.2437
116 | 2523538.7429 | 1147629.429
117 | 2523774.6952 | 1147723.0335
118 | 2523802.589 | 1147727.7386
119 | 2523352.6624 | 1147535.2535
120 | 2522931.6819 | 1148121.2838
121 | 2522799.5509 | 1148011.765
122 | 2524790.3479 | 1148101.4028
123 | 2524813.5243 | 1148074.8427
124 | 2524825.7996 | 1148057.8464
125 | 2524850.7736 | 1148026.9948
126 | 2524801.885 | 1148037.0073
127 | 2524869.6771 | 1148043.5353
128 | 2524768.9234 | 1148008.2847
129 | 2525213.3292 | 1149081.3293
130 | 2524854.7418 | 1148650.053
131 | 2525183.2286 | 1149052.3204
132 | 2525144.9751 | 1149015.4754
133 | 2522642.6264 | 1148024.8052
134 | 2524713.2363 | 1148048.2814
135 | 2524719.0813 | 1148052.6108
136 | 2524679.9837 | 1148301.7187
137 | 2524612.8605 | 1148326.6622
138 | 2524591.0569 | 1148218.174
139 | 2524744.4368 | 1148319.9004
140 | 2524617.0323 | 1148337.6437
141 | 2524573.1753 | 1148203.2452
142 | 2524891.5861 | 1148062.7055
143 | 2524847.2711 | 1148316.4466
144 | 2524898.3949 | 1148040.1239
145 | 2524903.381 | 1148026.0504
146 | 2524904.9086 | 1147978.8585
147 | 2524897.4279 | 1147978.8408
148 | 2524854.2122 | 1148345.9127
149 | 2524889.3197 | 1147977.7747
150 | 2524520.035 | 1148318.248
151 | 2524757.7267 | 1148738.4907
152 | 2524800.1574 | 1148780.8645
153 | 2524857.8265 | 1148655.3953
154 | 2524909.1386 | 1148809.6976
155 | 2524731.9882 | 1148926.4055
156 | 2524931.477 | 1148784.4712
157 | 2524706.999 | 1148913.1153
158 | 2523290.8775 | 1147516.5188
159 | 2521771.3053 | 1147592.043
160 | 2521771.0898 | 1147589.0552
161 | 2524161.0934 | 1148408.2626

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99619 | -0.079124 | 0.074046 | 0.035862
1 | 0.99617 | -0.078962 | 0 | 0
2 | 0.99625 | -0.079556 | 0 | 0
3 | 0.99591 | -0.076828 | 0 | 0
4 | 0.99653 | -0.081408 | 0 | 0
5 | 0.99591 | -0.076796 | 0.34306 | 0.16615
6 | 0.99639 | -0.08036 | 0 | 0
7 | 0.99639 | -0.080322 | 0.21176 | 0.10256
8 | 0.99696 | -0.077914 | 0 | 0
9 | 0.99652 | -0.081343 | 0.37804 | 0.18309
10 | 0.99703 | -0.076305 | 0 | 0
11 | 0.99695 | -0.077808 | 0.076207 | 0.036909
12 | 0.99652 | -0.081346 | 0 | 0
13 | 0.99255 | -0.090522 | 0.12526 | 0.060667
14 | 0.99238 | -0.092138 | 0 | 0
15 | 0.99347 | -0.082018 | 0 | 0
16 | 0.99151 | -0.085817 | 0 | 0
17 | 0.9935 | -0.082191 | 0.14168 | 0.068617
18 | 0.99534 | -0.066064 | 0.21769 | 0.10543
19 | 0.99543 | -0.065301 | 0 | 0
20 | 0.99133 | -0.084208 | 0 | 0
21 | 0.9915 | -0.085713 | 0.1452 | 0.070324
22 | 0.9913 | -0.083952 | 0.40882 | 0.198
23 | 0.99836 | -0.014147 | 0.18204 | 0.088165
24 | 0.9984 | -0.014455 | 0 | 0
25 | 0.99222 | -0.06576 | 0 | 0
26 | 0.99229 | -0.066465 | 0 | 0
27 | 0.9922 | -0.065642 | 0.35817 | 0.17347
28 | 0.99227 | -0.066268 | 0.10531 | 0.051003
29 | 0.99243 | -0.067719 | 0 | 0
30 | 0.9922 | -0.065618 | 0.13868 | 0.067167
31 | 0.99271 | -0.068738 | 0.3259 | 0.15784
32 | 0.99278 | -0.068289 | 0 | 0
33 | 0.99226 | -0.066222 | 0.1089 | 0.052743
34 | 0.99259 | -0.066607 | 0 | 0
35 | 0.99254 | -0.066086 | 0.38132 | 0.18468
36 | 0.99854 | -0.039085 | 0.32816 | 0.15894
37 | 0.99857 | -0.03887 | 0 | 0
38 | 0.99861 | -0.038162 | 0 | 0
39 | 0.99855 | -0.039349 | 0 | 0
40 | 0.99862 | -0.037924 | 0.2996 | 0.1451
41 | 0.99855 | -0.0394 | 0.37589 | 0.18205
42 | 0.99865 | -0.037024 | 0 | 0
43 | 0.99824 | -0.045755 | 0 | 0
44 | 0.99917 | -0.025812 | 0 | 0
45 | 0.99816 | -0.046239 | 0.29135 | 0.14111
46 | 0.99804 | -0.053031 | 0.23826 | 0.1154
47 | 0.99916 | -0.025706 | 0.31732 | 0.15369
48 | 0.99968 | -0.0068394 | 0.097646 | 0.047292
49 | 0.99791 | -0.055981 | 0 | 0
50 | 1 | 0 | -19.3637 | -8.5922
51 | 0.99893 | -0.018321 | 0.26665 | 0.12914
52 | 0.99894 | -0.018413 | 0 | 0
53 | 0.99888 | -0.017885 | 0 | 0
54 | 0.99908 | -0.016868 | 0 | 0
55 | 0.99861 | -0.015649 | 0 | 0
56 | 0.99877 | -0.016863 | 1.0171 | 0.4926
57 | 0.99909 | -0.016712 | 0.11563 | 0.056
58 | 0.99859 | -0.015481 | 0.29145 | 0.14116
59 | 0.9986 | -0.015534 | 0.19601 | 0.094933
60 | 0.99876 | -0.016752 | 0.13213 | 0.063993
61 | 0.99909 | -0.016631 | 0.34953 | 0.16929
62 | 0.99855 | -0.015095 | 0 | 0
63 | 0.99859 | -0.015461 | 0.11568 | 0.056028
64 | 0.99847 | -0.015007 | 0.13534 | 0.06555
65 | 0.99847 | -0.01497 | 0 | 0
66 | 0.99862 | -0.013815 | 0 | 0
67 | 0.9987 | -0.014361 | 0 | 0
68 | 0.99873 | -0.01455 | 0.37279 | 0.18055
69 | 0.99892 | -0.013109 | 0 | 0
70 | 0.99917 | -0.015139 | 0 | 0
71 | 0.99733 | -0.067976 | 0.25982 | 0.12584
72 | 0.99734 | -0.068099 | 0 | 0
73 | 0.99735 | -0.068229 | 0 | 0
74 | 0.99752 | -0.064195 | 0 | 0
75 | 0.99719 | -0.072161 | 0 | 0
76 | 0.99726 | -0.068809 | 0.25201 | 0.12205
77 | 0.99751 | -0.064086 | 0 | 0
78 | 0.99751 | -0.064078 | 0.091277 | 0.044208
79 | 0.99751 | -0.064491 | 0.10016 | 0.048509
80 | 0.99751 | -0.064475 | 0.4098 | 0.19848
81 | 0.99751 | -0.064449 | 0 | 0
82 | 0.99708 | -0.075063 | 0 | 0
83 | 0.99711 | -0.072689 | 0.3424 | 0.16583
84 | 0.99303 | -0.070417 | 0.29623 | 0.14347
85 | 0.99305 | -0.070599 | 0 | 0
86 | 0.99306 | -0.070728 | 0.11238 | 0.05443
87 | 0.99311 | -0.071171 | 0 | 0
88 | 0.99321 | -0.072049 | 0.077152 | 0.037366
89 | 0.9931 | -0.07108 | 0.096941 | 0.046951
90 | 0.99373 | -0.076561 | 0.36549 | 0.17701
91 | 0.99374 | -0.076655 | 0 | 0
92 | 0.99333 | -0.073112 | 0 | 0
93 | 0.99423 | -0.081004 | 0 | 0
94 | 0.99872 | -0.023627 | 0 | 0
95 | 0.99826 | -0.032002 | 0 | 0
96 | 0.99811 | -0.034788 | 0 | 0
97 | 0.99824 | -0.031847 | 0.11004 | 0.053295
98 | 0.99959 | -0.0074947 | 0 | 0
99 | 0.99912 | -0.016059 | 0.62201 | 0.30126
100 | 0.99804 | -0.036037 | 0 | 0
101 | 0.99808 | -0.034578 | 0.16446 | 0.079652
102 | 0.99957 | -0.007254 | 0.34574 | 0.16745
103 | 0.99964 | -0.0065403 | 0 | 0
104 | 0.99434 | -0.081943 | 0.38663 | 0.18726
105 | 0.99422 | -0.080931 | 0 | 0
106 | 0.99823 | -0.031709 | 0.20763 | 0.10056
107 | 0.99779 | -0.040504 | 0 | 0
108 | 0.99803 | -0.036093 | 0.34024 | 0.16479
109 | 0.99982 | -0.003257 | 0.12875 | 0.062356
110 | 0.9955 | -0.073902 | 0.076912 | 0.03725
111 | 0.99421 | -0.080784 | 0.19263 | 0.093295
112 | 0.99749 | -0.064516 | 0.3662 | 0.17736
113 | 0.99741 | -0.067279 | 0 | 0
114 | 0.99741 | -0.067357 | 0.40034 | 0.19389
115 | 0.99742 | -0.067063 | 0 | 0
116 | 0.9975 | -0.064733 | 0.35535 | 0.17211
117 | 0.9975 | -0.06456 | 0 | 0
118 | 0.99749 | -0.064423 | 0.40817 | 0.19768
119 | 0.99743 | -0.066886 | 0 | 0
120 | 0.99708 | -0.075074 | 0.07066 | 0.034222
121 | 0.99702 | -0.076193 | 0.095216 | 0.046115
122 | 0.99717 | -0.003449 | 0.33969 | 0.16452
123 | 0.99718 | -0.003592 | 0 | 0
124 | 0.99719 | -0.0036762 | 0 | 0
125 | 0.99717 | -0.0034634 | 0 | 0
126 | 0.99723 | -0.0039716 | 0.11187 | 0.054179
127 | 0.99715 | -0.0033274 | 0.071726 | 0.034739
128 | 0.99728 | -0.004435 | 0 | 0
129 | 0.99562 | -0.066685 | 0 | 0
130 | 0.99761 | -0.046613 | 0.37896 | 0.18354
131 | 0.99567 | -0.067084 | 0.18274 | 0.088506
132 | 0.99576 | -0.067704 | 0 | 0
133 | 0.99694 | -0.077738 | 0.081941 | 0.039686
134 | 0.99758 | -0.0069724 | 0 | 0
135 | 0.99758 | -0.0069419 | 0.35029 | 0.16965
136 | 0.99827 | -0.01276 | 0 | 0
137 | 0.99847 | -0.014409 | 0 | 0
138 | 0.9982 | -0.012124 | 0 | 0
139 | 0.99826 | -0.012653 | 0.13353 | 0.064671
140 | 0.99846 | -0.014391 | 0.097759 | 0.047347
141 | 0.99819 | -0.012009 | 0.41398 | 0.2005
142 | 0.99713 | -0.0031936 | 0 | 0
143 | 0.9971 | -0.0029917 | 0 | 0
144 | 0.99712 | -0.0030917 | 0.07554 | 0.036586
145 | 0.99712 | -0.0030404 | 0.10776 | 0.05219
146 | 0.99711 | -0.002931 | 0 | 0
147 | 0.9971 | -0.0029143 | 0 | 0
148 | 0.9971 | -0.0029654 | 0.074063 | 0.035871
149 | 0.9971 | -0.0028915 | 0.18751 | 0.090814
150 | 0.99859 | -0.015443 | 0.089479 | 0.043337
151 | 0.9968 | -0.067152 | 0.50804 | 0.24606
152 | 0.99665 | -0.068893 | 0 | 0
153 | 0.9976 | -0.046741 | 0 | 0
154 | 0.9963 | -0.071686 | 0.40813 | 0.19767
155 | 0.99569 | -0.075533 | 0.068994 | 0.033415
156 | 0.99624 | -0.07131 | 0 | 0
157 | 0.99558 | -0.074573 | 0 | 0
158 | 0.99742 | -0.067044 | 0.20528 | 0.099422
159 | 0.99646 | -0.081115 | 0 | 0
160 | 0.99646 | -0.081113 | 0.071141 | 0.034455
161 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.34316 | 0.15108 | -0.34315 | -0.15228 | 7.9984e-06 | -0.0011986 | 0.010865 | 0.010879 | 0.010879 | 0.99619 | -0.079124 | 0.99617 | -0.078962 | 4.9451
1 | -0.41721 | -0.18694 | 0.41723 | 0.18438 | 2.5401e-05 | -0.0025673 | 0.013248 | 0.013218 | 0.013248 | 0.99619 | -0.079124 | 0.99625 | -0.079556 | 6.0218
2 | 0.34315 | 0.15228 | -0.34306 | -0.16597 | 9.2858e-05 | -0.013685 | 0.010879 | 0.011046 | 0.011046 | 0.99617 | -0.078962 | 0.99591 | -0.076828 | 5.0211
3 | -0.41723 | -0.18438 | 0.41735 | 0.17183 | 0.00012248 | -0.012549 | 0.013218 | 0.013075 | 0.013218 | 0.99625 | -0.079556 | 0.99653 | -0.081408 | 6.008
4 | 0.34306 | 0.16597 | -0.34306 | -0.16615 | 1.2722e-06 | -0.00018453 | 0.011046 | 0.011049 | 0.011049 | 0.99591 | -0.076828 | 0.99591 | -0.076796 | 5.0222
5 | -1.0783 | -0.4636 | 1.0788 | 0.38385 | 0.00044602 | -0.079745 | 0.034002 | 0.033155 | 0.034002 | 0.99653 | -0.081408 | 0.99696 | -0.077914 | 5.3294
6 | 0.44919 | 0.20105 | -0.44918 | -0.2014 | 4.0042e-06 | -0.00034863 | 0.014256 | 0.01426 | 0.01426 | 0.99653 | -0.081408 | 0.99652 | -0.081343 | 6.4819
7 | 0.21179 | 0.090716 | -0.21176 | -0.10221 | 2.9446e-05 | -0.011496 | 0.0066743 | 0.0068124 | 0.0068124 | 0.99653 | -0.081408 | 0.99639 | -0.08036 | 3.0965
8 | 0.21176 | 0.10221 | -0.21176 | -0.10256 | 9.0767e-07 | -0.00034678 | 0.0068124 | 0.0068168 | 0.0068168 | 0.99639 | -0.08036 | 0.99639 | -0.080322 | 3.0985
9 | -1.2369 | -0.45724 | 1.237 | 0.43711 | 7.0569e-05 | -0.020127 | 0.038184 | 0.037986 | 0.038184 | 0.99696 | -0.077914 | 0.99703 | -0.076305 | 4.535
10 | 0.15815 | 0.073384 | -0.15815 | -0.074827 | 2.0778e-06 | -0.0014436 | 0.0050483 | 0.005066 | 0.005066 | 0.99696 | -0.077914 | 0.99695 | -0.077808 | 2.3027
11 | 0.071146 | 0.018311 | -0.071146 | -0.018709 | 1.0145e-07 | -0.00039728 | 0.0021281 | 0.002131 | 0.002131 | 0.99652 | -0.081343 | 0.99652 | -0.081346 | 0.96866
12 | 0.095217 | 0.043619 | -0.095216 | -0.046115 | 1.3041e-06 | -0.0024959 | 0.0030324 | 0.0030632 | 0.0030632 | 0.99703 | -0.076305 | 0.99702 | -0.076193 | 1.3924
13 | -1.3322 | -0.48073 | 1.3323 | 0.46646 | 5.782e-05 | -0.014267 | 0.041007 | 0.040868 | 0.041007 | 0.99703 | -0.076305 | 0.99708 | -0.075063 | 4.8702
14 | 0.081941 | 0.037918 | -0.081941 | -0.039686 | 6.8524e-07 | -0.0017671 | 0.0026144 | 0.0026363 | 0.0026363 | 0.99695 | -0.077808 | 0.99694 | -0.077738 | 1.1983
15 | 0.071146 | 0.018709 | -0.071141 | -0.034384 | 4.2717e-06 | -0.015676 | 0.002131 | 0.0022891 | 0.0022891 | 0.99652 | -0.081346 | 0.99646 | -0.081115 | 1.0405
16 | 0.55472 | 0.22842 | -0.55463 | -0.22855 | 8.5338e-05 | -0.00013153 | 0.017448 | 0.01745 | 0.01745 | 0.99255 | -0.090522 | 0.99238 | -0.092138 | 8.3094
17 | -0.67998 | -0.28909 | 0.68057 | 0.28861 | 0.00059061 | -0.00047542 | 0.02149 | 0.02148 | 0.02149 | 0.99255 | -0.090522 | 0.99347 | -0.082018 | 10.2332
18 | 0.55463 | 0.22855 | -0.55412 | -0.25755 | 0.00051408 | -0.029 | 0.01745 | 0.01779 | 0.01779 | 0.99238 | -0.092138 | 0.99151 | -0.085817 | 8.0865
19 | -0.68057 | -0.28861 | 0.68059 | 0.28789 | 1.9111e-05 | -0.00072577 | 0.02148 | 0.021472 | 0.02148 | 0.99347 | -0.082018 | 0.9935 | -0.082191 | 9.7637
20 | 0.40891 | 0.18866 | -0.40883 | -0.19679 | 8.0329e-05 | -0.0081281 | 0.013111 | 0.013213 | 0.013213 | 0.99151 | -0.085817 | 0.99133 | -0.084208 | 6.0057
21 | 0.1452 | 0.068894 | -0.1452 | -0.070324 | 1.7883e-06 | -0.0014301 | 0.0046792 | 0.0046972 | 0.0046972 | 0.99151 | -0.085817 | 0.9915 | -0.085713 | 2.1351
22 | -0.82226 | -0.3565 | 0.82368 | 0.356 | 0.0014216 | -0.00049942 | 0.026041 | 0.026025 | 0.026041 | 0.9935 | -0.082191 | 0.99534 | -0.066064 | 12.4004
23 | -1.0414 | -0.46144 | 1.0415 | 0.46144 | 9.0503e-05 | 1.6321e-06 | 0.033035 | 0.033034 | 0.033035 | 0.99534 | -0.066064 | 0.99543 | -0.065301 | 15.7309
24 | -1.0415 | -0.46144 | 1.0417 | 0.45812 | 0.00020761 | -0.0033146 | 0.033034 | 0.032995 | 0.033034 | 0.99543 | -0.065301 | 0.99562 | -0.066685 | 15.0156
25 | 0.40883 | 0.19679 | -0.40882 | -0.198 | 1.2107e-05 | -0.0012139 | 0.013213 | 0.013228 | 0.013228 | 0.99133 | -0.084208 | 0.9913 | -0.083952 | 6.0127
26 | -0.18204 | -0.088165 | 0.18205 | 0.084632 | 6.7323e-06 | -0.0035335 | 0.0058484 | 0.0058046 | 0.0058484 | 0.99836 | -0.014147 | 0.9984 | -0.014455 | 2.6584
27 | -0.18205 | -0.084632 | 0.18206 | 0.077564 | 1.3169e-05 | -0.0070674 | 0.0058046 | 0.0057214 | 0.0058046 | 0.9984 | -0.014455 | 0.99847 | -0.01497 | 2.6385
28 | -0.49686 | -0.23983 | 0.4969 | 0.23703 | 4.1028e-05 | -0.002798 | 0.016052 | 0.016016 | 0.016052 | 0.99222 | -0.06576 | 0.99229 | -0.066465 | 7.2962
29 | 0.49686 | 0.23983 | -0.49685 | -0.24029 | 6.7752e-06 | -0.00046081 | 0.016052 | 0.016057 | 0.016057 | 0.99222 | -0.06576 | 0.9922 | -0.065642 | 7.2988
30 | 0.21421 | 0.10104 | -0.21421 | -0.1029 | 5.0357e-06 | -0.0018601 | 0.0068903 | 0.0069136 | 0.0069136 | 0.99229 | -0.066465 | 0.99227 | -0.066268 | 3.1425
31 | -0.71112 | -0.33808 | 0.71122 | 0.33447 | 0.00010808 | -0.0036029 | 0.022907 | 0.022861 | 0.022907 | 0.99229 | -0.066465 | 0.99243 | -0.067719 | 10.4121
32 | 0.13868 | 0.066823 | -0.13868 | -0.067167 | 3.9252e-07 | -0.00034406 | 0.0044789 | 0.0044832 | 0.0044832 | 0.9922 | -0.065642 | 0.9922 | -0.065618 | 2.0378
33 | 0.1089 | 0.051899 | -0.1089 | -0.052743 | 5.9212e-07 | -0.00084381 | 0.0035096 | 0.0035202 | 0.0035202 | 0.99227 | -0.066268 | 0.99226 | -0.066222 | 1.6001
34 | -0.71122 | -0.33447 | 0.71133 | 0.3344 | 0.00010792 | -6.8701e-05 | 0.022861 | 0.02286 | 0.022861 | 0.99243 | -0.067719 | 0.99259 | -0.066607 | 10.8863
35 | -0.3259 | -0.15784 | 0.32593 | 0.15772 | 2.2153e-05 | -0.00011807 | 0.01053 | 0.010528 | 0.01053 | 0.99271 | -0.068738 | 0.99278 | -0.068289 | 5.0144
36 | 1.0929 | 0.51325 | -1.0927 | -0.51639 | 0.00022466 | -0.003142 | 0.035108 | 0.035148 | 0.035148 | 0.99278 | -0.068289 | 0.99259 | -0.066607 | 15.9764
37 | -1.4188 | -0.67097 | 1.4193 | 0.66689 | 0.00049924 | -0.0040836 | 0.045636 | 0.045584 | 0.045636 | 0.99278 | -0.068289 | 0.99311 | -0.071171 | 20.7438
38 | 0.38134 | 0.18199 | -0.38132 | -0.18468 | 2.3193e-05 | -0.0026918 | 0.012289 | 0.012323 | 0.012323 | 0.99259 | -0.066607 | 0.99254 | -0.066086 | 5.6012
39 | -0.32816 | -0.15894 | 0.32817 | 0.15888 | 1.0722e-05 | -5.7757e-05 | 0.010541 | 0.01054 | 0.010541 | 0.99854 | -0.039085 | 0.99857 | -0.03887 | 5.0196
40 | -0.70407 | -0.31475 | 0.70409 | 0.2967 | 2.1371e-05 | -0.01805 | 0.022295 | 0.022087 | 0.022295 | 0.99857 | -0.03887 | 0.99861 | -0.038162 | 2.6479
41 | 0.3759 | 0.15587 | -0.37589 | -0.17936 | 7.9914e-06 | -0.023493 | 0.011764 | 0.01204 | 0.01204 | 0.99857 | -0.03887 | 0.99855 | -0.039349 | 1.43
42 | -0.70409 | -0.2967 | 0.7041 | 0.29084 | 6.8524e-06 | -0.0058594 | 0.022087 | 0.022022 | 0.022087 | 0.99861 | -0.038162 | 0.99862 | -0.037924 | 2.6232
43 | 0.37589 | 0.17936 | -0.37589 | -0.18205 | 9.3909e-07 | -0.0026883 | 0.01204 | 0.012074 | 0.012074 | 0.99855 | -0.039349 | 0.99855 | -0.0394 | 1.434
44 | -1.0037 | -0.43594 | 1.0037 | 0.43583 | 1.8498e-05 | -0.00010713 | 0.031633 | 0.031631 | 0.031633 | 0.99862 | -0.037924 | 0.99865 | -0.037024 | 3.8577
45 | 5.1287 | 2.0732 | -5.127 | -2.1005 | 0.0017822 | -0.027315 | 0.15991 | 0.16022 | 0.16022 | 0.99865 | -0.037024 | 0.99824 | -0.045755 | 19.029
46 | -6.1324 | -2.509 | 6.1352 | 2.4804 | 0.0027357 | -0.028611 | 0.19153 | 0.19119 | 0.19153 | 0.99865 | -0.037024 | 0.99917 | -0.025812 | 22.7472
47 | 0.29137 | 0.14096 | -0.29135 | -0.14111 | 2.1359e-05 | -0.00014934 | 0.0093603 | 0.0093624 | 0.0093624 | 0.99824 | -0.045755 | 0.99816 | -0.046239 | 4.4583
48 | 4.8356 | 1.9595 | -4.8349 | -1.9588 | 0.00068566 | 0.00077476 | 0.15088 | 0.15089 | 0.15089 | 0.99824 | -0.045755 | 0.99804 | -0.053031 | 18.4007
49 | 0.31732 | 0.15302 | -0.31732 | -0.15369 | 3.868e-06 | -0.00066496 | 0.010178 | 0.010187 | 0.010187 | 0.99917 | -0.025812 | 0.99916 | -0.025706 | 4.6303
50 | -6.4525 | -2.6334 | 6.4549 | 2.6365 | 0.0023985 | 0.0030433 | 0.20135 | 0.20135 | 0.20135 | 0.99917 | -0.025812 | 0.99968 | -0.0068394 | 24.5549
51 | 4.5966 | 1.8434 | -4.5961 | -1.8537 | 0.00053298 | -0.010303 | 0.14325 | 0.14336 | 0.14336 | 0.99804 | -0.053031 | 0.99791 | -0.055981 | 17.0264
52 | -6.5526 | -2.6838 | 6.5543 | 2.6675 | 0.0017905 | -0.016247 | 0.20447 | 0.20428 | 0.20447 | 0.99968 | -0.0068394 | 1 | 0 | 24.2842
53 | 4.5961 | 1.8537 | -4.5946 | -1.8826 | 0.0015007 | -0.028899 | 0.14336 | 0.14369 | 0.14369 | 0.99791 | -0.055981 | 0.99752 | -0.064195 | 17.0656
54 | 12.7953 | 5.9142 | -12.7934 | -5.9173 | 0.0019374 | -0.0031049 | 0.40692 | 0.40698 | 0.40698 | 1 | 0 | 0.99982 | -0.003257 | 48.3346
55 | -1.4161 | -0.6815 | 1.4161 | 0.68138 | 1.5192e-05 | -0.00012695 | 0.045415 | 0.045413 | 0.045415 | 0.99893 | -0.018321 | 0.99894 | -0.018413 | 20.6432
56 | 1.1494 | 0.55236 | -1.1494 | -0.55311 | 5.8401e-05 | -0.00074983 | 0.036853 | 0.036863 | 0.036863 | 0.99893 | -0.018321 | 0.99888 | -0.017885 | 16.7558
57 | -4.0755 | -1.9232 | 4.076 | 1.9213 | 0.00052668 | -0.0018191 | 0.13023 | 0.1302 | 0.13023 | 0.99894 | -0.018413 | 0.99908 | -0.016868 | 35.9751
58 | 2.6594 | 1.2418 | -2.6585 | -1.2438 | 0.00091538 | -0.0019978 | 0.084818 | 0.084846 | 0.084846 | 0.99894 | -0.018413 | 0.99861 | -0.015649 | 38.5664
59 | 1.1494 | 0.55311 | -1.1492 | -0.55486 | 0.00013627 | -0.0017478 | 0.036863 | 0.036885 | 0.036885 | 0.99888 | -0.017885 | 0.99877 | -0.016863 | 16.766
60 | -4.076 | -1.9213 | 4.0761 | 1.9206 | 3.0441e-05 | -0.00072042 | 0.1302 | 0.13019 | 0.1302 | 0.99908 | -0.016868 | 0.99909 | -0.016712 | 15.4635
61 | 2.2573 | 1.0512 | -2.2573 | -1.0514 | 4.7559e-05 | -0.00014959 | 0.071983 | 0.071985 | 0.071985 | 0.99861 | -0.015649 | 0.99859 | -0.015481 | 32.7203
62 | 0.40118 | 0.19258 | -0.40118 | -0.19316 | 5.3541e-06 | -0.00057511 | 0.012864 | 0.012871 | 0.012871 | 0.99861 | -0.015649 | 0.9986 | -0.015534 | 5.8506
63 | 0.13213 | 0.062255 | -0.13213 | -0.063993 | 1.746e-06 | -0.0017383 | 0.0042217 | 0.0042433 | 0.0042433 | 0.99877 | -0.016863 | 0.99876 | -0.016752 | 1.9288
64 | -4.1917 | -1.9766 | 4.1917 | 1.9763 | 1.6055e-05 | -0.00035842 | 0.13391 | 0.1339 | 0.13391 | 0.99909 | -0.016712 | 0.99909 | -0.016631 | 15.9032
65 | 1.9658 | 0.9102 | -1.9657 | -0.91061 | 9.6678e-05 | -0.00041091 | 0.062624 | 0.06263 | 0.06263 | 0.99859 | -0.015481 | 0.99855 | -0.015095 | 28.4681
66 | 0.20516 | 0.098227 | -0.20516 | -0.098947 | 1.7488e-06 | -0.00071982 | 0.0065756 | 0.0065846 | 0.0065846 | 0.9986 | -0.015534 | 0.99859 | -0.015461 | 2.993
67 | -4.5413 | -2.1456 | 4.5414 | 2.1432 | 0.00012454 | -0.0023506 | 0.14512 | 0.14509 | 0.14512 | 0.99909 | -0.016631 | 0.99912 | -0.016059 | 17.2353
68 | 1.9657 | 0.91061 | -1.9656 | -0.91133 | 0.00017127 | -0.00072764 | 0.06263 | 0.062639 | 0.062639 | 0.99855 | -0.015095 | 0.99847 | -0.014409 | 28.4724
69 | 0.08948 | 0.042919 | -0.089479 | -0.043337 | 1.9335e-07 | -0.00041816 | 0.0028689 | 0.0028741 | 0.0028741 | 0.99859 | -0.015461 | 0.99859 | -0.015443 | 1.3064
70 | 0.18206 | 0.076959 | -0.18206 | -0.077564 | 1.1108e-06 | -0.00060541 | 0.0057146 | 0.0057214 | 0.0057214 | 0.99847 | -0.015007 | 0.99847 | -0.01497 | 2.6007
71 | -0.3174 | -0.14251 | 0.31745 | 0.14224 | 4.4618e-05 | -0.00026675 | 0.010059 | 0.010056 | 0.010059 | 0.99847 | -0.015007 | 0.99862 | -0.013815 | 4.7901
72 | -0.31745 | -0.14224 | 0.31747 | 0.13782 | 2.5004e-05 | -0.0044262 | 0.010056 | 0.010004 | 0.010056 | 0.99862 | -0.013815 | 0.9987 | -0.014361 | 4.5708
73 | -0.31747 | -0.13782 | 0.31748 | 0.13617 | 9.2107e-06 | -0.0016421 | 0.010004 | 0.0099852 | 0.010004 | 0.9987 | -0.014361 | 0.99873 | -0.01455 | 4.5473
74 | -0.69027 | -0.31673 | 0.6904 | 0.31663 | 0.00012537 | -9.5395e-05 | 0.021952 | 0.02195 | 0.021952 | 0.99873 | -0.01455 | 0.99892 | -0.013109 | 10.4533
75 | -0.6904 | -0.31663 | 0.69059 | 0.30969 | 0.00018801 | -0.0069366 | 0.02195 | 0.021866 | 0.02195 | 0.99892 | -0.013109 | 0.99917 | -0.015139 | 9.9772
76 | -12.312 | -5.7009 | 12.3164 | 5.693 | 0.0043798 | -0.0078692 | 0.39199 | 0.39185 | 0.39199 | 0.99917 | -0.015139 | 0.99959 | -0.0074947 | 46.5551
77 | 5.1636 | 2.4412 | -5.1634 | -2.4445 | 0.00022798 | -0.0032793 | 0.16502 | 0.16506 | 0.16506 | 0.99917 | -0.015139 | 0.99912 | -0.016059 | 19.6032
78 | 6.4578 | 2.95 | -6.4553 | -2.9726 | 0.0025202 | -0.022605 | 0.20512 | 0.20542 | 0.20542 | 0.99917 | -0.015139 | 0.99872 | -0.023627 | 24.3968
79 | -0.25982 | -0.12584 | 0.25982 | 0.12489 | 3.6998e-06 | -0.00094285 | 0.0083561 | 0.0083442 | 0.0083561 | 0.99733 | -0.067976 | 0.99734 | -0.068099 | 3.7982
80 | -0.25982 | -0.12489 | 0.25983 | 0.12387 | 3.9904e-06 | -0.00102 | 0.0083442 | 0.0083315 | 0.0083442 | 0.99734 | -0.068099 | 0.99735 | -0.068229 | 3.7928
81 | -2.2576 | -0.84167 | 2.2579 | 0.81392 | 0.00032706 | -0.027747 | 0.069738 | 0.069458 | 0.069738 | 0.99735 | -0.068229 | 0.99752 | -0.064195 | 8.2824
82 | 1.7457 | 0.59595 | -1.7455 | -0.6301 | 0.00023737 | -0.034148 | 0.053392 | 0.053721 | 0.053721 | 0.99735 | -0.068229 | 0.99719 | -0.072161 | 6.3802
83 | 0.25203 | 0.12184 | -0.25201 | -0.12205 | 2.209e-05 | -0.00021032 | 0.0081026 | 0.0081054 | 0.0081054 | 0.99735 | -0.068229 | 0.99726 | -0.068809 | 3.8597
84 | 1.0612 | 0.48359 | -1.0612 | -0.48883 | 1.442e-05 | -0.0052367 | 0.033749 | 0.033812 | 0.033812 | 0.99752 | -0.064195 | 0.99751 | -0.064491 | 4.0157
85 | 0.81799 | 0.38752 | -0.81798 | -0.39423 | 1.1149e-05 | -0.0067185 | 0.026194 | 0.026278 | 0.026278 | 0.99752 | -0.064195 | 0.99751 | -0.064475 | 3.1209
86 | 0.36621 | 0.15609 | -0.36621 | -0.16875 | 4.0941e-06 | -0.012651 | 0.01152 | 0.011669 | 0.011669 | 0.99752 | -0.064195 | 0.99751 | -0.064449 | 1.3858
87 | 0.091279 | 0.041455 | -0.091277 | -0.044034 | 1.233e-06 | -0.0025787 | 0.0029012 | 0.0029328 | 0.0029328 | 0.99752 | -0.064195 | 0.99751 | -0.064086 | 1.3331
88 | 1.4031 | 0.4644 | -1.4029 | -0.49532 | 0.00013782 | -0.030921 | 0.042784 | 0.043075 | 0.043075 | 0.99719 | -0.072161 | 0.99708 | -0.075063 | 5.1158
89 | 0.34243 | 0.1657 | -0.3424 | -0.16583 | 2.7417e-05 | -0.00013342 | 0.011013 | 0.011014 | 0.011014 | 0.99719 | -0.072161 | 0.99711 | -0.072689 | 5.245
90 | 0.091277 | 0.044034 | -0.091277 | -0.044208 | 8.3878e-08 | -0.0001734 | 0.0029328 | 0.002935 | 0.002935 | 0.99751 | -0.064086 | 0.99751 | -0.064078 | 1.3341
91 | 0.96102 | 0.44032 | -0.96101 | -0.44508 | 1.0768e-05 | -0.0047609 | 0.030592 | 0.03065 | 0.03065 | 0.99751 | -0.064491 | 0.9975 | -0.064733 | 3.6401
92 | 0.40818 | 0.19576 | -0.40817 | -0.19702 | 3.0641e-06 | -0.001258 | 0.013101 | 0.013116 | 0.013116 | 0.99751 | -0.064475 | 0.9975 | -0.06456 | 3.6233
93 | 0.36621 | 0.16875 | -0.3662 | -0.17736 | 5.8514e-06 | -0.0086134 | 0.011669 | 0.011775 | 0.011775 | 0.99751 | -0.064449 | 0.99749 | -0.064516 | 1.8457
94 | 0.07066 | 0.028854 | -0.07066 | -0.034222 | 1.3328e-07 | -0.0053679 | 0.0022097 | 0.0022731 | 0.0022731 | 0.99708 | -0.075063 | 0.99708 | -0.075074 | 0.35628
95 | -0.29623 | -0.14347 | 0.29624 | 0.14227 | 6.2521e-06 | -0.0012045 | 0.0095684 | 0.0095531 | 0.0095684 | 0.99303 | -0.070417 | 0.99305 | -0.070599 | 4.3493
96 | -0.29624 | -0.14227 | 0.29624 | 0.1414 | 4.4705e-06 | -0.00086361 | 0.0095531 | 0.0095423 | 0.0095531 | 0.99305 | -0.070599 | 0.99306 | -0.070728 | 4.3423
97 | -0.40863 | -0.19583 | 0.40865 | 0.19364 | 2.1589e-05 | -0.0021929 | 0.013172 | 0.013145 | 0.013172 | 0.99306 | -0.070728 | 0.99311 | -0.071171 | 5.9873
98 | -1.9249 | -0.90555 | 1.9251 | 0.90466 | 0.00020737 | -0.00089542 | 0.061835 | 0.061824 | 0.061835 | 0.99311 | -0.071171 | 0.99321 | -0.072049 | 28.107
99 | 0.096942 | 0.045022 | -0.096941 | -0.046951 | 1.0636e-06 | -0.0019283 | 0.003107 | 0.003131 | 0.003131 | 0.99311 | -0.071171 | 0.9931 | -0.07108 | 1.4232
100 | -2.0023 | -0.94202 | 2.0025 | 0.94099 | 0.00026137 | -0.0010376 | 0.064315 | 0.064301 | 0.064315 | 0.99321 | -0.072049 | 0.99333 | -0.073112 | 29.2341
101 | -0.36549 | -0.17701 | 0.36549 | 0.17651 | 3.9475e-06 | -0.00050004 | 0.011797 | 0.011791 | 0.011797 | 0.99373 | -0.076561 | 0.99374 | -0.076655 | 5.3623
102 | 2.0034 | 0.9375 | -2.0025 | -0.94099 | 0.00087693 | -0.0034869 | 0.064255 | 0.064301 | 0.064301 | 0.99374 | -0.076655 | 0.99333 | -0.073112 | 29.2278
103 | -2.3689 | -1.114 | 2.3702 | 1.1105 | 0.0012705 | -0.0035076 | 0.076045 | 0.075997 | 0.076045 | 0.99374 | -0.076655 | 0.99423 | -0.081004 | 34.5659
104 | -2.5628 | -1.2015 | 2.5631 | 1.2008 | 0.00029769 | -0.0006911 | 0.082183 | 0.082173 | 0.082183 | 0.99423 | -0.081004 | 0.99434 | -0.081943 | 37.3558
105 | 0.19264 | 0.090996 | -0.19263 | -0.091771 | 1.6813e-06 | -0.00077509 | 0.0061858 | 0.0061954 | 0.0061954 | 0.99423 | -0.081004 | 0.99422 | -0.080931 | 2.8161
106 | 6.4553 | 2.9726 | -6.4528 | -2.9951 | 0.0025127 | -0.022443 | 0.20542 | 0.20572 | 0.20572 | 0.99872 | -0.023627 | 0.99826 | -0.032002 | 24.4325
107 | 6.1351 | 2.8436 | -6.1343 | -2.8515 | 0.00079883 | -0.0079525 | 0.19554 | 0.19565 | 0.19565 | 0.99826 | -0.032002 | 0.99811 | -0.034788 | 23.2363
108 | 0.31768 | 0.15151 | -0.31768 | -0.15251 | 5.806e-06 | -0.00099594 | 0.010178 | 0.01019 | 0.01019 | 0.99826 | -0.032002 | 0.99824 | -0.031847 | 4.632
109 | 5.9698 | 2.7745 | -5.9695 | -2.7782 | 0.00034929 | -0.0036856 | 0.1904 | 0.19045 | 0.19045 | 0.99811 | -0.034788 | 0.99804 | -0.036037 | 22.6183
110 | 0.16447 | 0.077009 | -0.16446 | -0.079652 | 4.1202e-06 | -0.0026433 | 0.0052523 | 0.0052852 | 0.0052852 | 0.99811 | -0.034788 | 0.99808 | -0.034578 | 2.4024
111 | 0.20764 | 0.099215 | -0.20763 | -0.10056 | 3.356e-06 | -0.0013461 | 0.0066547 | 0.0066716 | 0.0066716 | 0.99824 | -0.031847 | 0.99823 | -0.031709 | 3.0326
112 | 0.34575 | 0.16605 | -0.34574 | -0.16745 | 9.6413e-06 | -0.0013991 | 0.011077 | 0.011095 | 0.011095 | 0.99959 | -0.0074947 | 0.99957 | -0.007254 | 5.043
113 | -12.6622 | -5.8591 | 12.6627 | 5.8582 | 0.00056238 | -0.00092892 | 0.40293 | 0.40291 | 0.40293 | 0.99959 | -0.0074947 | 0.99964 | -0.0065403 | 47.8534
114 | 5.6293 | 2.6134 | -5.6281 | -2.6275 | 0.0011801 | -0.014126 | 0.17951 | 0.1797 | 0.1797 | 0.99804 | -0.036037 | 0.99779 | -0.040504 | 21.3419
115 | 0.34025 | 0.16477 | -0.34024 | -0.16479 | 2.9025e-06 | -1.4383e-05 | 0.010935 | 0.010935 | 0.010935 | 0.99804 | -0.036037 | 0.99803 | -0.036093 | 5.2071
116 | -12.6627 | -5.8582 | 12.6647 | 5.855 | 0.0019336 | -0.003196 | 0.40291 | 0.40285 | 0.40291 | 0.99964 | -0.0065403 | 0.99982 | -0.003257 | 47.8513
117 | -2.9497 | -1.3881 | 2.953 | 1.3899 | 0.0032484 | 0.0017942 | 0.094644 | 0.094641 | 0.094644 | 0.99434 | -0.081943 | 0.9955 | -0.073902 | 45.0686
118 | 0.19263 | 0.091771 | -0.19263 | -0.093295 | 3.3211e-06 | -0.0015239 | 0.0061954 | 0.0062146 | 0.0062146 | 0.99422 | -0.080931 | 0.99421 | -0.080784 | 2.8248
119 | 5.6281 | 2.6275 | -5.6273 | -2.6266 | 0.00074495 | 0.00091176 | 0.1797 | 0.1797 | 0.1797 | 0.99779 | -0.040504 | 0.99761 | -0.046613 | 21.9147
120 | -3.0299 | -1.4271 | 3.0301 | 1.4267 | 0.00024896 | -0.00039404 | 0.097119 | 0.097113 | 0.097119 | 0.9955 | -0.073902 | 0.99558 | -0.074573 | 44.145
121 | 0.40034 | 0.19005 | -0.40034 | -0.19389 | 1.5293e-06 | -0.0038453 | 0.012826 | 0.012874 | 0.012874 | 0.99741 | -0.067279 | 0.99741 | -0.067357 | 1.529
122 | -0.40034 | -0.19005 | 0.40035 | 0.1798 | 4.0213e-06 | -0.01025 | 0.012826 | 0.012702 | 0.012826 | 0.99741 | -0.067279 | 0.99742 | -0.067063 | 1.5233
123 | -0.40035 | -0.1798 | 0.40035 | 0.17894 | 3.3237e-07 | -0.00085603 | 0.012702 | 0.012692 | 0.012702 | 0.99742 | -0.067063 | 0.99742 | -0.067044 | 1.5085
124 | 0.60566 | 0.27298 | -0.60563 | -0.27347 | 2.7483e-05 | -0.00049735 | 0.019226 | 0.019232 | 0.019232 | 0.9975 | -0.064733 | 0.99743 | -0.066886 | 2.3454
125 | 0.40817 | 0.19702 | -0.40817 | -0.19768 | 6.4829e-06 | -0.0006682 | 0.013116 | 0.013125 | 0.013125 | 0.9975 | -0.06456 | 0.99749 | -0.064423 | 5.9659
126 | 0.60563 | 0.27347 | -0.60563 | -0.27836 | 4.3719e-06 | -0.0048906 | 0.019232 | 0.019291 | 0.019291 | 0.99743 | -0.066886 | 0.99742 | -0.067044 | 2.2911
127 | -0.33969 | -0.16452 | 0.3397 | 0.16368 | 5.6098e-06 | -0.00083477 | 0.010926 | 0.010916 | 0.010926 | 0.99717 | -0.003449 | 0.99718 | -0.003592 | 4.9666
128 | -0.3397 | -0.16368 | 0.3397 | 0.16319 | 3.3304e-06 | -0.00049636 | 0.010916 | 0.01091 | 0.010916 | 0.99718 | -0.003592 | 0.99719 | -0.0036762 | 4.9618
129 | 0.51664 | 0.23649 | -0.51663 | -0.23743 | 1.4332e-05 | -0.00093715 | 0.016448 | 0.01646 | 0.01646 | 0.99719 | -0.0036762 | 0.99717 | -0.0034634 | 7.4818
130 | -0.85634 | -0.39968 | 0.85637 | 0.39893 | 3.1682e-05 | -0.00074374 | 0.027357 | 0.027348 | 0.027357 | 0.99719 | -0.0036762 | 0.99723 | -0.0039716 | 12.435
131 | 0.51663 | 0.23743 | -0.51662 | -0.23802 | 9.0889e-06 | -0.00059363 | 0.01646 | 0.016467 | 0.016467 | 0.99717 | -0.0034634 | 0.99715 | -0.0033274 | 7.485
132 | -0.96824 | -0.45311 | 0.96829 | 0.45209 | 5.587e-05 | -0.0010216 | 0.030946 | 0.030933 | 0.030946 | 0.99723 | -0.0039716 | 0.99728 | -0.004435 | 14.0662
133 | 0.44489 | 0.20328 | -0.44488 | -0.20397 | 7.7975e-06 | -0.0006888 | 0.01416 | 0.014169 | 0.014169 | 0.99715 | -0.0033274 | 0.99713 | -0.0031936 | 6.4403
134 | -0.96829 | -0.45209 | 0.9686 | 0.44638 | 0.00031163 | -0.0057158 | 0.030933 | 0.030862 | 0.030933 | 0.99728 | -0.004435 | 0.99758 | -0.0069724 | 14.0604
135 | -1.0417 | -0.45812 | 1.0417 | 0.45715 | 6.0653e-05 | -0.00097013 | 0.032995 | 0.032983 | 0.032995 | 0.99562 | -0.066685 | 0.99567 | -0.067084 | 14.9976
136 | 5.2484 | 2.4431 | -5.2483 | -2.4435 | 3.1666e-05 | -0.00043978 | 0.16752 | 0.16752 | 0.16752 | 0.99761 | -0.046613 | 0.9976 | -0.046741 | 19.8959
137 | -1.2245 | -0.54566 | 1.2246 | 0.54444 | 0.00010693 | -0.0012239 | 0.038867 | 0.038852 | 0.038867 | 0.99567 | -0.067084 | 0.99576 | -0.067704 | 17.6667
138 | -1.2246 | -0.54444 | 1.2252 | 0.53713 | 0.00063584 | -0.0073019 | 0.038852 | 0.038764 | 0.038852 | 0.99576 | -0.067704 | 0.99624 | -0.07131 | 17.6599
139 | 0.35029 | 0.16948 | -0.35029 | -0.16965 | 1.2294e-06 | -0.00017216 | 0.011261 | 0.011263 | 0.011263 | 0.99758 | -0.0069724 | 0.99758 | -0.0069419 | 5.1195
140 | -1.3189 | -0.61586 | 1.3199 | 0.60636 | 0.00097187 | -0.0094956 | 0.042121 | 0.042002 | 0.042121 | 0.99758 | -0.0069724 | 0.99827 | -0.01276 | 19.1461
141 | -1.8674 | -0.86622 | 1.8678 | 0.86437 | 0.00039169 | -0.0018551 | 0.059528 | 0.059504 | 0.059528 | 0.99827 | -0.01276 | 0.99847 | -0.014409 | 27.0581
142 | 0.41401 | 0.19683 | -0.41398 | -0.19995 | 3.0954e-05 | -0.0031208 | 0.013256 | 0.013295 | 0.013295 | 0.99827 | -0.01276 | 0.9982 | -0.012124 | 6.0434
143 | 0.13353 | 0.063034 | -0.13353 | -0.064671 | 1.6835e-06 | -0.0016373 | 0.00427 | 0.0042904 | 0.0042904 | 0.99827 | -0.01276 | 0.99826 | -0.012653 | 1.9502
144 | 0.097759 | 0.046968 | -0.097759 | -0.047347 | 2.0922e-07 | -0.00037875 | 0.0031357 | 0.0031404 | 0.0031404 | 0.99847 | -0.014409 | 0.99846 | -0.014391 | 1.4275
145 | 0.41398 | 0.19995 | -0.41398 | -0.2005 | 5.4914e-06 | -0.00055168 | 0.013295 | 0.013302 | 0.013302 | 0.9982 | -0.012124 | 0.99819 | -0.012009 | 6.0465
146 | 0.074066 | 0.026894 | -0.074064 | -0.035152 | 2.51e-06 | -0.0082576 | 0.0022812 | 0.0023735 | 0.0023735 | 0.99713 | -0.0031936 | 0.9971 | -0.0029917 | 1.0789
147 | 0.37082 | 0.17708 | -0.37081 | -0.17763 | 4.4615e-06 | -0.00055891 | 0.011897 | 0.011903 | 0.011903 | 0.99713 | -0.0031936 | 0.99712 | -0.0030917 | 5.4107
148 | 0.074064 | 0.035152 | -0.074063 | -0.035871 | 2.2853e-07 | -0.00071854 | 0.0023735 | 0.0023825 | 0.0023825 | 0.9971 | -0.0029917 | 0.9971 | -0.0029654 | 1.083
149 | 0.29527 | 0.14105 | -0.29527 | -0.1414 | 1.7898e-06 | -0.00035391 | 0.0094736 | 0.009478 | 0.009478 | 0.99712 | -0.0030917 | 0.99712 | -0.0030404 | 4.3082
150 | 0.18751 | 0.089213 | -0.18751 | -0.090397 | 2.4141e-06 | -0.0011841 | 0.0060117 | 0.0060265 | 0.0060265 | 0.99712 | -0.0030404 | 0.99711 | -0.002931 | 2.7393
151 | 0.18751 | 0.090397 | -0.18751 | -0.090574 | 3.6178e-07 | -0.00017695 | 0.0060265 | 0.0060288 | 0.0060288 | 0.99711 | -0.002931 | 0.9971 | -0.0029143 | 2.7403
152 | 0.18751 | 0.090574 | -0.18751 | -0.090814 | 4.9162e-07 | -0.00024025 | 0.0060288 | 0.0060318 | 0.0060318 | 0.9971 | -0.0029143 | 0.9971 | -0.0028915 | 2.7417
153 | 4.7369 | 2.1938 | -4.7363 | -2.1954 | 0.00066391 | -0.0015669 | 0.15118 | 0.15121 | 0.15121 | 0.9968 | -0.067152 | 0.99665 | -0.068893 | 41.7694
154 | -5.245 | -2.4399 | 5.2483 | 2.4435 | 0.0033517 | 0.003671 | 0.16753 | 0.16752 | 0.16753 | 0.9968 | -0.067152 | 0.9976 | -0.046741 | 47.8645
155 | 1.634 | 0.73422 | -1.6334 | -0.73402 | 0.00054073 | 0.00020507 | 0.051885 | 0.051887 | 0.051887 | 0.99665 | -0.068893 | 0.9963 | -0.071686 | 24.7081
156 | 3.1023 | 1.4611 | -3.0995 | -1.4596 | 0.002825 | 0.0015791 | 0.099325 | 0.099327 | 0.099327 | 0.99665 | -0.068893 | 0.99569 | -0.075533 | 47.2988
157 | 1.2253 | 0.53635 | -1.2252 | -0.53713 | 6.7766e-05 | -0.00078064 | 0.038755 | 0.038764 | 0.038764 | 0.9963 | -0.071686 | 0.99624 | -0.07131 | 17.6201
158 | 3.0305 | 1.4262 | -3.0301 | -1.4267 | 0.00035632 | -0.00056419 | 0.097105 | 0.097113 | 0.097113 | 0.99569 | -0.075533 | 0.99558 | -0.074573 | 44.1424
159 | 0.071141 | 0.034384 | -0.071141 | -0.034455 | 2.0929e-08 | -7.1021e-05 | 0.0022891 | 0.00229 | 0.00229 | 0.99646 | -0.081115 | 0.99646 | -0.081113 | 1.0409

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 19.3637 | 8.5922

## res_load
| p_mw | q_mvar
0 | 0.074046 | 0.035862
1 | 0.34306 | 0.16615
2 | 0.21176 | 0.10256
3 | 0.37804 | 0.18309
4 | 0.076207 | 0.036909
5 | 0.12526 | 0.060667
6 | 0.14168 | 0.068617
7 | 0.21769 | 0.10543
8 | 0.1452 | 0.070324
9 | 0.40882 | 0.198
10 | 0.18204 | 0.088165
11 | 0.35817 | 0.17347
12 | 0.10531 | 0.051003
13 | 0.13868 | 0.067167
14 | 0.3259 | 0.15784
15 | 0.1089 | 0.052743
16 | 0.38132 | 0.18468
17 | 0.32816 | 0.15894
18 | 0.2996 | 0.1451
19 | 0.37589 | 0.18205
20 | 0.29135 | 0.14111
21 | 0.23826 | 0.1154
22 | 0.31732 | 0.15369
23 | 0.097646 | 0.047292
24 | 0.26665 | 0.12914
25 | 1.0171 | 0.4926
26 | 0.11563 | 0.056
27 | 0.29145 | 0.14116
28 | 0.19601 | 0.094933
29 | 0.13213 | 0.063993
30 | 0.34953 | 0.16929
31 | 0.11568 | 0.056028
32 | 0.13534 | 0.06555
33 | 0.37279 | 0.18055
34 | 0.25982 | 0.12584
35 | 0.25201 | 0.12205
36 | 0.091277 | 0.044208
37 | 0.10016 | 0.048509
38 | 0.4098 | 0.19848
39 | 0.3424 | 0.16583
40 | 0.29623 | 0.14347
41 | 0.11238 | 0.05443
42 | 0.077152 | 0.037366
43 | 0.096941 | 0.046951
44 | 0.36549 | 0.17701
45 | 0.11004 | 0.053295
46 | 0.62201 | 0.30126
47 | 0.16446 | 0.079652
48 | 0.34574 | 0.16745
49 | 0.38663 | 0.18726
50 | 0.20763 | 0.10056
51 | 0.34024 | 0.16479
52 | 0.12875 | 0.062356
53 | 0.076912 | 0.03725
54 | 0.19263 | 0.093295
55 | 0.3662 | 0.17736
56 | 0.40034 | 0.19389
57 | 0.35535 | 0.17211
58 | 0.40817 | 0.19768
59 | 0.07066 | 0.034222
60 | 0.095216 | 0.046115
61 | 0.33969 | 0.16452
62 | 0.11187 | 0.054179
63 | 0.071726 | 0.034739
64 | 0.37896 | 0.18354
65 | 0.18274 | 0.088506
66 | 0.081941 | 0.039686
67 | 0.35029 | 0.16965
68 | 0.13353 | 0.064671
69 | 0.097759 | 0.047347
70 | 0.41398 | 0.2005
71 | 0.07554 | 0.036586
72 | 0.10776 | 0.05219
73 | 0.074063 | 0.035871
74 | 0.18751 | 0.090814
75 | 0.089479 | 0.043337
76 | 0.50804 | 0.24606
77 | 0.40813 | 0.19767
78 | 0.068994 | 0.033415
79 | 0.20528 | 0.099422
80 | 0.071141 | 0.034455

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1