## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_456_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_456_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_456_0_node_7 | 20 | n |  | TRUE
3 | bus_MV_456_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_456_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_456_0_node_107 | 20 | n |  | TRUE
6 | bus_MV_456_0_node_118 | 20 | n |  | TRUE
7 | bus_MV_456_0_node_76 | 20 | n |  | TRUE
8 | bus_MV_456_0_node_6 | 20 | n |  | TRUE
9 | bus_MV_456_0_node_5 | 20 | n |  | TRUE
10 | bus_MV_456_0_node_8 | 20 | n |  | TRUE
11 | bus_MV_456_0_node_40 | 20 | n |  | TRUE
12 | bus_MV_456_0_node_38 | 20 | n |  | TRUE
13 | bus_MV_456_0_node_109 | 20 | n |  | TRUE
14 | bus_MV_456_0_node_73 | 20 | n |  | TRUE
15 | bus_MV_456_0_node_106 | 20 | n |  | TRUE
16 | bus_MV_456_0_node_108 | 20 | n |  | TRUE
17 | bus_MV_456_0_node_117 | 20 | n |  | TRUE
18 | bus_MV_456_0_node_77 | 20 | n |  | TRUE
19 | bus_MV_456_0_node_79 | 20 | n |  | TRUE
20 | bus_MV_456_0_node_37 | 20 | n |  | TRUE
21 | bus_MV_456_0_node_101 | 20 | n |  | TRUE
22 | bus_MV_456_0_node_30 | 20 | n |  | TRUE
23 | bus_MV_456_0_node_129 | 20 | n |  | TRUE
24 | bus_MV_456_0_node_103 | 20 | n |  | TRUE
25 | bus_MV_456_0_node_9 | 20 | n |  | TRUE
26 | bus_MV_456_0_node_10 | 20 | n |  | TRUE
27 | bus_MV_456_0_node_11 | 20 | n |  | TRUE
28 | bus_MV_456_0_node_12 | 20 | n |  | TRUE
29 | bus_MV_456_0_node_24 | 20 | n |  | TRUE
30 | bus_MV_456_0_node_13 | 20 | n |  | TRUE
31 | bus_MV_456_0_node_25 | 20 | n |  | TRUE
32 | bus_MV_456_0_node_15 | 20 | n |  | TRUE
33 | bus_MV_456_0_node_16 | 20 | n |  | TRUE
34 | bus_MV_456_0_node_17 | 20 | n |  | TRUE
35 | bus_MV_456_0_node_14 | 20 | n |  | TRUE
36 | bus_MV_456_0_node_31 | 20 | n |  | TRUE
37 | bus_MV_456_0_node_81 | 20 | n |  | TRUE
38 | bus_MV_456_0_node_111 | 20 | n |  | TRUE
39 | bus_MV_456_0_node_48 | 20 | n |  | TRUE
40 | bus_MV_456_0_node_18 | 20 | n |  | TRUE
41 | bus_MV_456_0_node_19 | 20 | n |  | TRUE
42 | bus_MV_456_0_node_20 | 20 | n |  | TRUE
43 | bus_MV_456_0_node_21 | 20 | n |  | TRUE
44 | bus_MV_456_0_node_110 | 20 | n |  | TRUE
45 | bus_MV_456_0_node_112 | 20 | n |  | TRUE
46 | bus_MV_456_0_node_58 | 20 | n |  | TRUE
47 | bus_MV_456_0_node_23 | 20 | n |  | TRUE
48 | bus_MV_456_0_node_22 | 20 | n |  | TRUE
49 | bus_MV_456_0_node_62 | 20 | n |  | TRUE
50 | bus_MV_456_0_node_51 | 20 | n |  | TRUE
51 | bus_MV_456_0_node_54 | 20 | n |  | TRUE
52 | bus_MV_456_0_node_114 | 20 | n |  | TRUE
53 | bus_MV_456_0_node_57 | 20 | n |  | TRUE
54 | bus_MV_456_0_node_56 | 20 | n |  | TRUE
55 | bus_MV_456_0_node_53 | 20 | n |  | TRUE
56 | bus_MV_456_0_node_26 | 20 | n |  | TRUE
57 | bus_MV_456_0_node_27 | 20 | n |  | TRUE
58 | bus_MV_456_0_node_28 | 20 | n |  | TRUE
59 | bus_MV_456_0_node_60 | 20 | n |  | TRUE
60 | bus_MV_456_0_node_121 | 20 | n |  | TRUE
61 | bus_MV_456_0_node_61 | 20 | n |  | TRUE
62 | bus_MV_456_0_node_59 | 20 | n |  | TRUE
63 | bus_MV_456_0_node_120 | 20 | n |  | TRUE
64 | bus_MV_456_0_node_102 | 20 | n |  | TRUE
65 | bus_MV_456_0_node_32 | 20 | n |  | TRUE
66 | bus_MV_456_0_node_33 | 20 | n |  | TRUE
67 | bus_MV_456_0_node_34 | 20 | n |  | TRUE
68 | bus_MV_456_0_node_35 | 20 | n |  | TRUE
69 | bus_MV_456_0_node_36 | 20 | n |  | TRUE
70 | bus_MV_456_0_node_99 | 20 | n |  | TRUE
71 | bus_MV_456_0_node_105 | 20 | n |  | TRUE
72 | bus_MV_456_0_node_39 | 20 | n |  | TRUE
73 | bus_MV_456_0_node_41 | 20 | n |  | TRUE
74 | bus_MV_456_0_node_42 | 20 | n |  | TRUE
75 | bus_MV_456_0_node_78 | 20 | n |  | TRUE
76 | bus_MV_456_0_node_115 | 20 | n |  | TRUE
77 | bus_MV_456_0_node_65 | 20 | n |  | TRUE
78 | bus_MV_456_0_node_67 | 20 | n |  | TRUE
79 | bus_MV_456_0_node_63 | 20 | n |  | TRUE
80 | bus_MV_456_0_node_45 | 20 | n |  | TRUE
81 | bus_MV_456_0_node_46 | 20 | n |  | TRUE
82 | bus_MV_456_0_node_47 | 20 | n |  | TRUE
83 | bus_MV_456_0_node_49 | 20 | n |  | TRUE
84 | bus_MV_456_0_node_50 | 20 | n |  | TRUE
85 | bus_MV_456_0_node_80 | 20 | n |  | TRUE
86 | bus_MV_456_0_node_75 | 20 | n |  | TRUE
87 | bus_MV_456_0_node_74 | 20 | n |  | TRUE
88 | bus_MV_456_0_node_55 | 20 | n |  | TRUE
89 | bus_MV_456_0_node_116 | 20 | n |  | TRUE
90 | bus_MV_456_0_node_71 | 20 | n |  | TRUE
91 | bus_MV_456_0_node_93 | 20 | n |  | TRUE
92 | bus_MV_456_0_node_83 | 20 | n |  | TRUE
93 | bus_MV_456_0_node_94 | 20 | n |  | TRUE
94 | bus_MV_456_0_node_82 | 20 | n |  | TRUE
95 | bus_MV_456_0_node_91 | 20 | n |  | TRUE
96 | bus_MV_456_0_node_92 | 20 | n |  | TRUE
97 | bus_MV_456_0_node_127 | 20 | n |  | TRUE
98 | bus_MV_456_0_node_104 | 20 | n |  | TRUE
99 | bus_MV_456_0_node_128 | 20 | n |  | TRUE
100 | bus_MV_456_0_node_89 | 20 | n |  | TRUE
101 | bus_MV_456_0_node_68 | 20 | n |  | TRUE
102 | bus_MV_456_0_node_69 | 20 | n |  | TRUE
103 | bus_MV_456_0_node_70 | 20 | n |  | TRUE
104 | bus_MV_456_0_node_113 | 20 | n |  | TRUE
105 | bus_MV_456_0_node_72 | 20 | n |  | TRUE
106 | bus_MV_456_0_node_119 | 20 | n |  | TRUE
107 | bus_MV_456_0_node_95 | 20 | n |  | TRUE
108 | bus_MV_456_0_node_85 | 20 | n |  | TRUE
109 | bus_MV_456_0_node_86 | 20 | n |  | TRUE
110 | bus_MV_456_0_node_87 | 20 | n |  | TRUE
111 | bus_MV_456_0_node_88 | 20 | n |  | TRUE
112 | bus_MV_456_0_node_90 | 20 | n |  | TRUE
113 | bus_MV_456_0_node_96 | 20 | n |  | TRUE
114 | bus_MV_456_0_node_97 | 20 | n |  | TRUE
115 | bus_MV_456_0_node_98 | 20 | n |  | TRUE
116 | bus_MV_456_0_node_122 | 20 | n |  | TRUE
117 | bus_MV_456_0_node_123 | 20 | n |  | TRUE
118 | bus_MV_456_0_node_124 | 20 | n |  | TRUE
119 | bus_MV_456_0_node_126 | 20 | n |  | TRUE
120 | bus_MV_456_0_node_125 | 20 | n |  | TRUE
121 | bus_MV_456_0_node_100 | 20 | n |  | TRUE
122 | bus_HV_456_0_node_0 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_456_0_load_0 | 0 | 0.36358 | 0.17609 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_456_0_load_2 | 1 | 0.093285 | 0.04518 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_456_0_load_118 | 6 | 0.40977 | 0.19846 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_456_0_load_76 | 7 | 0.071638 | 0.034696 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_456_0_load_8 | 10 | 0.3482 | 0.16864 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_456_0_load_109 | 13 | 0.10953 | 0.053047 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_456_0_load_106 | 15 | 0.082752 | 0.040078 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_456_0_load_77 | 18 | 0.068444 | 0.033149 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_456_0_load_79 | 19 | 0.30933 | 0.14982 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_456_0_load_37 | 20 | 0.12107 | 0.058637 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_456_0_load_101 | 21 | 0.36048 | 0.17459 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_456_0_load_129 | 23 | 0.30638 | 0.14838 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_456_0_load_103 | 24 | 0.50594 | 0.24504 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_456_0_load_9 | 25 | 0.26729 | 0.12946 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_456_0_load_24 | 29 | 0.19665 | 0.095242 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_456_0_load_25 | 31 | 0.12821 | 0.062095 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_456_0_load_14 | 35 | 0.34647 | 0.1678 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_456_0_load_31 | 36 | 0.2966 | 0.14365 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_456_0_load_81 | 37 | 0.21928 | 0.1062 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_456_0_load_111 | 38 | 0.24752 | 0.11988 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_456_0_load_18 | 40 | 0.29923 | 0.14493 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_456_0_load_110 | 44 | 0.26985 | 0.13069 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_456_0_load_112 | 45 | 0.27829 | 0.13478 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_456_0_load_62 | 49 | 0.30246 | 0.14649 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_456_0_load_51 | 50 | 0.26978 | 0.13066 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_456_0_load_54 | 51 | 0.40843 | 0.19781 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_456_0_load_114 | 52 | 0.24516 | 0.11874 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_456_0_load_56 | 54 | 0.3553 | 0.17208 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_456_0_load_26 | 56 | 0.30577 | 0.14809 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_456_0_load_59 | 62 | 0.22184 | 0.10744 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_456_0_load_120 | 63 | 0.11998 | 0.058109 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_456_0_load_102 | 64 | 1.926 | 0.93282 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_456_0_load_32 | 65 | 0.33182 | 0.16071 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_456_0_load_35 | 68 | 0.077206 | 0.037392 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_456_0_load_105 | 71 | 0.1121 | 0.054295 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_456_0_load_42 | 74 | 0.21921 | 0.10617 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_456_0_load_78 | 75 | 0.12415 | 0.060128 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_456_0_load_115 | 76 | 0.29627 | 0.14349 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_456_0_load_63 | 79 | 0.28636 | 0.13869 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_456_0_load_45 | 80 | 0.38697 | 0.18742 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_456_0_load_80 | 85 | 0.12106 | 0.05863 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_456_0_load_74 | 87 | 0.27002 | 0.13078 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_456_0_load_116 | 89 | 0.27132 | 0.13141 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_456_0_load_93 | 91 | 0.069247 | 0.033538 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_456_0_load_82 | 94 | 0.13497 | 0.065369 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_456_0_load_91 | 95 | 0.2257 | 0.10931 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_456_0_load_104 | 98 | 0.90983 | 0.44065 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_456_0_load_128 | 99 | 0.23832 | 0.11542 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_456_0_load_68 | 101 | 0.11752 | 0.056917 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_456_0_load_113 | 104 | 0.22765 | 0.11026 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_456_0_load_119 | 106 | 0.3642 | 0.17639 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_456_0_load_95 | 107 | 0.33041 | 0.16003 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_456_0_load_86 | 109 | 0.10492 | 0.050815 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_456_0_load_88 | 111 | 0.13871 | 0.067178 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_456_0_load_90 | 112 | 0.76421 | 0.37012 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_456_0_load_96 | 113 | 0.069865 | 0.033837 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_456_0_load_97 | 114 | 0.58692 | 0.28426 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_456_0_load_122 | 116 | 0.34621 | 0.16767 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_456_0_load_126 | 119 | 0.32393 | 0.15688 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_456_0_load_100 | 121 | 0.55096 | 0.26684 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_456_0_line_0 |  | 0 | 1 | 0.0014149 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
1 | MV_456_0_line_1 |  | 1 | 2 | 0.023409 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
2 | MV_456_0_line_2 |  | 2 | 14 | 0.14587 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
3 | MV_456_0_line_3 |  | 3 | 4 | 0.28094 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
4 | MV_456_0_line_4 |  | 3 | 5 | 0.092572 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_456_0_line_5 |  | 3 | 6 | 0.031287 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
6 | MV_456_0_line_6 |  | 4 | 7 | 0.028161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_456_0_line_7 |  | 4 | 8 | 0.20132 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
8 | MV_456_0_line_8 |  | 5 | 15 | 0.0075163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_456_0_line_9 |  | 6 | 16 | 0.051975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_456_0_line_10 |  | 7 | 18 | 0.043719 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_456_0_line_11 |  | 8 | 11 | 0.18229 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_456_0_line_12 |  | 8 | 12 | 0.13923 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
13 | MV_456_0_line_13 |  | 8 | 13 | 0.020076 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_456_0_line_14 |  | 8 | 9 | 0.055886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_456_0_line_15 |  | 9 | 10 | 0.005989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_456_0_line_16 |  | 11 | 19 | 0.07918 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_456_0_line_17 |  | 12 | 20 | 0.10251 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
18 | MV_456_0_line_18 |  | 14 | 21 | 0.036447 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
19 | MV_456_0_line_19 |  | 16 | 17 | 0.096125 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_456_0_line_20 |  | 17 | 89 | 0.044719 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_456_0_line_21 |  | 18 | 84 | 0.025117 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_456_0_line_22 |  | 19 | 75 | 0.053252 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_456_0_line_23 |  | 20 | 72 | 0.025561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_456_0_line_24 |  | 20 | 69 | 0.026027 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
25 | MV_456_0_line_25 |  | 21 | 68 | 0.062541 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
26 | MV_456_0_line_26 |  | 21 | 70 | 0.094992 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
27 | MV_456_0_line_27 |  | 22 | 23 | 0.097296 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_456_0_line_28 |  | 22 | 24 | 0.2338 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_456_0_line_29 |  | 24 | 64 | 0.024156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_456_0_line_30 |  | 24 | 58 | 0.43293 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_456_0_line_31 |  | 25 | 26 | 0.079753 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_456_0_line_32 |  | 26 | 27 | 0.4155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_456_0_line_33 |  | 27 | 28 | 0.3521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_456_0_line_34 |  | 27 | 29 | 0.003097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_456_0_line_35 |  | 28 | 30 | 0.10561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_456_0_line_36 |  | 28 | 31 | 0.015451 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_456_0_line_37 |  | 30 | 32 | 0.28263 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_456_0_line_38 |  | 30 | 33 | 0.289 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_456_0_line_39 |  | 30 | 34 | 0.33611 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_456_0_line_40 |  | 30 | 35 | 0.036604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_456_0_line_41 |  | 32 | 36 | 0.046984 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_456_0_line_42 |  | 33 | 37 | 0.057772 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_456_0_line_43 |  | 34 | 38 | 0.016225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_456_0_line_44 |  | 38 | 39 | 0.009638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_456_0_line_45 |  | 39 | 83 | 0.11561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_456_0_line_46 |  | 40 | 41 | 0.029842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_456_0_line_47 |  | 41 | 42 | 0.4716 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_456_0_line_48 |  | 42 | 43 | 0.49809 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_456_0_line_49 |  | 42 | 44 | 0.058135 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_456_0_line_50 |  | 43 | 45 | 0.03631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_456_0_line_51 |  | 43 | 46 | 0.2056 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_456_0_line_52 |  | 43 | 47 | 0.51705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_456_0_line_53 |  | 46 | 52 | 0.051214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_456_0_line_54 |  | 46 | 53 | 0.13709 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_456_0_line_55 |  | 47 | 51 | 0.009472 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_456_0_line_56 |  | 47 | 48 | 0.73412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_456_0_line_57 |  | 48 | 49 | 0.064321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_456_0_line_58 |  | 48 | 50 | 0.10949 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_456_0_line_59 |  | 51 | 55 | 0.087794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_456_0_line_60 |  | 52 | 90 | 0.005191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_456_0_line_61 |  | 53 | 54 | 0.090316 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
62 | MV_456_0_line_62 |  | 55 | 88 | 0.62729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_456_0_line_63 |  | 56 | 57 | 0.0047247 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_456_0_line_64 |  | 56 | 58 | 0.02978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_456_0_line_65 |  | 57 | 59 | 0.41051 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_456_0_line_66 |  | 58 | 60 | 0.95641 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_456_0_line_67 |  | 59 | 61 | 0.088399 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_456_0_line_68 |  | 59 | 62 | 0.079125 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_456_0_line_69 |  | 60 | 63 | 0.006273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_456_0_line_70 |  | 61 | 91 | 0.015942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_456_0_line_71 |  | 61 | 92 | 0.078673 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_456_0_line_72 |  | 64 | 121 | 0.011764 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
73 | MV_456_0_line_73 |  | 65 | 66 | 0.041774 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
74 | MV_456_0_line_74 |  | 65 | 67 | 0.044409 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
75 | MV_456_0_line_75 |  | 66 | 68 | 0.088366 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
76 | MV_456_0_line_76 |  | 67 | 69 | 0.23884 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_456_0_line_77 |  | 70 | 71 | 0.099972 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
78 | MV_456_0_line_78 |  | 70 | 115 | 0.008113 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_456_0_line_79 |  | 72 | 73 | 0.14896 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_456_0_line_80 |  | 73 | 74 | 0.042841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_456_0_line_81 |  | 76 | 77 | 0.21126 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_456_0_line_82 |  | 77 | 78 | 0.26638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_456_0_line_83 |  | 77 | 79 | 0.013909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_456_0_line_84 |  | 78 | 98 | 0.049424 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_456_0_line_85 |  | 80 | 81 | 0.021173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_456_0_line_86 |  | 80 | 82 | 0.048879 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_456_0_line_87 |  | 81 | 83 | 0.29087 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_456_0_line_88 |  | 82 | 84 | 0.23641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_456_0_line_89 |  | 83 | 85 | 0.053746 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_456_0_line_90 |  | 84 | 86 | 0.013352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_456_0_line_91 |  | 86 | 87 | 0.011771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_456_0_line_92 |  | 88 | 89 | 0.05293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_456_0_line_93 |  | 90 | 105 | 0.48916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_456_0_line_94 |  | 90 | 103 | 0.54217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_456_0_line_95 |  | 91 | 93 | 0.034517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_456_0_line_96 |  | 92 | 94 | 0.040102 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_456_0_line_97 |  | 93 | 107 | 0.021549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_456_0_line_98 |  | 95 | 96 | 0.045053 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_456_0_line_99 |  | 95 | 97 | 0.62997 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_456_0_line_100 |  | 96 | 107 | 0.090032 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
101 | MV_456_0_line_101 |  | 97 | 99 | 0.01168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_456_0_line_102 |  | 97 | 120 | 0.38888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_456_0_line_103 |  | 98 | 100 | 0.017944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_456_0_line_104 |  | 100 | 110 | 0.023638 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_456_0_line_105 |  | 101 | 102 | 0.046341 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_456_0_line_106 |  | 102 | 103 | 0.38318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_456_0_line_107 |  | 103 | 104 | 0.088083 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_456_0_line_108 |  | 105 | 106 | 0.033778 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_456_0_line_109 |  | 108 | 109 | 0.0093589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_456_0_line_110 |  | 108 | 110 | 0.012831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_456_0_line_111 |  | 109 | 111 | 0.0076513 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_456_0_line_112 |  | 110 | 112 | 0.11613 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_456_0_line_113 |  | 111 | 113 | 0.00078152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_456_0_line_114 |  | 112 | 114 | 0.021724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_456_0_line_115 |  | 114 | 115 | 0.031955 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_456_0_line_116 |  | 115 | 121 | 0.016674 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
117 | MV_456_0_line_117 |  | 116 | 117 | 0.027511 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_456_0_line_118 |  | 117 | 118 | 0.14412 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_456_0_line_119 |  | 118 | 119 | 0.030045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_456_0_line_120 |  | 119 | 120 | 0.006591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_456_0_trafo_0 | 25 MVA 110/20 kV | 122 | 0 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2605256.649 | 1197924.7323
1 | 2605257.7522 | 1197923.8464
2 | 2605276.8039 | 1197910.3088
3 | 2605028.9173 | 1197912.7437
4 | 2604997.4486 | 1198109.5116
5 | 2604976.043 | 1197988.7295
6 | 2605016.7263 | 1197883.9293
7 | 2604970.692 | 1198118.2947
8 | 2605112.3256 | 1198158.2668
9 | 2605128.0999 | 1198117.8919
10 | 2605132.094 | 1198122.3643
11 | 2605013.9605 | 1198253.68
12 | 2605134.224 | 1198295.6253
13 | 2605127.8066 | 1198145.4837
14 | 2605402.0556 | 1197949.1844
15 | 2604968.5656 | 1197989.4935
16 | 2604964.5997 | 1197883.7752
17 | 2604926.5266 | 1197935.7941
18 | 2604929.1542 | 1198131.9299
19 | 2604988.8826 | 1198311.8681
20 | 2605236.6612 | 1198291.8665
21 | 2605436.5649 | 1197960.9104
22 | 2605396.8592 | 1197713.3206
23 | 2605316.4112 | 1197658.598
24 | 2605534.9716 | 1197901.9673
25 | 2604334.5565 | 1198916.6888
26 | 2604414.281 | 1198918.814
27 | 2604600.4275 | 1198818.5208
28 | 2604586.3828 | 1198582.6062
29 | 2604601.3466 | 1198821.4786
30 | 2604550.7531 | 1198503.9151
31 | 2604594.6954 | 1198595.6306
32 | 2604423.1118 | 1198576.0149
33 | 2604679.575 | 1198326.774
34 | 2604385.9216 | 1198293.3813
35 | 2604579.1879 | 1198480.7686
36 | 2604387.2792 | 1198606.4051
37 | 2604726.886 | 1198359.9284
38 | 2604401.6795 | 1198289.335
39 | 2604400.4833 | 1198279.7735
40 | 2604139.9119 | 1197118.171
41 | 2604160.9335 | 1197139.4078
42 | 2604069.5899 | 1197415.3707
43 | 2604409.3227 | 1197317.1331
44 | 2604043.0067 | 1197363.6699
45 | 2604393.3145 | 1197284.5264
46 | 2604594.1479 | 1197227.2
47 | 2604465.958 | 1197769.0487
48 | 2604187.8342 | 1197824.4357
49 | 2604147.0814 | 1197873.2783
50 | 2604291.6529 | 1197859.2045
51 | 2604466.8497 | 1197778.4766
52 | 2604640.2428 | 1197204.612
53 | 2604593.5719 | 1197324.0623
54 | 2604612.4153 | 1197412.3903
55 | 2604476.6245 | 1197865.6748
56 | 2605642.2618 | 1197485.1463
57 | 2605646.8449 | 1197486.2942
58 | 2605613.8702 | 1197476.2916
59 | 2605884.658 | 1197820.8993
60 | 2605777.4748 | 1196533.9773
61 | 2605926.7944 | 1197867.0318
62 | 2605880.2418 | 1197741.8973
63 | 2605782.7567 | 1196530.5694
64 | 2605537.0505 | 1197926.0342
65 | 2605436.7834 | 1198149.956
66 | 2605429.6083 | 1198109.528
67 | 2605394.3334 | 1198163.1473
68 | 2605435.534 | 1198023.4429
69 | 2605262.7128 | 1198290.2883
70 | 2605531.4401 | 1197955.4935
71 | 2605514.1783 | 1198053.9638
72 | 2605237.2864 | 1198317.4141
73 | 2605254.8271 | 1198453.1907
74 | 2605255.4601 | 1198496.003
75 | 2604940.3475 | 1198289.9567
76 | 2605527.9492 | 1198417.2591
77 | 2605666.9052 | 1198258.136
78 | 2605702.2001 | 1198039.9749
79 | 2605678.1446 | 1198266.3731
80 | 2604674.6133 | 1198144.8841
81 | 2604668.0342 | 1198124.7572
82 | 2604720.2561 | 1198127.0544
83 | 2604483.681 | 1198240.6801
84 | 2604905.2901 | 1198139.7636
85 | 2604454.1457 | 1198195.8202
86 | 2604913.9172 | 1198149.9538
87 | 2604921.5172 | 1198158.9425
88 | 2604830.5806 | 1197947.3453
89 | 2604882.0801 | 1197940.7275
90 | 2604644.8829 | 1197202.2587
91 | 2605942.7199 | 1197866.307
92 | 2605890.759 | 1197936.9672
93 | 2605972.371 | 1197860.4509
94 | 2605852.5457 | 1197946.3117
95 | 2606090.9713 | 1197902.8703
96 | 2606083.9911 | 1197858.361
97 | 2606690.441 | 1198096.507
98 | 2605708.6975 | 1197990.9971
99 | 2606690.1159 | 1198108.1462
100 | 2605709.6651 | 1197973.0795
101 | 2604783.2025 | 1197492.0282
102 | 2604812.8385 | 1197456.4028
103 | 2605075.1992 | 1197244.5594
104 | 2605150.5676 | 1197290.1473
105 | 2604620.3681 | 1196940.0893
106 | 2604614.4525 | 1196906.8338
107 | 2605993.9689 | 1197859.6607
108 | 2605706.638 | 1197936.8796
109 | 2605705.2455 | 1197927.6248
110 | 2605708.545 | 1197949.5659
111 | 2605704.1071 | 1197920.0586
112 | 2605592.877 | 1197948.7017
113 | 2605703.9908 | 1197919.2858
114 | 2605571.2743 | 1197950.9944
115 | 2605539.498 | 1197954.3669
116 | 2606900.1928 | 1197794.0372
117 | 2606903.68 | 1197821.2557
118 | 2606760.0899 | 1197829.8311
119 | 2606730.504 | 1197829.9092
120 | 2606728.8205 | 1197823.5373
121 | 2605538.063 | 1197937.7544
122 | 2605256.649 | 1197924.7323

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -17.571 | -8.1702
1 | 1 | -1.8022e-05 | 0.093285 | 0.04518
2 | 0.99993 | -0.00031467 | 0 | 0
3 | 0.99607 | -0.076571 | 0 | 0
4 | 0.99666 | -0.069527 | 0 | 0
5 | 0.99606 | -0.076666 | 0 | 0
6 | 0.99593 | -0.08024 | 0.40977 | 0.19846
7 | 0.99657 | -0.068757 | 0.071638 | 0.034696
8 | 0.99737 | -0.061162 | 0 | 0
9 | 0.99734 | -0.060931 | 0 | 0
10 | 0.99734 | -0.060905 | 0.3482 | 0.16864
11 | 0.99727 | -0.060259 | 0 | 0
12 | 0.99782 | -0.052737 | 0 | 0
13 | 0.99737 | -0.061136 | 0.10953 | 0.053047
14 | 0.99952 | -0.0021526 | 0 | 0
15 | 0.99605 | -0.076658 | 0.082752 | 0.040078
16 | 0.9957 | -0.078504 | 0 | 0
17 | 0.99529 | -0.075279 | 0 | 0
18 | 0.99643 | -0.067597 | 0.068444 | 0.033149
19 | 0.99722 | -0.059851 | 0.30933 | 0.14982
20 | 0.99857 | -0.026849 | 0.12107 | 0.058637
21 | 0.9993 | -0.014222 | 0.36048 | 0.17459
22 | 0.99887 | -0.01519 | 0 | 0
23 | 0.99881 | -0.015551 | 0.30638 | 0.14838
24 | 0.99901 | -0.014317 | 0.50594 | 0.24504
25 | 0.99343 | -0.043913 | 0.26729 | 0.12946
26 | 0.99347 | -0.043652 | 0 | 0
27 | 0.99361 | -0.044864 | 0 | 0
28 | 0.99382 | -0.046523 | 0 | 0
29 | 0.99361 | -0.044857 | 0.19665 | 0.095242
30 | 0.9939 | -0.047147 | 0 | 0
31 | 0.99382 | -0.046547 | 0.12821 | 0.062095
32 | 0.99379 | -0.046194 | 0 | 0
33 | 0.99382 | -0.046469 | 0 | 0
34 | 0.99452 | -0.052187 | 0 | 0
35 | 0.99388 | -0.046995 | 0.34647 | 0.1678
36 | 0.99377 | -0.046364 | 0.2966 | 0.14365
37 | 0.9938 | -0.046318 | 0.21928 | 0.1062
38 | 0.99455 | -0.052425 | 0.24752 | 0.11988
39 | 0.99457 | -0.052596 | 0 | 0
40 | 0.98992 | -0.037892 | 0.29923 | 0.14493
41 | 0.98993 | -0.038 | 0 | 0
42 | 0.99011 | -0.039532 | 0 | 0
43 | 0.99047 | -0.042419 | 0 | 0
44 | 0.99008 | -0.039725 | 0.26985 | 0.13069
45 | 0.99046 | -0.042297 | 0.27829 | 0.13478
46 | 0.99013 | -0.039686 | 0 | 0
47 | 0.99189 | -0.053515 | 0 | 0
48 | 0.99136 | -0.048892 | 0 | 0
49 | 0.99133 | -0.048658 | 0.30246 | 0.14649
50 | 0.9913 | -0.049255 | 0.26978 | 0.13066
51 | 0.99193 | -0.053769 | 0.40843 | 0.19781
52 | 0.99007 | -0.039206 | 0.24516 | 0.11874
53 | 0.99007 | -0.039107 | 0 | 0
54 | 0.99 | -0.039503 | 0.3553 | 0.17208
55 | 0.99228 | -0.056547 | 0 | 0
56 | 0.99698 | -0.026638 | 0.30577 | 0.14809
57 | 0.99697 | -0.026537 | 0 | 0
58 | 0.99707 | -0.027385 | 0 | 0
59 | 0.99547 | -0.036751 | 0 | 0
60 | 0.99685 | -0.028839 | 0 | 0
61 | 0.99528 | -0.035082 | 0 | 0
62 | 0.99544 | -0.036966 | 0.22184 | 0.10744
63 | 0.99684 | -0.02883 | 0.11998 | 0.058109
64 | 0.9991 | -0.015189 | 1.926 | 0.93282
65 | 0.99896 | -0.024898 | 0.33182 | 0.16071
66 | 0.99902 | -0.02462 | 0 | 0
67 | 0.99891 | -0.025183 | 0 | 0
68 | 0.99913 | -0.024026 | 0.077206 | 0.037392
69 | 0.99861 | -0.026688 | 0 | 0
70 | 0.99916 | -0.014747 | 0 | 0
71 | 0.99914 | -0.014883 | 0.1121 | 0.054295
72 | 0.99857 | -0.02679 | 0 | 0
73 | 0.99852 | -0.026425 | 0 | 0
74 | 0.99851 | -0.026313 | 0.21921 | 0.10617
75 | 0.99721 | -0.059932 | 0.12415 | 0.060128
76 | 0.99825 | -0.0084444 | 0.29627 | 0.14349
77 | 0.99837 | -0.0076832 | 0 | 0
78 | 0.99857 | -0.009482 | 0 | 0
79 | 0.99837 | -0.0076356 | 0.28636 | 0.13869
80 | 0.99555 | -0.060442 | 0.38697 | 0.18742
81 | 0.9955 | -0.060052 | 0 | 0
82 | 0.99568 | -0.061566 | 0 | 0
83 | 0.99482 | -0.054629 | 0 | 0
84 | 0.99635 | -0.06695 | 0 | 0
85 | 0.99481 | -0.054553 | 0.12106 | 0.05863
86 | 0.99634 | -0.066907 | 0 | 0
87 | 0.99634 | -0.066869 | 0.27002 | 0.13078
88 | 0.99478 | -0.076 | 0 | 0
89 | 0.99499 | -0.077609 | 0.27132 | 0.13141
90 | 0.99006 | -0.039173 | 0 | 0
91 | 0.99525 | -0.034804 | 0.069247 | 0.033538
92 | 0.99526 | -0.035218 | 0 | 0
93 | 0.99519 | -0.034231 | 0 | 0
94 | 0.99525 | -0.035154 | 0.13497 | 0.065369
95 | 0.99488 | -0.034672 | 0.2257 | 0.10931
96 | 0.99495 | -0.035245 | 0 | 0
97 | 0.99378 | -0.042469 | 0 | 0
98 | 0.99861 | -0.0098038 | 0.90983 | 0.44065
99 | 0.99377 | -0.042435 | 0.23832 | 0.11542
100 | 0.99864 | -0.010116 | 0 | 0
101 | 0.98976 | -0.036994 | 0.11752 | 0.056917
102 | 0.98977 | -0.037059 | 0 | 0
103 | 0.98983 | -0.03747 | 0 | 0
104 | 0.98979 | -0.037718 | 0.22765 | 0.11026
105 | 0.98983 | -0.037181 | 0 | 0
106 | 0.98981 | -0.037333 | 0.3642 | 0.17639
107 | 0.99515 | -0.033872 | 0.33041 | 0.16003
108 | 0.99868 | -0.010478 | 0 | 0
109 | 0.99868 | -0.010443 | 0.10492 | 0.050815
110 | 0.99869 | -0.010525 | 0 | 0
111 | 0.99868 | -0.010424 | 0.13871 | 0.067178
112 | 0.99895 | -0.012958 | 0.76421 | 0.37012
113 | 0.99868 | -0.010423 | 0.069865 | 0.033837
114 | 0.99902 | -0.013609 | 0.58692 | 0.28426
115 | 0.99915 | -0.014791 | 0 | 0
116 | 0.99335 | -0.038682 | 0.34621 | 0.16767
117 | 0.99336 | -0.038797 | 0 | 0
118 | 0.99343 | -0.03938 | 0 | 0
119 | 0.99344 | -0.039498 | 0.32393 | 0.15688
120 | 0.99345 | -0.039549 | 0 | 0
121 | 0.99914 | -0.014848 | 0.55096 | 0.26684
122 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 17.557 | 8.1597 | -17.557 | -8.1599 | 6.8281e-05 | -0.00013935 | 0.55889 | 0.55889 | 0.55889 | 1 | 0 | 1 | -1.8022e-05 | 43.8004
1 | 17.4637 | 8.1147 | -17.4626 | -8.117 | 0.0011177 | -0.002312 | 0.5559 | 0.55594 | 0.55594 | 1 | -1.8022e-05 | 0.99993 | -0.00031467 | 43.5687
2 | 17.4626 | 8.117 | -17.4556 | -8.1314 | 0.0069681 | -0.014396 | 0.55594 | 0.55616 | 0.55616 | 0.99993 | -0.00031467 | 0.99952 | -0.0021526 | 43.5862
3 | -3.9206 | -1.7747 | 3.9227 | 1.7667 | 0.0021089 | -0.0080355 | 0.12472 | 0.12461 | 0.12472 | 0.99607 | -0.076571 | 0.99666 | -0.069527 | 34.4538
4 | 0.082753 | 0.039791 | -0.082752 | -0.0399 | 1.1686e-06 | -0.00010891 | 0.0026611 | 0.0026625 | 0.0026625 | 0.99607 | -0.076571 | 0.99606 | -0.076666 | 1.2679
5 | 3.8378 | 1.7349 | -3.8374 | -1.7344 | 0.00042793 | 0.00045046 | 0.12206 | 0.12206 | 0.12206 | 0.99607 | -0.076571 | 0.99593 | -0.08024 | 34.8751
6 | 2.6261 | 1.2047 | -2.6258 | -1.2053 | 0.00026331 | -0.00058973 | 0.083684 | 0.083692 | 0.083692 | 0.99666 | -0.069527 | 0.99657 | -0.068757 | 38.0419
7 | -6.5488 | -2.9713 | 6.553 | 2.9675 | 0.0042169 | -0.0038007 | 0.20829 | 0.20821 | 0.20829 | 0.99666 | -0.069527 | 0.99737 | -0.061162 | 57.5391
8 | 0.082752 | 0.0399 | -0.082752 | -0.040078 | 7.1197e-08 | -0.00017803 | 0.0026625 | 0.0026648 | 0.0026648 | 0.99606 | -0.076666 | 0.99605 | -0.076658 | 1.2113
9 | 3.4276 | 1.536 | -3.4268 | -1.537 | 0.00082254 | -0.00098661 | 0.10887 | 0.10889 | 0.10889 | 0.99593 | -0.08024 | 0.9957 | -0.078504 | 49.4934
10 | 2.5542 | 1.1706 | -2.5538 | -1.1715 | 0.00038666 | -0.00092183 | 0.081387 | 0.0814 | 0.0814 | 0.99657 | -0.068757 | 0.99643 | -0.067597 | 36.9998
11 | 0.43355 | 0.20369 | -0.4335 | -0.20801 | 4.696e-05 | -0.0043151 | 0.013865 | 0.013918 | 0.013918 | 0.99737 | -0.061162 | 0.99727 | -0.060259 | 6.3265
12 | -7.4443 | -3.3909 | 7.4472 | 3.3883 | 0.0028559 | -0.0026715 | 0.23677 | 0.2367 | 0.23677 | 0.99737 | -0.061162 | 0.99782 | -0.052737 | 56.2389
13 | 0.10953 | 0.05257 | -0.10953 | -0.053047 | 3.3198e-07 | -0.00047673 | 0.0035164 | 0.0035224 | 0.0035224 | 0.99737 | -0.061162 | 0.99737 | -0.061136 | 1.6011
14 | 0.34821 | 0.16717 | -0.3482 | -0.1685 | 9.3389e-06 | -0.0013245 | 0.01118 | 0.011196 | 0.011196 | 0.99737 | -0.061162 | 0.99734 | -0.060931 | 5.0893
15 | 0.3482 | 0.1685 | -0.3482 | -0.16864 | 1.0025e-06 | -0.00014194 | 0.011196 | 0.011198 | 0.011198 | 0.99734 | -0.060931 | 0.99734 | -0.060905 | 5.0901
16 | 0.4335 | 0.20801 | -0.43348 | -0.20988 | 2.0512e-05 | -0.001874 | 0.013918 | 0.013942 | 0.013942 | 0.99727 | -0.060259 | 0.99722 | -0.059851 | 6.3372
17 | -7.4472 | -3.3883 | 7.4512 | 3.3941 | 0.0040937 | 0.0057948 | 0.2367 | 0.2367 | 0.2367 | 0.99782 | -0.052737 | 0.99857 | -0.026849 | 57.7322
18 | 17.4556 | 8.1314 | -17.4536 | -8.1261 | 0.0020123 | 0.0053107 | 0.55616 | 0.55616 | 0.55616 | 0.99952 | -0.0021526 | 0.9993 | -0.014222 | 43.1133
19 | 3.4268 | 1.537 | -3.4253 | -1.5388 | 0.0015218 | -0.001823 | 0.10889 | 0.10891 | 0.10891 | 0.9957 | -0.078504 | 0.99529 | -0.075279 | 49.5057
20 | 3.4253 | 1.5388 | -3.4243 | -1.5383 | 0.00094512 | 0.00053913 | 0.10891 | 0.10891 | 0.10891 | 0.99529 | -0.075279 | 0.99499 | -0.077609 | 51.8634
21 | 2.4854 | 1.1383 | -2.4852 | -1.1389 | 0.00021033 | -0.00053298 | 0.079197 | 0.079204 | 0.079204 | 0.99643 | -0.067597 | 0.99635 | -0.06695 | 36.0018
22 | 0.12415 | 0.060065 | -0.12415 | -0.060128 | 1.5126e-06 | -6.2272e-05 | 0.0039924 | 0.0039932 | 0.0039932 | 0.99722 | -0.059851 | 0.99721 | -0.059932 | 1.9015
23 | 0.21923 | 0.101 | -0.21923 | -0.10161 | 1.6633e-06 | -0.00060806 | 0.0069779 | 0.0069853 | 0.0069853 | 0.99857 | -0.026849 | 0.99857 | -0.02679 | 3.1751
24 | -7.7915 | -3.5537 | 7.7918 | 3.5506 | 0.00024641 | -0.0031227 | 0.24757 | 0.24753 | 0.24757 | 0.99857 | -0.026849 | 0.99861 | -0.026688 | 19.4017
25 | 8.2056 | 3.701 | -8.2048 | -3.6991 | 0.00075487 | 0.0018573 | 0.26004 | 0.26004 | 0.26004 | 0.9993 | -0.014222 | 0.99913 | -0.024026 | 20.1579
26 | 8.8875 | 4.2505 | -8.8863 | -4.2618 | 0.0011893 | -0.011249 | 0.28459 | 0.28474 | 0.28474 | 0.9993 | -0.014222 | 0.99916 | -0.014747 | 22.3151
27 | 0.30639 | 0.14828 | -0.30638 | -0.14838 | 1.6778e-05 | -0.00010537 | 0.0098373 | 0.0098387 | 0.0098387 | 0.99887 | -0.01519 | 0.99881 | -0.015551 | 4.6851
28 | -0.30639 | -0.14828 | 0.30643 | 0.14803 | 4.0297e-05 | -0.00025328 | 0.0098373 | 0.0098338 | 0.0098373 | 0.99887 | -0.01519 | 0.99901 | -0.014317 | 4.6844
29 | -3.138 | -1.4961 | 3.1384 | 1.4956 | 0.00032541 | -0.00047915 | 0.10046 | 0.10045 | 0.10046 | 0.99901 | -0.014317 | 0.9991 | -0.015189 | 45.6616
30 | 2.3257 | 1.103 | -2.3214 | -1.1009 | 0.0042676 | 0.0021583 | 0.074378 | 0.074385 | 0.074385 | 0.99901 | -0.014317 | 0.99707 | -0.027385 | 35.4213
31 | -0.26729 | -0.12946 | 0.2673 | 0.12937 | 1.0582e-05 | -8.7338e-05 | 0.0086301 | 0.0086289 | 0.0086301 | 0.99343 | -0.043913 | 0.99347 | -0.043652 | 4.1096
32 | -0.2673 | -0.12937 | 0.26734 | 0.11959 | 4.072e-05 | -0.0097808 | 0.0086289 | 0.0085088 | 0.0086289 | 0.99347 | -0.043652 | 0.99361 | -0.044864 | 3.9222
33 | -0.46399 | -0.21476 | 0.4641 | 0.20649 | 0.00010302 | -0.0082708 | 0.014854 | 0.014755 | 0.014854 | 0.99361 | -0.044864 | 0.99382 | -0.046523 | 6.752
34 | 0.19665 | 0.095169 | -0.19665 | -0.095242 | 1.6657e-07 | -7.2953e-05 | 0.0063472 | 0.0063481 | 0.0063481 | 0.99361 | -0.044864 | 0.99361 | -0.044857 | 2.8855
35 | -0.59231 | -0.26856 | 0.59236 | 0.26609 | 5.0234e-05 | -0.0024758 | 0.018891 | 0.018861 | 0.018891 | 0.99382 | -0.046523 | 0.9939 | -0.047147 | 8.5867
36 | 0.12821 | 0.062077 | -0.12821 | -0.062095 | 4.7134e-07 | -1.7923e-05 | 0.0041377 | 0.0041379 | 0.0041379 | 0.99382 | -0.046523 | 0.99382 | -0.046547 | 1.9704
37 | 0.29664 | 0.13694 | -0.2966 | -0.1436 | 3.4272e-05 | -0.0066552 | 0.0094896 | 0.0095723 | 0.0095723 | 0.9939 | -0.047147 | 0.99379 | -0.046194 | 4.3511
38 | 0.2193 | 0.098032 | -0.21929 | -0.10484 | 1.9003e-05 | -0.0068101 | 0.0069771 | 0.0070602 | 0.0070602 | 0.9939 | -0.047147 | 0.99382 | -0.046469 | 3.2092
39 | -1.4548 | -0.668 | 1.4557 | 0.66036 | 0.00096801 | -0.0076452 | 0.046495 | 0.046399 | 0.046495 | 0.9939 | -0.047147 | 0.99452 | -0.052187 | 21.1341
40 | 0.34647 | 0.16694 | -0.34647 | -0.1678 | 6.1034e-06 | -0.00086151 | 0.01117 | 0.011181 | 0.011181 | 0.9939 | -0.047147 | 0.99388 | -0.046995 | 5.0824
41 | 0.2966 | 0.1436 | -0.2966 | -0.14365 | 7.6711e-06 | -5.059e-05 | 0.0095723 | 0.009573 | 0.009573 | 0.99379 | -0.046194 | 0.99377 | -0.046364 | 4.5586
42 | 0.21929 | 0.10484 | -0.21928 | -0.1062 | 3.8537e-06 | -0.0013612 | 0.0070602 | 0.0070773 | 0.0070773 | 0.99382 | -0.046469 | 0.9938 | -0.046318 | 3.217
43 | -1.4557 | -0.66036 | 1.4558 | 0.65999 | 4.6628e-05 | -0.00036934 | 0.046399 | 0.046395 | 0.046399 | 0.99452 | -0.052187 | 0.99455 | -0.052425 | 21.0906
44 | -1.7033 | -0.77987 | 1.7033 | 0.77965 | 3.8041e-05 | -0.00021634 | 0.054375 | 0.054373 | 0.054375 | 0.99455 | -0.052425 | 0.99457 | -0.052596 | 24.7161
45 | -1.7033 | -0.77965 | 1.7038 | 0.77706 | 0.000456 | -0.0025958 | 0.054373 | 0.05434 | 0.054373 | 0.99457 | -0.052596 | 0.99482 | -0.054629 | 24.7148
46 | -0.29923 | -0.14493 | 0.29924 | 0.14423 | 3.7417e-06 | -0.00069712 | 0.0096957 | 0.0096868 | 0.0096957 | 0.98992 | -0.037892 | 0.98993 | -0.038 | 4.4071
47 | -0.29924 | -0.14423 | 0.2993 | 0.13321 | 5.8241e-05 | -0.011019 | 0.0096868 | 0.0095515 | 0.0096868 | 0.98993 | -0.038 | 0.99011 | -0.039532 | 4.4031
48 | -0.56915 | -0.26384 | 0.56937 | 0.25224 | 0.00022073 | -0.011597 | 0.01829 | 0.01815 | 0.01829 | 0.99011 | -0.039532 | 0.99047 | -0.042419 | 8.3138
49 | 0.26986 | 0.13063 | -0.26985 | -0.13069 | 7.9151e-06 | -6.3076e-05 | 0.0087412 | 0.0087421 | 0.0087421 | 0.99011 | -0.039532 | 0.99008 | -0.039725 | 4.1629
50 | 0.2783 | 0.13393 | -0.27829 | -0.13478 | 3.9323e-06 | -0.00084932 | 0.0090014 | 0.0090122 | 0.0090122 | 0.99047 | -0.042419 | 0.99046 | -0.042297 | 4.0964
51 | 1.3106 | 0.59086 | -1.3101 | -0.59553 | 0.00048256 | -0.004671 | 0.041901 | 0.041959 | 0.041959 | 0.99047 | -0.042419 | 0.99013 | -0.039686 | 19.0721
52 | -2.1583 | -0.97704 | 2.1616 | 0.96588 | 0.0032841 | -0.011154 | 0.069049 | 0.068904 | 0.069049 | 0.99047 | -0.042419 | 0.99189 | -0.053515 | 31.386
53 | 0.9548 | 0.42674 | -0.95473 | -0.42792 | 6.3595e-05 | -0.0011798 | 0.030491 | 0.030506 | 0.030506 | 0.99013 | -0.039686 | 0.99007 | -0.039206 | 13.8662
54 | 0.35535 | 0.16879 | -0.35532 | -0.17199 | 2.416e-05 | -0.0032015 | 0.01147 | 0.01151 | 0.01151 | 0.99013 | -0.039686 | 0.99007 | -0.039107 | 5.2319
55 | -2.7342 | -1.2243 | 2.7343 | 1.2241 | 9.612e-05 | -0.000194 | 0.087187 | 0.087184 | 0.087187 | 0.99189 | -0.053515 | 0.99193 | -0.053769 | 39.6304
56 | 0.5726 | 0.25839 | -0.57226 | -0.27552 | 0.00033135 | -0.017137 | 0.018283 | 0.018495 | 0.018495 | 0.99189 | -0.053515 | 0.99136 | -0.048892 | 8.4067
57 | 0.30247 | 0.14498 | -0.30246 | -0.14649 | 8.2079e-06 | -0.0015068 | 0.0097673 | 0.0097864 | 0.0097864 | 0.99136 | -0.048892 | 0.99133 | -0.048658 | 4.4484
58 | 0.26979 | 0.13054 | -0.26978 | -0.13066 | 1.4861e-05 | -0.00011914 | 0.0087274 | 0.008729 | 0.008729 | 0.99136 | -0.048892 | 0.9913 | -0.049255 | 4.1567
59 | -3.1427 | -1.4219 | 3.1439 | 1.4202 | 0.0011808 | -0.0017129 | 0.10039 | 0.10036 | 0.10039 | 0.99193 | -0.053769 | 0.99228 | -0.056547 | 45.63
60 | 0.70957 | 0.30919 | -0.70957 | -0.30931 | 3.5297e-06 | -0.00012044 | 0.022568 | 0.022569 | 0.022569 | 0.99007 | -0.039206 | 0.99006 | -0.039173 | 10.2587
61 | 0.35532 | 0.17199 | -0.3553 | -0.17208 | 2.1321e-05 | -9.2327e-05 | 0.01151 | 0.011511 | 0.011511 | 0.99007 | -0.039107 | 0.99 | -0.039503 | 5.4816
62 | -3.1439 | -1.4202 | 3.1523 | 1.4079 | 0.0084202 | -0.012286 | 0.10036 | 0.10019 | 0.10036 | 0.99228 | -0.056547 | 0.99478 | -0.076 | 45.6188
63 | 1.8954 | 0.89658 | -1.8954 | -0.89669 | 2.325e-05 | -0.00010523 | 0.060712 | 0.060714 | 0.060714 | 0.99698 | -0.026638 | 0.99697 | -0.026537 | 27.5971
64 | -2.2012 | -1.0447 | 2.2014 | 1.044 | 0.00019785 | -0.00064812 | 0.070549 | 0.07054 | 0.070549 | 0.99698 | -0.026638 | 0.99707 | -0.027385 | 32.0678
65 | 1.8954 | 0.89669 | -1.8927 | -0.89549 | 0.0026963 | 0.0012025 | 0.060714 | 0.06072 | 0.06072 | 0.99697 | -0.026537 | 0.99547 | -0.036751 | 28.9141
66 | 0.12001 | 0.056841 | -0.11998 | -0.05796 | 2.5279e-05 | -0.001119 | 0.0038445 | 0.0038587 | 0.0038587 | 0.99707 | -0.027385 | 0.99685 | -0.028839 | 1.8375
67 | 1.6709 | 0.78813 | -1.6705 | -0.79012 | 0.00033887 | -0.0019906 | 0.053573 | 0.053599 | 0.053599 | 0.99547 | -0.036751 | 0.99528 | -0.035082 | 24.3632
68 | 0.22185 | 0.10735 | -0.22184 | -0.10744 | 7.2021e-06 | -8.9092e-05 | 0.0071469 | 0.0071481 | 0.0071481 | 0.99547 | -0.036751 | 0.99544 | -0.036966 | 3.4039
69 | 0.11998 | 0.05796 | -0.11998 | -0.058109 | 1.2473e-07 | -0.00014879 | 0.0038587 | 0.0038606 | 0.0038606 | 0.99685 | -0.028839 | 0.99684 | -0.02883 | 1.7548
70 | 1.5356 | 0.72579 | -1.5355 | -0.72616 | 5.1653e-05 | -0.00036172 | 0.049262 | 0.049267 | 0.049267 | 0.99528 | -0.035082 | 0.99525 | -0.034804 | 22.3941
71 | 0.13497 | 0.06433 | -0.13497 | -0.064421 | 2.637e-06 | -9.1383e-05 | 0.0043367 | 0.0043379 | 0.0043379 | 0.99528 | -0.035082 | 0.99526 | -0.035218 | 2.0657
72 | -5.0644 | -2.4284 | 5.0645 | 2.4281 | 0.00014963 | -0.00029413 | 0.16228 | 0.16228 | 0.16228 | 0.9991 | -0.015189 | 0.99914 | -0.014848 | 44.8289
73 | -8.1263 | -3.6773 | 8.1267 | 3.6723 | 0.00042869 | -0.0049975 | 0.25775 | 0.25769 | 0.25775 | 0.99896 | -0.024898 | 0.99902 | -0.02462 | 20.2001
74 | 7.7945 | 3.5166 | -7.794 | -3.5219 | 0.00041906 | -0.0053327 | 0.2471 | 0.24717 | 0.24717 | 0.99896 | -0.024898 | 0.99891 | -0.025183 | 19.3707
75 | -8.1267 | -3.6723 | 8.1276 | 3.6617 | 0.00090613 | -0.010574 | 0.25769 | 0.25756 | 0.25769 | 0.99902 | -0.02462 | 0.99913 | -0.024026 | 20.1952
76 | 7.794 | 3.5219 | -7.7918 | -3.5506 | 0.0022576 | -0.028668 | 0.24717 | 0.24753 | 0.24753 | 0.99891 | -0.025183 | 0.99861 | -0.026688 | 19.3987
77 | 0.11211 | 0.054177 | -0.1121 | -0.054295 | 2.306e-06 | -0.0001177 | 0.0035973 | 0.0035988 | 0.0035988 | 0.99916 | -0.014747 | 0.99914 | -0.014883 | 1.7137
78 | 8.7742 | 4.2076 | -8.7741 | -4.2086 | 9.9079e-05 | -0.000962 | 0.28114 | 0.28116 | 0.28116 | 0.99916 | -0.014747 | 0.99915 | -0.014791 | 22.0341
79 | 0.21923 | 0.10161 | -0.21922 | -0.10515 | 9.7638e-06 | -0.0035434 | 0.0069853 | 0.007029 | 0.007029 | 0.99857 | -0.02679 | 0.99852 | -0.026425 | 3.195
80 | 0.21922 | 0.10515 | -0.21921 | -0.10617 | 2.8309e-06 | -0.001019 | 0.007029 | 0.0070418 | 0.0070418 | 0.99852 | -0.026425 | 0.99851 | -0.026313 | 3.2008
81 | -0.29627 | -0.14349 | 0.2963 | 0.14326 | 3.4097e-05 | -0.00022999 | 0.0095194 | 0.0095163 | 0.0095194 | 0.99825 | -0.0084444 | 0.99837 | -0.0076832 | 4.5331
82 | -0.58266 | -0.28162 | 0.58279 | 0.27531 | 0.00012399 | -0.0063039 | 0.018712 | 0.018633 | 0.018712 | 0.99837 | -0.0076832 | 0.99857 | -0.009482 | 8.5055
83 | 0.28636 | 0.13836 | -0.28636 | -0.13869 | 1.5709e-06 | -0.00033055 | 0.0091958 | 0.0092 | 0.0092 | 0.99837 | -0.0076832 | 0.99837 | -0.0076356 | 4.1818
84 | -0.58279 | -0.27531 | 0.58281 | 0.27415 | 2.289e-05 | -0.0011699 | 0.018633 | 0.018619 | 0.018633 | 0.99857 | -0.009482 | 0.99861 | -0.0098038 | 8.4696
85 | 1.8263 | 0.82746 | -1.8262 | -0.82793 | 9.5549e-05 | -0.00047267 | 0.058138 | 0.058144 | 0.058144 | 0.99555 | -0.060442 | 0.9955 | -0.060052 | 26.429
86 | -2.2132 | -1.0149 | 2.2136 | 1.0138 | 0.0003252 | -0.0010604 | 0.070602 | 0.070588 | 0.070602 | 0.99555 | -0.060442 | 0.99568 | -0.061566 | 32.0918
87 | 1.8262 | 0.82793 | -1.8249 | -0.83442 | 0.0013146 | -0.0064879 | 0.058144 | 0.058226 | 0.058226 | 0.9955 | -0.060052 | 0.99482 | -0.054629 | 26.4666
88 | -2.2136 | -1.0138 | 2.2151 | 1.0087 | 0.0015711 | -0.0051337 | 0.070588 | 0.070521 | 0.070588 | 0.99568 | -0.061566 | 0.99635 | -0.06695 | 32.0854
89 | 0.12106 | 0.05736 | -0.12106 | -0.05863 | 1.0886e-06 | -0.0012697 | 0.0038872 | 0.0039031 | 0.0039031 | 0.99482 | -0.054629 | 0.99481 | -0.054553 | 1.7741
90 | 0.27003 | 0.13018 | -0.27002 | -0.1305 | 1.3452e-06 | -0.00031607 | 0.0086853 | 0.0086893 | 0.0086893 | 0.99635 | -0.06695 | 0.99634 | -0.066907 | 3.9497
91 | 0.27002 | 0.1305 | -0.27002 | -0.13078 | 1.187e-06 | -0.00027864 | 0.0086893 | 0.0086928 | 0.0086928 | 0.99634 | -0.066907 | 0.99634 | -0.066869 | 3.9513
92 | -3.1523 | -1.4079 | 3.153 | 1.4068 | 0.00070913 | -0.0010405 | 0.10019 | 0.10017 | 0.10019 | 0.99478 | -0.076 | 0.99499 | -0.077609 | 45.5388
93 | 0.36429 | 0.16494 | -0.3642 | -0.17635 | 8.9846e-05 | -0.011419 | 0.01166 | 0.011801 | 0.011801 | 0.99006 | -0.039173 | 0.98983 | -0.037181 | 5.3642
94 | 0.34527 | 0.14437 | -0.34519 | -0.15703 | 8.7334e-05 | -0.01266 | 0.010912 | 0.01106 | 0.01106 | 0.99006 | -0.039173 | 0.98983 | -0.03747 | 5.0272
95 | 1.4663 | 0.69262 | -1.4662 | -0.6934 | 0.00010196 | -0.00078601 | 0.047035 | 0.047045 | 0.047045 | 0.99525 | -0.034804 | 0.99519 | -0.034231 | 21.3843
96 | 0.13497 | 0.064421 | -0.13497 | -0.065369 | 1.0102e-06 | -0.00094813 | 0.0043379 | 0.0043498 | 0.0043498 | 0.99526 | -0.035218 | 0.99525 | -0.035154 | 1.9772
97 | 1.4662 | 0.6934 | -1.4661 | -0.6939 | 6.368e-05 | -0.00049066 | 0.047045 | 0.047052 | 0.047052 | 0.99519 | -0.034231 | 0.99515 | -0.033872 | 21.3872
98 | -1.1354 | -0.53488 | 1.1355 | 0.53384 | 7.9738e-05 | -0.0010411 | 0.036417 | 0.036404 | 0.036417 | 0.99488 | -0.034672 | 0.99495 | -0.035245 | 16.5532
99 | 0.90968 | 0.42557 | -0.90873 | -0.42572 | 0.00095345 | -0.00014635 | 0.029141 | 0.02915 | 0.02915 | 0.99488 | -0.034672 | 0.99378 | -0.042469 | 13.881
100 | -1.1355 | -0.53384 | 1.1357 | 0.53387 | 0.00021257 | 2.6732e-05 | 0.036404 | 0.036403 | 0.036404 | 0.99495 | -0.035245 | 0.99515 | -0.033872 | 17.3352
101 | 0.23832 | 0.11515 | -0.23832 | -0.11542 | 9.2217e-07 | -0.00027514 | 0.0076886 | 0.007692 | 0.007692 | 0.99378 | -0.042469 | 0.99377 | -0.042435 | 3.4964
102 | 0.67041 | 0.31057 | -0.67017 | -0.31966 | 0.0002404 | -0.0090955 | 0.021462 | 0.021576 | 0.021576 | 0.99378 | -0.042469 | 0.99345 | -0.039549 | 9.8071
103 | -1.4926 | -0.7148 | 1.4927 | 0.71439 | 5.4822e-05 | -0.00041099 | 0.047841 | 0.047836 | 0.047841 | 0.99861 | -0.0098038 | 0.99864 | -0.010116 | 21.7461
104 | -1.4927 | -0.71439 | 1.4928 | 0.71385 | 7.2201e-05 | -0.00054146 | 0.047836 | 0.047829 | 0.047836 | 0.99864 | -0.010116 | 0.99869 | -0.010525 | 21.7437
105 | -0.11752 | -0.056917 | 0.11752 | 0.055833 | 8.9404e-07 | -0.0010836 | 0.0038084 | 0.0037947 | 0.0038084 | 0.98976 | -0.036994 | 0.98977 | -0.037059 | 1.7311
106 | -0.11752 | -0.055833 | 0.11753 | 0.046872 | 7.1571e-06 | -0.0089609 | 0.0037947 | 0.0036901 | 0.0037947 | 0.98977 | -0.037059 | 0.98983 | -0.03747 | 1.7249
107 | 0.22766 | 0.11016 | -0.22765 | -0.11026 | 8.5397e-06 | -9.7672e-05 | 0.007376 | 0.0073773 | 0.0073773 | 0.98983 | -0.03747 | 0.98979 | -0.037718 | 3.513
108 | 0.3642 | 0.17635 | -0.3642 | -0.17639 | 8.3819e-06 | -3.4257e-05 | 0.011801 | 0.011802 | 0.011802 | 0.98983 | -0.037181 | 0.98981 | -0.037333 | 5.6199
109 | 0.31349 | 0.15141 | -0.31349 | -0.15163 | 1.2656e-06 | -0.00022249 | 0.010063 | 0.010066 | 0.010066 | 0.99868 | -0.010478 | 0.99868 | -0.010443 | 4.5755
110 | -0.31349 | -0.15141 | 0.31349 | 0.1511 | 1.734e-06 | -0.00030503 | 0.010063 | 0.010059 | 0.010063 | 0.99868 | -0.010478 | 0.99869 | -0.010525 | 4.5742
111 | 0.20857 | 0.10081 | -0.20857 | -0.101 | 4.5819e-07 | -0.00018206 | 0.0066962 | 0.0066985 | 0.0066985 | 0.99868 | -0.010443 | 0.99868 | -0.010424 | 3.0448
112 | -1.8063 | -0.86495 | 1.8068 | 0.86234 | 0.00051924 | -0.0026123 | 0.057888 | 0.057854 | 0.057888 | 0.99869 | -0.010525 | 0.99895 | -0.012958 | 26.3129
113 | 0.069865 | 0.033818 | -0.069865 | -0.033837 | 5.3549e-09 | -1.8609e-05 | 0.0022436 | 0.0022439 | 0.0022439 | 0.99868 | -0.010424 | 0.99868 | -0.010423 | 1.0199
114 | -2.571 | -1.2325 | 2.5712 | 1.232 | 0.00019686 | -0.00045924 | 0.082391 | 0.082385 | 0.082391 | 0.99895 | -0.012958 | 0.99902 | -0.013609 | 37.4506
115 | -3.1581 | -1.5163 | 3.1585 | 1.5156 | 0.0004371 | -0.00063191 | 0.10123 | 0.10122 | 0.10123 | 0.99902 | -0.013609 | 0.99915 | -0.014791 | 46.013
116 | 5.6156 | 2.6929 | -5.6155 | -2.695 | 8.3422e-05 | -0.0020448 | 0.17994 | 0.17996 | 0.17996 | 0.99915 | -0.014791 | 0.99914 | -0.014848 | 14.1036
117 | -0.34621 | -0.16767 | 0.34621 | 0.16703 | 4.5863e-06 | -0.0006468 | 0.011179 | 0.011171 | 0.011179 | 0.99335 | -0.038682 | 0.99336 | -0.038797 | 5.0813
118 | -0.34621 | -0.16703 | 0.34623 | 0.16364 | 2.3917e-05 | -0.0033886 | 0.011171 | 0.011128 | 0.011171 | 0.99336 | -0.038797 | 0.99343 | -0.03938 | 5.0776
119 | -0.34623 | -0.16364 | 0.34624 | 0.16293 | 4.9631e-06 | -0.00070649 | 0.011128 | 0.011119 | 0.011128 | 0.99343 | -0.03938 | 0.99344 | -0.039498 | 5.0582
120 | -0.67016 | -0.31982 | 0.67017 | 0.31966 | 4.0964e-06 | -0.0001541 | 0.021578 | 0.021576 | 0.021578 | 0.99344 | -0.039498 | 0.99345 | -0.039549 | 9.808

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 17.9346 | 8.3463

## res_load
| p_mw | q_mvar
0 | 0.36358 | 0.17609
1 | 0.093285 | 0.04518
2 | 0.40977 | 0.19846
3 | 0.071638 | 0.034696
4 | 0.3482 | 0.16864
5 | 0.10953 | 0.053047
6 | 0.082752 | 0.040078
7 | 0.068444 | 0.033149
8 | 0.30933 | 0.14982
9 | 0.12107 | 0.058637
10 | 0.36048 | 0.17459
11 | 0.30638 | 0.14838
12 | 0.50594 | 0.24504
13 | 0.26729 | 0.12946
14 | 0.19665 | 0.095242
15 | 0.12821 | 0.062095
16 | 0.34647 | 0.1678
17 | 0.2966 | 0.14365
18 | 0.21928 | 0.1062
19 | 0.24752 | 0.11988
20 | 0.29923 | 0.14493
21 | 0.26985 | 0.13069
22 | 0.27829 | 0.13478
23 | 0.30246 | 0.14649
24 | 0.26978 | 0.13066
25 | 0.40843 | 0.19781
26 | 0.24516 | 0.11874
27 | 0.3553 | 0.17208
28 | 0.30577 | 0.14809
29 | 0.22184 | 0.10744
30 | 0.11998 | 0.058109
31 | 1.926 | 0.93282
32 | 0.33182 | 0.16071
33 | 0.077206 | 0.037392
34 | 0.1121 | 0.054295
35 | 0.21921 | 0.10617
36 | 0.12415 | 0.060128
37 | 0.29627 | 0.14349
38 | 0.28636 | 0.13869
39 | 0.38697 | 0.18742
40 | 0.12106 | 0.05863
41 | 0.27002 | 0.13078
42 | 0.27132 | 0.13141
43 | 0.069247 | 0.033538
44 | 0.13497 | 0.065369
45 | 0.2257 | 0.10931
46 | 0.90983 | 0.44065
47 | 0.23832 | 0.11542
48 | 0.11752 | 0.056917
49 | 0.22765 | 0.11026
50 | 0.3642 | 0.17639
51 | 0.33041 | 0.16003
52 | 0.10492 | 0.050815
53 | 0.13871 | 0.067178
54 | 0.76421 | 0.37012
55 | 0.069865 | 0.033837
56 | 0.58692 | 0.28426
57 | 0.34621 | 0.16767
58 | 0.32393 | 0.15688
59 | 0.55096 | 0.26684

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1