## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_463_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_463_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_463_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_463_0_node_152 | 20 | n |  | TRUE
4 | bus_MV_463_0_node_10 | 20 | n |  | TRUE
5 | bus_MV_463_0_node_19 | 20 | n |  | TRUE
6 | bus_MV_463_0_node_3 | 20 | n |  | TRUE
7 | bus_MV_463_0_node_4 | 20 | n |  | TRUE
8 | bus_MV_463_0_node_11 | 20 | n |  | TRUE
9 | bus_MV_463_0_node_5 | 20 | n |  | TRUE
10 | bus_MV_463_0_node_149 | 20 | n |  | TRUE
11 | bus_MV_463_0_node_6 | 20 | n |  | TRUE
12 | bus_MV_463_0_node_46 | 20 | n |  | TRUE
13 | bus_MV_463_0_node_14 | 20 | n |  | TRUE
14 | bus_MV_463_0_node_7 | 20 | n |  | TRUE
15 | bus_MV_463_0_node_8 | 20 | n |  | TRUE
16 | bus_MV_463_0_node_9 | 20 | n |  | TRUE
17 | bus_MV_463_0_node_150 | 20 | n |  | TRUE
18 | bus_MV_463_0_node_45 | 20 | n |  | TRUE
19 | bus_MV_463_0_node_13 | 20 | n |  | TRUE
20 | bus_MV_463_0_node_71 | 20 | n |  | TRUE
21 | bus_MV_463_0_node_17 | 20 | n |  | TRUE
22 | bus_MV_463_0_node_12 | 20 | n |  | TRUE
23 | bus_MV_463_0_node_24 | 20 | n |  | TRUE
24 | bus_MV_463_0_node_26 | 20 | n |  | TRUE
25 | bus_MV_463_0_node_15 | 20 | n |  | TRUE
26 | bus_MV_463_0_node_16 | 20 | n |  | TRUE
27 | bus_MV_463_0_node_18 | 20 | n |  | TRUE
28 | bus_MV_463_0_node_21 | 20 | n |  | TRUE
29 | bus_MV_463_0_node_75 | 20 | n |  | TRUE
30 | bus_MV_463_0_node_20 | 20 | n |  | TRUE
31 | bus_MV_463_0_node_101 | 20 | n |  | TRUE
32 | bus_MV_463_0_node_23 | 20 | n |  | TRUE
33 | bus_MV_463_0_node_100 | 20 | n |  | TRUE
34 | bus_MV_463_0_node_29 | 20 | n |  | TRUE
35 | bus_MV_463_0_node_113 | 20 | n |  | TRUE
36 | bus_MV_463_0_node_90 | 20 | n |  | TRUE
37 | bus_MV_463_0_node_28 | 20 | n |  | TRUE
38 | bus_MV_463_0_node_30 | 20 | n |  | TRUE
39 | bus_MV_463_0_node_52 | 20 | n |  | TRUE
40 | bus_MV_463_0_node_98 | 20 | n |  | TRUE
41 | bus_MV_463_0_node_97 | 20 | n |  | TRUE
42 | bus_MV_463_0_node_25 | 20 | n |  | TRUE
43 | bus_MV_463_0_node_27 | 20 | n |  | TRUE
44 | bus_MV_463_0_node_49 | 20 | n |  | TRUE
45 | bus_MV_463_0_node_35 | 20 | n |  | TRUE
46 | bus_MV_463_0_node_48 | 20 | n |  | TRUE
47 | bus_MV_463_0_node_47 | 20 | n |  | TRUE
48 | bus_MV_463_0_node_79 | 20 | n |  | TRUE
49 | bus_MV_463_0_node_33 | 20 | n |  | TRUE
50 | bus_MV_463_0_node_50 | 20 | n |  | TRUE
51 | bus_MV_463_0_node_99 | 20 | n |  | TRUE
52 | bus_MV_463_0_node_31 | 20 | n |  | TRUE
53 | bus_MV_463_0_node_32 | 20 | n |  | TRUE
54 | bus_MV_463_0_node_34 | 20 | n |  | TRUE
55 | bus_MV_463_0_node_157 | 20 | n |  | TRUE
56 | bus_MV_463_0_node_80 | 20 | n |  | TRUE
57 | bus_MV_463_0_node_81 | 20 | n |  | TRUE
58 | bus_MV_463_0_node_74 | 20 | n |  | TRUE
59 | bus_MV_463_0_node_36 | 20 | n |  | TRUE
60 | bus_MV_463_0_node_37 | 20 | n |  | TRUE
61 | bus_MV_463_0_node_38 | 20 | n |  | TRUE
62 | bus_MV_463_0_node_128 | 20 | n |  | TRUE
63 | bus_MV_463_0_node_39 | 20 | n |  | TRUE
64 | bus_MV_463_0_node_129 | 20 | n |  | TRUE
65 | bus_MV_463_0_node_41 | 20 | n |  | TRUE
66 | bus_MV_463_0_node_127 | 20 | n |  | TRUE
67 | bus_MV_463_0_node_126 | 20 | n |  | TRUE
68 | bus_MV_463_0_node_143 | 20 | n |  | TRUE
69 | bus_MV_463_0_node_42 | 20 | n |  | TRUE
70 | bus_MV_463_0_node_43 | 20 | n |  | TRUE
71 | bus_MV_463_0_node_44 | 20 | n |  | TRUE
72 | bus_MV_463_0_node_136 | 20 | n |  | TRUE
73 | bus_MV_463_0_node_135 | 20 | n |  | TRUE
74 | bus_MV_463_0_node_137 | 20 | n |  | TRUE
75 | bus_MV_463_0_node_85 | 20 | n |  | TRUE
76 | bus_MV_463_0_node_51 | 20 | n |  | TRUE
77 | bus_MV_463_0_node_53 | 20 | n |  | TRUE
78 | bus_MV_463_0_node_54 | 20 | n |  | TRUE
79 | bus_MV_463_0_node_55 | 20 | n |  | TRUE
80 | bus_MV_463_0_node_57 | 20 | n |  | TRUE
81 | bus_MV_463_0_node_60 | 20 | n |  | TRUE
82 | bus_MV_463_0_node_56 | 20 | n |  | TRUE
83 | bus_MV_463_0_node_87 | 20 | n |  | TRUE
84 | bus_MV_463_0_node_78 | 20 | n |  | TRUE
85 | bus_MV_463_0_node_76 | 20 | n |  | TRUE
86 | bus_MV_463_0_node_65 | 20 | n |  | TRUE
87 | bus_MV_463_0_node_58 | 20 | n |  | TRUE
88 | bus_MV_463_0_node_59 | 20 | n |  | TRUE
89 | bus_MV_463_0_node_61 | 20 | n |  | TRUE
90 | bus_MV_463_0_node_92 | 20 | n |  | TRUE
91 | bus_MV_463_0_node_110 | 20 | n |  | TRUE
92 | bus_MV_463_0_node_154 | 20 | n |  | TRUE
93 | bus_MV_463_0_node_62 | 20 | n |  | TRUE
94 | bus_MV_463_0_node_120 | 20 | n |  | TRUE
95 | bus_MV_463_0_node_72 | 20 | n |  | TRUE
96 | bus_MV_463_0_node_63 | 20 | n |  | TRUE
97 | bus_MV_463_0_node_67 | 20 | n |  | TRUE
98 | bus_MV_463_0_node_96 | 20 | n |  | TRUE
99 | bus_MV_463_0_node_64 | 20 | n |  | TRUE
100 | bus_MV_463_0_node_95 | 20 | n |  | TRUE
101 | bus_MV_463_0_node_91 | 20 | n |  | TRUE
102 | bus_MV_463_0_node_88 | 20 | n |  | TRUE
103 | bus_MV_463_0_node_77 | 20 | n |  | TRUE
104 | bus_MV_463_0_node_66 | 20 | n |  | TRUE
105 | bus_MV_463_0_node_93 | 20 | n |  | TRUE
106 | bus_MV_463_0_node_109 | 20 | n |  | TRUE
107 | bus_MV_463_0_node_125 | 20 | n |  | TRUE
108 | bus_MV_463_0_node_156 | 20 | n |  | TRUE
109 | bus_MV_463_0_node_117 | 20 | n |  | TRUE
110 | bus_MV_463_0_node_115 | 20 | n |  | TRUE
111 | bus_MV_463_0_node_121 | 20 | n |  | TRUE
112 | bus_MV_463_0_node_122 | 20 | n |  | TRUE
113 | bus_MV_463_0_node_123 | 20 | n |  | TRUE
114 | bus_MV_463_0_node_119 | 20 | n |  | TRUE
115 | bus_MV_463_0_node_142 | 20 | n |  | TRUE
116 | bus_MV_463_0_node_124 | 20 | n |  | TRUE
117 | bus_MV_463_0_node_141 | 20 | n |  | TRUE
118 | bus_MV_463_0_node_144 | 20 | n |  | TRUE
119 | bus_MV_463_0_node_82 | 20 | n |  | TRUE
120 | bus_MV_463_0_node_73 | 20 | n |  | TRUE
121 | bus_MV_463_0_node_158 | 20 | n |  | TRUE
122 | bus_MV_463_0_node_68 | 20 | n |  | TRUE
123 | bus_MV_463_0_node_69 | 20 | n |  | TRUE
124 | bus_MV_463_0_node_70 | 20 | n |  | TRUE
125 | bus_MV_463_0_node_107 | 20 | n |  | TRUE
126 | bus_MV_463_0_node_108 | 20 | n |  | TRUE
127 | bus_MV_463_0_node_86 | 20 | n |  | TRUE
128 | bus_MV_463_0_node_83 | 20 | n |  | TRUE
129 | bus_MV_463_0_node_84 | 20 | n |  | TRUE
130 | bus_MV_463_0_node_130 | 20 | n |  | TRUE
131 | bus_MV_463_0_node_148 | 20 | n |  | TRUE
132 | bus_MV_463_0_node_112 | 20 | n |  | TRUE
133 | bus_MV_463_0_node_102 | 20 | n |  | TRUE
134 | bus_MV_463_0_node_147 | 20 | n |  | TRUE
135 | bus_MV_463_0_node_111 | 20 | n |  | TRUE
136 | bus_MV_463_0_node_103 | 20 | n |  | TRUE
137 | bus_MV_463_0_node_89 | 20 | n |  | TRUE
138 | bus_MV_463_0_node_94 | 20 | n |  | TRUE
139 | bus_MV_463_0_node_134 | 20 | n |  | TRUE
140 | bus_MV_463_0_node_132 | 20 | n |  | TRUE
141 | bus_MV_463_0_node_131 | 20 | n |  | TRUE
142 | bus_MV_463_0_node_106 | 20 | n |  | TRUE
143 | bus_MV_463_0_node_105 | 20 | n |  | TRUE
144 | bus_MV_463_0_node_104 | 20 | n |  | TRUE
145 | bus_MV_463_0_node_114 | 20 | n |  | TRUE
146 | bus_MV_463_0_node_116 | 20 | n |  | TRUE
147 | bus_MV_463_0_node_155 | 20 | n |  | TRUE
148 | bus_MV_463_0_node_118 | 20 | n |  | TRUE
149 | bus_MV_463_0_node_140 | 20 | n |  | TRUE
150 | bus_MV_463_0_node_133 | 20 | n |  | TRUE
151 | bus_MV_463_0_node_138 | 20 | n |  | TRUE
152 | bus_MV_463_0_node_139 | 20 | n |  | TRUE
153 | bus_MV_463_0_node_145 | 20 | n |  | TRUE
154 | bus_MV_463_0_node_146 | 20 | n |  | TRUE
155 | bus_HV_463_0_node_67 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_463_0_load_0 | 0 | 0.052374 | 0.025366 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_463_0_load_152 | 3 | 0.084639 | 0.040992 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_463_0_load_4 | 7 | 0.31733 | 0.15369 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_463_0_load_11 | 8 | 0.27859 | 0.13493 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_463_0_load_149 | 10 | 0.2507 | 0.12142 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_463_0_load_14 | 13 | 0.33064 | 0.16014 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_463_0_load_7 | 14 | 0.32625 | 0.15801 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_463_0_load_150 | 17 | 0.33828 | 0.16383 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_463_0_load_45 | 18 | 0.070806 | 0.034293 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_463_0_load_71 | 20 | 0.75837 | 0.3673 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_463_0_load_12 | 22 | 0.30483 | 0.14764 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_463_0_load_24 | 23 | 0.32749 | 0.15861 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_463_0_load_15 | 25 | 0.25648 | 0.12422 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_463_0_load_75 | 29 | 0.09502 | 0.04602 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_463_0_load_101 | 31 | 0.18938 | 0.091719 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_463_0_load_100 | 33 | 2.5156 | 1.2184 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_463_0_load_113 | 35 | 0.068339 | 0.033098 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_463_0_load_90 | 36 | 0.65512 | 0.31729 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_463_0_load_52 | 39 | 0.092601 | 0.044849 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_463_0_load_97 | 41 | 0.13619 | 0.065961 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_463_0_load_49 | 44 | 0.079355 | 0.038433 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_463_0_load_35 | 45 | 0.11546 | 0.055919 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_463_0_load_48 | 46 | 0.32555 | 0.15767 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_463_0_load_47 | 47 | 0.16595 | 0.080371 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_463_0_load_79 | 48 | 0.233 | 0.11285 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_463_0_load_50 | 50 | 0.10707 | 0.051856 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_463_0_load_99 | 51 | 0.074237 | 0.035955 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_463_0_load_31 | 52 | 0.19986 | 0.096797 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_463_0_load_157 | 55 | 0.079671 | 0.038586 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_463_0_load_80 | 56 | 0.17865 | 0.086526 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_463_0_load_36 | 59 | 0.26276 | 0.12726 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_463_0_load_128 | 62 | 0.1012 | 0.049012 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_463_0_load_39 | 63 | 0.26151 | 0.12666 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_463_0_load_129 | 64 | 0.10304 | 0.049903 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_463_0_load_126 | 67 | 0.092562 | 0.04483 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_463_0_load_143 | 68 | 0.64426 | 0.31203 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_463_0_load_42 | 69 | 0.25471 | 0.12336 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_463_0_load_136 | 72 | 0.3088 | 0.14956 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_463_0_load_135 | 73 | 0.23838 | 0.11545 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_463_0_load_137 | 74 | 0.56784 | 0.27502 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_463_0_load_85 | 75 | 0.42541 | 0.20604 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_463_0_load_51 | 76 | 0.074623 | 0.036142 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_463_0_load_53 | 77 | 0.13314 | 0.064484 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_463_0_load_87 | 83 | 0.091904 | 0.044511 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_463_0_load_78 | 84 | 0.09234 | 0.044722 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_463_0_load_76 | 85 | 0.13047 | 0.06319 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_463_0_load_65 | 86 | 0.20749 | 0.10049 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_463_0_load_92 | 90 | 0.14496 | 0.070205 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_463_0_load_110 | 91 | 0.34721 | 0.16816 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_463_0_load_154 | 92 | 0.3664 | 0.17745 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_463_0_load_72 | 95 | 0.1 | 0.048434 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_463_0_load_67 | 97 | 0.25656 | 0.12426 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_463_0_load_95 | 100 | 0.13061 | 0.063256 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_463_0_load_91 | 101 | 0.32799 | 0.15885 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_463_0_load_88 | 102 | 0.20909 | 0.10127 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_463_0_load_77 | 103 | 0.092964 | 0.045024 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_463_0_load_66 | 104 | 0.078715 | 0.038123 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_463_0_load_156 | 108 | 0.19393 | 0.093925 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_463_0_load_121 | 111 | 0.088937 | 0.043074 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_463_0_load_142 | 115 | 0.22111 | 0.10709 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_463_0_load_141 | 117 | 1.2552 | 0.60792 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_463_0_load_144 | 118 | 0.07236 | 0.035045 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_463_0_load_73 | 120 | 0.26436 | 0.12803 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_463_0_load_158 | 121 | 0.1554 | 0.075264 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_463_0_load_68 | 122 | 0.06876 | 0.033302 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_463_0_load_69 | 123 | 0.068762 | 0.033303 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_463_0_load_70 | 124 | 0.27723 | 0.13427 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_463_0_load_107 | 125 | 0.27161 | 0.13155 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_463_0_load_108 | 126 | 0.16674 | 0.080758 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_463_0_load_130 | 130 | 0.081499 | 0.039472 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_463_0_load_148 | 131 | 0.1823 | 0.08829 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_463_0_load_102 | 133 | 0.29512 | 0.14293 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_463_0_load_111 | 135 | 0.35458 | 0.17173 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_463_0_load_103 | 136 | 0.10284 | 0.049807 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_463_0_load_89 | 137 | 0.13409 | 0.06494 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_463_0_load_134 | 139 | 0.10181 | 0.049308 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_463_0_load_131 | 141 | 0.071062 | 0.034417 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_463_0_load_104 | 144 | 0.094016 | 0.045534 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_463_0_load_114 | 145 | 0.098697 | 0.047801 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_463_0_load_155 | 147 | 0.077229 | 0.037404 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_463_0_load_118 | 148 | 0.087574 | 0.042414 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_463_0_load_140 | 149 | 0.44734 | 0.21666 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_463_0_load_133 | 150 | 0.12247 | 0.059313 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_463_0_load_138 | 151 | 0.61928 | 0.29993 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_463_0_load_145 | 153 | 0.077968 | 0.037761 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 97 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_463_0_line_0 |  | 0 | 1 | 0.19473 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_463_0_line_1 |  | 1 | 2 | 1.1439 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_463_0_line_2 |  | 2 | 6 | 0.12183 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_463_0_line_3 |  | 2 | 7 | 0.04853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_463_0_line_4 |  | 3 | 4 | 0.89205 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_463_0_line_5 |  | 3 | 5 | 0.64485 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_463_0_line_6 |  | 4 | 17 | 0.13589 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_463_0_line_7 |  | 4 | 15 | 0.49624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_463_0_line_8 |  | 5 | 20 | 0.11975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_463_0_line_9 |  | 5 | 21 | 0.29267 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_463_0_line_10 |  | 6 | 8 | 0.03542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_463_0_line_11 |  | 7 | 14 | 0.12078 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_463_0_line_12 |  | 9 | 10 | 0.037254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_463_0_line_13 |  | 9 | 11 | 0.55413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_463_0_line_14 |  | 9 | 12 | 0.18579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_463_0_line_15 |  | 10 | 16 | 0.043158 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_463_0_line_16 |  | 11 | 13 | 0.040463 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_463_0_line_17 |  | 12 | 18 | 0.017215 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_463_0_line_18 |  | 13 | 19 | 1.2949 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_463_0_line_19 |  | 14 | 15 | 0.012265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_463_0_line_20 |  | 15 | 16 | 0.32497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_463_0_line_21 |  | 19 | 22 | 0.013835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_463_0_line_22 |  | 21 | 28 | 0.19432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_463_0_line_23 |  | 21 | 25 | 0.12036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_463_0_line_24 |  | 23 | 24 | 0.006251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_463_0_line_25 |  | 24 | 37 | 0.037229 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_463_0_line_26 |  | 24 | 38 | 0.27014 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
27 | MV_463_0_line_27 |  | 25 | 26 | 0.024933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_463_0_line_28 |  | 26 | 27 | 0.080995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_463_0_line_29 |  | 27 | 29 | 0.082474 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_463_0_line_30 |  | 28 | 34 | 0.27775 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
31 | MV_463_0_line_31 |  | 28 | 35 | 0.0090022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_463_0_line_32 |  | 28 | 30 | 0.08698 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_463_0_line_33 |  | 30 | 31 | 0.044356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_463_0_line_34 |  | 30 | 32 | 0.045842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_463_0_line_35 |  | 30 | 33 | 0.055569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_463_0_line_36 |  | 32 | 36 | 0.08691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_463_0_line_37 |  | 34 | 38 | 0.18317 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
38 | MV_463_0_line_38 |  | 34 | 39 | 0.064581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_463_0_line_39 |  | 37 | 46 | 0.058697 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
40 | MV_463_0_line_40 |  | 37 | 47 | 0.064158 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_463_0_line_41 |  | 38 | 40 | 0.013327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_463_0_line_42 |  | 38 | 41 | 0.037661 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_463_0_line_43 |  | 39 | 50 | 0.050985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_463_0_line_44 |  | 40 | 51 | 0.03448 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_463_0_line_45 |  | 42 | 43 | 0.13823 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
46 | MV_463_0_line_46 |  | 42 | 44 | 0.11493 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
47 | MV_463_0_line_47 |  | 43 | 45 | 0.076257 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
48 | MV_463_0_line_48 |  | 44 | 46 | 0.11496 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
49 | MV_463_0_line_49 |  | 45 | 48 | 0.23183 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
50 | MV_463_0_line_50 |  | 47 | 49 | 0.19033 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_463_0_line_51 |  | 48 | 56 | 0.027642 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_463_0_line_52 |  | 48 | 57 | 0.11685 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_463_0_line_53 |  | 48 | 58 | 0.028639 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
54 | MV_463_0_line_54 |  | 49 | 54 | 0.40333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_463_0_line_55 |  | 49 | 53 | 0.088545 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_463_0_line_56 |  | 50 | 76 | 0.0061933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_463_0_line_57 |  | 51 | 142 | 0.0040404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_463_0_line_58 |  | 52 | 53 | 0.027842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_463_0_line_59 |  | 54 | 55 | 0.001591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_463_0_line_60 |  | 57 | 128 | 0.047754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_463_0_line_61 |  | 58 | 119 | 0.011134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_463_0_line_62 |  | 58 | 89 | 0.14105 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_463_0_line_63 |  | 59 | 60 | 0.074585 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_463_0_line_64 |  | 60 | 61 | 0.22639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_463_0_line_65 |  | 61 | 62 | 0.028112 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_463_0_line_66 |  | 61 | 63 | 0.11893 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_463_0_line_67 |  | 62 | 64 | 0.078163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_463_0_line_68 |  | 64 | 109 | 0.090953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_463_0_line_69 |  | 65 | 66 | 0.015975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_463_0_line_70 |  | 65 | 67 | 0.036151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_463_0_line_71 |  | 66 | 68 | 0.051973 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_463_0_line_72 |  | 68 | 115 | 0.034376 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_463_0_line_73 |  | 69 | 70 | 0.006582 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_463_0_line_74 |  | 70 | 71 | 0.10921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_463_0_line_75 |  | 71 | 72 | 0.034118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_463_0_line_76 |  | 71 | 73 | 0.075483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_463_0_line_77 |  | 72 | 74 | 0.086624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_463_0_line_78 |  | 73 | 75 | 0.063075 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_463_0_line_79 |  | 75 | 119 | 0.099888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_463_0_line_80 |  | 77 | 78 | 0.010044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_463_0_line_81 |  | 78 | 79 | 0.064907 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_463_0_line_82 |  | 78 | 80 | 0.051043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_463_0_line_83 |  | 78 | 81 | 0.29005 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_463_0_line_84 |  | 79 | 82 | 0.076204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_463_0_line_85 |  | 79 | 83 | 0.021866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_463_0_line_86 |  | 80 | 86 | 0.048466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_463_0_line_87 |  | 81 | 92 | 0.004761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_463_0_line_88 |  | 81 | 93 | 0.36288 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
89 | MV_463_0_line_89 |  | 81 | 94 | 0.23579 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
90 | MV_463_0_line_90 |  | 81 | 88 | 0.35396 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
91 | MV_463_0_line_91 |  | 82 | 84 | 0.031002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_463_0_line_92 |  | 82 | 85 | 0.041291 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_463_0_line_93 |  | 83 | 102 | 0.018503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_463_0_line_94 |  | 85 | 103 | 0.02114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_463_0_line_95 |  | 86 | 104 | 0.083482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_463_0_line_96 |  | 87 | 88 | 0.12574 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
97 | MV_463_0_line_97 |  | 87 | 89 | 0.10463 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
98 | MV_463_0_line_98 |  | 87 | 90 | 0.058347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_463_0_line_99 |  | 88 | 91 | 0.23203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_463_0_line_100 |  | 89 | 95 | 0.014714 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_463_0_line_101 |  | 90 | 105 | 0.042339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_463_0_line_102 |  | 91 | 106 | 0.016042 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_463_0_line_103 |  | 93 | 96 | 0.19277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_463_0_line_104 |  | 93 | 97 | 0.07058 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
105 | MV_463_0_line_105 |  | 94 | 111 | 0.084404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_463_0_line_106 |  | 94 | 112 | 0.014222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_463_0_line_107 |  | 94 | 113 | 0.038641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_463_0_line_108 |  | 94 | 114 | 0.031366 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_463_0_line_109 |  | 94 | 107 | 0.51801 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_463_0_line_110 |  | 95 | 120 | 0.02364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_463_0_line_111 |  | 96 | 98 | 0.07249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_463_0_line_112 |  | 96 | 99 | 0.012684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_463_0_line_113 |  | 96 | 100 | 0.078025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_463_0_line_114 |  | 98 | 121 | 0.039264 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
115 | MV_463_0_line_115 |  | 99 | 101 | 0.012233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_463_0_line_116 |  | 102 | 137 | 0.026489 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_463_0_line_117 |  | 105 | 138 | 0.045943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_463_0_line_118 |  | 106 | 126 | 0.031381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_463_0_line_119 |  | 107 | 108 | 0.094566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_463_0_line_120 |  | 107 | 109 | 0.081326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_463_0_line_121 |  | 109 | 110 | 0.97223 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_463_0_line_122 |  | 110 | 146 | 1.1988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_463_0_line_123 |  | 110 | 145 | 0.05121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_463_0_line_124 |  | 112 | 115 | 0.13952 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_463_0_line_125 |  | 113 | 116 | 0.18125 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_463_0_line_126 |  | 113 | 117 | 0.072768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_463_0_line_127 |  | 114 | 148 | 0.013912 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_463_0_line_128 |  | 116 | 118 | 0.012337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_463_0_line_129 |  | 117 | 149 | 0.062239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_463_0_line_130 |  | 119 | 127 | 0.014716 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_463_0_line_131 |  | 122 | 123 | 0.00010536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_463_0_line_132 |  | 123 | 124 | 0.037914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_463_0_line_133 |  | 124 | 125 | 0.0053445 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_463_0_line_134 |  | 125 | 126 | 0.042859 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_463_0_line_135 |  | 127 | 133 | 0.026377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_463_0_line_136 |  | 128 | 129 | 0.1505 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_463_0_line_137 |  | 128 | 130 | 0.047417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_463_0_line_138 |  | 129 | 131 | 0.10198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_463_0_line_139 |  | 129 | 132 | 0.1909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_463_0_line_140 |  | 131 | 134 | 0.081257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_463_0_line_141 |  | 132 | 135 | 0.0020535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_463_0_line_142 |  | 133 | 136 | 0.034318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_463_0_line_143 |  | 134 | 154 | 0.00631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_463_0_line_144 |  | 138 | 139 | 0.035943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_463_0_line_145 |  | 138 | 140 | 0.011289 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_463_0_line_146 |  | 140 | 141 | 0.037383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_463_0_line_147 |  | 141 | 150 | 0.053233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_463_0_line_148 |  | 142 | 143 | 0.086138 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_463_0_line_149 |  | 143 | 144 | 0.010964 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_463_0_line_150 |  | 146 | 147 | 0.066946 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
151 | MV_463_0_line_151 |  | 149 | 152 | 0.084621 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_463_0_line_152 |  | 151 | 152 | 0.061448 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_463_0_line_153 |  | 153 | 154 | 0.050509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_463_0_trafo_67 | 25 MVA 110/20 kV | 155 | 97 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2490628.8048 | 1118684.6356
1 | 2490730.3389 | 1118850.798
2 | 2491580.2052 | 1119069.1705
3 | 2492047.2914 | 1120158.0883
4 | 2491328.397 | 1119629.9309
5 | 2492630.852 | 1119883.7121
6 | 2491519.251 | 1118983.4188
7 | 2491544.0885 | 1119100.3728
8 | 2491498.5281 | 1118954.6606
9 | 2491827.7935 | 1119166.7123
10 | 2491800.9269 | 1119192.5985
11 | 2491883.8617 | 1118877.3224
12 | 2491956.8628 | 1119167.0614
13 | 2491872.4972 | 1118839.1897
14 | 2491546.9023 | 1119221.1216
15 | 2491555.7836 | 1119229.6012
16 | 2491771.1854 | 1119223.873
17 | 2491194.7117 | 1119654.3056
18 | 2491949.3413 | 1119182.36
19 | 2492142.1924 | 1117572.6773
20 | 2492718.557 | 1119964.1138
21 | 2492876.6372 | 1119831.8983
22 | 2492129.1683 | 1117567.9064
23 | 2493387.75 | 1119362.7879
24 | 2493393.8112 | 1119361.1911
25 | 2492933.3873 | 1119938.0508
26 | 2492955.1026 | 1119948.9067
27 | 2493014.8894 | 1120002.2277
28 | 2492988.3868 | 1119723.5614
29 | 2493078.8467 | 1120054.2993
30 | 2493040.4987 | 1119758.6845
31 | 2493071.8081 | 1119727.2647
32 | 2493043.6308 | 1119791.3279
33 | 2493081.616 | 1119796.0641
34 | 2493167.9567 | 1119527.5942
35 | 2492993.2004 | 1119731.0986
36 | 2493108.1192 | 1119849.5916
37 | 2493429.8179 | 1119351.7283
38 | 2493288.4228 | 1119506.6987
39 | 2493153.5186 | 1119567.6736
40 | 2493297.7976 | 1119516.1949
41 | 2493315.1187 | 1119480.1341
42 | 2493612.4377 | 1119568.7975
43 | 2493710.5514 | 1119654.839
44 | 2493537.469 | 1119481.6854
45 | 2493727.2779 | 1119708.5462
46 | 2493456.2015 | 1119400.3728
47 | 2493490.4077 | 1119338.1112
48 | 2493808.7518 | 1119925.5893
49 | 2493679.1492 | 1119335.8526
50 | 2493129.6316 | 1119607.9824
51 | 2493321.9137 | 1119540.8386
52 | 2493753.9447 | 1119403.1371
53 | 2493733.2052 | 1119384.5896
54 | 2494023.2304 | 1119367.3346
55 | 2494022.0765 | 1119368.4333
56 | 2493819.3318 | 1119951.1259
57 | 2493916.7724 | 1119881.0304
58 | 2493782.5844 | 1119937.1215
59 | 2493815.6827 | 1120648.2079
60 | 2493793.275 | 1120719.347
61 | 2493609.8808 | 1120661.1555
62 | 2493587.419 | 1120644.2593
63 | 2493704.5814 | 1120589.2107
64 | 2493525.8574 | 1120596.1021
65 | 2493776.6915 | 1120445.7404
66 | 2493772.019 | 1120434.5375
67 | 2493803.5621 | 1120469.9244
68 | 2493733.42 | 1120399.7338
69 | 2493868.5692 | 1120057.6005
70 | 2493873.0921 | 1120052.8069
71 | 2493952.0455 | 1120106.9901
72 | 2493984.4296 | 1120099.169
73 | 2493894.9186 | 1120058.0083
74 | 2494064.4247 | 1120065.9358
75 | 2493847.9816 | 1120015.8735
76 | 2493134.0462 | 1119612.3256
77 | 2493219.2444 | 1120168.4188
78 | 2493211.4273 | 1120162.1128
79 | 2493175.1809 | 1120119.7367
80 | 2493242.2319 | 1120186.9627
81 | 2493447.9331 | 1120149.4555
82 | 2493122.8572 | 1120077.2227
83 | 2493188.9586 | 1120102.7576
84 | 2493098.7861 | 1120057.6848
85 | 2493148.7523 | 1120045.0612
86 | 2493279.9387 | 1120217.4121
87 | 2493654.7062 | 1120043.3591
88 | 2493566.8475 | 1119970.1131
89 | 2493661.33 | 1119986.9286
90 | 2493698.0901 | 1120082.3748
91 | 2493387.2543 | 1119823.1933
92 | 2493444.786 | 1120153.0355
93 | 2493310.4815 | 1119917.3516
94 | 2493596.3223 | 1120292.9241
95 | 2493670.9447 | 1119997.8555
96 | 2493181.2923 | 1119901.8218
97 | 2493259.3082 | 1119868.7432
98 | 2493183.6207 | 1119851.4816
99 | 2493176.3029 | 1119911.1938
100 | 2493236.8311 | 1119910.4812
101 | 2493165.3766 | 1119916.5013
102 | 2493200.6175 | 1120088.3896
103 | 2493162.0102 | 1120028.5949
104 | 2493344.8499 | 1120269.908
105 | 2493729.5715 | 1120110.6864
106 | 2493371.9353 | 1119819.0491
107 | 2493408.5152 | 1120489.4132
108 | 2493480.8558 | 1120523.9608
109 | 2493455.0252 | 1120539.0589
110 | 2492863.0126 | 1120714.5308
111 | 2493517.2922 | 1120311.809
112 | 2493605.5461 | 1120282.0993
113 | 2493608.078 | 1120270.3139
114 | 2493619.7101 | 1120313.8928
115 | 2493707.8806 | 1120376.7239
116 | 2493613.5036 | 1120216.873
117 | 2493675.9759 | 1120245.0656
118 | 2493621.7871 | 1120207.7311
119 | 2493777.6371 | 1119946.7479
120 | 2493688.7217 | 1120004.703
121 | 2493170.5877 | 1119814.4435
122 | 2493281.4903 | 1119743.9403
123 | 2493281.573 | 1119744.0056
124 | 2493311.3316 | 1119767.4976
125 | 2493315.5265 | 1119770.8092
126 | 2493348.3297 | 1119798.372
127 | 2493766.3273 | 1119956.1637
128 | 2493949.5605 | 1119871.238
129 | 2494053.7625 | 1119837.6125
130 | 2493979.6899 | 1119905.5652
131 | 2494137.2293 | 1119893.8759
132 | 2494063.998 | 1119692.8848
133 | 2493785.8824 | 1119973.8649
134 | 2494197.6062 | 1119948.4322
135 | 2494062.5009 | 1119691.4792
136 | 2493762.8518 | 1119999.3074
137 | 2493220.6024 | 1120105.1423
138 | 2493757.1114 | 1120141.767
139 | 2493781.1337 | 1120114.9723
140 | 2493765.5091 | 1120149.3355
141 | 2493790.4575 | 1120121.4958
142 | 2493324.7396 | 1119543.7263
143 | 2493385.4168 | 1119542.0554
144 | 2493386.4435 | 1119549.5088
145 | 2492906.3651 | 1120687.2725
146 | 2493363.91 | 1121314.7413
147 | 2493420.5437 | 1121279.0421
148 | 2493627.0788 | 1120325.693
149 | 2493733.5295 | 1120221.3743
150 | 2493827.5498 | 1120121.9957
151 | 2493858.1948 | 1120240.4095
152 | 2493812.4652 | 1120199.3652
153 | 2494156.0689 | 1119918.757
154 | 2494193.2176 | 1119952.9785
155 | 2493259.3082 | 1119868.7432

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98356 | -0.12212 | 0.052374 | 0.025366
1 | 0.98358 | -0.12199 | 0 | 0
2 | 0.98365 | -0.12172 | 0 | 0
3 | 0.98899 | -0.099444 | 0.084639 | 0.040992
4 | 0.98506 | -0.1303 | 0 | 0
5 | 0.99193 | -0.076569 | 0 | 0
6 | 0.9836 | -0.12131 | 0 | 0
7 | 0.98367 | -0.12182 | 0.31733 | 0.15369
8 | 0.98359 | -0.12119 | 0.27859 | 0.13493
9 | 0.98332 | -0.11763 | 0 | 0
10 | 0.98335 | -0.11791 | 0.2507 | 0.12142
11 | 0.98287 | -0.1136 | 0 | 0
12 | 0.9833 | -0.1175 | 0 | 0
13 | 0.98283 | -0.11329 | 0.33064 | 0.16014
14 | 0.98382 | -0.1205 | 0.32625 | 0.15801
15 | 0.98383 | -0.12063 | 0 | 0
16 | 0.98343 | -0.11731 | 0 | 0
17 | 0.98497 | -0.13088 | 0.33828 | 0.16383
18 | 0.9833 | -0.11749 | 0.070806 | 0.034293
19 | 0.98206 | -0.11836 | 0 | 0
20 | 0.99181 | -0.075475 | 0.75837 | 0.3673
21 | 0.9931 | -0.086212 | 0 | 0
22 | 0.98205 | -0.1183 | 0.30483 | 0.14764
23 | 0.99535 | -0.07552 | 0.32749 | 0.15861
24 | 0.99535 | -0.075545 | 0 | 0
25 | 0.99304 | -0.085745 | 0.25648 | 0.12422
26 | 0.99304 | -0.085722 | 0 | 0
27 | 0.99303 | -0.085644 | 0 | 0
28 | 0.99396 | -0.093267 | 0 | 0
29 | 0.99302 | -0.085554 | 0.09502 | 0.04602
30 | 0.99358 | -0.089763 | 0 | 0
31 | 0.99357 | -0.089663 | 0.18938 | 0.091719
32 | 0.99355 | -0.089407 | 0 | 0
33 | 0.99341 | -0.088071 | 2.5156 | 1.2184
34 | 0.9948 | -0.078 | 0 | 0
35 | 0.99396 | -0.09326 | 0.068339 | 0.033098
36 | 0.99347 | -0.088722 | 0.65512 | 0.31729
37 | 0.9954 | -0.075324 | 0 | 0
38 | 0.99502 | -0.077053 | 0 | 0
39 | 0.99478 | -0.077794 | 0.092601 | 0.044849
40 | 0.99501 | -0.077029 | 0 | 0
41 | 0.99501 | -0.076992 | 0.13619 | 0.065961
42 | 0.99597 | -0.055049 | 0 | 0
43 | 0.99617 | -0.054114 | 0 | 0
44 | 0.99564 | -0.074189 | 0.079355 | 0.038433
45 | 0.99627 | -0.053591 | 0.11546 | 0.055919
46 | 0.99548 | -0.074951 | 0.32555 | 0.15767
47 | 0.99536 | -0.075052 | 0.16595 | 0.080371
48 | 0.99695 | -0.014474 | 0.233 | 0.11285
49 | 0.99529 | -0.074588 | 0 | 0
50 | 0.99477 | -0.077685 | 0.10707 | 0.051856
51 | 0.99501 | -0.076965 | 0.074237 | 0.035955
52 | 0.99526 | -0.074317 | 0.19986 | 0.096797
53 | 0.99527 | -0.074384 | 0 | 0
54 | 0.99525 | -0.074324 | 0 | 0
55 | 0.99525 | -0.074323 | 0.079671 | 0.038586
56 | 0.99695 | -0.014415 | 0.17865 | 0.086526
57 | 0.99685 | -0.013625 | 0 | 0
58 | 0.997 | -0.014253 | 0 | 0
59 | 0.99689 | -0.006713 | 0.26276 | 0.12726
60 | 0.99693 | -0.0064744 | 0 | 0
61 | 0.99701 | -0.0071502 | 0 | 0
62 | 0.99703 | -0.0073169 | 0.1012 | 0.049012
63 | 0.99695 | -0.007529 | 0.26151 | 0.12666
64 | 0.99709 | -0.0078692 | 0.10304 | 0.049903
65 | 0.99775 | -0.011482 | 0 | 0
66 | 0.99775 | -0.011499 | 0 | 0
67 | 0.99775 | -0.011443 | 0.092562 | 0.04483
68 | 0.99776 | -0.01155 | 0.64426 | 0.31203
69 | 0.99648 | -0.0095243 | 0.25471 | 0.12336
70 | 0.99648 | -0.0095444 | 0 | 0
71 | 0.99652 | -0.0098694 | 0 | 0
72 | 0.99648 | -0.0095144 | 0.3088 | 0.14956
73 | 0.99663 | -0.010867 | 0.23838 | 0.11545
74 | 0.99642 | -0.0089274 | 0.56784 | 0.27502
75 | 0.99674 | -0.011874 | 0.42541 | 0.20604
76 | 0.99477 | -0.077679 | 0.074623 | 0.036142
77 | 0.99813 | -0.0030569 | 0.13314 | 0.064484
78 | 0.99813 | -0.0030728 | 0 | 0
79 | 0.99807 | -0.0025141 | 0 | 0
80 | 0.99812 | -0.0029096 | 0 | 0
81 | 0.99857 | -0.0068649 | 0 | 0
82 | 0.99804 | -0.0022404 | 0 | 0
83 | 0.99806 | -0.0024017 | 0.091904 | 0.044511
84 | 0.99804 | -0.0022067 | 0.09234 | 0.044722
85 | 0.99803 | -0.0021322 | 0.13047 | 0.06319
86 | 0.9981 | -0.002751 | 0.20749 | 0.10049
87 | 0.99749 | -0.011965 | 0 | 0
88 | 0.99775 | -0.010719 | 0 | 0
89 | 0.99728 | -0.012959 | 0 | 0
90 | 0.99746 | -0.011679 | 0.14496 | 0.070205
91 | 0.9974 | -0.0074586 | 0.34721 | 0.16816
92 | 0.99856 | -0.006844 | 0.3664 | 0.17745
93 | 0.99976 | -0.0011533 | 0 | 0
94 | 0.99798 | -0.013568 | 0 | 0
95 | 0.99727 | -0.012895 | 0.1 | 0.048434
96 | 0.99961 | 0.00018337 | 0 | 0
97 | 1 | 0 | -20.9654 | -9.5894
98 | 0.9996 | 0.00031404 | 0 | 0
99 | 0.99961 | 0.00023283 | 0 | 0
100 | 0.9996 | 0.00030076 | 0.13061 | 0.063256
101 | 0.9996 | 0.00028075 | 0.32799 | 0.15885
102 | 0.99805 | -0.0023265 | 0.20909 | 0.10127
103 | 0.99803 | -0.0021089 | 0.092964 | 0.045024
104 | 0.99809 | -0.0026774 | 0.078715 | 0.038123
105 | 0.99744 | -0.011542 | 0 | 0
106 | 0.99738 | -0.0072971 | 0 | 0
107 | 0.99726 | -0.0091638 | 0 | 0
108 | 0.99724 | -0.00895 | 0.19393 | 0.093925
109 | 0.99717 | -0.0086128 | 0 | 0
110 | 0.99697 | -0.0091275 | 0 | 0
111 | 0.99797 | -0.013483 | 0.088937 | 0.043074
112 | 0.99796 | -0.01341 | 0 | 0
113 | 0.99786 | -0.012485 | 0 | 0
114 | 0.99797 | -0.013536 | 0 | 0
115 | 0.99779 | -0.011849 | 0.22111 | 0.10709
116 | 0.99784 | -0.012356 | 0 | 0
117 | 0.99764 | -0.010482 | 1.2552 | 0.60792
118 | 0.99784 | -0.012345 | 0.07236 | 0.035045
119 | 0.99697 | -0.013968 | 0 | 0
120 | 0.99726 | -0.012821 | 0.26436 | 0.12803
121 | 0.99958 | 0.00024017 | 0.1554 | 0.075264
122 | 0.9973 | -0.0065423 | 0.06876 | 0.033302
123 | 0.9973 | -0.0065424 | 0.068762 | 0.033303
124 | 0.99731 | -0.006604 | 0.27723 | 0.13427
125 | 0.99731 | -0.0066303 | 0.27161 | 0.13155
126 | 0.99735 | -0.0069799 | 0.16674 | 0.080758
127 | 0.99696 | -0.013899 | 0 | 0
128 | 0.99681 | -0.013272 | 0 | 0
129 | 0.99669 | -0.012275 | 0 | 0
130 | 0.9968 | -0.013228 | 0.081499 | 0.039472
131 | 0.99666 | -0.011984 | 0.1823 | 0.08829
132 | 0.9966 | -0.011488 | 0 | 0
133 | 0.99695 | -0.013775 | 0.29512 | 0.14293
134 | 0.99665 | -0.01192 | 0 | 0
135 | 0.9966 | -0.011479 | 0.35458 | 0.17173
136 | 0.99694 | -0.013733 | 0.10284 | 0.049807
137 | 0.99805 | -0.0022843 | 0.13409 | 0.06494
138 | 0.99742 | -0.01139 | 0 | 0
139 | 0.99742 | -0.011347 | 0.10181 | 0.049308
140 | 0.99742 | -0.011365 | 0 | 0
141 | 0.99741 | -0.011282 | 0.071062 | 0.034417
142 | 0.99501 | -0.076961 | 0 | 0
143 | 0.995 | -0.07687 | 0 | 0
144 | 0.995 | -0.076858 | 0.094016 | 0.045534
145 | 0.99696 | -0.0090687 | 0.098697 | 0.047801
146 | 0.99685 | -0.0091125 | 0 | 0
147 | 0.99684 | -0.0091756 | 0.077229 | 0.037404
148 | 0.99797 | -0.013521 | 0.087574 | 0.042414
149 | 0.99756 | -0.0097005 | 0.44734 | 0.21666
150 | 0.9974 | -0.011206 | 0.12247 | 0.059313
151 | 0.99744 | -0.0086291 | 0.61928 | 0.29993
152 | 0.99749 | -0.0090838 | 0 | 0
153 | 0.99664 | -0.011869 | 0.077968 | 0.037761
154 | 0.99665 | -0.011915 | 0 | 0
155 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.052374 | -0.025366 | 0.052375 | 0.025141 | 1.0104e-06 | -0.00022426 | 0.001708 | 0.0017051 | 0.001708 | 0.98356 | -0.12212 | 0.98358 | -0.12199 | 0.81332
1 | -0.052375 | -0.025141 | 0.052378 | -0.0012822 | 3.7957e-06 | -0.026424 | 0.0017051 | 0.0015376 | 0.0017051 | 0.98358 | -0.12199 | 0.98365 | -0.12172 | 0.77505
2 | 0.27861 | 0.1313 | -0.2786 | -0.13411 | 1.3341e-05 | -0.0028105 | 0.009039 | 0.0090745 | 0.0090745 | 0.98365 | -0.12172 | 0.9836 | -0.12131 | 4.1248
3 | -0.33099 | -0.13002 | 0.331 | 0.1289 | 7.0483e-06 | -0.0011191 | 0.010436 | 0.010424 | 0.010436 | 0.98365 | -0.12172 | 0.98367 | -0.12182 | 4.7438
4 | 2.2821 | 1.0328 | -2.2736 | -1.0285 | 0.0084982 | 0.0042855 | 0.073116 | 0.073129 | 0.073129 | 0.98899 | -0.099444 | 0.98506 | -0.1303 | 34.8232
5 | -2.3668 | -1.0738 | 2.3734 | 1.0771 | 0.006611 | 0.0033857 | 0.07586 | 0.075851 | 0.07586 | 0.98899 | -0.099444 | 0.99193 | -0.076569 | 36.124
6 | 0.3383 | 0.1637 | -0.33828 | -0.16383 | 2.9374e-05 | -0.000139 | 0.011014 | 0.011016 | 0.011016 | 0.98506 | -0.1303 | 0.98497 | -0.13088 | 5.2456
7 | 1.9353 | 0.86479 | -1.9327 | -0.87551 | 0.0025621 | -0.010723 | 0.062119 | 0.062258 | 0.062258 | 0.98506 | -0.1303 | 0.98383 | -0.12063 | 28.2989
8 | 0.75847 | 0.36451 | -0.75837 | -0.3673 | 9.6024e-05 | -0.0027845 | 0.02449 | 0.024526 | 0.024526 | 0.99193 | -0.076569 | 0.99181 | -0.075475 | 11.148
9 | -3.1318 | -1.4417 | 3.1358 | 1.4359 | 0.0039302 | -0.0057177 | 0.10034 | 0.10025 | 0.10034 | 0.99193 | -0.076569 | 0.9931 | -0.086212 | 45.6077
10 | 0.2786 | 0.13411 | -0.27859 | -0.13493 | 3.8983e-06 | -0.00081702 | 0.0090745 | 0.009085 | 0.009085 | 0.9836 | -0.12131 | 0.98359 | -0.12119 | 4.1295
11 | -0.64832 | -0.28259 | 0.64842 | 0.28251 | 9.2693e-05 | -8.148e-05 | 0.020755 | 0.020753 | 0.020755 | 0.98367 | -0.12182 | 0.98382 | -0.1205 | 9.8834
12 | -0.70685 | -0.32209 | 0.70688 | 0.32124 | 2.5851e-05 | -0.00085242 | 0.022804 | 0.022794 | 0.022804 | 0.98332 | -0.11763 | 0.98335 | -0.11791 | 10.3655
13 | 0.63604 | 0.29249 | -0.63573 | -0.30518 | 0.00031488 | -0.012693 | 0.020552 | 0.020712 | 0.020712 | 0.98332 | -0.11763 | 0.98287 | -0.1136 | 9.4145
14 | 0.070807 | 0.029607 | -0.070806 | -0.033895 | 1.2872e-06 | -0.0042887 | 0.0022531 | 0.0023046 | 0.0023046 | 0.98332 | -0.11763 | 0.9833 | -0.1175 | 1.0475
15 | -0.95758 | -0.44266 | 0.95765 | 0.44266 | 7.3748e-05 | -3.6323e-06 | 0.030969 | 0.030969 | 0.030969 | 0.98335 | -0.11791 | 0.98343 | -0.11731 | 14.7472
16 | 0.63573 | 0.30518 | -0.63571 | -0.30611 | 2.3186e-05 | -0.00092637 | 0.020712 | 0.020724 | 0.020724 | 0.98287 | -0.1136 | 0.98283 | -0.11329 | 9.4199
17 | 0.070806 | 0.033895 | -0.070806 | -0.034293 | 1.2233e-07 | -0.00039737 | 0.0023046 | 0.0023097 | 0.0023097 | 0.9833 | -0.1175 | 0.9833 | -0.11749 | 1.0498
18 | 0.30506 | 0.14597 | -0.30484 | -0.14732 | 0.00022808 | -0.0013492 | 0.0099332 | 0.0099522 | 0.0099522 | 0.98283 | -0.11329 | 0.98206 | -0.11836 | 4.7391
19 | -0.97466 | -0.44052 | 0.97468 | 0.44024 | 1.6126e-05 | -0.00027866 | 0.031384 | 0.031381 | 0.031384 | 0.98382 | -0.1205 | 0.98383 | -0.12063 | 14.2656
20 | 0.95807 | 0.43528 | -0.95765 | -0.44266 | 0.00041484 | -0.0073841 | 0.030877 | 0.030969 | 0.030969 | 0.98383 | -0.12063 | 0.98343 | -0.11731 | 14.0766
21 | 0.30484 | 0.14732 | -0.30483 | -0.14764 | 1.8301e-06 | -0.00031803 | 0.0099522 | 0.0099562 | 0.0099562 | 0.98206 | -0.11836 | 0.98205 | -0.1183 | 4.5256
22 | -3.4873 | -1.5989 | 3.4905 | 1.5953 | 0.0032246 | -0.0036234 | 0.11152 | 0.11146 | 0.11152 | 0.9931 | -0.086212 | 0.99396 | -0.093267 | 50.6892
23 | 0.35152 | 0.16298 | -0.3515 | -0.1658 | 2.0446e-05 | -0.002828 | 0.011263 | 0.011298 | 0.011298 | 0.9931 | -0.086212 | 0.99304 | -0.085745 | 5.1353
24 | -0.32749 | -0.15861 | 0.3275 | 0.15847 | 9.2928e-07 | -0.00014759 | 0.010554 | 0.010552 | 0.010554 | 0.99535 | -0.07552 | 0.99535 | -0.075545 | 4.797
25 | -7.8361 | -3.62 | 7.8364 | 3.6156 | 0.0003604 | -0.0044322 | 0.25034 | 0.25029 | 0.25034 | 0.99535 | -0.075545 | 0.9954 | -0.075324 | 19.6194
26 | 7.5086 | 3.4615 | -7.5062 | -3.4938 | 0.002404 | -0.032266 | 0.23979 | 0.2402 | 0.2402 | 0.99535 | -0.075545 | 0.99502 | -0.077053 | 18.8247
27 | 0.095022 | 0.041585 | -0.095022 | -0.042172 | 3.0332e-07 | -0.00058696 | 0.0030152 | 0.0030221 | 0.0030221 | 0.99304 | -0.085745 | 0.99304 | -0.085722 | 1.3737
28 | 0.095022 | 0.042172 | -0.095021 | -0.044079 | 9.9498e-07 | -0.0019067 | 0.0030221 | 0.003045 | 0.003045 | 0.99304 | -0.085722 | 0.99303 | -0.085644 | 1.3841
29 | 0.095021 | 0.044079 | -0.09502 | -0.04602 | 1.0289e-06 | -0.0019415 | 0.003045 | 0.0030692 | 0.0030692 | 0.99303 | -0.085644 | 0.99302 | -0.085554 | 1.3951
30 | -6.9209 | -3.2486 | 6.9259 | 3.2427 | 0.0050092 | -0.005893 | 0.22205 | 0.22192 | 0.22205 | 0.99396 | -0.093267 | 0.9948 | -0.078 | 52.7424
31 | 0.068339 | 0.032886 | -0.068339 | -0.033098 | 5.8371e-08 | -0.00021233 | 0.0022026 | 0.0022053 | 0.0022053 | 0.99396 | -0.093267 | 0.99396 | -0.09326 | 1.0024
32 | 3.3621 | 1.6204 | -3.3607 | -1.6221 | 0.0013646 | -0.0016462 | 0.10839 | 0.10842 | 0.10842 | 0.99396 | -0.093267 | 0.99358 | -0.089763 | 49.2816
33 | 0.18938 | 0.090674 | -0.18938 | -0.091719 | 2.2084e-06 | -0.0010448 | 0.0061004 | 0.0061135 | 0.0061135 | 0.99358 | -0.089763 | 0.99357 | -0.089663 | 2.7789
34 | 0.6552 | 0.31418 | -0.65517 | -0.31526 | 2.7294e-05 | -0.0010724 | 0.021112 | 0.021125 | 0.021125 | 0.99358 | -0.089763 | 0.99355 | -0.089407 | 9.6024
35 | 2.5161 | 1.2172 | -2.5156 | -1.2184 | 0.00048932 | -0.0011644 | 0.081208 | 0.081224 | 0.081224 | 0.99358 | -0.089763 | 0.99341 | -0.088071 | 36.9201
36 | 0.65517 | 0.31526 | -0.65512 | -0.31729 | 5.1842e-05 | -0.0020329 | 0.021125 | 0.021151 | 0.021151 | 0.99355 | -0.089407 | 0.99347 | -0.088722 | 9.6141
37 | -7.2002 | -3.3727 | 7.2017 | 3.3507 | 0.0015046 | -0.021936 | 0.23072 | 0.23044 | 0.23072 | 0.9948 | -0.078 | 0.99502 | -0.077053 | 18.0818
38 | 0.2743 | 0.12997 | -0.2743 | -0.1315 | 6.7034e-06 | -0.0015239 | 0.0088082 | 0.0088272 | 0.0088272 | 0.9948 | -0.078 | 0.99478 | -0.077794 | 4.0124
39 | -8.282 | -3.813 | 8.2826 | 3.806 | 0.00063384 | -0.006952 | 0.26442 | 0.26433 | 0.26442 | 0.9954 | -0.075324 | 0.99548 | -0.074951 | 20.7224
40 | 0.44552 | 0.19742 | -0.44551 | -0.19893 | 1.7128e-05 | -0.0015126 | 0.014132 | 0.01415 | 0.01415 | 0.9954 | -0.075324 | 0.99536 | -0.075052 | 6.4319
41 | 0.16826 | 0.077969 | -0.16826 | -0.078284 | 5.1536e-07 | -0.00031488 | 0.0053801 | 0.005384 | 0.005384 | 0.99502 | -0.077053 | 0.99501 | -0.077029 | 2.4473
42 | 0.13619 | 0.065071 | -0.13619 | -0.065961 | 9.6661e-07 | -0.00088997 | 0.0043791 | 0.0043903 | 0.0043903 | 0.99502 | -0.077053 | 0.99501 | -0.076992 | 1.9956
43 | 0.1817 | 0.086648 | -0.18169 | -0.087852 | 2.3286e-06 | -0.0012039 | 0.0058415 | 0.0058566 | 0.0058566 | 0.99478 | -0.077794 | 0.99477 | -0.077685 | 2.6621
44 | 0.16826 | 0.078284 | -0.16825 | -0.079098 | 1.3368e-06 | -0.00081467 | 0.005384 | 0.005394 | 0.005394 | 0.99501 | -0.077029 | 0.99501 | -0.076965 | 2.4518
45 | -8.6904 | -3.9925 | 8.692 | 3.9762 | 0.0016397 | -0.01631 | 0.2772 | 0.27699 | 0.2772 | 0.99597 | -0.055049 | 0.99617 | -0.054114 | 21.7238
46 | 8.6904 | 3.9925 | -8.6888 | -3.9886 | 0.0015763 | 0.0039238 | 0.2772 | 0.2772 | 0.2772 | 0.99597 | -0.055049 | 0.99564 | -0.074189 | 21.4883
47 | -8.692 | -3.9762 | 8.6929 | 3.9672 | 0.00090354 | -0.0090016 | 0.27699 | 0.27687 | 0.27699 | 0.99617 | -0.054114 | 0.99627 | -0.053591 | 21.7075
48 | 8.6095 | 3.9501 | -8.6081 | -3.9637 | 0.0013406 | -0.013563 | 0.27464 | 0.27482 | 0.27482 | 0.99564 | -0.074189 | 0.99548 | -0.074951 | 21.5374
49 | -8.8084 | -4.0231 | 8.8117 | 4.0312 | 0.0032579 | 0.0081242 | 0.28059 | 0.28058 | 0.28059 | 0.99627 | -0.053591 | 0.99695 | -0.014474 | 21.7511
50 | 0.27956 | 0.11856 | -0.27954 | -0.12306 | 1.9822e-05 | -0.004496 | 0.0088068 | 0.0088586 | 0.0088586 | 0.99536 | -0.075052 | 0.99529 | -0.074588 | 4.0267
51 | 0.17866 | 0.085871 | -0.17865 | -0.086526 | 1.2174e-06 | -0.00065559 | 0.0057396 | 0.0057479 | 0.0057479 | 0.99695 | -0.014474 | 0.99695 | -0.014415 | 2.6127
52 | 0.69657 | 0.31845 | -0.6965 | -0.3212 | 7.6842e-05 | -0.0027499 | 0.022178 | 0.022211 | 0.022211 | 0.99695 | -0.014474 | 0.99685 | -0.013625 | 10.096
53 | -9.9199 | -4.5484 | 9.9203 | 4.5451 | 0.00044176 | -0.0033284 | 0.31599 | 0.31595 | 0.31599 | 0.99695 | -0.014474 | 0.997 | -0.014253 | 24.7643
54 | 0.079675 | 0.029011 | -0.079671 | -0.038549 | 3.3923e-06 | -0.0095381 | 0.0024593 | 0.0025672 | 0.0025672 | 0.99529 | -0.074588 | 0.99525 | -0.074324 | 1.1669
55 | 0.19987 | 0.094046 | -0.19986 | -0.096139 | 4.8715e-06 | -0.0020928 | 0.0064066 | 0.0064327 | 0.0064327 | 0.99529 | -0.074588 | 0.99527 | -0.074384 | 2.924
56 | 0.074624 | 0.035995 | -0.074623 | -0.036142 | 4.7844e-08 | -0.00014631 | 0.0024043 | 0.0024061 | 0.0024061 | 0.99477 | -0.077685 | 0.99477 | -0.077679 | 1.0937
57 | 0.094018 | 0.043144 | -0.094018 | -0.043239 | 4.8596e-08 | -9.5493e-05 | 0.0030012 | 0.0030023 | 0.0030023 | 0.99501 | -0.076965 | 0.99501 | -0.076961 | 1.3647
58 | -0.19986 | -0.096797 | 0.19986 | 0.096139 | 1.54e-06 | -0.00065802 | 0.006441 | 0.0064327 | 0.006441 | 0.99526 | -0.074317 | 0.99527 | -0.074384 | 2.9277
59 | 0.079671 | 0.038549 | -0.079671 | -0.038586 | 1.4027e-08 | -3.7623e-05 | 0.0025672 | 0.0025676 | 0.0025676 | 0.99525 | -0.074324 | 0.99525 | -0.074323 | 1.1671
60 | 0.6965 | 0.3212 | -0.69647 | -0.32233 | 3.1471e-05 | -0.0011236 | 0.022211 | 0.022225 | 0.022225 | 0.99685 | -0.013625 | 0.99681 | -0.013272 | 10.1022
61 | 2.194 | 1.0491 | -2.1939 | -1.0494 | 7.3703e-05 | -0.00024237 | 0.070415 | 0.070419 | 0.070419 | 0.997 | -0.014253 | 0.99697 | -0.013968 | 32.0085
62 | -12.1143 | -5.5942 | 12.1176 | 5.5784 | 0.0032513 | -0.015793 | 0.38636 | 0.38614 | 0.38636 | 0.997 | -0.014253 | 0.99728 | -0.012959 | 30.2787
63 | -0.26276 | -0.12726 | 0.26277 | 0.12718 | 9.4969e-06 | -8.2542e-05 | 0.0084543 | 0.0084532 | 0.0084543 | 0.99689 | -0.006713 | 0.99693 | -0.0064744 | 4.0258
64 | -0.26277 | -0.12718 | 0.26279 | 0.12181 | 2.1425e-05 | -0.0053662 | 0.0084532 | 0.0083866 | 0.0084532 | 0.99693 | -0.0064744 | 0.99701 | -0.0071502 | 3.8423
65 | -0.52432 | -0.24834 | 0.52433 | 0.24767 | 1.0585e-05 | -0.00066407 | 0.016798 | 0.01679 | 0.016798 | 0.99701 | -0.0071502 | 0.99703 | -0.0073169 | 7.6354
66 | 0.26153 | 0.12652 | -0.26151 | -0.12666 | 1.4997e-05 | -0.00013173 | 0.0084119 | 0.0084137 | 0.0084137 | 0.99701 | -0.0071502 | 0.99695 | -0.007529 | 4.0065
67 | -0.62553 | -0.29668 | 0.62557 | 0.29484 | 4.188e-05 | -0.0018428 | 0.020045 | 0.020022 | 0.020045 | 0.99703 | -0.0073169 | 0.99709 | -0.0078692 | 9.1114
68 | -0.7286 | -0.34474 | 0.72867 | 0.3426 | 6.605e-05 | -0.0021396 | 0.023337 | 0.02331 | 0.023337 | 0.99709 | -0.0078692 | 0.99717 | -0.0086128 | 10.6075
69 | -0.092562 | -0.043971 | 0.092562 | 0.043591 | 1.8717e-07 | -0.00037965 | 0.0029649 | 0.0029602 | 0.0029649 | 0.99775 | -0.011482 | 0.99775 | -0.011499 | 1.3477
70 | 0.092562 | 0.043971 | -0.092562 | -0.04483 | 4.2577e-07 | -0.00085913 | 0.0029649 | 0.0029756 | 0.0029756 | 0.99775 | -0.011482 | 0.99775 | -0.011443 | 1.3526
71 | -0.092562 | -0.043591 | 0.092563 | 0.042356 | 6.0488e-07 | -0.0012352 | 0.0029602 | 0.0029451 | 0.0029602 | 0.99775 | -0.011499 | 0.99776 | -0.01155 | 1.3455
72 | -0.73683 | -0.35439 | 0.73685 | 0.35358 | 2.567e-05 | -0.0008095 | 0.023656 | 0.023646 | 0.023656 | 0.99776 | -0.01155 | 0.99779 | -0.011849 | 10.7526
73 | -0.25471 | -0.12336 | 0.25471 | 0.1232 | 5.9047e-07 | -0.00015587 | 0.0081985 | 0.0081966 | 0.0081985 | 0.99648 | -0.0095243 | 0.99648 | -0.0095444 | 3.7266
74 | -0.25471 | -0.1232 | 0.25472 | 0.12062 | 9.756e-06 | -0.0025863 | 0.0081966 | 0.0081642 | 0.0081966 | 0.99648 | -0.0095444 | 0.99652 | -0.0098694 | 3.7257
75 | 0.87671 | 0.42174 | -0.87668 | -0.42253 | 3.619e-05 | -0.00079819 | 0.028183 | 0.028193 | 0.028193 | 0.99652 | -0.0098694 | 0.99648 | -0.0095144 | 12.8149
76 | -1.1314 | -0.54235 | 1.1316 | 0.5406 | 0.00013304 | -0.0017504 | 0.036347 | 0.036324 | 0.036347 | 0.99652 | -0.0098694 | 0.99663 | -0.010867 | 16.5212
77 | 0.56788 | 0.27298 | -0.56784 | -0.27502 | 3.8584e-05 | -0.0020421 | 0.018253 | 0.018279 | 0.018279 | 0.99648 | -0.0095144 | 0.99642 | -0.0089274 | 8.3086
78 | -1.3699 | -0.65606 | 1.3701 | 0.65461 | 0.00016292 | -0.0014477 | 0.043996 | 0.043977 | 0.043996 | 0.99663 | -0.010867 | 0.99674 | -0.011874 | 19.9983
79 | -1.7955 | -0.86064 | 1.796 | 0.85841 | 0.00044323 | -0.0022385 | 0.057667 | 0.057637 | 0.057667 | 0.99674 | -0.011874 | 0.99697 | -0.013968 | 26.2123
80 | -0.13314 | -0.064484 | 0.13314 | 0.064245 | 2.4528e-07 | -0.00023883 | 0.0042785 | 0.0042755 | 0.0042785 | 0.99813 | -0.0030569 | 0.99813 | -0.0030728 | 1.9448
81 | 0.75093 | 0.35651 | -0.75088 | -0.35804 | 5.0123e-05 | -0.001529 | 0.024041 | 0.02406 | 0.02406 | 0.99813 | -0.0030728 | 0.99807 | -0.0025141 | 10.9366
82 | 0.28621 | 0.13427 | -0.28621 | -0.13548 | 5.706e-06 | -0.0012124 | 0.0091433 | 0.0091583 | 0.0091583 | 0.99813 | -0.0030728 | 0.99812 | -0.0029096 | 4.1628
83 | -1.1703 | -0.55502 | 1.1708 | 0.54828 | 0.00054212 | -0.0067416 | 0.03746 | 0.037375 | 0.03746 | 0.99813 | -0.0030728 | 0.99857 | -0.0068649 | 17.0272
84 | 0.31579 | 0.14891 | -0.31578 | -0.15072 | 1.0397e-05 | -0.0018093 | 0.010098 | 0.010121 | 0.010121 | 0.99807 | -0.0025141 | 0.99804 | -0.0022404 | 4.6003
85 | 0.43509 | 0.20913 | -0.43508 | -0.20965 | 5.6934e-06 | -0.00051837 | 0.013962 | 0.013969 | 0.013969 | 0.99807 | -0.0025141 | 0.99806 | -0.0024017 | 6.3495
86 | 0.28621 | 0.13548 | -0.2862 | -0.13663 | 5.4353e-06 | -0.0011512 | 0.0091583 | 0.0091726 | 0.0091726 | 0.99812 | -0.0029096 | 0.9981 | -0.002751 | 4.1694
87 | 0.3664 | 0.17734 | -0.3664 | -0.17745 | 8.8028e-07 | -0.00011309 | 0.011768 | 0.011769 | 0.011769 | 0.99857 | -0.0068649 | 0.99856 | -0.006844 | 5.3496
88 | -20.3091 | -9.3288 | 20.3325 | 9.2965 | 0.023384 | -0.032357 | 0.64609 | 0.64554 | 0.64609 | 0.99857 | -0.0068649 | 0.99976 | -0.0011533 | 50.6342
89 | 4.6318 | 2.1336 | -4.6293 | -2.1398 | 0.0024769 | -0.0062612 | 0.14742 | 0.14752 | 0.14752 | 0.99857 | -0.0068649 | 0.99798 | -0.013568 | 40.7519
90 | 14.14 | 6.4696 | -14.129 | -6.5077 | 0.011064 | -0.038086 | 0.44953 | 0.45006 | 0.45006 | 0.99857 | -0.0068649 | 0.99775 | -0.010719 | 35.2715
91 | 0.09234 | 0.043985 | -0.09234 | -0.044722 | 3.6336e-07 | -0.00073721 | 0.0029584 | 0.0029676 | 0.0029676 | 0.99804 | -0.0022404 | 0.99804 | -0.0022067 | 1.3489
92 | 0.22344 | 0.10673 | -0.22344 | -0.10771 | 2.8325e-06 | -0.00098115 | 0.0071622 | 0.0071745 | 0.0071745 | 0.99804 | -0.0022404 | 0.99803 | -0.0021322 | 3.2611
93 | 0.34318 | 0.16514 | -0.34318 | -0.16558 | 2.9988e-06 | -0.00043918 | 0.011015 | 0.011021 | 0.011021 | 0.99806 | -0.0024017 | 0.99805 | -0.0023265 | 5.0095
94 | 0.092964 | 0.044522 | -0.092964 | -0.045024 | 2.5139e-07 | -0.00050268 | 0.0029814 | 0.0029877 | 0.0029877 | 0.99803 | -0.0021322 | 0.99803 | -0.0021089 | 1.358
95 | 0.078716 | 0.036138 | -0.078715 | -0.038123 | 7.0619e-07 | -0.0019854 | 0.0025051 | 0.0025296 | 0.0025296 | 0.9981 | -0.002751 | 0.99809 | -0.0026774 | 1.1498
96 | -12.9248 | -5.9488 | 12.9281 | 5.9349 | 0.0032922 | -0.013872 | 0.41176 | 0.41157 | 0.41176 | 0.99749 | -0.011965 | 0.99775 | -0.010719 | 32.27
97 | 12.4845 | 5.7423 | -12.482 | -5.7539 | 0.0025577 | -0.011639 | 0.39769 | 0.39785 | 0.39785 | 0.99749 | -0.011965 | 0.99728 | -0.012959 | 31.1794
98 | 0.44032 | 0.20649 | -0.4403 | -0.20788 | 1.5449e-05 | -0.0013815 | 0.014075 | 0.014092 | 0.014092 | 0.99749 | -0.011965 | 0.99746 | -0.011679 | 6.4053
99 | 1.2009 | 0.57281 | -1.2004 | -0.57819 | 0.00045982 | -0.0053768 | 0.038494 | 0.038563 | 0.038563 | 0.99775 | -0.010719 | 0.9974 | -0.0074586 | 17.5286
100 | 0.36437 | 0.17556 | -0.36436 | -0.17591 | 2.6934e-06 | -0.00034859 | 0.011707 | 0.011712 | 0.011712 | 0.99728 | -0.012959 | 0.99727 | -0.012895 | 5.3236
101 | 0.29535 | 0.13767 | -0.29534 | -0.13867 | 5.0337e-06 | -0.0010043 | 0.0094308 | 0.0094431 | 0.0094431 | 0.99746 | -0.011679 | 0.99744 | -0.011542 | 4.2923
102 | 0.85318 | 0.41002 | -0.85316 | -0.4104 | 1.6078e-05 | -0.00037626 | 0.027397 | 0.027402 | 0.027402 | 0.9974 | -0.0074586 | 0.99738 | -0.0072971 | 12.4553
103 | 0.6141 | 0.28857 | -0.614 | -0.29314 | 9.9071e-05 | -0.0045704 | 0.019592 | 0.019649 | 0.019649 | 0.99976 | -0.0011533 | 0.99961 | 0.00018337 | 8.9313
104 | -20.9466 | -9.5851 | 20.9514 | 9.5789 | 0.0048235 | -0.0061511 | 0.66514 | 0.66503 | 0.66514 | 0.99976 | -0.0011533 | 1 | 0 | 52.1266
105 | 0.088938 | 0.041067 | -0.088937 | -0.043074 | 9.1262e-07 | -0.0020068 | 0.0028336 | 0.0028585 | 0.0028585 | 0.99798 | -0.013568 | 0.99797 | -0.013483 | 1.2993
106 | 0.95816 | 0.45707 | -0.95814 | -0.4574 | 1.7905e-05 | -0.00033287 | 0.030708 | 0.030712 | 0.030712 | 0.99798 | -0.013568 | 0.99796 | -0.01341 | 13.9599
107 | 2.3952 | 1.1477 | -2.3949 | -1.1485 | 0.00030451 | -0.00082842 | 0.076826 | 0.076837 | 0.076837 | 0.99798 | -0.013568 | 0.99786 | -0.012485 | 34.9261
108 | 0.087574 | 0.041337 | -0.087574 | -0.042083 | 3.2966e-07 | -0.00074577 | 0.0028012 | 0.0028105 | 0.0028105 | 0.99798 | -0.013568 | 0.99797 | -0.013536 | 1.2775
109 | 1.0995 | 0.45272 | -1.0987 | -0.46478 | 0.00082133 | -0.012066 | 0.034394 | 0.034531 | 0.034531 | 0.99798 | -0.013568 | 0.99726 | -0.0091638 | 15.6961
110 | 0.26436 | 0.12747 | -0.26436 | -0.12803 | 2.2796e-06 | -0.00056067 | 0.0084955 | 0.0085026 | 0.0085026 | 0.99727 | -0.012895 | 0.99726 | -0.012821 | 3.8648
111 | 0.1554 | 0.073489 | -0.1554 | -0.075218 | 2.3953e-06 | -0.0017287 | 0.0049644 | 0.004986 | 0.004986 | 0.99961 | 0.00018337 | 0.9996 | 0.00031404 | 2.2663
112 | 0.32799 | 0.15826 | -0.32799 | -0.15856 | 1.8736e-06 | -0.00030206 | 0.010517 | 0.010521 | 0.010521 | 0.99961 | 0.00018337 | 0.99961 | 0.00023283 | 4.7821
113 | 0.13061 | 0.061395 | -0.13061 | -0.063256 | 1.8194e-06 | -0.0018609 | 0.0041678 | 0.0041909 | 0.0041909 | 0.99961 | 0.00018337 | 0.9996 | 0.00030076 | 1.905
114 | 0.1554 | 0.075218 | -0.1554 | -0.075264 | 1.7393e-06 | -4.5746e-05 | 0.004986 | 0.0049865 | 0.0049865 | 0.9996 | 0.00031404 | 0.99958 | 0.00024017 | 2.3745
115 | 0.32799 | 0.15856 | -0.32799 | -0.15885 | 1.8082e-06 | -0.00029131 | 0.010521 | 0.010524 | 0.010524 | 0.99961 | 0.00023283 | 0.9996 | 0.00028075 | 4.7838
116 | 0.13409 | 0.064311 | -0.13409 | -0.06494 | 6.5545e-07 | -0.0006298 | 0.0043013 | 0.0043092 | 0.0043092 | 0.99805 | -0.0023265 | 0.99805 | -0.0022843 | 1.9587
117 | 0.29534 | 0.13867 | -0.29534 | -0.13976 | 5.4771e-06 | -0.0010897 | 0.0094431 | 0.0094566 | 0.0094566 | 0.99744 | -0.011542 | 0.99742 | -0.01139 | 4.2984
118 | 0.85316 | 0.4104 | -0.85313 | -0.41114 | 3.1467e-05 | -0.00073598 | 0.027402 | 0.027411 | 0.027411 | 0.99738 | -0.0072971 | 0.99735 | -0.0069799 | 12.4596
119 | 0.19394 | 0.091681 | -0.19393 | -0.093925 | 4.8896e-06 | -0.002244 | 0.0062095 | 0.0062375 | 0.0062375 | 0.99726 | -0.0091638 | 0.99724 | -0.00895 | 2.8352
120 | 0.90473 | 0.3731 | -0.90464 | -0.37501 | 8.7194e-05 | -0.0019051 | 0.028328 | 0.02835 | 0.02835 | 0.99726 | -0.0091638 | 0.99717 | -0.0086128 | 12.8863
121 | 0.17597 | 0.032401 | -0.17594 | -0.055468 | 3.5784e-05 | -0.023067 | 0.0051799 | 0.0053415 | 0.0053415 | 0.99717 | -0.0086128 | 0.99697 | -0.0091275 | 2.4279
122 | 0.077238 | 0.0088818 | -0.07723 | -0.037325 | 8.721e-06 | -0.028443 | 0.0022512 | 0.002484 | 0.002484 | 0.99697 | -0.0091275 | 0.99685 | -0.0091125 | 1.1291
123 | 0.098697 | 0.046586 | -0.098697 | -0.047801 | 6.8601e-07 | -0.0012151 | 0.0031602 | 0.0031754 | 0.0031754 | 0.99697 | -0.0091275 | 0.99696 | -0.0090687 | 1.4433
124 | 0.95814 | 0.4574 | -0.95796 | -0.46067 | 0.00017592 | -0.0032648 | 0.030712 | 0.030753 | 0.030753 | 0.99796 | -0.01341 | 0.99779 | -0.011849 | 13.9788
125 | 0.072361 | 0.030444 | -0.07236 | -0.034752 | 1.2755e-06 | -0.0043085 | 0.0022711 | 0.0023223 | 0.0023223 | 0.99786 | -0.012485 | 0.99784 | -0.012356 | 1.0556
126 | 2.3225 | 1.118 | -2.322 | -1.1196 | 0.00054034 | -0.0015693 | 0.074569 | 0.074591 | 0.074591 | 0.99786 | -0.012485 | 0.99764 | -0.010482 | 33.9049
127 | 0.087574 | 0.042083 | -0.087574 | -0.042414 | 1.4692e-07 | -0.00033077 | 0.0028105 | 0.0028146 | 0.0028146 | 0.99797 | -0.013536 | 0.99797 | -0.013521 | 1.2794
128 | 0.07236 | 0.034752 | -0.07236 | -0.035045 | 8.8947e-08 | -0.00029325 | 0.0023223 | 0.002326 | 0.002326 | 0.99784 | -0.012356 | 0.99784 | -0.012345 | 1.0573
129 | 1.0668 | 0.51169 | -1.0667 | -0.51314 | 9.744e-05 | -0.00145 | 0.034236 | 0.034254 | 0.034254 | 0.99764 | -0.010482 | 0.99756 | -0.0097005 | 15.5701
130 | 0.39797 | 0.19095 | -0.39797 | -0.1913 | 3.2105e-06 | -0.00034828 | 0.012781 | 0.012786 | 0.012786 | 0.99697 | -0.013968 | 0.99696 | -0.013899 | 5.8116
131 | -0.06876 | -0.033302 | 0.06876 | 0.033299 | 4.0216e-10 | -2.502e-06 | 0.0022114 | 0.0022114 | 0.0022114 | 0.9973 | -0.0065423 | 0.9973 | -0.0065424 | 1.0052
132 | -0.13752 | -0.066602 | 0.13752 | 0.065702 | 9.876e-07 | -0.00090006 | 0.0044229 | 0.0044116 | 0.0044229 | 0.9973 | -0.0065424 | 0.99731 | -0.006604 | 2.0104
133 | -0.41475 | -0.19997 | 0.41475 | 0.19984 | 1.2672e-06 | -0.00012654 | 0.013328 | 0.013326 | 0.013328 | 0.99731 | -0.006604 | 0.99731 | -0.0066303 | 6.058
134 | -0.68636 | -0.33139 | 0.68639 | 0.33038 | 2.7832e-05 | -0.0010096 | 0.022061 | 0.022049 | 0.022061 | 0.99731 | -0.0066303 | 0.99735 | -0.0069799 | 10.0279
135 | 0.39797 | 0.1913 | -0.39796 | -0.19193 | 5.7599e-06 | -0.00062423 | 0.012786 | 0.012793 | 0.012793 | 0.99696 | -0.013899 | 0.99695 | -0.013775 | 5.8152
136 | 0.61497 | 0.28398 | -0.61489 | -0.28753 | 7.7485e-05 | -0.003547 | 0.019617 | 0.01966 | 0.01966 | 0.99681 | -0.013272 | 0.99669 | -0.012275 | 8.9364
137 | 0.081499 | 0.038347 | -0.081499 | -0.039472 | 4.33e-07 | -0.0011248 | 0.0026084 | 0.0026225 | 0.0026225 | 0.99681 | -0.013272 | 0.9968 | -0.013228 | 1.192
138 | 0.26028 | 0.12036 | -0.26027 | -0.12278 | 9.4244e-06 | -0.0024158 | 0.0083055 | 0.0083351 | 0.0083351 | 0.99669 | -0.012275 | 0.99666 | -0.011984 | 3.7887
139 | 0.35461 | 0.16716 | -0.35458 | -0.17168 | 3.3022e-05 | -0.0045177 | 0.011355 | 0.011411 | 0.011411 | 0.99669 | -0.012275 | 0.9966 | -0.011488 | 5.187
140 | 0.077969 | 0.034487 | -0.077968 | -0.036414 | 6.6761e-07 | -0.0019269 | 0.0024694 | 0.0024925 | 0.0024925 | 0.99666 | -0.011984 | 0.99665 | -0.01192 | 1.1329
141 | 0.35458 | 0.17168 | -0.35458 | -0.17173 | 3.5699e-07 | -4.8591e-05 | 0.011411 | 0.011412 | 0.011412 | 0.9966 | -0.011488 | 0.9966 | -0.011479 | 5.1872
142 | 0.10284 | 0.048993 | -0.10284 | -0.049807 | 4.9999e-07 | -0.00081423 | 0.0032984 | 0.0033087 | 0.0033087 | 0.99695 | -0.013775 | 0.99694 | -0.013733 | 1.5039
143 | 0.077968 | 0.036414 | -0.077968 | -0.036564 | 5.2383e-08 | -0.00014963 | 0.0024925 | 0.0024943 | 0.0024943 | 0.99665 | -0.01192 | 0.99665 | -0.011915 | 1.1338
144 | 0.10181 | 0.048454 | -0.10181 | -0.049308 | 5.1264e-07 | -0.00085361 | 0.0032632 | 0.0032739 | 0.0032739 | 0.99742 | -0.01139 | 0.99742 | -0.011347 | 1.4881
145 | 0.19353 | 0.09131 | -0.19353 | -0.091578 | 5.7839e-07 | -0.00026798 | 0.0061933 | 0.0061967 | 0.0061967 | 0.99742 | -0.01139 | 0.99742 | -0.011365 | 2.8167
146 | 0.19353 | 0.091578 | -0.19353 | -0.092466 | 1.9197e-06 | -0.00088738 | 0.0061967 | 0.0062077 | 0.0062077 | 0.99742 | -0.011365 | 0.99741 | -0.011282 | 2.8217
147 | 0.12247 | 0.058049 | -0.12247 | -0.059313 | 1.0978e-06 | -0.0012641 | 0.0039225 | 0.0039383 | 0.0039383 | 0.99741 | -0.011282 | 0.9974 | -0.011206 | 1.7901
148 | 0.094018 | 0.043239 | -0.094017 | -0.045275 | 1.0452e-06 | -0.0020358 | 0.0030023 | 0.0030275 | 0.0030275 | 0.99501 | -0.076961 | 0.995 | -0.07687 | 1.3761
149 | 0.094017 | 0.045275 | -0.094016 | -0.045534 | 1.3431e-07 | -0.00025912 | 0.0030275 | 0.0030307 | 0.0030307 | 0.995 | -0.07687 | 0.995 | -0.076858 | 1.3776
150 | 0.07723 | 0.037325 | -0.077229 | -0.037404 | 7.3625e-07 | -7.8957e-05 | 0.002484 | 0.002485 | 0.002485 | 0.99685 | -0.0091125 | 0.99684 | -0.0091756 | 1.1833
151 | 0.61936 | 0.29648 | -0.61931 | -0.29848 | 4.4662e-05 | -0.0019972 | 0.019871 | 0.019896 | 0.019896 | 0.99756 | -0.0097005 | 0.99749 | -0.0090838 | 9.0436
152 | -0.61928 | -0.29993 | 0.61931 | 0.29848 | 3.2503e-05 | -0.0014501 | 0.019914 | 0.019896 | 0.019914 | 0.99744 | -0.0086291 | 0.99749 | -0.0090838 | 9.052
153 | -0.077968 | -0.037761 | 0.077968 | 0.036564 | 4.2201e-07 | -0.0011978 | 0.0025092 | 0.0024943 | 0.0025092 | 0.99664 | -0.011869 | 0.99665 | -0.011915 | 1.1406

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.222 | 9.7137

## res_load
| p_mw | q_mvar
0 | 0.052374 | 0.025366
1 | 0.084639 | 0.040992
2 | 0.31733 | 0.15369
3 | 0.27859 | 0.13493
4 | 0.2507 | 0.12142
5 | 0.33064 | 0.16014
6 | 0.32625 | 0.15801
7 | 0.33828 | 0.16383
8 | 0.070806 | 0.034293
9 | 0.75837 | 0.3673
10 | 0.30483 | 0.14764
11 | 0.32749 | 0.15861
12 | 0.25648 | 0.12422
13 | 0.09502 | 0.04602
14 | 0.18938 | 0.091719
15 | 2.5156 | 1.2184
16 | 0.068339 | 0.033098
17 | 0.65512 | 0.31729
18 | 0.092601 | 0.044849
19 | 0.13619 | 0.065961
20 | 0.079355 | 0.038433
21 | 0.11546 | 0.055919
22 | 0.32555 | 0.15767
23 | 0.16595 | 0.080371
24 | 0.233 | 0.11285
25 | 0.10707 | 0.051856
26 | 0.074237 | 0.035955
27 | 0.19986 | 0.096797
28 | 0.079671 | 0.038586
29 | 0.17865 | 0.086526
30 | 0.26276 | 0.12726
31 | 0.1012 | 0.049012
32 | 0.26151 | 0.12666
33 | 0.10304 | 0.049903
34 | 0.092562 | 0.04483
35 | 0.64426 | 0.31203
36 | 0.25471 | 0.12336
37 | 0.3088 | 0.14956
38 | 0.23838 | 0.11545
39 | 0.56784 | 0.27502
40 | 0.42541 | 0.20604
41 | 0.074623 | 0.036142
42 | 0.13314 | 0.064484
43 | 0.091904 | 0.044511
44 | 0.09234 | 0.044722
45 | 0.13047 | 0.06319
46 | 0.20749 | 0.10049
47 | 0.14496 | 0.070205
48 | 0.34721 | 0.16816
49 | 0.3664 | 0.17745
50 | 0.1 | 0.048434
51 | 0.25656 | 0.12426
52 | 0.13061 | 0.063256
53 | 0.32799 | 0.15885
54 | 0.20909 | 0.10127
55 | 0.092964 | 0.045024
56 | 0.078715 | 0.038123
57 | 0.19393 | 0.093925
58 | 0.088937 | 0.043074
59 | 0.22111 | 0.10709
60 | 1.2552 | 0.60792
61 | 0.07236 | 0.035045
62 | 0.26436 | 0.12803
63 | 0.1554 | 0.075264
64 | 0.06876 | 0.033302
65 | 0.068762 | 0.033303
66 | 0.27723 | 0.13427
67 | 0.27161 | 0.13155
68 | 0.16674 | 0.080758
69 | 0.081499 | 0.039472
70 | 0.1823 | 0.08829
71 | 0.29512 | 0.14293
72 | 0.35458 | 0.17173
73 | 0.10284 | 0.049807
74 | 0.13409 | 0.06494
75 | 0.10181 | 0.049308
76 | 0.071062 | 0.034417
77 | 0.094016 | 0.045534
78 | 0.098697 | 0.047801
79 | 0.077229 | 0.037404
80 | 0.087574 | 0.042414
81 | 0.44734 | 0.21666
82 | 0.12247 | 0.059313
83 | 0.61928 | 0.29993
84 | 0.077968 | 0.037761

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1