## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_470_1_node_3 | 20 | n |  | TRUE
1 | bus_MV_470_1_node_4 | 20 | n |  | TRUE
2 | bus_MV_470_1_node_5 | 20 | n |  | TRUE
3 | bus_MV_470_1_node_6 | 20 | n |  | TRUE
4 | bus_MV_470_1_node_347 | 20 | n |  | TRUE
5 | bus_MV_470_1_node_302 | 20 | n |  | TRUE
6 | bus_MV_470_1_node_7 | 20 | n |  | TRUE
7 | bus_MV_470_1_node_8 | 20 | n |  | TRUE
8 | bus_MV_470_1_node_9 | 20 | n |  | TRUE
9 | bus_MV_470_1_node_10 | 20 | n |  | TRUE
10 | bus_MV_470_1_node_12 | 20 | n |  | TRUE
11 | bus_MV_470_1_node_13 | 20 | n |  | TRUE
12 | bus_MV_470_1_node_11 | 20 | n |  | TRUE
13 | bus_MV_470_1_node_304 | 20 | n |  | TRUE
14 | bus_MV_470_1_node_303 | 20 | n |  | TRUE
15 | bus_MV_470_1_node_14 | 20 | n |  | TRUE
16 | bus_MV_470_1_node_15 | 20 | n |  | TRUE
17 | bus_MV_470_1_node_17 | 20 | n |  | TRUE
18 | bus_MV_470_1_node_16 | 20 | n |  | TRUE
19 | bus_MV_470_1_node_21 | 20 | n |  | TRUE
20 | bus_MV_470_1_node_19 | 20 | n |  | TRUE
21 | bus_MV_470_1_node_18 | 20 | n |  | TRUE
22 | bus_MV_470_1_node_24 | 20 | n |  | TRUE
23 | bus_MV_470_1_node_23 | 20 | n |  | TRUE
24 | bus_MV_470_1_node_20 | 20 | n |  | TRUE
25 | bus_MV_470_1_node_33 | 20 | n |  | TRUE
26 | bus_MV_470_1_node_22 | 20 | n |  | TRUE
27 | bus_MV_470_1_node_27 | 20 | n |  | TRUE
28 | bus_MV_470_1_node_30 | 20 | n |  | TRUE
29 | bus_MV_470_1_node_31 | 20 | n |  | TRUE
30 | bus_MV_470_1_node_25 | 20 | n |  | TRUE
31 | bus_MV_470_1_node_26 | 20 | n |  | TRUE
32 | bus_MV_470_1_node_321 | 20 | n |  | TRUE
33 | bus_MV_470_1_node_293 | 20 | n |  | TRUE
34 | bus_MV_470_1_node_28 | 20 | n |  | TRUE
35 | bus_MV_470_1_node_32 | 20 | n |  | TRUE
36 | bus_MV_470_1_node_55 | 20 | n |  | TRUE
37 | bus_MV_470_1_node_29 | 20 | n |  | TRUE
38 | bus_MV_470_1_node_286 | 20 | n |  | TRUE
39 | bus_MV_470_1_node_80 | 20 | n |  | TRUE
40 | bus_MV_470_1_node_79 | 20 | n |  | TRUE
41 | bus_MV_470_1_node_292 | 20 | n |  | TRUE
42 | bus_MV_470_1_node_34 | 20 | n |  | TRUE
43 | bus_MV_470_1_node_36 | 20 | n |  | TRUE
44 | bus_MV_470_1_node_35 | 20 | n |  | TRUE
45 | bus_MV_470_1_node_37 | 20 | n |  | TRUE
46 | bus_MV_470_1_node_38 | 20 | n |  | TRUE
47 | bus_MV_470_1_node_45 | 20 | n |  | TRUE
48 | bus_MV_470_1_node_44 | 20 | n |  | TRUE
49 | bus_MV_470_1_node_337 | 20 | n |  | TRUE
50 | bus_MV_470_1_node_39 | 20 | n |  | TRUE
51 | bus_MV_470_1_node_40 | 20 | n |  | TRUE
52 | bus_MV_470_1_node_41 | 20 | n |  | TRUE
53 | bus_MV_470_1_node_42 | 20 | n |  | TRUE
54 | bus_MV_470_1_node_43 | 20 | n |  | TRUE
55 | bus_MV_470_1_node_85 | 20 | n |  | TRUE
56 | bus_MV_470_1_node_350 | 20 | n |  | TRUE
57 | bus_MV_470_1_node_51 | 20 | n |  | TRUE
58 | bus_MV_470_1_node_46 | 20 | n |  | TRUE
59 | bus_MV_470_1_node_47 | 20 | n |  | TRUE
60 | bus_MV_470_1_node_49 | 20 | n |  | TRUE
61 | bus_MV_470_1_node_322 | 20 | n |  | TRUE
62 | bus_MV_470_1_node_52 | 20 | n |  | TRUE
63 | bus_MV_470_1_node_53 | 20 | n |  | TRUE
64 | bus_MV_470_1_node_54 | 20 | n |  | TRUE
65 | bus_MV_470_1_node_59 | 20 | n |  | TRUE
66 | bus_MV_470_1_node_90 | 20 | n |  | TRUE
67 | bus_MV_470_1_node_56 | 20 | n |  | TRUE
68 | bus_MV_470_1_node_57 | 20 | n |  | TRUE
69 | bus_MV_470_1_node_58 | 20 | n |  | TRUE
70 | bus_MV_470_1_node_308 | 20 | n |  | TRUE
71 | bus_MV_470_1_node_325 | 20 | n |  | TRUE
72 | bus_MV_470_1_node_60 | 20 | n |  | TRUE
73 | bus_MV_470_1_node_61 | 20 | n |  | TRUE
74 | bus_MV_470_1_node_62 | 20 | n |  | TRUE
75 | bus_MV_470_1_node_63 | 20 | n |  | TRUE
76 | bus_MV_470_1_node_64 | 20 | n |  | TRUE
77 | bus_MV_470_1_node_65 | 20 | n |  | TRUE
78 | bus_MV_470_1_node_66 | 20 | n |  | TRUE
79 | bus_MV_470_1_node_67 | 20 | n |  | TRUE
80 | bus_MV_470_1_node_68 | 20 | n |  | TRUE
81 | bus_MV_470_1_node_69 | 20 | n |  | TRUE
82 | bus_MV_470_1_node_324 | 20 | n |  | TRUE
83 | bus_MV_470_1_node_71 | 20 | n |  | TRUE
84 | bus_MV_470_1_node_70 | 20 | n |  | TRUE
85 | bus_MV_470_1_node_72 | 20 | n |  | TRUE
86 | bus_MV_470_1_node_73 | 20 | n |  | TRUE
87 | bus_MV_470_1_node_74 | 20 | n |  | TRUE
88 | bus_MV_470_1_node_89 | 20 | n |  | TRUE
89 | bus_MV_470_1_node_75 | 20 | n |  | TRUE
90 | bus_MV_470_1_node_76 | 20 | n |  | TRUE
91 | bus_MV_470_1_node_77 | 20 | n |  | TRUE
92 | bus_MV_470_1_node_78 | 20 | n |  | TRUE
93 | bus_MV_470_1_node_84 | 20 | n |  | TRUE
94 | bus_MV_470_1_node_281 | 20 | n |  | TRUE
95 | bus_MV_470_1_node_289 | 20 | n |  | TRUE
96 | bus_MV_470_1_node_81 | 20 | n |  | TRUE
97 | bus_MV_470_1_node_82 | 20 | n |  | TRUE
98 | bus_MV_470_1_node_83 | 20 | n |  | TRUE
99 | bus_MV_470_1_node_86 | 20 | n |  | TRUE
100 | bus_MV_470_1_node_87 | 20 | n |  | TRUE
101 | bus_MV_470_1_node_88 | 20 | n |  | TRUE
102 | bus_MV_470_1_node_323 | 20 | n |  | TRUE
103 | bus_MV_470_1_node_91 | 20 | n |  | TRUE
104 | bus_MV_470_1_node_279 | 20 | n |  | TRUE
105 | bus_MV_470_1_node_280 | 20 | n |  | TRUE
106 | bus_MV_470_1_node_282 | 20 | n |  | TRUE
107 | bus_MV_470_1_node_306 | 20 | n |  | TRUE
108 | bus_MV_470_1_node_283 | 20 | n |  | TRUE
109 | bus_MV_470_1_node_284 | 20 | n |  | TRUE
110 | bus_MV_470_1_node_285 | 20 | n |  | TRUE
111 | bus_MV_470_1_node_331 | 20 | n |  | TRUE
112 | bus_MV_470_1_node_305 | 20 | n |  | TRUE
113 | bus_MV_470_1_node_287 | 20 | n |  | TRUE
114 | bus_MV_470_1_node_288 | 20 | n |  | TRUE
115 | bus_MV_470_1_node_290 | 20 | n |  | TRUE
116 | bus_MV_470_1_node_291 | 20 | n |  | TRUE
117 | bus_MV_470_1_node_309 | 20 | n |  | TRUE
118 | bus_MV_470_1_node_329 | 20 | n |  | TRUE
119 | bus_MV_470_1_node_327 | 20 | n |  | TRUE
120 | bus_MV_470_1_node_328 | 20 | n |  | TRUE
121 | bus_HV_470_1_node_289 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_470_1_load_3 | 0 | 0.064827 | 0.031397 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_470_1_load_347 | 4 | 0.13134 | 0.063609 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_470_1_load_302 | 5 | 0.091912 | 0.044515 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_470_1_load_8 | 7 | 0.080911 | 0.039187 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_470_1_load_9 | 8 | 0.10098 | 0.048904 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_470_1_load_304 | 13 | 0.15122 | 0.07324 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_470_1_load_303 | 14 | 0.15363 | 0.074407 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_470_1_load_14 | 15 | 0.089575 | 0.043383 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_470_1_load_19 | 20 | 0.064961 | 0.031462 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_470_1_load_24 | 22 | 0.13505 | 0.065409 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_470_1_load_23 | 23 | 0.092214 | 0.044662 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_470_1_load_33 | 25 | 0.41776 | 0.20233 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_470_1_load_27 | 27 | 0.12625 | 0.061145 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_470_1_load_31 | 29 | 0.14783 | 0.071597 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_470_1_load_321 | 32 | 0.058757 | 0.028457 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_470_1_load_293 | 33 | 0.081867 | 0.03965 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_470_1_load_55 | 36 | 0.11679 | 0.056562 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_470_1_load_286 | 38 | 0.22278 | 0.1079 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_470_1_load_80 | 39 | 0.23185 | 0.11229 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_470_1_load_79 | 40 | 0.13072 | 0.063312 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_470_1_load_292 | 41 | 0.067808 | 0.032841 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_470_1_load_34 | 42 | 0.14043 | 0.068015 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_470_1_load_44 | 48 | 0.14738 | 0.071378 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_470_1_load_337 | 49 | 0.1283 | 0.062139 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_470_1_load_39 | 50 | 0.14047 | 0.068033 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_470_1_load_85 | 55 | 0.12989 | 0.06291 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_470_1_load_350 | 56 | 0.14087 | 0.068228 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_470_1_load_51 | 57 | 0.076466 | 0.037034 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_470_1_load_46 | 58 | 0.1634 | 0.079136 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_470_1_load_322 | 61 | 0.078026 | 0.03779 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_470_1_load_52 | 62 | 0.15232 | 0.07377 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_470_1_load_90 | 66 | 0.16476 | 0.079798 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_470_1_load_56 | 67 | 0.12052 | 0.058369 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_470_1_load_308 | 70 | 0.12429 | 0.060197 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_470_1_load_325 | 71 | 0.15013 | 0.072712 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_470_1_load_61 | 73 | 0.13168 | 0.063775 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_470_1_load_63 | 75 | 0.1297 | 0.062816 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_470_1_load_66 | 78 | 0.13668 | 0.066198 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_470_1_load_324 | 82 | 0.12493 | 0.060508 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_470_1_load_70 | 84 | 0.11665 | 0.056496 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_470_1_load_73 | 86 | 0.15758 | 0.076319 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_470_1_load_89 | 88 | 0.088575 | 0.042899 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_470_1_load_75 | 89 | 0.11011 | 0.053327 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_470_1_load_84 | 93 | 0.10553 | 0.051109 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_470_1_load_289 | 95 | 0.14415 | 0.069813 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_470_1_load_81 | 96 | 0.10585 | 0.051266 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_470_1_load_86 | 99 | 0.050339 | 0.02438 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_470_1_load_323 | 102 | 0.070957 | 0.034366 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_470_1_load_91 | 103 | 0.077071 | 0.037327 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_470_1_load_279 | 104 | 0.079395 | 0.038453 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_470_1_load_280 | 105 | 0.075922 | 0.036771 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_470_1_load_283 | 108 | 0.21602 | 0.10462 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_470_1_load_331 | 111 | 0.10911 | 0.052845 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_470_1_load_305 | 112 | 0.15737 | 0.076217 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_470_1_load_288 | 114 | 0.090164 | 0.043668 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_470_1_load_290 | 115 | 0.069191 | 0.033511 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_470_1_load_327 | 119 | 0.14981 | 0.072558 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_470_1_load_328 | 120 | 0.062657 | 0.030346 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 95 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_470_1_line_0 |  | 0 | 1 | 0.088243 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_470_1_line_1 |  | 1 | 2 | 0.27158 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_470_1_line_2 |  | 2 | 3 | 0.51314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_470_1_line_3 |  | 2 | 4 | 0.032677 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_470_1_line_4 |  | 3 | 5 | 0.04848 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_470_1_line_5 |  | 3 | 6 | 0.5164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_470_1_line_6 |  | 4 | 11 | 0.004385 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_470_1_line_7 |  | 6 | 7 | 0.071714 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_470_1_line_8 |  | 8 | 9 | 0.086321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_470_1_line_9 |  | 9 | 10 | 0.50041 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_470_1_line_10 |  | 9 | 11 | 0.18216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_470_1_line_11 |  | 10 | 14 | 0.029609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_470_1_line_12 |  | 11 | 12 | 0.32885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_470_1_line_13 |  | 12 | 13 | 0.073669 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_470_1_line_14 |  | 14 | 106 | 0.10895 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_470_1_line_15 |  | 15 | 16 | 0.022556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_470_1_line_16 |  | 16 | 17 | 0.68782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_470_1_line_17 |  | 17 | 21 | 0.21218 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_470_1_line_18 |  | 17 | 22 | 0.065719 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_470_1_line_19 |  | 17 | 18 | 0.3421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_470_1_line_20 |  | 18 | 19 | 0.38152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_470_1_line_21 |  | 18 | 20 | 0.051653 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_470_1_line_22 |  | 19 | 26 | 0.72069 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_470_1_line_23 |  | 19 | 27 | 0.10475 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_470_1_line_24 |  | 21 | 23 | 0.057748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_470_1_line_25 |  | 22 | 30 | 0.007418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_470_1_line_26 |  | 24 | 25 | 0.17536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_470_1_line_27 |  | 24 | 26 | 0.12044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_470_1_line_28 |  | 26 | 28 | 0.76334 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_470_1_line_29 |  | 26 | 29 | 0.065155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_470_1_line_30 |  | 28 | 39 | 0.04863 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
31 | MV_470_1_line_31 |  | 28 | 40 | 0.00424 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_470_1_line_32 |  | 28 | 34 | 0.054232 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
33 | MV_470_1_line_33 |  | 28 | 37 | 0.10094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_470_1_line_34 |  | 30 | 31 | 0.42928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_470_1_line_35 |  | 31 | 32 | 0.042179 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_470_1_line_36 |  | 31 | 33 | 0.99543 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_470_1_line_37 |  | 33 | 91 | 0.15084 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_470_1_line_38 |  | 34 | 35 | 0.34774 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
39 | MV_470_1_line_39 |  | 34 | 36 | 0.068972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_470_1_line_40 |  | 35 | 41 | 0.007749 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
41 | MV_470_1_line_41 |  | 37 | 38 | 0.00097431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_470_1_line_42 |  | 38 | 113 | 0.032968 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_470_1_line_43 |  | 39 | 95 | 0.087967 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
44 | MV_470_1_line_44 |  | 41 | 116 | 0.058347 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
45 | MV_470_1_line_45 |  | 42 | 43 | 0.25943 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
46 | MV_470_1_line_46 |  | 42 | 44 | 0.23959 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
47 | MV_470_1_line_47 |  | 43 | 46 | 0.16625 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
48 | MV_470_1_line_48 |  | 44 | 45 | 0.36705 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
49 | MV_470_1_line_49 |  | 45 | 47 | 0.22249 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
50 | MV_470_1_line_50 |  | 45 | 48 | 0.023697 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_470_1_line_51 |  | 46 | 49 | 0.042678 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
52 | MV_470_1_line_52 |  | 47 | 57 | 0.036501 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
53 | MV_470_1_line_53 |  | 49 | 98 | 0.031625 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
54 | MV_470_1_line_54 |  | 50 | 51 | 0.053994 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_470_1_line_55 |  | 50 | 52 | 0.071222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_470_1_line_56 |  | 51 | 53 | 0.15349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_470_1_line_57 |  | 52 | 54 | 0.094255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_470_1_line_58 |  | 53 | 55 | 0.012662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_470_1_line_59 |  | 54 | 56 | 0.1357 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_470_1_line_60 |  | 55 | 87 | 0.11594 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
61 | MV_470_1_line_61 |  | 56 | 101 | 0.10702 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_470_1_line_62 |  | 57 | 59 | 1.2001 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
63 | MV_470_1_line_63 |  | 58 | 59 | 0.111 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_470_1_line_64 |  | 59 | 60 | 0.49293 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
65 | MV_470_1_line_65 |  | 60 | 61 | 0.062622 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
66 | MV_470_1_line_66 |  | 61 | 115 | 0.29553 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
67 | MV_470_1_line_67 |  | 62 | 63 | 0.004828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_470_1_line_68 |  | 63 | 64 | 0.038899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_470_1_line_69 |  | 64 | 65 | 0.12914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_470_1_line_70 |  | 64 | 66 | 0.009518 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_470_1_line_71 |  | 65 | 71 | 0.058263 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_470_1_line_72 |  | 66 | 103 | 0.0058649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_470_1_line_73 |  | 67 | 68 | 0.003985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_470_1_line_74 |  | 68 | 69 | 0.027355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_470_1_line_75 |  | 69 | 70 | 0.026969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_470_1_line_76 |  | 70 | 117 | 0.012 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_470_1_line_77 |  | 70 | 74 | 0.020166 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_470_1_line_78 |  | 71 | 80 | 0.004193 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_470_1_line_79 |  | 72 | 73 | 0.040006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_470_1_line_80 |  | 72 | 74 | 0.052268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_470_1_line_81 |  | 73 | 75 | 0.10059 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_470_1_line_82 |  | 75 | 76 | 0.038 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_470_1_line_83 |  | 76 | 77 | 0.039759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_470_1_line_84 |  | 77 | 78 | 0.002538 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_470_1_line_85 |  | 77 | 79 | 0.047376 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
86 | MV_470_1_line_86 |  | 79 | 80 | 0.027339 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
87 | MV_470_1_line_87 |  | 80 | 81 | 0.24216 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
88 | MV_470_1_line_88 |  | 81 | 82 | 0.016235 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_470_1_line_89 |  | 81 | 83 | 0.55095 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
90 | MV_470_1_line_90 |  | 83 | 85 | 0.040947 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
91 | MV_470_1_line_91 |  | 83 | 84 | 0.049308 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_470_1_line_92 |  | 85 | 86 | 0.080708 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_470_1_line_93 |  | 85 | 87 | 0.78091 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
94 | MV_470_1_line_94 |  | 87 | 88 | 1.2346 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
95 | MV_470_1_line_95 |  | 88 | 96 | 2.0246 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
96 | MV_470_1_line_96 |  | 89 | 90 | 0.005458 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_470_1_line_97 |  | 90 | 91 | 0.30519 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_470_1_line_98 |  | 90 | 92 | 0.31983 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_470_1_line_99 |  | 92 | 93 | 0.004506 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_470_1_line_100 |  | 92 | 94 | 1.3368 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
101 | MV_470_1_line_101 |  | 94 | 106 | 0.56001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_470_1_line_102 |  | 94 | 107 | 0.77246 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
103 | MV_470_1_line_103 |  | 94 | 104 | 0.045954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_470_1_line_104 |  | 96 | 97 | 0.065771 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
105 | MV_470_1_line_105 |  | 97 | 98 | 0.078134 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
106 | MV_470_1_line_106 |  | 99 | 100 | 0.066419 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_470_1_line_107 |  | 100 | 101 | 0.39554 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_470_1_line_108 |  | 100 | 102 | 1.9303 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_470_1_line_109 |  | 104 | 105 | 0.0023088 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_470_1_line_110 |  | 107 | 112 | 0.036106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_470_1_line_111 |  | 108 | 109 | 0.051919 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_470_1_line_112 |  | 109 | 110 | 0.70891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_470_1_line_113 |  | 109 | 111 | 1.4548 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
114 | MV_470_1_line_114 |  | 110 | 112 | 0.021922 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
115 | MV_470_1_line_115 |  | 113 | 114 | 0.031159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_470_1_line_116 |  | 115 | 116 | 0.044827 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
117 | MV_470_1_line_117 |  | 117 | 118 | 0.076352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_470_1_line_118 |  | 118 | 120 | 0.033417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_470_1_line_119 |  | 119 | 120 | 0.13989 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_470_1_trafo_289 | 25 MVA 110/20 kV | 121 | 95 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2660504.0933 | 1234480.015
1 | 2660590.9361 | 1234463.0438
2 | 2660732.5324 | 1234303.595
3 | 2660966.2235 | 1234692.9428
4 | 2660738.9157 | 1234271.5503
5 | 2660978.5832 | 1234738.733
6 | 2660649.1871 | 1234676.9116
7 | 2660700.1586 | 1234626.4654
8 | 2660642.4037 | 1234281.794
9 | 2660648.3086 | 1234195.72
10 | 2660531.1739 | 1233869.5236
11 | 2660743.2694 | 1234272.173
12 | 2660718.5967 | 1233981.3746
13 | 2660692.0163 | 1233912.6471
14 | 2660539.5181 | 1233841.1121
15 | 2660761.4349 | 1230474.2938
16 | 2660783.669 | 1230478.4569
17 | 2660810.705 | 1231047.6133
18 | 2660924.4854 | 1230808.9783
19 | 2661231.5553 | 1230825.0971
20 | 2660968.2243 | 1230836.4553
21 | 2660651.0555 | 1231179.1687
22 | 2660875.2569 | 1231060.8821
23 | 2660699.0384 | 1231211.4012
24 | 2661707.2108 | 1230377.5328
25 | 2661841.3378 | 1230264.5981
26 | 2661622.1711 | 1230403.7349
27 | 2661261.6661 | 1230724.7643
28 | 2662006.7231 | 1230847.8972
29 | 2661575.5056 | 1230358.2111
30 | 2660882.5268 | 1231062.4576
31 | 2660597.8344 | 1231359.8213
32 | 2660558.9914 | 1231343.3817
33 | 2661354.1559 | 1232007.014
34 | 2662023.1118 | 1230815.3802
35 | 2662288.3743 | 1230867.2746
36 | 2662062.7717 | 1230758.9585
37 | 2661933.3972 | 1230813.1218
38 | 2661932.4371 | 1230812.9561
39 | 2661987.2901 | 1230892.2764
40 | 2662010.4973 | 1230849.8489
41 | 2662295.2364 | 1230870.8933
42 | 2663935.3301 | 1232268.8452
43 | 2664193.264 | 1232250.1004
44 | 2663726.8253 | 1232386.8737
45 | 2663432.1386 | 1232306.1034
46 | 2664267.4345 | 1232243.8641
47 | 2663330.0475 | 1232136.4485
48 | 2663408.9864 | 1232310.7151
49 | 2664310.1972 | 1232243.0147
50 | 2662717.8718 | 1229680.1266
51 | 2662691.5963 | 1229725.7126
52 | 2662764.5098 | 1229634.6667
53 | 2662748.137 | 1229856.6381
54 | 2662815.6639 | 1229566.9404
55 | 2662753.2112 | 1229868.2436
56 | 2662861.9669 | 1229439.38
57 | 2663293.5836 | 1232138.0947
58 | 2662695.5397 | 1230973.677
59 | 2662763.6965 | 1231061.2863
60 | 2662341.7852 | 1231292.7669
61 | 2662329.2165 | 1231236.1094
62 | 2662452.1317 | 1230863.0889
63 | 2662455.92 | 1230860.0823
64 | 2662479.5007 | 1230829.5656
65 | 2662396.6063 | 1230759.8835
66 | 2662487.9523 | 1230833.9906
67 | 2662484.1691 | 1230712.5718
68 | 2662487.8956 | 1230714.0119
69 | 2662507.374 | 1230703.4541
70 | 2662516.3594 | 1230678.0208
71 | 2662338.766 | 1230767.4597
72 | 2662498.5289 | 1230624.0428
73 | 2662462.636 | 1230607.6679
74 | 2662497.1456 | 1230672.0484
75 | 2662364.3059 | 1230628.8595
76 | 2662379.0797 | 1230663.8705
77 | 2662360.9754 | 1230696.5241
78 | 2662358.7771 | 1230695.2447
79 | 2662338.2032 | 1230738.068
80 | 2662338.7115 | 1230763.2675
81 | 2662151.3648 | 1230672.626
82 | 2662164.4903 | 1230672.6965
83 | 2662306.5096 | 1230372.665
84 | 2662351.341 | 1230393.1925
85 | 2662273.1003 | 1230350.0005
86 | 2662213.7639 | 1230295.333
87 | 2662843.3446 | 1229941.1646
88 | 2664042.3239 | 1230235.5313
89 | 2661593.713 | 1232112.6078
90 | 2661591.4504 | 1232117.5765
91 | 2661385.4688 | 1232123.7842
92 | 2661466.2276 | 1232406.5251
93 | 2661470.3659 | 1232408.3358
94 | 2660424.9941 | 1233244.946
95 | 2661965.5905 | 1230977.521
96 | 2664448.8207 | 1232218.9218
97 | 2664406.1348 | 1232268.5587
98 | 2664338.0451 | 1232258.0036
99 | 2662994.0073 | 1229011.0098
100 | 2662933.1863 | 1229010.755
101 | 2662904.5852 | 1229341.6226
102 | 2661212.2218 | 1228136.5172
103 | 2662488.0717 | 1230828.1269
104 | 2660447.3389 | 1233284.3328
105 | 2660448.7795 | 1233286.1369
106 | 2660561.2653 | 1233734.3526
107 | 2659729.8674 | 1232908.0478
108 | 2659725.4885 | 1232472.8317
109 | 2659738.8487 | 1232423.5338
110 | 2659674.3413 | 1232891.2127
111 | 2658530.261 | 1231613.6924
112 | 2659694.7647 | 1232899.1785
113 | 2661899.9494 | 1230807.3477
114 | 2661868.9514 | 1230803.4338
115 | 2662314.3861 | 1230940.948
116 | 2662342.0269 | 1230905.7506
117 | 2662527.2816 | 1230683.0611
118 | 2662598.0676 | 1230699.2161
119 | 2662692.7942 | 1230554.5973
120 | 2662620.2886 | 1230674.2337
121 | 2661965.5905 | 1230977.521

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98201 | -0.014383 | 0.064827 | 0.031397
1 | 0.98201 | -0.014448 | 0 | 0
2 | 0.98203 | -0.014574 | 0 | 0
3 | 0.98192 | -0.014118 | 0 | 0
4 | 0.98204 | -0.014598 | 0.13134 | 0.063609
5 | 0.98192 | -0.014064 | 0.091912 | 0.044515
6 | 0.98187 | -0.013805 | 0 | 0
7 | 0.98186 | -0.013878 | 0.080911 | 0.039187
8 | 0.98216 | -0.015134 | 0.10098 | 0.048904
9 | 0.98217 | -0.015237 | 0 | 0
10 | 0.98256 | -0.017264 | 0 | 0
11 | 0.98205 | -0.014608 | 0 | 0
12 | 0.98198 | -0.01411 | 0 | 0
13 | 0.98197 | -0.013976 | 0.15122 | 0.07324
14 | 0.98258 | -0.017372 | 0.15363 | 0.074407
15 | 0.99275 | 0.031331 | 0.089575 | 0.043383
16 | 0.99276 | 0.031307 | 0 | 0
17 | 0.99283 | 0.030942 | 0 | 0
18 | 0.99374 | 0.025678 | 0 | 0
19 | 0.99477 | 0.019731 | 0 | 0
20 | 0.99373 | 0.025637 | 0.064961 | 0.031462
21 | 0.99281 | 0.031127 | 0 | 0
22 | 0.99267 | 0.031928 | 0.13505 | 0.065409
23 | 0.9928 | 0.031189 | 0.092214 | 0.044662
24 | 0.99679 | 0.0086047 | 0 | 0
25 | 0.99669 | 0.0094635 | 0.41776 | 0.20233
26 | 0.99685 | 0.008042 | 0 | 0
27 | 0.99475 | 0.019569 | 0.12625 | 0.061145
28 | 0.99959 | -0.0081845 | 0 | 0
29 | 0.99684 | 0.0081548 | 0.14783 | 0.071597
30 | 0.99266 | 0.032028 | 0 | 0
31 | 0.99169 | 0.037936 | 0 | 0
32 | 0.99169 | 0.037906 | 0.058757 | 0.028457
33 | 0.98845 | 0.0067199 | 0.081867 | 0.03965
34 | 0.99951 | -0.0097954 | 0 | 0
35 | 0.999 | -0.019765 | 0 | 0
36 | 0.9995 | -0.0097025 | 0.11679 | 0.056562
37 | 0.99955 | -0.007824 | 0 | 0
38 | 0.99955 | -0.0078205 | 0.22278 | 0.1079
39 | 0.99973 | -0.0053265 | 0.23185 | 0.11229
40 | 0.99959 | -0.0081779 | 0.13072 | 0.063312
41 | 0.99899 | -0.019987 | 0.067808 | 0.032841
42 | 0.99193 | -0.24388 | 0.14043 | 0.068015
43 | 0.99163 | -0.2497 | 0 | 0
44 | 0.99259 | -0.22053 | 0 | 0
45 | 0.99304 | -0.21185 | 0 | 0
46 | 0.99144 | -0.25341 | 0 | 0
47 | 0.99333 | -0.20629 | 0 | 0
48 | 0.99304 | -0.2118 | 0.14738 | 0.071378
49 | 0.99139 | -0.25436 | 0.1283 | 0.062139
50 | 0.98266 | -0.52319 | 0.14047 | 0.068033
51 | 0.98268 | -0.52339 | 0 | 0
52 | 0.98263 | -0.52304 | 0 | 0
53 | 0.98276 | -0.52393 | 0 | 0
54 | 0.9826 | -0.52284 | 0 | 0
55 | 0.98277 | -0.52397 | 0.12989 | 0.06291
56 | 0.98253 | -0.52347 | 0.14087 | 0.068228
57 | 0.99343 | -0.20253 | 0.076466 | 0.037034
58 | 0.99698 | -0.076568 | 0.1634 | 0.079136
59 | 0.99701 | -0.076346 | 0 | 0
60 | 0.99769 | -0.063135 | 0 | 0
61 | 0.99778 | -0.061447 | 0.078026 | 0.03779
62 | 0.98133 | -0.53897 | 0.15232 | 0.07377
63 | 0.98133 | -0.53898 | 0 | 0
64 | 0.98134 | -0.53906 | 0 | 0
65 | 0.98141 | -0.53966 | 0 | 0
66 | 0.98134 | -0.53903 | 0.16476 | 0.079798
67 | 0.98109 | -0.54149 | 0.12052 | 0.058369
68 | 0.9811 | -0.54149 | 0 | 0
69 | 0.9811 | -0.54153 | 0 | 0
70 | 0.9811 | -0.54157 | 0.12429 | 0.060197
71 | 0.98144 | -0.53993 | 0.15013 | 0.072712
72 | 0.98115 | -0.54196 | 0 | 0
73 | 0.98117 | -0.54217 | 0.13168 | 0.063775
74 | 0.98112 | -0.54168 | 0 | 0
75 | 0.98129 | -0.54136 | 0.1297 | 0.062816
76 | 0.98134 | -0.541 | 0 | 0
77 | 0.98138 | -0.54133 | 0 | 0
78 | 0.98138 | -0.54133 | 0.13668 | 0.066198
79 | 0.98143 | -0.5401 | 0 | 0
80 | 0.98144 | -0.53996 | 0 | 0
81 | 0.98163 | -0.53788 | 0 | 0
82 | 0.98162 | -0.53786 | 0.12493 | 0.060508
83 | 0.98209 | -0.53258 | 0 | 0
84 | 0.98207 | -0.53266 | 0.11665 | 0.056496
85 | 0.98212 | -0.53215 | 0 | 0
86 | 0.98211 | -0.532 | 0.15758 | 0.076319
87 | 0.98289 | -0.52295 | 0 | 0
88 | 0.98627 | -0.43171 | 0.088575 | 0.042899
89 | 0.98751 | 0.012564 | 0.11011 | 0.053327
90 | 0.98751 | 0.012557 | 0 | 0
91 | 0.98814 | 0.0086145 | 0 | 0
92 | 0.98689 | 0.016417 | 0 | 0
93 | 0.98689 | 0.016423 | 0.10553 | 0.051109
94 | 0.98329 | -0.018573 | 0 | 0
95 | 1 | 0 | -7.1197 | -3.0681
96 | 0.99115 | -0.2602 | 0.10585 | 0.051266
97 | 0.99122 | -0.2588 | 0 | 0
98 | 0.99131 | -0.25715 | 0 | 0
99 | 0.98245 | -0.52299 | 0.050339 | 0.02438
100 | 0.98246 | -0.52303 | 0 | 0
101 | 0.98252 | -0.52341 | 0 | 0
102 | 0.98219 | -0.52493 | 0.070957 | 0.034366
103 | 0.98134 | -0.53902 | 0.077071 | 0.037327
104 | 0.98328 | -0.018486 | 0.079395 | 0.038453
105 | 0.98328 | -0.018484 | 0.075922 | 0.036771
106 | 0.98274 | -0.015722 | 0 | 0
107 | 0.98257 | -0.024632 | 0 | 0
108 | 0.98223 | -0.022111 | 0.21602 | 0.10462
109 | 0.98224 | -0.022248 | 0 | 0
110 | 0.98254 | -0.024589 | 0 | 0
111 | 0.98193 | -0.024344 | 0.10911 | 0.052845
112 | 0.98255 | -0.024463 | 0.15737 | 0.076217
113 | 0.99955 | -0.0077873 | 0 | 0
114 | 0.99954 | -0.0077544 | 0.090164 | 0.043668
115 | 0.99873 | -0.02798 | 0.069191 | 0.033511
116 | 0.99879 | -0.026722 | 0 | 0
117 | 0.9811 | -0.54154 | 0 | 0
118 | 0.98108 | -0.54135 | 0 | 0
119 | 0.98103 | -0.54153 | 0.14981 | 0.072558
120 | 0.98107 | -0.54126 | 0.062657 | 0.030346
121 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.064827 | -0.031397 | 0.064827 | 0.029365 | 5.2178e-07 | -0.0020316 | 0.0021174 | 0.0020921 | 0.0021174 | 0.98201 | -0.014383 | 0.98201 | -0.014448 | 0.96246
1 | -0.064827 | -0.029365 | 0.064829 | 0.023113 | 1.5324e-06 | -0.0062527 | 0.0020921 | 0.0020232 | 0.0020921 | 0.98201 | -0.014448 | 0.98203 | -0.014574 | 0.95094
2 | 0.17285 | 0.05881 | -0.17283 | -0.070618 | 2.0165e-05 | -0.011808 | 0.005367 | 0.0054888 | 0.0054888 | 0.98203 | -0.014574 | 0.98192 | -0.014118 | 2.4949
3 | -0.23768 | -0.081922 | 0.23768 | 0.08117 | 2.3801e-06 | -0.00075172 | 0.00739 | 0.0073829 | 0.00739 | 0.98203 | -0.014574 | 0.98204 | -0.014598 | 3.3591
4 | 0.091912 | 0.043399 | -0.091912 | -0.044515 | 5.8065e-07 | -0.0011159 | 0.0029882 | 0.0030024 | 0.0030024 | 0.98192 | -0.014118 | 0.98192 | -0.014064 | 1.3647
5 | 0.080916 | 0.027219 | -0.080911 | -0.039105 | 4.5565e-06 | -0.011886 | 0.0025098 | 0.0026421 | 0.0026421 | 0.98192 | -0.014118 | 0.98187 | -0.013805 | 1.201
6 | -0.36902 | -0.14478 | 0.36902 | 0.14468 | 7.9475e-07 | -0.00010074 | 0.011652 | 0.011651 | 0.011652 | 0.98204 | -0.014598 | 0.98205 | -0.014608 | 5.2965
7 | 0.080911 | 0.039105 | -0.080911 | -0.039187 | 8.923e-07 | -8.1977e-05 | 0.0026421 | 0.0026432 | 0.0026432 | 0.98187 | -0.013805 | 0.98186 | -0.013878 | 1.2586
8 | -0.10098 | -0.048904 | 0.10098 | 0.046917 | 1.2436e-06 | -0.0019878 | 0.0032976 | 0.0032726 | 0.0032976 | 0.98216 | -0.015134 | 0.98217 | -0.015237 | 1.4989
9 | -0.62129 | -0.2514 | 0.62155 | 0.23994 | 0.00025758 | -0.011454 | 0.019699 | 0.019575 | 0.019699 | 0.98217 | -0.015237 | 0.98256 | -0.017264 | 8.9541
10 | 0.52032 | 0.20448 | -0.52025 | -0.20865 | 6.5841e-05 | -0.0041756 | 0.016432 | 0.016477 | 0.016477 | 0.98217 | -0.015237 | 0.98205 | -0.014608 | 7.4896
11 | -0.62155 | -0.23994 | 0.62157 | 0.23926 | 1.514e-05 | -0.00067803 | 0.019575 | 0.019567 | 0.019575 | 0.98256 | -0.017264 | 0.98258 | -0.017372 | 8.8975
12 | 0.15123 | 0.063976 | -0.15122 | -0.071545 | 1.0418e-05 | -0.0075688 | 0.004827 | 0.004918 | 0.004918 | 0.98205 | -0.014608 | 0.98198 | -0.01411 | 2.2354
13 | 0.15122 | 0.071545 | -0.15122 | -0.07324 | 2.3891e-06 | -0.0016954 | 0.004918 | 0.0049395 | 0.0049395 | 0.98198 | -0.01411 | 0.98197 | -0.013976 | 2.2452
14 | -0.7752 | -0.31367 | 0.77532 | 0.31362 | 0.00011717 | -5.2208e-05 | 0.024568 | 0.024567 | 0.024568 | 0.98258 | -0.017372 | 0.98274 | -0.015722 | 11.6993
15 | -0.089575 | -0.043383 | 0.089575 | 0.042852 | 2.5163e-07 | -0.0005307 | 0.0028941 | 0.0028874 | 0.0028941 | 0.99275 | 0.031331 | 0.99276 | 0.031307 | 1.3155
16 | -0.089575 | -0.042852 | 0.089582 | 0.026668 | 7.1677e-06 | -0.016184 | 0.0028874 | 0.0027176 | 0.0028874 | 0.99276 | 0.031307 | 0.99283 | 0.030942 | 1.3124
17 | 0.092218 | 0.03831 | -0.092215 | -0.043303 | 2.4352e-06 | -0.0049928 | 0.0029035 | 0.0029622 | 0.0029622 | 0.99283 | 0.030942 | 0.99281 | 0.031127 | 1.3465
18 | 1.9202 | 0.80074 | -1.9199 | -0.80219 | 0.00032114 | -0.0014512 | 0.060492 | 0.06051 | 0.06051 | 0.99283 | 0.030942 | 0.99267 | 0.031928 | 27.5044
19 | -2.102 | -0.86571 | 2.104 | 0.85825 | 0.0019927 | -0.0074677 | 0.066099 | 0.06601 | 0.066099 | 0.99283 | 0.030942 | 0.99374 | 0.025678 | 30.045
20 | -2.169 | -0.88965 | 2.1713 | 0.88134 | 0.0023588 | -0.0083052 | 0.068102 | 0.068003 | 0.068102 | 0.99374 | 0.025678 | 0.99477 | 0.019731 | 30.9555
21 | 0.064962 | 0.031402 | -0.064961 | -0.031462 | 4.0446e-07 | -6.064e-05 | 0.002096 | 0.0020968 | 0.0020968 | 0.99374 | 0.025678 | 0.99373 | 0.025637 | 0.99847
22 | -2.2976 | -0.94237 | 2.3026 | 0.92678 | 0.0049837 | -0.015585 | 0.072065 | 0.071878 | 0.072065 | 0.99477 | 0.019731 | 0.99685 | 0.008042 | 32.7566
23 | 0.12625 | 0.061023 | -0.12625 | -0.061145 | 3.0917e-06 | -0.00012181 | 0.0040692 | 0.0040708 | 0.0040708 | 0.99477 | 0.019731 | 0.99475 | 0.019569 | 1.9385
24 | 0.092215 | 0.043303 | -0.092214 | -0.044662 | 6.8034e-07 | -0.0013588 | 0.0029622 | 0.0029792 | 0.0029792 | 0.99281 | 0.031127 | 0.9928 | 0.031189 | 1.3542
25 | 1.7849 | 0.73678 | -1.7848 | -0.73694 | 3.1227e-05 | -0.00016526 | 0.056153 | 0.056155 | 0.056155 | 0.99267 | 0.031928 | 0.99266 | 0.032028 | 25.525
26 | 0.41781 | 0.19818 | -0.41776 | -0.20233 | 4.2149e-05 | -0.0041471 | 0.013392 | 0.013444 | 0.013444 | 0.99679 | 0.0086047 | 0.99669 | 0.0094635 | 6.111
27 | -0.41781 | -0.19818 | 0.41783 | 0.19534 | 2.8761e-05 | -0.0028488 | 0.013392 | 0.013357 | 0.013392 | 0.99679 | 0.0086047 | 0.99685 | 0.008042 | 6.0873
28 | -2.8682 | -1.1922 | 2.8765 | 1.1764 | 0.0082268 | -0.01572 | 0.08995 | 0.08975 | 0.08995 | 0.99685 | 0.008042 | 0.99959 | -0.0081845 | 40.8863
29 | 0.14783 | 0.070051 | -0.14783 | -0.071597 | 1.96e-06 | -0.0015453 | 0.0047373 | 0.0047566 | 0.0047566 | 0.99685 | 0.008042 | 0.99684 | 0.0081548 | 2.1621
30 | -6.8714 | -2.9483 | 6.8723 | 2.9472 | 0.00082984 | -0.0010947 | 0.21594 | 0.21592 | 0.21594 | 0.99959 | -0.0081845 | 0.99973 | -0.0053265 | 51.2913
31 | 0.13072 | 0.063211 | -0.13072 | -0.063312 | 9.958e-08 | -0.00010112 | 0.0041934 | 0.0041946 | 0.0041946 | 0.99959 | -0.0081845 | 0.99959 | -0.0081779 | 1.9067
32 | 3.5513 | 1.561 | -3.551 | -1.5628 | 0.00024916 | -0.0018411 | 0.11203 | 0.11205 | 0.11205 | 0.99959 | -0.0081845 | 0.99951 | -0.0097954 | 26.6158
33 | 0.31296 | 0.14761 | -0.31295 | -0.15001 | 1.3497e-05 | -0.0024041 | 0.0099929 | 0.010023 | 0.010023 | 0.99959 | -0.0081845 | 0.99955 | -0.007824 | 4.5558
34 | 1.7848 | 0.73694 | -1.783 | -0.7465 | 0.0018108 | -0.0095526 | 0.056155 | 0.056268 | 0.056268 | 0.99266 | 0.032028 | 0.99169 | 0.037936 | 25.5762
35 | 0.058757 | 0.028408 | -0.058757 | -0.028457 | 2.7132e-07 | -4.935e-05 | 0.0018998 | 0.0019004 | 0.0019004 | 0.99169 | 0.037936 | 0.99169 | 0.037906 | 0.90497
36 | 1.7243 | 0.71809 | -1.719 | -0.71597 | 0.0052442 | 0.0021199 | 0.054371 | 0.054384 | 0.054384 | 0.99169 | 0.037936 | 0.98845 | 0.0067199 | 25.8971
37 | 1.6371 | 0.67632 | -1.6366 | -0.67968 | 0.00053933 | -0.0033578 | 0.051732 | 0.051771 | 0.051771 | 0.98845 | 0.0067199 | 0.98814 | 0.0086145 | 23.5323
38 | 3.4342 | 1.5079 | -3.4327 | -1.5198 | 0.0014956 | -0.011891 | 0.10833 | 0.10848 | 0.10848 | 0.99951 | -0.0097954 | 0.999 | -0.019765 | 25.7675
39 | 0.11679 | 0.054917 | -0.11679 | -0.056562 | 1.2862e-06 | -0.0016448 | 0.0037273 | 0.0037478 | 0.0037478 | 0.99951 | -0.0097954 | 0.9995 | -0.0097025 | 1.7035
40 | 3.4327 | 1.5198 | -3.4327 | -1.5201 | 3.3377e-05 | -0.00026479 | 0.10848 | 0.10848 | 0.10848 | 0.999 | -0.019765 | 0.99899 | -0.019987 | 25.7683
41 | 0.31295 | 0.15001 | -0.31295 | -0.15004 | 1.3064e-07 | -2.3203e-05 | 0.010023 | 0.010023 | 0.010023 | 0.99955 | -0.007824 | 0.99955 | -0.0078205 | 4.556
42 | 0.090165 | 0.042139 | -0.090164 | -0.042925 | 3.6485e-07 | -0.00078634 | 0.0028743 | 0.002884 | 0.002884 | 0.99955 | -0.0078205 | 0.99955 | -0.0077873 | 1.3109
43 | -7.1041 | -3.0594 | 7.1057 | 3.0576 | 0.0016058 | -0.0018855 | 0.22335 | 0.22331 | 0.22335 | 0.99973 | -0.0053265 | 1 | 0 | 53.0514
44 | 3.3649 | 1.4872 | -3.3644 | -1.4866 | 0.00047003 | 0.00060517 | 0.10631 | 0.10631 | 0.10631 | 0.99899 | -0.019987 | 0.99879 | -0.026722 | 25.9292
45 | 2.6736 | 1.1868 | -2.6729 | -1.1959 | 0.00068903 | -0.0091159 | 0.085128 | 0.085244 | 0.085244 | 0.99193 | -0.24388 | 0.99163 | -0.2497 | 20.248
46 | -2.814 | -1.2548 | 2.8154 | 1.2565 | 0.0013731 | 0.0016826 | 0.089667 | 0.089664 | 0.089667 | 0.99193 | -0.24388 | 0.99259 | -0.22053 | 21.87
47 | 2.6729 | 1.1959 | -2.6724 | -1.2017 | 0.00044255 | -0.0058378 | 0.085244 | 0.085318 | 0.085318 | 0.99163 | -0.2497 | 0.99144 | -0.25341 | 20.2656
48 | -2.8154 | -1.2565 | 2.8165 | 1.2437 | 0.0010781 | -0.012831 | 0.089664 | 0.0895 | 0.089664 | 0.99259 | -0.22053 | 0.99304 | -0.21185 | 21.2977
49 | -2.9638 | -1.3145 | 2.9646 | 1.3068 | 0.00072263 | -0.0077207 | 0.094251 | 0.094153 | 0.094251 | 0.99304 | -0.21185 | 0.99333 | -0.20629 | 22.3875
50 | 0.14738 | 0.07082 | -0.14738 | -0.071378 | 7.158e-07 | -0.00055773 | 0.0047532 | 0.0047603 | 0.0047603 | 0.99304 | -0.21185 | 0.99304 | -0.2118 | 2.1638
51 | 2.6724 | 1.2017 | -2.6723 | -1.2032 | 0.00011373 | -0.0014981 | 0.085318 | 0.085337 | 0.085337 | 0.99144 | -0.25341 | 0.99139 | -0.25436 | 20.2702
52 | -2.9646 | -1.3068 | 2.9648 | 1.307 | 0.00023064 | 0.0002873 | 0.094153 | 0.094152 | 0.094153 | 0.99333 | -0.20629 | 0.99343 | -0.20253 | 22.9641
53 | 2.544 | 1.1411 | -2.5439 | -1.1409 | 0.00014859 | 0.0001749 | 0.081188 | 0.081189 | 0.081189 | 0.99139 | -0.25436 | 0.99131 | -0.25715 | 19.8021
54 | -0.4027 | -0.17573 | 0.40271 | 0.17449 | 1.1995e-05 | -0.0012413 | 0.012907 | 0.012893 | 0.012907 | 0.98266 | -0.52319 | 0.98268 | -0.52339 | 5.867
55 | 0.26223 | 0.1077 | -0.26222 | -0.10934 | 6.6088e-06 | -0.00164 | 0.0083279 | 0.0083463 | 0.0083463 | 0.98266 | -0.52319 | 0.98263 | -0.52304 | 3.7938
56 | -0.40271 | -0.17449 | 0.40275 | 0.17096 | 3.3954e-05 | -0.0035292 | 0.012893 | 0.012852 | 0.012893 | 0.98268 | -0.52339 | 0.98276 | -0.52393 | 5.8604
57 | 0.26222 | 0.10934 | -0.26221 | -0.11151 | 8.7914e-06 | -0.0021703 | 0.0083463 | 0.0083711 | 0.0083711 | 0.98263 | -0.52304 | 0.9826 | -0.52284 | 3.8051
58 | -0.40275 | -0.17096 | 0.40275 | 0.17067 | 2.7913e-06 | -0.00029116 | 0.012852 | 0.012849 | 0.012852 | 0.98276 | -0.52393 | 0.98277 | -0.52397 | 5.8418
59 | 0.26221 | 0.11151 | -0.2622 | -0.11165 | 1.6947e-05 | -0.00014579 | 0.0083711 | 0.0083729 | 0.0083729 | 0.9826 | -0.52284 | 0.98253 | -0.52347 | 3.9871
60 | -0.53264 | -0.23358 | 0.5327 | 0.23348 | 6.0282e-05 | -9.5935e-05 | 0.017084 | 0.017082 | 0.017084 | 0.98277 | -0.52397 | 0.98289 | -0.52295 | 8.1352
61 | 0.12132 | 0.043424 | -0.12132 | -0.04589 | 2.0614e-06 | -0.0024662 | 0.0037861 | 0.0038111 | 0.0038111 | 0.98253 | -0.52347 | 0.98252 | -0.52341 | 1.7323
62 | -3.0412 | -1.3441 | 3.0492 | 1.3541 | 0.0079844 | 0.010021 | 0.09662 | 0.096602 | 0.09662 | 0.99343 | -0.20253 | 0.99701 | -0.076346 | 23.5658
63 | -0.1634 | -0.079136 | 0.1634 | 0.079008 | 5.4634e-06 | -0.00012829 | 0.0052568 | 0.0052552 | 0.0052568 | 0.99698 | -0.076568 | 0.99701 | -0.076346 | 2.5032
64 | -3.2126 | -1.4331 | 3.2145 | 1.4161 | 0.0018676 | -0.017017 | 0.10185 | 0.10163 | 0.10185 | 0.99701 | -0.076346 | 0.99769 | -0.063135 | 24.1934
65 | -3.2145 | -1.4161 | 3.2147 | 1.4139 | 0.00023668 | -0.0021642 | 0.10163 | 0.10161 | 0.10163 | 0.99769 | -0.063135 | 0.99778 | -0.061447 | 24.1412
66 | -3.2928 | -1.4517 | 3.295 | 1.4546 | 0.0022833 | 0.0029246 | 0.10411 | 0.10411 | 0.10411 | 0.99778 | -0.061447 | 0.99873 | -0.02798 | 25.3935
67 | -0.15232 | -0.07377 | 0.15232 | 0.073659 | 1.5971e-07 | -0.00011096 | 0.0049785 | 0.0049771 | 0.0049785 | 0.98133 | -0.53897 | 0.98133 | -0.53898 | 2.2629
68 | -0.15232 | -0.073659 | 0.15232 | 0.072765 | 1.2834e-06 | -0.00089403 | 0.0049771 | 0.0049657 | 0.0049771 | 0.98133 | -0.53898 | 0.98134 | -0.53906 | 2.2623
69 | -0.39415 | -0.18954 | 0.39418 | 0.18658 | 2.8452e-05 | -0.0029611 | 0.012865 | 0.012828 | 0.012865 | 0.98134 | -0.53906 | 0.98141 | -0.53966 | 5.8479
70 | 0.24183 | 0.11677 | -0.24183 | -0.11699 | 7.9324e-07 | -0.00021861 | 0.0078998 | 0.0079026 | 0.0079026 | 0.98134 | -0.53906 | 0.98134 | -0.53903 | 3.5921
71 | -0.39418 | -0.18658 | 0.39419 | 0.18524 | 1.2782e-05 | -0.0013361 | 0.012828 | 0.012811 | 0.012828 | 0.98141 | -0.53966 | 0.98144 | -0.53993 | 5.8308
72 | 0.077071 | 0.037192 | -0.077071 | -0.037327 | 4.9649e-08 | -0.00013484 | 0.0025173 | 0.0025191 | 0.0025191 | 0.98134 | -0.53903 | 0.98134 | -0.53902 | 1.145
73 | -0.12052 | -0.058369 | 0.12052 | 0.058278 | 8.2569e-08 | -9.1558e-05 | 0.0039401 | 0.0039389 | 0.0039401 | 0.98109 | -0.54149 | 0.9811 | -0.54149 | 1.791
74 | -0.12052 | -0.058278 | 0.12052 | 0.057649 | 5.6544e-07 | -0.0006285 | 0.0039389 | 0.0039309 | 0.0039389 | 0.9811 | -0.54149 | 0.9811 | -0.54153 | 1.7904
75 | -0.12052 | -0.057649 | 0.12052 | 0.05703 | 5.5522e-07 | -0.00061964 | 0.0039309 | 0.0039231 | 0.0039309 | 0.9811 | -0.54153 | 0.9811 | -0.54157 | 1.7868
76 | 0.21248 | 0.099951 | -0.21248 | -0.10023 | 7.6515e-07 | -0.00027556 | 0.0069092 | 0.0069127 | 0.0069127 | 0.9811 | -0.54157 | 0.9811 | -0.54154 | 3.1421
77 | -0.4573 | -0.21718 | 0.4573 | 0.21672 | 5.971e-06 | -0.0004617 | 0.014896 | 0.01489 | 0.014896 | 0.9811 | -0.54157 | 0.98112 | -0.54168 | 6.7707
78 | -0.54432 | -0.25795 | 0.54433 | 0.25786 | 1.757e-06 | -9.5909e-05 | 0.017717 | 0.017716 | 0.017717 | 0.98144 | -0.53993 | 0.98144 | -0.53996 | 8.0533
79 | -0.45732 | -0.21552 | 0.45733 | 0.2146 | 1.1807e-05 | -0.00091602 | 0.014875 | 0.014863 | 0.014875 | 0.98115 | -0.54196 | 0.98117 | -0.54217 | 6.7612
80 | 0.45732 | 0.21552 | -0.4573 | -0.21672 | 1.5454e-05 | -0.0011967 | 0.014875 | 0.01489 | 0.01489 | 0.98115 | -0.54196 | 0.98112 | -0.54168 | 6.7681
81 | -0.58901 | -0.27838 | 0.58907 | 0.2783 | 6.5838e-05 | -7.4377e-05 | 0.019168 | 0.019166 | 0.019168 | 0.98117 | -0.54217 | 0.98129 | -0.54136 | 9.1274
82 | -0.71877 | -0.34112 | 0.71881 | 0.3411 | 3.7089e-05 | -2.0454e-05 | 0.023405 | 0.023405 | 0.023405 | 0.98129 | -0.54136 | 0.98134 | -0.541 | 11.1454
83 | -0.71881 | -0.3411 | 0.71884 | 0.34019 | 2.9061e-05 | -0.0009056 | 0.023405 | 0.023393 | 0.023405 | 0.98134 | -0.541 | 0.98138 | -0.54133 | 10.6385
84 | 0.13668 | 0.06614 | -0.13668 | -0.066198 | 6.7631e-08 | -5.8341e-05 | 0.0044665 | 0.0044673 | 0.0044673 | 0.98138 | -0.54133 | 0.98138 | -0.54133 | 2.0306
85 | -0.85552 | -0.40633 | 0.85555 | 0.40632 | 3.3755e-05 | -1.8732e-05 | 0.02786 | 0.027859 | 0.02786 | 0.98138 | -0.54133 | 0.98143 | -0.5401 | 7.9599
86 | -0.85555 | -0.40632 | 0.85556 | 0.40542 | 1.0244e-05 | -0.00089593 | 0.027859 | 0.027848 | 0.027859 | 0.98143 | -0.5401 | 0.98144 | -0.53996 | 7.6958
87 | -1.3999 | -0.66328 | 1.4001 | 0.65545 | 0.00024229 | -0.0078276 | 0.045564 | 0.045463 | 0.045564 | 0.98144 | -0.53996 | 0.98163 | -0.53788 | 12.5866
88 | 0.12493 | 0.060134 | -0.12493 | -0.060508 | 3.6077e-07 | -0.00037341 | 0.0040775 | 0.0040822 | 0.0040822 | 0.98163 | -0.53788 | 0.98162 | -0.53786 | 1.8556
89 | -1.5251 | -0.71558 | 1.5257 | 0.69783 | 0.00065012 | -0.017749 | 0.049541 | 0.049315 | 0.049541 | 0.98163 | -0.53788 | 0.98209 | -0.53258 | 13.6852
90 | -1.6424 | -0.75427 | 1.6424 | 0.75296 | 5.5797e-05 | -0.0013144 | 0.053124 | 0.053107 | 0.053124 | 0.98209 | -0.53258 | 0.98212 | -0.53215 | 14.675
91 | 0.11665 | 0.05644 | -0.11665 | -0.056496 | 1.2749e-06 | -5.5974e-05 | 0.0038091 | 0.0038098 | 0.0038098 | 0.98209 | -0.53258 | 0.98207 | -0.53266 | 1.8142
92 | 0.15758 | 0.074461 | -0.15758 | -0.076319 | 2.8406e-06 | -0.0018578 | 0.0051229 | 0.0051465 | 0.0051465 | 0.98212 | -0.53215 | 0.98211 | -0.532 | 2.3393
93 | -1.8 | -0.82742 | 1.8013 | 0.80248 | 0.001272 | -0.024936 | 0.05823 | 0.057916 | 0.05823 | 0.98212 | -0.53215 | 0.98289 | -0.52295 | 16.0855
94 | -2.334 | -1.036 | 2.3404 | 1.0417 | 0.0063733 | 0.0057858 | 0.074998 | 0.07498 | 0.074998 | 0.98289 | -0.52295 | 0.98627 | -0.43171 | 21.4281
95 | -2.4289 | -1.0846 | 2.4377 | 1.0947 | 0.0087451 | 0.0101 | 0.07786 | 0.077829 | 0.07786 | 0.98627 | -0.43171 | 0.99115 | -0.2602 | 18.9901
96 | -0.11011 | -0.053327 | 0.11011 | 0.053199 | 9.3162e-08 | -0.00012705 | 0.0035763 | 0.0035747 | 0.0035763 | 0.98751 | 0.012564 | 0.98751 | 0.012557 | 1.6256
97 | -1.6355 | -0.68646 | 1.6366 | 0.67968 | 0.0010937 | -0.0067859 | 0.051851 | 0.051771 | 0.051851 | 0.98751 | 0.012557 | 0.98814 | 0.0086145 | 23.5687
98 | 1.5254 | 0.63326 | -1.5244 | -0.64041 | 0.00099705 | -0.0071463 | 0.048282 | 0.048366 | 0.048366 | 0.98751 | 0.012557 | 0.98689 | 0.016417 | 21.9844
99 | 0.10553 | 0.051004 | -0.10553 | -0.051109 | 7.0719e-08 | -0.00010476 | 0.0034284 | 0.0034297 | 0.0034297 | 0.98689 | 0.016417 | 0.98689 | 0.016423 | 1.559
100 | 1.4189 | 0.58941 | -1.4141 | -0.58794 | 0.0048127 | 0.0014658 | 0.044942 | 0.04496 | 0.04496 | 0.98689 | 0.016417 | 0.98329 | -0.018573 | 21.4094
101 | 0.77576 | 0.30083 | -0.77532 | -0.31362 | 0.00044863 | -0.012787 | 0.024427 | 0.024567 | 0.024567 | 0.98329 | -0.018573 | 0.98274 | -0.015722 | 11.1669
102 | 0.48299 | 0.213 | -0.48266 | -0.21368 | 0.00033076 | -0.00068378 | 0.015497 | 0.015508 | 0.015508 | 0.98329 | -0.018573 | 0.98257 | -0.024632 | 7.3847
103 | 0.15532 | 0.07411 | -0.15532 | -0.07517 | 1.5701e-06 | -0.0010604 | 0.0050523 | 0.0050658 | 0.0050658 | 0.98329 | -0.018573 | 0.98328 | -0.018486 | 2.3026
104 | -2.5435 | -1.146 | 2.5437 | 1.1437 | 0.00015887 | -0.0023226 | 0.081253 | 0.081224 | 0.081253 | 0.99115 | -0.2602 | 0.99122 | -0.2588 | 19.3
105 | -2.5437 | -1.1437 | 2.5439 | 1.1409 | 0.00018858 | -0.0027598 | 0.081224 | 0.081189 | 0.081224 | 0.99122 | -0.2588 | 0.99131 | -0.25715 | 19.293
106 | -0.050339 | -0.02438 | 0.050339 | 0.02285 | 2.3668e-07 | -0.0015306 | 0.0016435 | 0.0016244 | 0.0016435 | 0.98245 | -0.52299 | 0.98246 | -0.52303 | 0.74703
107 | -0.12131 | -0.055004 | 0.12132 | 0.04589 | 7.8696e-06 | -0.0091136 | 0.0039139 | 0.0038111 | 0.0039139 | 0.98246 | -0.52303 | 0.98252 | -0.52341 | 1.779
108 | 0.070976 | 0.032154 | -0.070957 | -0.034366 | 1.8244e-05 | -0.0022122 | 0.0022895 | 0.0023172 | 0.0023172 | 0.98246 | -0.52303 | 0.98219 | -0.52493 | 1.1034
109 | 0.075922 | 0.036717 | -0.075922 | -0.036771 | 1.8932e-08 | -5.3291e-05 | 0.0024759 | 0.0024766 | 0.0024766 | 0.98328 | -0.018486 | 0.98328 | -0.018484 | 1.1257
110 | 0.48266 | 0.21368 | -0.48265 | -0.21451 | 1.16e-05 | -0.00082883 | 0.015508 | 0.015518 | 0.015518 | 0.98257 | -0.024632 | 0.98255 | -0.024463 | 7.0535
111 | -0.21602 | -0.10462 | 0.21603 | 0.10343 | 3.4417e-06 | -0.0011949 | 0.0070543 | 0.007039 | 0.0070543 | 0.98223 | -0.022111 | 0.98224 | -0.022248 | 3.2065
112 | -0.32517 | -0.15462 | 0.32527 | 0.13832 | 0.00010397 | -0.016304 | 0.010582 | 0.010385 | 0.010582 | 0.98224 | -0.022248 | 0.98254 | -0.024589 | 4.81
113 | 0.10914 | 0.051191 | -0.10911 | -0.052845 | 3.2731e-05 | -0.0016546 | 0.003543 | 0.0035642 | 0.0035642 | 0.98224 | -0.022248 | 0.98193 | -0.024344 | 1.6972
114 | -0.32527 | -0.13832 | 0.32528 | 0.13829 | 4.2121e-06 | -2.2626e-05 | 0.010385 | 0.010385 | 0.010385 | 0.98254 | -0.024589 | 0.98255 | -0.024463 | 4.9452
115 | 0.090164 | 0.042925 | -0.090164 | -0.043668 | 3.4711e-07 | -0.00074318 | 0.002884 | 0.0028933 | 0.0028933 | 0.99955 | -0.0077873 | 0.99954 | -0.0077544 | 1.3151
116 | -3.3642 | -1.4882 | 3.3644 | 1.4866 | 0.00018546 | -0.001538 | 0.10633 | 0.10631 | 0.10633 | 0.99873 | -0.02798 | 0.99879 | -0.026722 | 25.2564
117 | 0.21248 | 0.10023 | -0.21248 | -0.10198 | 4.8863e-06 | -0.0017533 | 0.0069127 | 0.0069348 | 0.0069348 | 0.9811 | -0.54154 | 0.98108 | -0.54135 | 3.1522
118 | 0.21248 | 0.10198 | -0.21248 | -0.10275 | 2.1485e-06 | -0.00076732 | 0.0069348 | 0.0069446 | 0.0069446 | 0.98108 | -0.54135 | 0.98107 | -0.54126 | 3.1567
119 | -0.14981 | -0.072558 | 0.14982 | 0.072401 | 5.9775e-06 | -0.00015699 | 0.0048982 | 0.0048961 | 0.0048982 | 0.98103 | -0.54153 | 0.98107 | -0.54126 | 2.3325

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 7.2639 | 3.1379

## res_load
| p_mw | q_mvar
0 | 0.064827 | 0.031397
1 | 0.13134 | 0.063609
2 | 0.091912 | 0.044515
3 | 0.080911 | 0.039187
4 | 0.10098 | 0.048904
5 | 0.15122 | 0.07324
6 | 0.15363 | 0.074407
7 | 0.089575 | 0.043383
8 | 0.064961 | 0.031462
9 | 0.13505 | 0.065409
10 | 0.092214 | 0.044662
11 | 0.41776 | 0.20233
12 | 0.12625 | 0.061145
13 | 0.14783 | 0.071597
14 | 0.058757 | 0.028457
15 | 0.081867 | 0.03965
16 | 0.11679 | 0.056562
17 | 0.22278 | 0.1079
18 | 0.23185 | 0.11229
19 | 0.13072 | 0.063312
20 | 0.067808 | 0.032841
21 | 0.14043 | 0.068015
22 | 0.14738 | 0.071378
23 | 0.1283 | 0.062139
24 | 0.14047 | 0.068033
25 | 0.12989 | 0.06291
26 | 0.14087 | 0.068228
27 | 0.076466 | 0.037034
28 | 0.1634 | 0.079136
29 | 0.078026 | 0.03779
30 | 0.15232 | 0.07377
31 | 0.16476 | 0.079798
32 | 0.12052 | 0.058369
33 | 0.12429 | 0.060197
34 | 0.15013 | 0.072712
35 | 0.13168 | 0.063775
36 | 0.1297 | 0.062816
37 | 0.13668 | 0.066198
38 | 0.12493 | 0.060508
39 | 0.11665 | 0.056496
40 | 0.15758 | 0.076319
41 | 0.088575 | 0.042899
42 | 0.11011 | 0.053327
43 | 0.10553 | 0.051109
44 | 0.14415 | 0.069813
45 | 0.10585 | 0.051266
46 | 0.050339 | 0.02438
47 | 0.070957 | 0.034366
48 | 0.077071 | 0.037327
49 | 0.079395 | 0.038453
50 | 0.075922 | 0.036771
51 | 0.21602 | 0.10462
52 | 0.10911 | 0.052845
53 | 0.15737 | 0.076217
54 | 0.090164 | 0.043668
55 | 0.069191 | 0.033511
56 | 0.14981 | 0.072558
57 | 0.062657 | 0.030346

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1