## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_488_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_488_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_488_0_node_25 | 20 | n |  | TRUE
3 | bus_MV_488_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_488_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_488_0_node_21 | 20 | n |  | TRUE
6 | bus_MV_488_0_node_122 | 20 | n |  | TRUE
7 | bus_MV_488_0_node_4 | 20 | n |  | TRUE
8 | bus_MV_488_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_488_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_488_0_node_128 | 20 | n |  | TRUE
11 | bus_MV_488_0_node_7 | 20 | n |  | TRUE
12 | bus_MV_488_0_node_8 | 20 | n |  | TRUE
13 | bus_MV_488_0_node_9 | 20 | n |  | TRUE
14 | bus_MV_488_0_node_10 | 20 | n |  | TRUE
15 | bus_MV_488_0_node_127 | 20 | n |  | TRUE
16 | bus_MV_488_0_node_11 | 20 | n |  | TRUE
17 | bus_MV_488_0_node_12 | 20 | n |  | TRUE
18 | bus_MV_488_0_node_13 | 20 | n |  | TRUE
19 | bus_MV_488_0_node_14 | 20 | n |  | TRUE
20 | bus_MV_488_0_node_15 | 20 | n |  | TRUE
21 | bus_MV_488_0_node_16 | 20 | n |  | TRUE
22 | bus_MV_488_0_node_17 | 20 | n |  | TRUE
23 | bus_MV_488_0_node_22 | 20 | n |  | TRUE
24 | bus_MV_488_0_node_171 | 20 | n |  | TRUE
25 | bus_MV_488_0_node_18 | 20 | n |  | TRUE
26 | bus_MV_488_0_node_20 | 20 | n |  | TRUE
27 | bus_MV_488_0_node_19 | 20 | n |  | TRUE
28 | bus_MV_488_0_node_172 | 20 | n |  | TRUE
29 | bus_MV_488_0_node_126 | 20 | n |  | TRUE
30 | bus_MV_488_0_node_23 | 20 | n |  | TRUE
31 | bus_MV_488_0_node_24 | 20 | n |  | TRUE
32 | bus_MV_488_0_node_27 | 20 | n |  | TRUE
33 | bus_MV_488_0_node_26 | 20 | n |  | TRUE
34 | bus_MV_488_0_node_41 | 20 | n |  | TRUE
35 | bus_MV_488_0_node_42 | 20 | n |  | TRUE
36 | bus_MV_488_0_node_28 | 20 | n |  | TRUE
37 | bus_MV_488_0_node_30 | 20 | n |  | TRUE
38 | bus_MV_488_0_node_36 | 20 | n |  | TRUE
39 | bus_MV_488_0_node_29 | 20 | n |  | TRUE
40 | bus_MV_488_0_node_31 | 20 | n |  | TRUE
41 | bus_MV_488_0_node_32 | 20 | n |  | TRUE
42 | bus_MV_488_0_node_34 | 20 | n |  | TRUE
43 | bus_MV_488_0_node_39 | 20 | n |  | TRUE
44 | bus_MV_488_0_node_33 | 20 | n |  | TRUE
45 | bus_MV_488_0_node_35 | 20 | n |  | TRUE
46 | bus_MV_488_0_node_40 | 20 | n |  | TRUE
47 | bus_MV_488_0_node_37 | 20 | n |  | TRUE
48 | bus_MV_488_0_node_38 | 20 | n |  | TRUE
49 | bus_MV_488_0_node_175 | 20 | n |  | TRUE
50 | bus_MV_488_0_node_173 | 20 | n |  | TRUE
51 | bus_MV_488_0_node_124 | 20 | n |  | TRUE
52 | bus_MV_488_0_node_123 | 20 | n |  | TRUE
53 | bus_MV_488_0_node_125 | 20 | n |  | TRUE
54 | bus_HV_488_0_node_125 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_488_0_load_0 | 0 | 0.094319 | 0.045681 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_488_0_load_122 | 6 | 0.46342 | 0.22445 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_488_0_load_4 | 7 | 0.065576 | 0.03176 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_488_0_load_128 | 10 | 0.13106 | 0.063474 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_488_0_load_7 | 11 | 0.14338 | 0.069444 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_488_0_load_8 | 12 | 0.074466 | 0.036065 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_488_0_load_127 | 15 | 0.30581 | 0.14811 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_488_0_load_11 | 16 | 0.057228 | 0.027717 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_488_0_load_14 | 19 | 0.12506 | 0.06057 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_488_0_load_22 | 23 | 0.073274 | 0.035488 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_488_0_load_171 | 24 | 0.15401 | 0.074591 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_488_0_load_18 | 25 | 0.14545 | 0.070445 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_488_0_load_126 | 29 | 0.075218 | 0.03643 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_488_0_load_23 | 30 | 0.14629 | 0.07085 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_488_0_load_41 | 34 | 0.055635 | 0.026945 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_488_0_load_42 | 35 | 0.077293 | 0.037435 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_488_0_load_36 | 38 | 0.14012 | 0.067864 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_488_0_load_29 | 39 | 0.15863 | 0.076829 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_488_0_load_34 | 42 | 0.11303 | 0.054741 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_488_0_load_39 | 43 | 0.15865 | 0.076838 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_488_0_load_33 | 44 | 0.06087 | 0.029481 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_488_0_load_40 | 46 | 0.073606 | 0.035649 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_488_0_load_175 | 49 | 0.090845 | 0.043998 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_488_0_load_173 | 50 | 0.089579 | 0.043385 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_488_0_load_124 | 51 | 0.12122 | 0.058709 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_488_0_load_123 | 52 | 0.18179 | 0.088044 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_488_0_load_125 | 53 | 0.15971 | 0.077351 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 53 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_488_0_line_0 |  | 0 | 1 | 0.0054672 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_488_0_line_1 |  | 0 | 2 | 1.8008 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_488_0_line_2 |  | 1 | 3 | 0.11683 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_488_0_line_3 |  | 1 | 4 | 0.093506 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_488_0_line_4 |  | 2 | 30 | 0.090873 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_488_0_line_5 |  | 3 | 5 | 0.52936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_488_0_line_6 |  | 3 | 6 | 0.076572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_488_0_line_7 |  | 4 | 7 | 0.19718 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_488_0_line_8 |  | 5 | 29 | 0.035372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_488_0_line_9 |  | 5 | 27 | 0.6589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_488_0_line_10 |  | 6 | 51 | 0.14836 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_488_0_line_11 |  | 7 | 8 | 0.069914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_488_0_line_12 |  | 8 | 9 | 0.84797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_488_0_line_13 |  | 9 | 10 | 0.076869 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_488_0_line_14 |  | 10 | 15 | 0.064467 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_488_0_line_15 |  | 11 | 12 | 0.020058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_488_0_line_16 |  | 11 | 13 | 0.076987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_488_0_line_17 |  | 13 | 14 | 0.035644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_488_0_line_18 |  | 14 | 15 | 0.035266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_488_0_line_19 |  | 16 | 17 | 0.037749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_488_0_line_20 |  | 17 | 18 | 0.81189 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_488_0_line_21 |  | 18 | 19 | 0.014236 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_488_0_line_22 |  | 19 | 20 | 0.041865 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_488_0_line_23 |  | 20 | 21 | 0.35146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_488_0_line_24 |  | 20 | 22 | 1.21 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_488_0_line_25 |  | 21 | 23 | 0.13462 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
26 | MV_488_0_line_26 |  | 22 | 24 | 0.008073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_488_0_line_27 |  | 24 | 28 | 1.5701 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_488_0_line_28 |  | 25 | 26 | 0.11743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_488_0_line_29 |  | 25 | 27 | 0.053552 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_488_0_line_30 |  | 26 | 28 | 1.4817 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_488_0_line_31 |  | 28 | 50 | 0.016734 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_488_0_line_32 |  | 30 | 31 | 0.071448 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_488_0_line_33 |  | 31 | 32 | 0.23434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_488_0_line_34 |  | 32 | 35 | 0.098869 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_488_0_line_35 |  | 32 | 33 | 0.33698 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_488_0_line_36 |  | 33 | 34 | 0.018413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_488_0_line_37 |  | 34 | 48 | 0.52738 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_488_0_line_38 |  | 36 | 37 | 0.094201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_488_0_line_39 |  | 36 | 38 | 0.090008 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_488_0_line_40 |  | 37 | 40 | 0.23015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_488_0_line_41 |  | 37 | 41 | 0.23428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_488_0_line_42 |  | 37 | 39 | 0.030859 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_488_0_line_43 |  | 38 | 47 | 0.05072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_488_0_line_44 |  | 40 | 42 | 0.13908 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_488_0_line_45 |  | 41 | 43 | 0.031498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_488_0_line_46 |  | 42 | 45 | 0.15887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_488_0_line_47 |  | 42 | 44 | 0.085278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_488_0_line_48 |  | 45 | 46 | 0.055926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_488_0_line_49 |  | 47 | 48 | 0.6696 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_488_0_line_50 |  | 48 | 49 | 0.10295 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_488_0_line_51 |  | 51 | 52 | 0.016845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_488_0_line_52 |  | 52 | 53 | 0.018089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_488_0_trafo_125 | 25 MVA 110/20 kV | 54 | 53 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2730127.0754 | 1274754.6215
1 | 2730126.4651 | 1274749.6116
2 | 2731743.9857 | 1275547.4326
3 | 2730011.7891 | 1274727.2966
4 | 2730119.65 | 1274705.3521
5 | 2729643.7464 | 1274835.6392
6 | 2730020.2458 | 1274802.9647
7 | 2730105.073 | 1274508.7081
8 | 2730174.2902 | 1274497.5011
9 | 2730290.0794 | 1273787.2948
10 | 2730250.5469 | 1273721.3703
11 | 2730378.2456 | 1273629.8657
12 | 2730397.8184 | 1273625.48
13 | 2730384.4193 | 1273706.1107
14 | 2730348.8141 | 1273704.5118
15 | 2730314.1942 | 1273711.1216
16 | 2728049.2064 | 1276040.5874
17 | 2728011.736 | 1276035.1581
18 | 2727496.4256 | 1275916.2222
19 | 2727495.7027 | 1275902.0152
20 | 2727490.7285 | 1275860.468
21 | 2727360.114 | 1275537.2053
22 | 2727585.311 | 1275043.2303
23 | 2727230.2948 | 1275501.5601
24 | 2727582.0719 | 1275035.831
25 | 2729125.0808 | 1274620.7308
26 | 2729010.9626 | 1274592.6086
27 | 2729178.2963 | 1274626.7231
28 | 2727989.2913 | 1273519.4229
29 | 2729637.6482 | 1274870.4833
30 | 2731824.6634 | 1275589.6751
31 | 2731854.2201 | 1275524.6276
32 | 2732037.1252 | 1275503.3626
33 | 2732045.4385 | 1275721.4609
34 | 2732063.5479 | 1275725.0808
35 | 2732011.5292 | 1275407.8638
36 | 2731925.5414 | 1276308.9299
37 | 2731928.9291 | 1276401.8184
38 | 2732015.4456 | 1276304.614
39 | 2731940.6516 | 1276430.3528
40 | 2731806.8904 | 1276475.085
41 | 2731768.3631 | 1276340.2264
42 | 2731686.1525 | 1276544.1123
43 | 2731742.7753 | 1276321.7482
44 | 2731617.4113 | 1276594.8504
45 | 2731766.8372 | 1276680.9692
46 | 2731714.6448 | 1276701.0602
47 | 2732066.145 | 1276302.335
48 | 2732558.4669 | 1275907.254
49 | 2732598.54 | 1276001.8244
50 | 2727975.7077 | 1273509.6303
51 | 2729931.9766 | 1274922.2046
52 | 2729945.8735 | 1274931.7256
53 | 2729960.4943 | 1274942.3741
54 | 2729960.4943 | 1274942.3741

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99846 | -0.0034174 | 0.094319 | 0.045681
1 | 0.99847 | -0.0034735 | 0 | 0
2 | 0.99478 | -0.036173 | 0 | 0
3 | 0.99874 | -0.0054597 | 0 | 0
4 | 0.99838 | -0.0028279 | 0 | 0
5 | 0.99827 | -0.003864 | 0 | 0
6 | 0.999 | -0.0069493 | 0.46342 | 0.22445
7 | 0.99811 | -0.0049924 | 0.065576 | 0.03176
8 | 0.99805 | -0.004555 | 0 | 0
9 | 0.99735 | 0.0013471 | 0 | 0
10 | 0.99725 | 0.00070856 | 0.13106 | 0.063474
11 | 0.99714 | 0.00064263 | 0.14338 | 0.069444
12 | 0.99714 | 0.00066029 | 0.074466 | 0.036065
13 | 0.99717 | 0.00044769 | 0 | 0
14 | 0.99718 | 0.00036049 | 0 | 0
15 | 0.99719 | 0.00027612 | 0.30581 | 0.14811
16 | 0.99464 | -0.034676 | 0.057228 | 0.027717
17 | 0.99465 | -0.034701 | 0 | 0
18 | 0.9947 | -0.034715 | 0 | 0
19 | 0.9947 | -0.034706 | 0.12506 | 0.06057
20 | 0.99471 | -0.034742 | 0 | 0
21 | 0.99468 | -0.034529 | 0 | 0
22 | 0.99509 | -0.03504 | 0 | 0
23 | 0.99466 | -0.03465 | 0.073274 | 0.035488
24 | 0.99509 | -0.035034 | 0.15401 | 0.074591
25 | 0.99768 | -0.0025584 | 0.14545 | 0.070445
26 | 0.99761 | -0.0023329 | 0 | 0
27 | 0.99775 | -0.0018395 | 0 | 0
28 | 0.99626 | -0.019165 | 0 | 0
29 | 0.99827 | -0.003833 | 0.075218 | 0.03643
30 | 0.99466 | -0.035324 | 0.14629 | 0.07085
31 | 0.99454 | -0.036481 | 0 | 0
32 | 0.99426 | -0.034648 | 0 | 0
33 | 0.9939 | -0.032177 | 0 | 0
34 | 0.99388 | -0.032037 | 0.055635 | 0.026945
35 | 0.99425 | -0.034742 | 0.077293 | 0.037435
36 | 0.99234 | -0.035119 | 0 | 0
37 | 0.99227 | -0.034599 | 0 | 0
38 | 0.99244 | -0.034325 | 0.14012 | 0.067864
39 | 0.99227 | -0.03454 | 0.15863 | 0.076829
40 | 0.9922 | -0.034055 | 0 | 0
41 | 0.99222 | -0.034201 | 0 | 0
42 | 0.99213 | -0.034563 | 0.11303 | 0.054741
43 | 0.99222 | -0.034141 | 0.15865 | 0.076838
44 | 0.99213 | -0.034505 | 0.06087 | 0.029481
45 | 0.99212 | -0.034454 | 0 | 0
46 | 0.99211 | -0.034406 | 0.073606 | 0.035649
47 | 0.99248 | -0.034686 | 0 | 0
48 | 0.99308 | -0.039074 | 0 | 0
49 | 0.99307 | -0.038969 | 0.090845 | 0.043998
50 | 0.99626 | -0.019147 | 0.089579 | 0.043385
51 | 0.99986 | 0.00096036 | 0.12122 | 0.058709
52 | 0.99992 | 0.00051598 | 0.18179 | 0.088044
53 | 1 | 0 | -3.4027 | -1.4629
54 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -1.1751 | -0.50919 | 1.1751 | 0.50907 | 1.0006e-05 | -0.00012717 | 0.037027 | 0.037025 | 0.037027 | 0.99846 | -0.0034174 | 0.99847 | -0.0034735 | 16.8303
1 | 1.0808 | 0.46351 | -1.0771 | -0.46332 | 0.0037116 | 0.00018953 | 0.034 | 0.034024 | 0.034024 | 0.99846 | -0.0034174 | 0.99478 | -0.036173 | 16.202
2 | -1.8963 | -0.82985 | 1.8968 | 0.82723 | 0.00055829 | -0.0026161 | 0.059845 | 0.059813 | 0.059845 | 0.99847 | -0.0034735 | 0.99874 | -0.0054597 | 27.2022
3 | 0.72118 | 0.32078 | -0.72112 | -0.32298 | 6.5082e-05 | -0.0022062 | 0.02282 | 0.022846 | 0.022846 | 0.99847 | -0.0034735 | 0.99838 | -0.0028279 | 10.3848
4 | 1.0771 | 0.46332 | -1.0769 | -0.46543 | 0.00014054 | -0.0021052 | 0.034024 | 0.034049 | 0.034049 | 0.99478 | -0.036173 | 0.99466 | -0.035324 | 15.4767
5 | 0.72177 | 0.25494 | -0.72142 | -0.26744 | 0.00034786 | -0.012498 | 0.022125 | 0.022249 | 0.022249 | 0.99874 | -0.0054597 | 0.99827 | -0.003864 | 10.1132
6 | -2.6186 | -1.0822 | 2.6193 | 1.0806 | 0.00068545 | -0.0016208 | 0.081896 | 0.081876 | 0.081896 | 0.99874 | -0.0054597 | 0.999 | -0.0069493 | 37.2255
7 | 0.72112 | 0.32298 | -0.72093 | -0.3231 | 0.0001834 | -0.0001197 | 0.022846 | 0.022849 | 0.022849 | 0.99838 | -0.0028279 | 0.99811 | -0.0049924 | 10.8806
8 | 0.075218 | 0.035588 | -0.075218 | -0.03643 | 2.7461e-07 | -0.00084155 | 0.0024063 | 0.0024168 | 0.0024168 | 0.99827 | -0.003864 | 0.99827 | -0.003833 | 1.0985
9 | 0.6462 | 0.23185 | -0.64585 | -0.24742 | 0.00034941 | -0.015566 | 0.019853 | 0.02001 | 0.02001 | 0.99827 | -0.003864 | 0.99775 | -0.0018395 | 9.0957
10 | -3.0827 | -1.305 | 3.0852 | 1.3064 | 0.0024733 | 0.0013723 | 0.096733 | 0.096731 | 0.096733 | 0.999 | -0.0069493 | 0.99986 | 0.00096036 | 46.0632
11 | 0.65536 | 0.29134 | -0.65532 | -0.29299 | 4.0197e-05 | -0.001651 | 0.020743 | 0.020763 | 0.020763 | 0.99811 | -0.0049924 | 0.99805 | -0.004555 | 9.4375
12 | 0.65532 | 0.29299 | -0.65482 | -0.313 | 0.0004937 | -0.020007 | 0.020763 | 0.021007 | 0.021007 | 0.99805 | -0.004555 | 0.99735 | 0.0013471 | 9.5488
13 | 0.65482 | 0.313 | -0.65476 | -0.31305 | 6.0444e-05 | -5.3412e-05 | 0.021007 | 0.021008 | 0.021008 | 0.99735 | 0.0013471 | 0.99725 | 0.00070856 | 10.004
14 | 0.52371 | 0.24958 | -0.52367 | -0.24964 | 3.2394e-05 | -5.6243e-05 | 0.016793 | 0.016794 | 0.016794 | 0.99725 | 0.00070856 | 0.99719 | 0.00027612 | 7.9973
15 | 0.074466 | 0.035589 | -0.074466 | -0.036065 | 1.5325e-07 | -0.00047613 | 0.0023894 | 0.0023953 | 0.0023953 | 0.99714 | 0.00064263 | 0.99714 | 0.00066029 | 1.0888
16 | -0.21785 | -0.10503 | 0.21785 | 0.10321 | 5.0219e-06 | -0.0018262 | 0.0070015 | 0.0069787 | 0.0070015 | 0.99714 | 0.00064263 | 0.99717 | 0.00044769 | 3.1825
17 | -0.21785 | -0.10321 | 0.21786 | 0.10236 | 2.314e-06 | -0.00084554 | 0.0069787 | 0.0069683 | 0.0069787 | 0.99717 | 0.00044769 | 0.99718 | 0.00036049 | 3.1721
18 | -0.21786 | -0.10236 | 0.21786 | 0.10152 | 2.2827e-06 | -0.0008366 | 0.0069683 | 0.006958 | 0.0069683 | 0.99718 | 0.00036049 | 0.99719 | 0.00027612 | 3.1674
19 | -0.057228 | -0.027717 | 0.057228 | 0.026825 | 1.7059e-07 | -0.00089162 | 0.0018455 | 0.0018343 | 0.0018455 | 0.99464 | -0.034676 | 0.99465 | -0.034701 | 0.83885
20 | -0.057228 | -0.026825 | 0.057231 | 0.0076473 | 3.2613e-06 | -0.019178 | 0.0018343 | 0.0016757 | 0.0018343 | 0.99465 | -0.034701 | 0.9947 | -0.034715 | 0.83379
21 | -0.057231 | -0.0076473 | 0.057231 | 0.007311 | 5.3323e-08 | -0.00033629 | 0.0016757 | 0.0016744 | 0.0016757 | 0.9947 | -0.034715 | 0.9947 | -0.034706 | 0.76168
22 | -0.18229 | -0.067881 | 0.18229 | 0.066892 | 1.778e-06 | -0.0009885 | 0.0056452 | 0.0056353 | 0.0056452 | 0.9947 | -0.034706 | 0.99471 | -0.034742 | 2.566
23 | 0.073278 | 0.027028 | -0.073275 | -0.03533 | 2.506e-06 | -0.0083019 | 0.0022666 | 0.0023609 | 0.0023609 | 0.99471 | -0.034742 | 0.99468 | -0.034529 | 1.0731
24 | -0.25557 | -0.09392 | 0.25567 | 0.065354 | 9.7485e-05 | -0.028566 | 0.0079019 | 0.0076554 | 0.0079019 | 0.99471 | -0.034742 | 0.99509 | -0.03504 | 3.5918
25 | 0.073275 | 0.03533 | -0.073274 | -0.035488 | 1.338e-06 | -0.00015817 | 0.0023609 | 0.0023629 | 0.0023629 | 0.99468 | -0.034529 | 0.99466 | -0.03465 | 1.1252
26 | -0.25567 | -0.065354 | 0.25567 | 0.065163 | 6.315e-07 | -0.00019068 | 0.0076554 | 0.0076541 | 0.0076554 | 0.99509 | -0.03504 | 0.99509 | -0.035034 | 3.4797
27 | -0.40968 | -0.13975 | 0.41012 | 0.13817 | 0.00044052 | -0.0015823 | 0.012557 | 0.01254 | 0.012557 | 0.99509 | -0.035034 | 0.99626 | -0.019165 | 5.9796
28 | 0.50036 | 0.17701 | -0.50033 | -0.17979 | 3.7037e-05 | -0.0027796 | 0.015357 | 0.015384 | 0.015384 | 0.99768 | -0.0025584 | 0.99761 | -0.0023329 | 6.9928
29 | -0.64581 | -0.24746 | 0.64585 | 0.24742 | 3.8207e-05 | -3.9707e-05 | 0.020011 | 0.02001 | 0.020011 | 0.99768 | -0.0025584 | 0.99775 | -0.0018395 | 9.5291
30 | 0.50033 | 0.17979 | -0.4997 | -0.18116 | 0.00062552 | -0.0013663 | 0.015384 | 0.015401 | 0.015401 | 0.99761 | -0.0023329 | 0.99626 | -0.019165 | 7.334
31 | 0.089579 | 0.042989 | -0.089579 | -0.043385 | 1.855e-07 | -0.0003965 | 0.0028791 | 0.002884 | 0.002884 | 0.99626 | -0.019165 | 0.99626 | -0.019147 | 1.3109
32 | 0.93063 | 0.39458 | -0.93052 | -0.3946 | 0.00010956 | -1.575e-05 | 0.029337 | 0.029337 | 0.029337 | 0.99466 | -0.035324 | 0.99454 | -0.036481 | 13.9702
33 | 0.93052 | 0.3946 | -0.93025 | -0.40005 | 0.00026984 | -0.0054525 | 0.029337 | 0.029401 | 0.029401 | 0.99454 | -0.036481 | 0.99426 | -0.034648 | 13.3639
34 | 0.077294 | 0.037319 | -0.077293 | -0.037435 | 1.0946e-06 | -0.00011599 | 0.0024921 | 0.0024935 | 0.0024935 | 0.99426 | -0.034648 | 0.99425 | -0.034742 | 1.1874
35 | 0.85295 | 0.36273 | -0.85263 | -0.37058 | 0.0003269 | -0.0078538 | 0.026911 | 0.027002 | 0.027002 | 0.99426 | -0.034648 | 0.9939 | -0.032177 | 12.2738
36 | 0.85263 | 0.37058 | -0.85261 | -0.37101 | 1.7926e-05 | -0.00042896 | 0.027002 | 0.027007 | 0.027007 | 0.9939 | -0.032177 | 0.99388 | -0.032037 | 12.2761
37 | 0.79697 | 0.34407 | -0.79638 | -0.34431 | 0.00059751 | -0.00024714 | 0.025213 | 0.025221 | 0.025221 | 0.99388 | -0.032037 | 0.99308 | -0.039074 | 12.0098
38 | 0.56487 | 0.25176 | -0.56483 | -0.25396 | 4.0762e-05 | -0.0022026 | 0.017991 | 0.018017 | 0.018017 | 0.99234 | -0.035119 | 0.99227 | -0.034599 | 8.1895
39 | -0.56487 | -0.25176 | 0.56493 | 0.25168 | 5.1901e-05 | -7.3313e-05 | 0.017991 | 0.017989 | 0.017991 | 0.99234 | -0.035119 | 0.99244 | -0.034325 | 8.5669
40 | 0.24754 | 0.10726 | -0.24752 | -0.11267 | 1.9079e-05 | -0.0054043 | 0.0078485 | 0.0079124 | 0.0079124 | 0.99227 | -0.034599 | 0.9922 | -0.034055 | 3.5965
41 | 0.15866 | 0.070593 | -0.15865 | -0.076098 | 8.0876e-06 | -0.0055049 | 0.005052 | 0.0051193 | 0.0051193 | 0.99227 | -0.034599 | 0.99222 | -0.034201 | 2.3269
42 | 0.15863 | 0.076104 | -0.15863 | -0.076829 | 1.0813e-06 | -0.00072512 | 0.0051187 | 0.0051278 | 0.0051278 | 0.99227 | -0.034599 | 0.99227 | -0.03454 | 2.3308
43 | -0.70505 | -0.31955 | 0.70508 | 0.31836 | 3.4306e-05 | -0.0011826 | 0.022516 | 0.022502 | 0.022516 | 0.99244 | -0.034325 | 0.99248 | -0.034686 | 10.2346
44 | 0.24752 | 0.11267 | -0.2475 | -0.11282 | 1.5517e-05 | -0.00015372 | 0.0079124 | 0.0079144 | 0.0079144 | 0.9922 | -0.034055 | 0.99213 | -0.034563 | 3.7688
45 | 0.15865 | 0.076098 | -0.15865 | -0.076838 | 1.104e-06 | -0.00074007 | 0.0051193 | 0.0051286 | 0.0051286 | 0.99222 | -0.034201 | 0.99222 | -0.034141 | 2.3312
46 | 0.073607 | 0.030601 | -0.073606 | -0.034335 | 1.1621e-06 | -0.0037334 | 0.0023194 | 0.0023633 | 0.0023633 | 0.99213 | -0.034563 | 0.99212 | -0.034454 | 1.0742
47 | 0.060871 | 0.027477 | -0.06087 | -0.029481 | 4.3529e-07 | -0.0020041 | 0.0019432 | 0.0019679 | 0.0019679 | 0.99213 | -0.034563 | 0.99213 | -0.034505 | 0.89451
48 | 0.073606 | 0.034335 | -0.073606 | -0.035649 | 4.1986e-07 | -0.0013142 | 0.0023633 | 0.0023797 | 0.0023797 | 0.99212 | -0.034454 | 0.99211 | -0.034406 | 1.0817
49 | -0.70508 | -0.31836 | 0.70553 | 0.30274 | 0.00044887 | -0.015624 | 0.022502 | 0.022317 | 0.022502 | 0.99248 | -0.034686 | 0.99308 | -0.039074 | 10.2281
50 | 0.090846 | 0.041574 | -0.090845 | -0.043998 | 1.171e-06 | -0.0024237 | 0.0029042 | 0.0029342 | 0.0029342 | 0.99308 | -0.039074 | 0.99307 | -0.038969 | 1.3337
51 | -3.2064 | -1.3651 | 3.2066 | 1.3647 | 0.00022765 | -0.00033459 | 0.10061 | 0.10061 | 0.10061 | 0.99986 | 0.00096036 | 0.99992 | 0.00051598 | 45.7339
52 | -3.3884 | -1.4528 | 3.3887 | 1.4524 | 0.00027356 | -0.00035072 | 0.10643 | 0.10643 | 0.10643 | 0.99992 | 0.00051598 | 1 | 0 | 48.3795

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 3.5624 | 1.5403

## res_load
| p_mw | q_mvar
0 | 0.094319 | 0.045681
1 | 0.46342 | 0.22445
2 | 0.065576 | 0.03176
3 | 0.13106 | 0.063474
4 | 0.14338 | 0.069444
5 | 0.074466 | 0.036065
6 | 0.30581 | 0.14811
7 | 0.057228 | 0.027717
8 | 0.12506 | 0.06057
9 | 0.073274 | 0.035488
10 | 0.15401 | 0.074591
11 | 0.14545 | 0.070445
12 | 0.075218 | 0.03643
13 | 0.14629 | 0.07085
14 | 0.055635 | 0.026945
15 | 0.077293 | 0.037435
16 | 0.14012 | 0.067864
17 | 0.15863 | 0.076829
18 | 0.11303 | 0.054741
19 | 0.15865 | 0.076838
20 | 0.06087 | 0.029481
21 | 0.073606 | 0.035649
22 | 0.090845 | 0.043998
23 | 0.089579 | 0.043385
24 | 0.12122 | 0.058709
25 | 0.18179 | 0.088044
26 | 0.15971 | 0.077351

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1