## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_500_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_500_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_500_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_500_0_node_103 | 20 | n |  | TRUE
4 | bus_MV_500_0_node_90 | 20 | n |  | TRUE
5 | bus_MV_500_0_node_101 | 20 | n |  | TRUE
6 | bus_MV_500_0_node_4 | 20 | n |  | TRUE
7 | bus_MV_500_0_node_15 | 20 | n |  | TRUE
8 | bus_MV_500_0_node_14 | 20 | n |  | TRUE
9 | bus_MV_500_0_node_74 | 20 | n |  | TRUE
10 | bus_MV_500_0_node_83 | 20 | n |  | TRUE
11 | bus_MV_500_0_node_66 | 20 | n |  | TRUE
12 | bus_MV_500_0_node_23 | 20 | n |  | TRUE
13 | bus_MV_500_0_node_81 | 20 | n |  | TRUE
14 | bus_MV_500_0_node_5 | 20 | n |  | TRUE
15 | bus_MV_500_0_node_6 | 20 | n |  | TRUE
16 | bus_MV_500_0_node_114 | 20 | n |  | TRUE
17 | bus_MV_500_0_node_43 | 20 | n |  | TRUE
18 | bus_MV_500_0_node_89 | 20 | n |  | TRUE
19 | bus_MV_500_0_node_104 | 20 | n |  | TRUE
20 | bus_MV_500_0_node_42 | 20 | n |  | TRUE
21 | bus_MV_500_0_node_88 | 20 | n |  | TRUE
22 | bus_MV_500_0_node_7 | 20 | n |  | TRUE
23 | bus_MV_500_0_node_16 | 20 | n |  | TRUE
24 | bus_MV_500_0_node_17 | 20 | n |  | TRUE
25 | bus_MV_500_0_node_8 | 20 | n |  | TRUE
26 | bus_MV_500_0_node_9 | 20 | n |  | TRUE
27 | bus_MV_500_0_node_13 | 20 | n |  | TRUE
28 | bus_MV_500_0_node_105 | 20 | n |  | TRUE
29 | bus_MV_500_0_node_106 | 20 | n |  | TRUE
30 | bus_MV_500_0_node_10 | 20 | n |  | TRUE
31 | bus_MV_500_0_node_12 | 20 | n |  | TRUE
32 | bus_MV_500_0_node_109 | 20 | n |  | TRUE
33 | bus_MV_500_0_node_11 | 20 | n |  | TRUE
34 | bus_MV_500_0_node_28 | 20 | n |  | TRUE
35 | bus_MV_500_0_node_30 | 20 | n |  | TRUE
36 | bus_MV_500_0_node_40 | 20 | n |  | TRUE
37 | bus_MV_500_0_node_108 | 20 | n |  | TRUE
38 | bus_MV_500_0_node_29 | 20 | n |  | TRUE
39 | bus_MV_500_0_node_31 | 20 | n |  | TRUE
40 | bus_MV_500_0_node_41 | 20 | n |  | TRUE
41 | bus_MV_500_0_node_54 | 20 | n |  | TRUE
42 | bus_MV_500_0_node_39 | 20 | n |  | TRUE
43 | bus_MV_500_0_node_18 | 20 | n |  | TRUE
44 | bus_MV_500_0_node_65 | 20 | n |  | TRUE
45 | bus_MV_500_0_node_20 | 20 | n |  | TRUE
46 | bus_MV_500_0_node_71 | 20 | n |  | TRUE
47 | bus_MV_500_0_node_19 | 20 | n |  | TRUE
48 | bus_MV_500_0_node_72 | 20 | n |  | TRUE
49 | bus_MV_500_0_node_64 | 20 | n |  | TRUE
50 | bus_MV_500_0_node_69 | 20 | n |  | TRUE
51 | bus_MV_500_0_node_60 | 20 | n |  | TRUE
52 | bus_MV_500_0_node_61 | 20 | n |  | TRUE
53 | bus_MV_500_0_node_62 | 20 | n |  | TRUE
54 | bus_MV_500_0_node_21 | 20 | n |  | TRUE
55 | bus_MV_500_0_node_22 | 20 | n |  | TRUE
56 | bus_MV_500_0_node_24 | 20 | n |  | TRUE
57 | bus_MV_500_0_node_92 | 20 | n |  | TRUE
58 | bus_MV_500_0_node_25 | 20 | n |  | TRUE
59 | bus_MV_500_0_node_26 | 20 | n |  | TRUE
60 | bus_MV_500_0_node_67 | 20 | n |  | TRUE
61 | bus_MV_500_0_node_27 | 20 | n |  | TRUE
62 | bus_MV_500_0_node_93 | 20 | n |  | TRUE
63 | bus_MV_500_0_node_55 | 20 | n |  | TRUE
64 | bus_MV_500_0_node_68 | 20 | n |  | TRUE
65 | bus_MV_500_0_node_32 | 20 | n |  | TRUE
66 | bus_MV_500_0_node_33 | 20 | n |  | TRUE
67 | bus_MV_500_0_node_34 | 20 | n |  | TRUE
68 | bus_MV_500_0_node_115 | 20 | n |  | TRUE
69 | bus_MV_500_0_node_35 | 20 | n |  | TRUE
70 | bus_MV_500_0_node_98 | 20 | n |  | TRUE
71 | bus_MV_500_0_node_38 | 20 | n |  | TRUE
72 | bus_MV_500_0_node_94 | 20 | n |  | TRUE
73 | bus_MV_500_0_node_111 | 20 | n |  | TRUE
74 | bus_MV_500_0_node_97 | 20 | n |  | TRUE
75 | bus_MV_500_0_node_36 | 20 | n |  | TRUE
76 | bus_MV_500_0_node_46 | 20 | n |  | TRUE
77 | bus_MV_500_0_node_37 | 20 | n |  | TRUE
78 | bus_MV_500_0_node_53 | 20 | n |  | TRUE
79 | bus_MV_500_0_node_44 | 20 | n |  | TRUE
80 | bus_MV_500_0_node_45 | 20 | n |  | TRUE
81 | bus_MV_500_0_node_107 | 20 | n |  | TRUE
82 | bus_MV_500_0_node_48 | 20 | n |  | TRUE
83 | bus_MV_500_0_node_49 | 20 | n |  | TRUE
84 | bus_MV_500_0_node_50 | 20 | n |  | TRUE
85 | bus_MV_500_0_node_47 | 20 | n |  | TRUE
86 | bus_MV_500_0_node_113 | 20 | n |  | TRUE
87 | bus_MV_500_0_node_51 | 20 | n |  | TRUE
88 | bus_MV_500_0_node_52 | 20 | n |  | TRUE
89 | bus_MV_500_0_node_86 | 20 | n |  | TRUE
90 | bus_MV_500_0_node_110 | 20 | n |  | TRUE
91 | bus_MV_500_0_node_112 | 20 | n |  | TRUE
92 | bus_MV_500_0_node_57 | 20 | n |  | TRUE
93 | bus_MV_500_0_node_58 | 20 | n |  | TRUE
94 | bus_MV_500_0_node_91 | 20 | n |  | TRUE
95 | bus_MV_500_0_node_79 | 20 | n |  | TRUE
96 | bus_MV_500_0_node_82 | 20 | n |  | TRUE
97 | bus_MV_500_0_node_77 | 20 | n |  | TRUE
98 | bus_MV_500_0_node_59 | 20 | n |  | TRUE
99 | bus_MV_500_0_node_95 | 20 | n |  | TRUE
100 | bus_MV_500_0_node_96 | 20 | n |  | TRUE
101 | bus_MV_500_0_node_85 | 20 | n |  | TRUE
102 | bus_MV_500_0_node_73 | 20 | n |  | TRUE
103 | bus_MV_500_0_node_75 | 20 | n |  | TRUE
104 | bus_MV_500_0_node_63 | 20 | n |  | TRUE
105 | bus_MV_500_0_node_70 | 20 | n |  | TRUE
106 | bus_MV_500_0_node_102 | 20 | n |  | TRUE
107 | bus_MV_500_0_node_76 | 20 | n |  | TRUE
108 | bus_MV_500_0_node_78 | 20 | n |  | TRUE
109 | bus_MV_500_0_node_84 | 20 | n |  | TRUE
110 | bus_MV_500_0_node_100 | 20 | n |  | TRUE
111 | bus_MV_500_0_node_87 | 20 | n |  | TRUE
112 | bus_MV_500_0_node_99 | 20 | n |  | TRUE
113 | bus_HV_500_0_node_103 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_500_0_load_0 | 0 | 0.23792 | 0.11523 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_500_0_load_103 | 3 | 0.3656 | 0.17707 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_500_0_load_101 | 5 | 0.40182 | 0.19461 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_500_0_load_14 | 8 | 0.27375 | 0.13258 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_500_0_load_83 | 10 | 0.58394 | 0.28281 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_500_0_load_66 | 11 | 0.081998 | 0.039714 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_500_0_load_23 | 12 | 0.090027 | 0.043602 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_500_0_load_81 | 13 | 0.2189 | 0.10602 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_500_0_load_5 | 14 | 0.31465 | 0.15239 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_500_0_load_114 | 16 | 0.071525 | 0.034641 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_500_0_load_104 | 19 | 0.22461 | 0.10879 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_500_0_load_42 | 20 | 0.31998 | 0.15497 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_500_0_load_16 | 23 | 0.19812 | 0.095952 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_500_0_load_8 | 25 | 0.14608 | 0.070747 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_500_0_load_106 | 29 | 0.073276 | 0.035489 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_500_0_load_109 | 32 | 0.15383 | 0.074504 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_500_0_load_28 | 34 | 0.15212 | 0.073675 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_500_0_load_40 | 36 | 0.29167 | 0.14126 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_500_0_load_108 | 37 | 0.3213 | 0.15561 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_500_0_load_31 | 39 | 0.21618 | 0.1047 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_500_0_load_54 | 41 | 0.14795 | 0.071654 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_500_0_load_71 | 46 | 0.25997 | 0.12591 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_500_0_load_72 | 48 | 0.83087 | 0.40241 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_500_0_load_64 | 49 | 0.31366 | 0.15191 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_500_0_load_21 | 54 | 0.38804 | 0.18794 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_500_0_load_92 | 57 | 0.084402 | 0.040878 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_500_0_load_67 | 60 | 0.24462 | 0.11848 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_500_0_load_93 | 62 | 0.095886 | 0.04644 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_500_0_load_55 | 63 | 0.23396 | 0.11331 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_500_0_load_32 | 65 | 0.28582 | 0.13843 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_500_0_load_115 | 68 | 0.21087 | 0.10213 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_500_0_load_94 | 72 | 0.091706 | 0.044415 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_500_0_load_111 | 73 | 0.091436 | 0.044285 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_500_0_load_36 | 75 | 0.15779 | 0.076422 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_500_0_load_53 | 78 | 0.070707 | 0.034245 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_500_0_load_44 | 79 | 0.2907 | 0.14079 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_500_0_load_107 | 81 | 0.34812 | 0.1686 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_500_0_load_113 | 86 | 0.17238 | 0.083486 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_500_0_load_52 | 88 | 0.40384 | 0.19559 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_500_0_load_86 | 89 | 0.5055 | 0.24483 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_500_0_load_110 | 90 | 0.077573 | 0.03757 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_500_0_load_112 | 91 | 0.2917 | 0.14128 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_500_0_load_91 | 94 | 0.077963 | 0.037759 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_500_0_load_79 | 95 | 0.094074 | 0.045562 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_500_0_load_59 | 98 | 0.12866 | 0.062314 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_500_0_load_85 | 101 | 0.18146 | 0.087885 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_500_0_load_73 | 102 | 0.069861 | 0.033835 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_500_0_load_75 | 103 | 0.1091 | 0.052841 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_500_0_load_63 | 104 | 0.2078 | 0.10064 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_500_0_load_102 | 106 | 0.27318 | 0.13231 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_500_0_load_76 | 107 | 0.09337 | 0.045221 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_500_0_load_78 | 108 | 0.27962 | 0.13543 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_500_0_load_100 | 110 | 1.1133 | 0.53922 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_500_0_load_87 | 111 | 0.12258 | 0.059367 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_500_0_load_99 | 112 | 0.088541 | 0.042882 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_500_0_line_0 |  | 0 | 1 | 0.005934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_500_0_line_1 |  | 1 | 2 | 0.13575 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
2 | MV_500_0_line_2 |  | 1 | 3 | 0.34794 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
3 | MV_500_0_line_3 |  | 2 | 5 | 0.030924 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
4 | MV_500_0_line_4 |  | 3 | 4 | 0.056837 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_500_0_line_5 |  | 4 | 18 | 0.287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_500_0_line_6 |  | 5 | 9 | 0.027217 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
7 | MV_500_0_line_7 |  | 6 | 7 | 0.1205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_500_0_line_8 |  | 6 | 8 | 0.0067885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_500_0_line_9 |  | 7 | 16 | 0.081957 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_500_0_line_10 |  | 7 | 17 | 0.30301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_500_0_line_11 |  | 9 | 52 | 0.1116 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
12 | MV_500_0_line_12 |  | 10 | 11 | 0.13987 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
13 | MV_500_0_line_13 |  | 10 | 12 | 0.18732 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_500_0_line_14 |  | 10 | 13 | 0.036472 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
15 | MV_500_0_line_15 |  | 11 | 45 | 0.043765 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
16 | MV_500_0_line_16 |  | 12 | 54 | 0.038946 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_500_0_line_17 |  | 13 | 96 | 0.0068917 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
18 | MV_500_0_line_18 |  | 14 | 15 | 0.014501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_500_0_line_19 |  | 15 | 22 | 0.49761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_500_0_line_20 |  | 17 | 20 | 0.077828 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_500_0_line_21 |  | 18 | 19 | 0.20663 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_500_0_line_22 |  | 18 | 20 | 0.46013 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_500_0_line_23 |  | 18 | 21 | 0.025859 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_500_0_line_24 |  | 19 | 28 | 0.17192 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_500_0_line_25 |  | 21 | 111 | 0.050484 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_500_0_line_26 |  | 22 | 23 | 0.004176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_500_0_line_27 |  | 23 | 24 | 0.040226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_500_0_line_28 |  | 24 | 43 | 0.076607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_500_0_line_29 |  | 25 | 26 | 0.099351 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_500_0_line_30 |  | 26 | 27 | 0.26748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_500_0_line_31 |  | 27 | 37 | 0.030684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_500_0_line_32 |  | 27 | 31 | 0.88277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_500_0_line_33 |  | 28 | 29 | 0.13991 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_500_0_line_34 |  | 29 | 38 | 0.6467 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_500_0_line_35 |  | 30 | 31 | 0.25966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_500_0_line_36 |  | 30 | 32 | 0.059113 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_500_0_line_37 |  | 31 | 36 | 0.052355 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_500_0_line_38 |  | 31 | 33 | 0.43845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_500_0_line_39 |  | 33 | 34 | 0.051774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_500_0_line_40 |  | 33 | 35 | 0.28836 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_500_0_line_41 |  | 34 | 38 | 0.037276 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_500_0_line_42 |  | 35 | 39 | 0.016603 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_500_0_line_43 |  | 40 | 41 | 0.14651 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_500_0_line_44 |  | 40 | 42 | 1.0812 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_500_0_line_45 |  | 42 | 78 | 0.034796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_500_0_line_46 |  | 42 | 77 | 0.49217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_500_0_line_47 |  | 43 | 44 | 0.013556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_500_0_line_48 |  | 43 | 45 | 0.074353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_500_0_line_49 |  | 43 | 46 | 0.047853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_500_0_line_50 |  | 44 | 49 | 0.00493 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_500_0_line_51 |  | 45 | 47 | 0.072867 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
52 | MV_500_0_line_52 |  | 46 | 50 | 0.053517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_500_0_line_53 |  | 47 | 48 | 0.02668 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
54 | MV_500_0_line_54 |  | 48 | 51 | 0.093481 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_500_0_line_55 |  | 48 | 52 | 0.09037 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
56 | MV_500_0_line_56 |  | 48 | 53 | 0.039839 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_500_0_line_57 |  | 49 | 104 | 0.0065221 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_500_0_line_58 |  | 50 | 64 | 0.032484 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_500_0_line_59 |  | 51 | 98 | 0.031065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_500_0_line_60 |  | 52 | 102 | 0.024152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_500_0_line_61 |  | 53 | 103 | 0.0094634 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_500_0_line_62 |  | 54 | 55 | 0.045259 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_500_0_line_63 |  | 55 | 56 | 0.25945 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_500_0_line_64 |  | 56 | 57 | 0.010046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_500_0_line_65 |  | 58 | 59 | 0.5408 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_500_0_line_66 |  | 58 | 60 | 0.042942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_500_0_line_67 |  | 59 | 61 | 0.41471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_500_0_line_68 |  | 59 | 62 | 0.044852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_500_0_line_69 |  | 60 | 64 | 0.06511 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_500_0_line_70 |  | 61 | 63 | 0.004276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_500_0_line_71 |  | 64 | 105 | 0.17826 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_500_0_line_72 |  | 65 | 66 | 0.014464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_500_0_line_73 |  | 66 | 67 | 0.096373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_500_0_line_74 |  | 67 | 68 | 0.021573 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_500_0_line_75 |  | 67 | 69 | 0.16502 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_500_0_line_76 |  | 67 | 70 | 0.007761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_500_0_line_77 |  | 69 | 71 | 0.31091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_500_0_line_78 |  | 69 | 72 | 0.058569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_500_0_line_79 |  | 70 | 73 | 0.021511 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_500_0_line_80 |  | 70 | 74 | 0.29426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_500_0_line_81 |  | 71 | 75 | 0.010578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_500_0_line_82 |  | 72 | 76 | 0.046224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_500_0_line_83 |  | 74 | 110 | 0.063492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_500_0_line_84 |  | 74 | 99 | 0.17485 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
85 | MV_500_0_line_85 |  | 75 | 77 | 0.007318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_500_0_line_86 |  | 76 | 84 | 0.071797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_500_0_line_87 |  | 79 | 80 | 0.004274 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_500_0_line_88 |  | 79 | 81 | 0.30985 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_500_0_line_89 |  | 80 | 82 | 0.47253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_500_0_line_90 |  | 80 | 83 | 1.1131 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_500_0_line_91 |  | 82 | 87 | 0.26601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_500_0_line_92 |  | 82 | 84 | 0.63974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_500_0_line_93 |  | 82 | 88 | 0.067265 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_500_0_line_94 |  | 83 | 89 | 0.026898 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_500_0_line_95 |  | 84 | 90 | 0.01052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_500_0_line_96 |  | 85 | 86 | 0.028954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_500_0_line_97 |  | 85 | 87 | 0.36333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_500_0_line_98 |  | 87 | 91 | 0.04261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_500_0_line_99 |  | 92 | 93 | 0.29011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_500_0_line_100 |  | 92 | 94 | 0.047867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_500_0_line_101 |  | 93 | 95 | 0.032371 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_500_0_line_102 |  | 95 | 97 | 0.033959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_500_0_line_103 |  | 96 | 109 | 0.004548 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
104 | MV_500_0_line_104 |  | 96 | 108 | 0.090795 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_500_0_line_105 |  | 97 | 107 | 0.013019 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_500_0_line_106 |  | 99 | 100 | 0.004271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_500_0_line_107 |  | 99 | 101 | 0.070313 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
108 | MV_500_0_line_108 |  | 100 | 112 | 0.062844 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_500_0_line_109 |  | 101 | 109 | 0.074965 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
110 | MV_500_0_line_110 |  | 105 | 106 | 0.004577 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_500_0_line_111 |  | 107 | 108 | 0.072637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_500_0_trafo_103 | 25 MVA 110/20 kV | 113 | 3 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2688119.0747 | 1250079.6795
1 | 2688117.8031 | 1250085.4761
2 | 2688168.8107 | 1250202.8343
3 | 2687772.928 | 1250039.358
4 | 2687779.4954 | 1249982.9016
5 | 2688186.4172 | 1250228.2377
6 | 2688520.477 | 1249892.2295
7 | 2688471.0021 | 1249809.5173
8 | 2688515.3796 | 1249896.7129
9 | 2688161.6141 | 1250239.4439
10 | 2687842.7686 | 1250450.3171
11 | 2687979.9232 | 1250422.8955
12 | 2687895.4834 | 1250630.0678
13 | 2687806.7349 | 1250454.7168
14 | 2688442.7257 | 1250249.895
15 | 2688428.4275 | 1250247.2352
16 | 2688409.0152 | 1249863.3331
17 | 2688367.7918 | 1249801.8609
18 | 2687852.7756 | 1249849.3531
19 | 2687752.2243 | 1249668.8389
20 | 2688312.8388 | 1249856.9725
21 | 2687830.8992 | 1249863.2394
22 | 2688142.9375 | 1250395.0282
23 | 2688143.6539 | 1250399.142
24 | 2688103.8508 | 1250405.7108
25 | 2688284.1377 | 1247941.8817
26 | 2688243.7138 | 1248032.6369
27 | 2688088.0862 | 1248211.3237
28 | 2687643.5441 | 1249535.6308
29 | 2687591.0528 | 1249530.2732
30 | 2687447.2577 | 1248463.5385
31 | 2687614.5671 | 1248579.4508
32 | 2687437.3024 | 1248405.2703
33 | 2687507.1118 | 1248817.309
34 | 2687512.1829 | 1248855.4014
35 | 2687221.7686 | 1248775.7067
36 | 2687662.5764 | 1248558.567
37 | 2688072.5663 | 1248184.8289
38 | 2687533.2439 | 1248886.1576
39 | 2687217.9725 | 1248759.6277
40 | 2686663.1116 | 1248680.9884
41 | 2686785.9979 | 1248601.2039
42 | 2686736.1072 | 1249759.7088
43 | 2688058.2228 | 1250428.7946
44 | 2688045.5345 | 1250433.6654
45 | 2688023.1805 | 1250416.298
46 | 2688076.0439 | 1250473.2052
47 | 2688035.6546 | 1250361.8421
48 | 2688028.4747 | 1250336.2697
49 | 2688040.9178 | 1250435.4315
50 | 2688096.0308 | 1250522.8498
51 | 2687966.473 | 1250266.3095
52 | 2688054.6104 | 1250249.7612
53 | 2687994.9576 | 1250314.7356
54 | 2687910.344 | 1250666.0671
55 | 2687952.1784 | 1250648.7977
56 | 2687895.1203 | 1250797.1858
57 | 2687886.4057 | 1250802.1833
58 | 2688187.0634 | 1250584.9283
59 | 2688231.3049 | 1250953.8662
60 | 2688172.2353 | 1250544.6281
61 | 2688018.6995 | 1251042.4166
62 | 2688235.6663 | 1250996.359
63 | 2688015.0796 | 1251044.709
64 | 2688126.1903 | 1250513.3465
65 | 2687619.9905 | 1250011.5189
66 | 2687605.664 | 1250013.7867
67 | 2687546.2733 | 1250055.0849
68 | 2687549.7564 | 1250076.3746
69 | 2687410.1937 | 1250048.3383
70 | 2687553.6275 | 1250057.6287
71 | 2687191.6646 | 1249874.8004
72 | 2687420.1394 | 1250106.0536
73 | 2687574.8952 | 1250054.6851
74 | 2687646.7097 | 1250246.8804
75 | 2687199.0924 | 1249867.2485
76 | 2687419.7502 | 1250150.3005
77 | 2687201.173 | 1249860.2961
78 | 2686723.0937 | 1249785.7379
79 | 2686848.398 | 1250630.2413
80 | 2686850.7539 | 1250633.8118
81 | 2686685.3008 | 1250366.7887
82 | 2687065.4336 | 1250488.6074
83 | 2687270.9306 | 1250794.1267
84 | 2687428.2691 | 1250215.1195
85 | 2687272.1047 | 1250523.84
86 | 2687244.9771 | 1250534.1706
87 | 2687181.2805 | 1250610.5355
88 | 2687128 | 1250463.9081
89 | 2687280.5016 | 1250819.2641
90 | 2687438.69 | 1250213.4719
91 | 2687221.5888 | 1250599.2199
92 | 2687758.6996 | 1250777.4383
93 | 2687763.9972 | 1250608.9449
94 | 2687735.2562 | 1250742.3666
95 | 2687752.0724 | 1250578.8506
96 | 2687800.4019 | 1250452.0765
97 | 2687739.6422 | 1250547.2488
98 | 2687935.8194 | 1250266.0413
99 | 2687765.4399 | 1250310.8299
100 | 2687761.3876 | 1250312.2153
101 | 2687781.5624 | 1250379.2691
102 | 2688049.1531 | 1250226.234
103 | 2687992.0439 | 1250305.7318
104 | 2688036.9974 | 1250440.6439
105 | 2688274.7032 | 1250553.3756
106 | 2688275.6708 | 1250557.8489
107 | 2687735.0067 | 1250535.0834
108 | 2687710.7873 | 1250466.6719
109 | 2687803.9919 | 1250449.2721
110 | 2687584.6103 | 1250260.1058
111 | 2687787.9211 | 1249889.7254
112 | 2687775.6915 | 1250373.4102
113 | 2687772.928 | 1250039.358

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99755 | -0.13859 | 0.23792 | 0.11523
1 | 0.99755 | -0.13861 | 0 | 0
2 | 0.9971 | -0.14066 | 0 | 0
3 | 1 | 0 | -12.8785 | -5.9812
4 | 0.99974 | -0.0019834 | 0 | 0
5 | 0.997 | -0.14113 | 0.40182 | 0.19461
6 | 0.99807 | 0.001773 | 0 | 0
7 | 0.99811 | 0.0013891 | 0 | 0
8 | 0.99807 | 0.0017953 | 0.27375 | 0.13258
9 | 0.99682 | -0.15134 | 0 | 0
10 | 0.99489 | -0.22304 | 0.58394 | 0.28281
11 | 0.9955 | -0.18842 | 0.081998 | 0.039714
12 | 0.99469 | -0.22445 | 0.090027 | 0.043602
13 | 0.99483 | -0.22335 | 0.2189 | 0.10602
14 | 0.99511 | -0.18392 | 0.31465 | 0.15239
15 | 0.99511 | -0.18398 | 0 | 0
16 | 0.9981 | 0.0014544 | 0.071525 | 0.034641
17 | 0.99824 | 0.0002992 | 0 | 0
18 | 0.99888 | 0.0049093 | 0 | 0
19 | 0.99826 | 4.7383e-05 | 0.22461 | 0.10879
20 | 0.99829 | 0.00070645 | 0.31998 | 0.15497
21 | 0.99888 | 0.0049448 | 0 | 0
22 | 0.99531 | -0.18567 | 0 | 0
23 | 0.99531 | -0.18568 | 0.19812 | 0.095952
24 | 0.99534 | -0.1859 | 0 | 0
25 | 0.99472 | -0.0066235 | 0.14608 | 0.070747
26 | 0.99475 | -0.0064457 | 0 | 0
27 | 0.9948 | -0.0068617 | 0 | 0
28 | 0.99781 | -0.0035304 | 0 | 0
29 | 0.99757 | -0.0016867 | 0.073276 | 0.035489
30 | 0.99527 | -0.010417 | 0 | 0
31 | 0.99532 | -0.010847 | 0 | 0
32 | 0.99525 | -0.010528 | 0.15383 | 0.074504
33 | 0.99583 | -0.014565 | 0 | 0
34 | 0.9959 | -0.015117 | 0.15212 | 0.073675
35 | 0.9957 | -0.015339 | 0 | 0
36 | 0.99529 | -0.011034 | 0.29167 | 0.14126
37 | 0.99478 | -0.0067432 | 0.3213 | 0.15561
38 | 0.99599 | -0.014385 | 0 | 0
39 | 0.9957 | -0.015296 | 0.21618 | 0.1047
40 | 0.99185 | -0.21553 | 0 | 0
41 | 0.99181 | -0.2158 | 0.14795 | 0.071654
42 | 0.99216 | -0.21349 | 0 | 0
43 | 0.99539 | -0.18631 | 0 | 0
44 | 0.99538 | -0.18622 | 0 | 0
45 | 0.99559 | -0.18799 | 0 | 0
46 | 0.99532 | -0.18577 | 0.25997 | 0.12591
47 | 0.9958 | -0.18703 | 0 | 0
48 | 0.99587 | -0.18667 | 0.83087 | 0.40241
49 | 0.99538 | -0.18619 | 0.31366 | 0.15191
50 | 0.99526 | -0.18533 | 0 | 0
51 | 0.99585 | -0.18682 | 0 | 0
52 | 0.99646 | -0.15297 | 0 | 0
53 | 0.99586 | -0.18673 | 0 | 0
54 | 0.99467 | -0.22425 | 0.38804 | 0.18794
55 | 0.99466 | -0.22432 | 0 | 0
56 | 0.99463 | -0.22411 | 0 | 0
57 | 0.99463 | -0.2241 | 0.084402 | 0.040878
58 | 0.99516 | -0.18461 | 0 | 0
59 | 0.99494 | -0.18306 | 0 | 0
60 | 0.99518 | -0.18472 | 0.24462 | 0.11848
61 | 0.99481 | -0.18202 | 0 | 0
62 | 0.99493 | -0.18301 | 0.095886 | 0.04644
63 | 0.99481 | -0.18201 | 0.23396 | 0.11331
64 | 0.99523 | -0.18506 | 0 | 0
65 | 0.99295 | -0.21937 | 0.28582 | 0.13843
66 | 0.99295 | -0.21942 | 0 | 0
67 | 0.99299 | -0.21974 | 0 | 0
68 | 0.99298 | -0.21969 | 0.21087 | 0.10213
69 | 0.99245 | -0.21566 | 0 | 0
70 | 0.99302 | -0.21998 | 0 | 0
71 | 0.9923 | -0.2146 | 0 | 0
72 | 0.99229 | -0.21438 | 0.091706 | 0.044415
73 | 0.99302 | -0.21996 | 0.091436 | 0.044285
74 | 0.9942 | -0.22917 | 0 | 0
75 | 0.9923 | -0.21456 | 0.15779 | 0.076422
76 | 0.99217 | -0.21343 | 0 | 0
77 | 0.9923 | -0.21455 | 0 | 0
78 | 0.99216 | -0.21346 | 0.070707 | 0.034245
79 | 0.98964 | -0.1932 | 0.2907 | 0.14079
80 | 0.98964 | -0.19323 | 0 | 0
81 | 0.98943 | -0.19454 | 0.34812 | 0.1686
82 | 0.99033 | -0.19883 | 0 | 0
83 | 0.98892 | -0.18734 | 0 | 0
84 | 0.99197 | -0.21193 | 0 | 0
85 | 0.9901 | -0.19691 | 0 | 0
86 | 0.99009 | -0.19685 | 0.17238 | 0.083486
87 | 0.99018 | -0.19756 | 0 | 0
88 | 0.99028 | -0.19917 | 0.40384 | 0.19559
89 | 0.98891 | -0.18718 | 0.5055 | 0.24483
90 | 0.99197 | -0.21192 | 0.077573 | 0.03757
91 | 0.99016 | -0.19741 | 0.2917 | 0.14128
92 | 0.99466 | -0.22365 | 0 | 0
93 | 0.99468 | -0.22384 | 0 | 0
94 | 0.99465 | -0.2236 | 0.077963 | 0.037759
95 | 0.99469 | -0.22385 | 0.094074 | 0.045562
96 | 0.99482 | -0.22341 | 0 | 0
97 | 0.9947 | -0.2239 | 0 | 0
98 | 0.99584 | -0.18678 | 0.12866 | 0.062314
99 | 0.9946 | -0.22447 | 0 | 0
100 | 0.9946 | -0.22447 | 0 | 0
101 | 0.9947 | -0.22398 | 0.18146 | 0.087885
102 | 0.99646 | -0.15295 | 0.069861 | 0.033835
103 | 0.99586 | -0.18671 | 0.1091 | 0.052841
104 | 0.99537 | -0.18621 | 0.2078 | 0.10064
105 | 0.99517 | -0.1845 | 0 | 0
106 | 0.99516 | -0.18448 | 0.27318 | 0.13231
107 | 0.9947 | -0.22392 | 0.09337 | 0.045221
108 | 0.99472 | -0.2241 | 0.27962 | 0.13543
109 | 0.99481 | -0.22344 | 0 | 0
110 | 0.99411 | -0.22832 | 1.1133 | 0.53922
111 | 0.99887 | 0.0050171 | 0.12258 | 0.059367
112 | 0.99459 | -0.2244 | 0.088541 | 0.042882
113 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.23792 | -0.11523 | 0.23792 | 0.11509 | 4.6352e-07 | -0.00014085 | 0.00765 | 0.0076483 | 0.00765 | 0.99755 | -0.13859 | 0.99755 | -0.13861 | 3.4773
1 | 10.2379 | 4.7414 | -10.2334 | -4.7473 | 0.0044729 | -0.0059652 | 0.3265 | 0.3266 | 0.3266 | 0.99755 | -0.13861 | 0.9971 | -0.14066 | 51.1911
2 | -10.4758 | -4.8565 | 10.4897 | 4.8933 | 0.013869 | 0.036814 | 0.33414 | 0.33414 | 0.33414 | 0.99755 | -0.13861 | 1 | 0 | 51.8051
3 | 10.2334 | 4.7473 | -10.2324 | -4.7487 | 0.0010193 | -0.0013576 | 0.3266 | 0.32662 | 0.32662 | 0.9971 | -0.14066 | 0.997 | -0.14113 | 51.1948
4 | 2.3749 | 1.0774 | -2.3743 | -1.0771 | 0.00057392 | 0.00029165 | 0.075282 | 0.075282 | 0.075282 | 1 | 0 | 0.99974 | -0.0019834 | 35.8488
5 | 2.3743 | 1.0771 | -2.3721 | -1.0833 | 0.0021738 | -0.0061982 | 0.075282 | 0.075364 | 0.075364 | 0.99974 | -0.0019834 | 0.99888 | 0.0049093 | 34.2565
6 | 9.8306 | 4.5541 | -9.8296 | -4.5516 | 0.00095617 | 0.0025338 | 0.3137 | 0.3137 | 0.3137 | 0.997 | -0.14113 | 0.99682 | -0.15134 | 48.6353
7 | -0.27375 | -0.13242 | 0.27376 | 0.12956 | 1.2395e-05 | -0.0028625 | 0.0087956 | 0.0087598 | 0.0087956 | 0.99807 | 0.001773 | 0.99811 | 0.0013891 | 3.998
8 | 0.27375 | 0.13242 | -0.27375 | -0.13258 | 7.0127e-07 | -0.00016125 | 0.0087956 | 0.0087976 | 0.0087976 | 0.99807 | 0.001773 | 0.99807 | 0.0017953 | 3.9989
9 | 0.071526 | 0.032692 | -0.071525 | -0.034641 | 5.7196e-07 | -0.0019492 | 0.0022745 | 0.0022985 | 0.0022985 | 0.99811 | 0.0013891 | 0.9981 | 0.0014544 | 1.0448
10 | -0.34529 | -0.16225 | 0.34534 | 0.15506 | 4.8859e-05 | -0.0071938 | 0.011034 | 0.010947 | 0.011034 | 0.99811 | 0.0013891 | 0.99824 | 0.0002992 | 5.0155
11 | 9.8296 | 4.5516 | -9.8262 | -4.5566 | 0.0033943 | -0.0050534 | 0.3137 | 0.31378 | 0.31378 | 0.99682 | -0.15134 | 0.99646 | -0.15297 | 49.1822
12 | -6.4547 | -2.974 | 6.4569 | 2.9795 | 0.0021233 | 0.0055183 | 0.20621 | 0.20621 | 0.20621 | 0.99489 | -0.22304 | 0.9955 | -0.18842 | 31.9709
13 | 0.5626 | 0.26493 | -0.56249 | -0.26508 | 0.00010867 | -0.00015323 | 0.018044 | 0.018046 | 0.018046 | 0.99489 | -0.22304 | 0.99469 | -0.22445 | 8.5935
14 | 5.3082 | 2.4262 | -5.3079 | -2.4283 | 0.00032326 | -0.0020861 | 0.16935 | 0.16938 | 0.16938 | 0.99489 | -0.22304 | 0.99483 | -0.22335 | 26.5478
15 | -6.5389 | -3.0192 | 6.5394 | 3.0168 | 0.00058978 | -0.0023933 | 0.20885 | 0.20882 | 0.20885 | 0.9955 | -0.18842 | 0.99559 | -0.18799 | 32.7353
16 | 0.47246 | 0.22148 | -0.47245 | -0.2224 | 1.1932e-05 | -0.00091647 | 0.015143 | 0.015155 | 0.015155 | 0.99469 | -0.22445 | 0.99467 | -0.22425 | 6.8885
17 | 5.089 | 2.3223 | -5.0889 | -2.3227 | 5.611e-05 | -0.00039695 | 0.16232 | 0.16232 | 0.16232 | 0.99483 | -0.22335 | 0.99482 | -0.22341 | 25.4427
18 | -0.31465 | -0.15239 | 0.31465 | 0.15205 | 1.9904e-06 | -0.00034226 | 0.010142 | 0.010138 | 0.010142 | 0.99511 | -0.18392 | 0.99511 | -0.18398 | 4.61
19 | -0.31465 | -0.15205 | 0.31472 | 0.1403 | 6.7291e-05 | -0.011747 | 0.010138 | 0.0099939 | 0.010138 | 0.99511 | -0.18398 | 0.99531 | -0.18567 | 4.608
20 | -0.34534 | -0.15506 | 0.34536 | 0.15498 | 1.6616e-05 | -8.2182e-05 | 0.010947 | 0.010946 | 0.010947 | 0.99824 | 0.0002992 | 0.99829 | 0.00070645 | 5.2129
21 | 1.5838 | 0.71613 | -1.5829 | -0.7158 | 0.00092906 | 0.00033596 | 0.050234 | 0.050237 | 0.050237 | 0.99888 | 0.0049093 | 0.99826 | 4.7383e-05 | 23.9222
22 | 0.66571 | 0.30963 | -0.66534 | -0.30995 | 0.0003692 | -0.0003165 | 0.021218 | 0.021225 | 0.021225 | 0.99888 | 0.0049093 | 0.99829 | 0.00070645 | 10.107
23 | 0.12258 | 0.057549 | -0.12258 | -0.058165 | 5.2975e-07 | -0.00061587 | 0.0039135 | 0.0039211 | 0.0039211 | 0.99888 | 0.0049093 | 0.99888 | 0.0049448 | 1.7823
24 | 1.3583 | 0.60701 | -1.3577 | -0.60686 | 0.00056699 | 0.00015071 | 0.043023 | 0.043025 | 0.043025 | 0.99826 | 4.7383e-05 | 0.99781 | -0.0035304 | 20.4881
25 | 0.12258 | 0.058165 | -0.12258 | -0.059367 | 1.0402e-06 | -0.0012023 | 0.0039211 | 0.0039361 | 0.0039361 | 0.99888 | 0.0049448 | 0.99887 | 0.0050171 | 1.7892
26 | -0.31472 | -0.1403 | 0.31472 | 0.1402 | 5.5671e-07 | -9.8609e-05 | 0.0099939 | 0.0099927 | 0.0099939 | 0.99531 | -0.18567 | 0.99531 | -0.18568 | 4.5427
27 | -0.51283 | -0.23615 | 0.51285 | 0.23521 | 1.439e-05 | -0.00094721 | 0.016375 | 0.016364 | 0.016375 | 0.99531 | -0.18568 | 0.99534 | -0.1859 | 7.4433
28 | -0.51285 | -0.23521 | 0.51288 | 0.2334 | 2.7348e-05 | -0.001804 | 0.016364 | 0.016342 | 0.016364 | 0.99534 | -0.1859 | 0.99539 | -0.18631 | 7.438
29 | -0.14608 | -0.070747 | 0.14608 | 0.070632 | 3.926e-06 | -0.0001149 | 0.0047102 | 0.0047088 | 0.0047102 | 0.99472 | -0.0066235 | 0.99475 | -0.0064457 | 2.243
30 | -0.14608 | -0.070632 | 0.14609 | 0.064315 | 7.7863e-06 | -0.0063176 | 0.0047088 | 0.0046319 | 0.0047088 | 0.99475 | -0.0064457 | 0.9948 | -0.0068617 | 2.1403
31 | 0.3213 | 0.15489 | -0.3213 | -0.15561 | 4.3924e-06 | -0.0007237 | 0.010351 | 0.01036 | 0.01036 | 0.9948 | -0.0068617 | 0.99478 | -0.0067432 | 4.709
32 | -0.46739 | -0.2192 | 0.46765 | 0.19841 | 0.00026004 | -0.020792 | 0.014981 | 0.014734 | 0.014981 | 0.9948 | -0.0068617 | 0.99532 | -0.010847 | 6.8093
33 | 1.3577 | 0.60686 | -1.3574 | -0.61008 | 0.00034607 | -0.0032224 | 0.043025 | 0.043064 | 0.043064 | 0.99781 | -0.0035304 | 0.99757 | -0.0016867 | 19.5747
34 | 1.2841 | 0.57459 | -1.2822 | -0.57416 | 0.00191 | 0.00042926 | 0.040709 | 0.040718 | 0.040718 | 0.99757 | -0.0016867 | 0.99599 | -0.014385 | 19.3897
35 | -0.15383 | -0.074435 | 0.15384 | 0.068296 | 8.3865e-06 | -0.006139 | 0.0049568 | 0.0048818 | 0.0049568 | 0.99527 | -0.010417 | 0.99532 | -0.010847 | 2.2531
36 | 0.15383 | 0.074435 | -0.15383 | -0.074504 | 2.5882e-06 | -6.828e-05 | 0.0049568 | 0.0049577 | 0.0049577 | 0.99527 | -0.010417 | 0.99525 | -0.010528 | 2.3608
37 | 0.29168 | 0.14121 | -0.29167 | -0.14126 | 8.2411e-06 | -5.6754e-05 | 0.0093989 | 0.0093997 | 0.0093997 | 0.99532 | -0.010847 | 0.99529 | -0.011034 | 4.476
38 | -0.91317 | -0.40792 | 0.91366 | 0.39768 | 0.00049044 | -0.01023 | 0.029007 | 0.028886 | 0.029007 | 0.99532 | -0.010847 | 0.99583 | -0.014565 | 13.1852
39 | -1.1299 | -0.50166 | 1.13 | 0.50046 | 8.873e-05 | -0.0011996 | 0.035836 | 0.035822 | 0.035836 | 0.99583 | -0.014565 | 0.9959 | -0.015117 | 16.2893
40 | 0.2162 | 0.10398 | -0.21618 | -0.10431 | 2.4864e-05 | -0.00032576 | 0.0069545 | 0.0069588 | 0.0069588 | 0.99583 | -0.014565 | 0.9957 | -0.015339 | 3.3137
41 | -1.2821 | -0.57414 | 1.2822 | 0.57416 | 0.00011012 | 2.4833e-05 | 0.040719 | 0.040718 | 0.040719 | 0.9959 | -0.015117 | 0.99599 | -0.014385 | 19.3899
42 | 0.21618 | 0.10431 | -0.21618 | -0.1047 | 1.0741e-06 | -0.0003927 | 0.0069588 | 0.0069638 | 0.0069638 | 0.9957 | -0.015339 | 0.9957 | -0.015296 | 3.1653
43 | 0.14795 | 0.071485 | -0.14795 | -0.071654 | 5.9732e-06 | -0.00016832 | 0.0047824 | 0.0047846 | 0.0047846 | 0.99185 | -0.21553 | 0.99181 | -0.2158 | 2.2784
44 | -0.14795 | -0.071485 | 0.148 | 0.070243 | 4.3911e-05 | -0.0012427 | 0.0047824 | 0.0047664 | 0.0047824 | 0.99185 | -0.21553 | 0.99216 | -0.21349 | 2.2773
45 | 0.070708 | 0.033427 | -0.070707 | -0.034245 | 2.4163e-07 | -0.00081774 | 0.0022756 | 0.0022859 | 0.0022859 | 0.99216 | -0.21349 | 0.99216 | -0.21346 | 1.039
46 | -0.2187 | -0.10367 | 0.21874 | 0.09211 | 3.1935e-05 | -0.01156 | 0.007042 | 0.0069046 | 0.007042 | 0.99216 | -0.21349 | 0.9923 | -0.21455 | 3.2009
47 | 0.52147 | 0.25212 | -0.52147 | -0.25243 | 5.1079e-06 | -0.00031917 | 0.016798 | 0.016802 | 0.016802 | 0.99539 | -0.18631 | 0.99538 | -0.18622 | 7.6374
48 | -2.1423 | -0.98827 | 2.1428 | 0.98665 | 0.00046455 | -0.0016215 | 0.068422 | 0.0684 | 0.068422 | 0.99539 | -0.18631 | 0.99559 | -0.18799 | 31.1008
49 | 1.108 | 0.50275 | -1.1079 | -0.50386 | 7.9569e-05 | -0.0011083 | 0.035285 | 0.035299 | 0.035299 | 0.99539 | -0.18631 | 0.99532 | -0.18577 | 16.045
50 | 0.52147 | 0.25243 | -0.52147 | -0.25255 | 1.8582e-06 | -0.00011607 | 0.016802 | 0.016804 | 0.016804 | 0.99538 | -0.18622 | 0.99538 | -0.18619 | 7.638
51 | -8.6822 | -4.0035 | 8.6839 | 3.9999 | 0.00173 | -0.0035649 | 0.27722 | 0.27716 | 0.27722 | 0.99559 | -0.18799 | 0.9958 | -0.18703 | 43.4512
52 | 0.8479 | 0.37795 | -0.84784 | -0.3792 | 5.182e-05 | -0.0012504 | 0.026924 | 0.026939 | 0.026939 | 0.99532 | -0.18577 | 0.99526 | -0.18533 | 12.2451
53 | -8.6839 | -3.9999 | 8.6846 | 3.9986 | 0.00063326 | -0.0013058 | 0.27716 | 0.27714 | 0.27716 | 0.9958 | -0.18703 | 0.99587 | -0.18667 | 43.4426
54 | 0.12867 | 0.06147 | -0.12866 | -0.061579 | 2.8466e-06 | -0.00010889 | 0.0041335 | 0.0041349 | 0.0041349 | 0.99587 | -0.18667 | 0.99585 | -0.18682 | 1.969
55 | -9.7532 | -4.5151 | 9.7563 | 4.5234 | 0.0031313 | 0.0082964 | 0.31154 | 0.31154 | 0.31154 | 0.99587 | -0.18667 | 0.99646 | -0.15297 | 48.3012
56 | 0.1091 | 0.05257 | -0.1091 | -0.052617 | 8.7494e-07 | -4.6619e-05 | 0.0035106 | 0.0035112 | 0.0035112 | 0.99587 | -0.18667 | 0.99586 | -0.18673 | 1.672
57 | 0.2078 | 0.10064 | -0.2078 | -0.10064 | 5.2107e-07 | -7.3879e-06 | 0.0066961 | 0.0066962 | 0.0066962 | 0.99538 | -0.18619 | 0.99537 | -0.18621 | 3.1887
58 | 0.84784 | 0.3792 | -0.84781 | -0.37996 | 3.1482e-05 | -0.00075889 | 0.026939 | 0.026948 | 0.026948 | 0.99526 | -0.18533 | 0.99523 | -0.18506 | 12.2492
59 | 0.12866 | 0.061579 | -0.12866 | -0.062314 | 7.1064e-07 | -0.00073536 | 0.0041349 | 0.0041441 | 0.0041441 | 0.99585 | -0.18682 | 0.99584 | -0.18678 | 1.8837
60 | 0.069861 | 0.033263 | -0.069861 | -0.033835 | 1.6252e-07 | -0.00057253 | 0.0022416 | 0.0022487 | 0.0022487 | 0.99646 | -0.15297 | 0.99646 | -0.15295 | 1.0222
61 | 0.1091 | 0.052617 | -0.1091 | -0.052841 | 1.5589e-07 | -0.00022404 | 0.0035112 | 0.003514 | 0.003514 | 0.99586 | -0.18673 | 0.99586 | -0.18671 | 1.5973
62 | 0.084405 | 0.03446 | -0.084404 | -0.034513 | 5.6466e-07 | -5.3101e-05 | 0.0026459 | 0.0026465 | 0.0026465 | 0.99467 | -0.22425 | 0.99466 | -0.22432 | 1.2602
63 | 0.084404 | 0.034513 | -0.084402 | -0.04064 | 2.4904e-06 | -0.0061277 | 0.0026465 | 0.0027188 | 0.0027188 | 0.99466 | -0.22432 | 0.99463 | -0.22411 | 1.2358
64 | 0.084402 | 0.04064 | -0.084402 | -0.040878 | 9.9242e-08 | -0.00023726 | 0.0027188 | 0.0027218 | 0.0027218 | 0.99463 | -0.22411 | 0.99463 | -0.2241 | 1.2372
65 | 0.32996 | 0.13604 | -0.32988 | -0.1488 | 7.8465e-05 | -0.012761 | 0.010353 | 0.0105 | 0.0105 | 0.99516 | -0.18461 | 0.99494 | -0.18306 | 4.7727
66 | -0.32996 | -0.13604 | 0.32997 | 0.13503 | 6.1379e-06 | -0.0010136 | 0.010353 | 0.010342 | 0.010353 | 0.99516 | -0.18461 | 0.99518 | -0.18472 | 4.7059
67 | 0.23399 | 0.10342 | -0.23396 | -0.11321 | 3.0988e-05 | -0.0097914 | 0.0074227 | 0.0075422 | 0.0075422 | 0.99494 | -0.18306 | 0.99481 | -0.18202 | 3.4283
68 | 0.095887 | 0.04538 | -0.095886 | -0.04644 | 5.697e-07 | -0.0010599 | 0.0030779 | 0.0030912 | 0.0030912 | 0.99494 | -0.18306 | 0.99493 | -0.18301 | 1.4051
69 | -0.57459 | -0.2535 | 0.57462 | 0.25197 | 2.8818e-05 | -0.0015311 | 0.018217 | 0.018199 | 0.018217 | 0.99518 | -0.18472 | 0.99523 | -0.18506 | 8.2806
70 | 0.23396 | 0.11321 | -0.23396 | -0.11331 | 3.2477e-07 | -0.00010094 | 0.0075422 | 0.0075435 | 0.0075435 | 0.99481 | -0.18202 | 0.99481 | -0.18201 | 3.4289
71 | 0.2732 | 0.12799 | -0.27318 | -0.1322 | 1.8332e-05 | -0.0042098 | 0.0087508 | 0.0088034 | 0.0088034 | 0.99523 | -0.18506 | 0.99517 | -0.1845 | 4.0015
72 | -0.28582 | -0.13843 | 0.28582 | 0.13809 | 1.6452e-06 | -0.00034 | 0.0092328 | 0.0092285 | 0.0092328 | 0.99295 | -0.21937 | 0.99295 | -0.21942 | 4.1967
73 | -0.28582 | -0.13809 | 0.28583 | 0.13582 | 1.0923e-05 | -0.0022655 | 0.0092285 | 0.0092 | 0.0092285 | 0.99295 | -0.21942 | 0.99299 | -0.21974 | 4.1948
74 | 0.21087 | 0.10162 | -0.21087 | -0.10213 | 1.335e-06 | -0.00050748 | 0.0068051 | 0.0068115 | 0.0068115 | 0.99299 | -0.21974 | 0.99298 | -0.21969 | 3.0961
75 | 2.5657 | 1.1417 | -2.5642 | -1.1452 | 0.0014691 | -0.0034471 | 0.081639 | 0.081685 | 0.081685 | 0.99299 | -0.21974 | 0.99245 | -0.21566 | 37.1294
76 | -3.0624 | -1.3792 | 3.0625 | 1.379 | 9.8772e-05 | -0.00015342 | 0.097639 | 0.097637 | 0.097639 | 0.99299 | -0.21974 | 0.99302 | -0.21998 | 44.3813
77 | 0.37659 | 0.16082 | -0.37653 | -0.16811 | 5.9303e-05 | -0.0072931 | 0.011911 | 0.011996 | 0.011996 | 0.99245 | -0.21566 | 0.9923 | -0.2146 | 5.4527
78 | 2.1876 | 0.98435 | -2.1872 | -0.98561 | 0.00038077 | -0.0012642 | 0.069776 | 0.069792 | 0.069792 | 0.99245 | -0.21566 | 0.99229 | -0.21438 | 31.7238
79 | 0.091436 | 0.043778 | -0.091436 | -0.044285 | 2.4995e-07 | -0.00050638 | 0.0029471 | 0.0029534 | 0.0029534 | 0.99302 | -0.21998 | 0.99302 | -0.21996 | 1.3425
80 | -3.1539 | -1.4228 | 3.1579 | 1.417 | 0.003971 | -0.0057583 | 0.10058 | 0.1005 | 0.10058 | 0.99302 | -0.21998 | 0.9942 | -0.22917 | 45.7195
81 | 0.37653 | 0.16811 | -0.37653 | -0.16836 | 2.0326e-06 | -0.00024808 | 0.011996 | 0.011999 | 0.011999 | 0.9923 | -0.2146 | 0.9923 | -0.21456 | 5.4541
82 | 2.0955 | 0.94119 | -2.0952 | -0.9422 | 0.00027565 | -0.0010048 | 0.066829 | 0.066842 | 0.066842 | 0.99229 | -0.21438 | 0.99217 | -0.21343 | 30.3828
83 | 1.1135 | 0.53775 | -1.1133 | -0.53922 | 0.00010932 | -0.0014658 | 0.035903 | 0.035922 | 0.035922 | 0.9942 | -0.22917 | 0.99411 | -0.22832 | 16.3283
84 | -4.2713 | -1.9548 | 4.2729 | 1.95 | 0.0015703 | -0.0047904 | 0.13639 | 0.13632 | 0.13639 | 0.9942 | -0.22917 | 0.9946 | -0.22447 | 37.6776
85 | 0.21874 | 0.091938 | -0.21874 | -0.09211 | 4.6562e-07 | -0.00017191 | 0.0069026 | 0.0069046 | 0.0069046 | 0.9923 | -0.21456 | 0.9923 | -0.21455 | 3.1384
86 | 2.0952 | 0.9422 | -2.0948 | -0.94376 | 0.00042837 | -0.0015601 | 0.066842 | 0.066862 | 0.066862 | 0.99217 | -0.21343 | 0.99197 | -0.21193 | 30.3919
87 | -0.63889 | -0.30908 | 0.63889 | 0.30898 | 2.4453e-06 | -9.9218e-05 | 0.020702 | 0.020701 | 0.020702 | 0.98964 | -0.1932 | 0.98964 | -0.19323 | 9.4102
88 | 0.34819 | 0.16828 | -0.34812 | -0.1686 | 7.028e-05 | -0.00031818 | 0.011281 | 0.011285 | 0.011285 | 0.98964 | -0.1932 | 0.98943 | -0.19454 | 5.3739
89 | -1.1448 | -0.52728 | 1.1456 | 0.51648 | 0.00084956 | -0.010805 | 0.036765 | 0.036631 | 0.036765 | 0.98964 | -0.19323 | 0.99033 | -0.19883 | 16.7114
90 | 0.50591 | 0.21831 | -0.50551 | -0.2442 | 0.00039126 | -0.025893 | 0.016072 | 0.016388 | 0.016388 | 0.98964 | -0.19323 | 0.98892 | -0.18734 | 7.4491
91 | 0.46418 | 0.20839 | -0.4641 | -0.21459 | 7.8511e-05 | -0.0062047 | 0.014831 | 0.014907 | 0.014907 | 0.99033 | -0.19883 | 0.99018 | -0.19756 | 6.7758
92 | -2.0137 | -0.92039 | 2.0172 | 0.90644 | 0.0035473 | -0.013953 | 0.064538 | 0.064358 | 0.064538 | 0.99033 | -0.19883 | 0.99197 | -0.21193 | 29.3356
93 | 0.40386 | 0.19552 | -0.40384 | -0.19559 | 2.0504e-05 | -6.5909e-05 | 0.013079 | 0.01308 | 0.01308 | 0.99033 | -0.19883 | 0.99028 | -0.19917 | 6.2288
94 | 0.50551 | 0.2442 | -0.5055 | -0.24483 | 9.6485e-06 | -0.00062519 | 0.016388 | 0.016396 | 0.016396 | 0.98892 | -0.18734 | 0.98891 | -0.18718 | 7.4527
95 | 0.077573 | 0.037323 | -0.077573 | -0.03757 | 8.8253e-08 | -0.00024713 | 0.0025052 | 0.0025083 | 0.0025083 | 0.99197 | -0.21193 | 0.99197 | -0.21192 | 1.1401
96 | 0.17238 | 0.082809 | -0.17238 | -0.083486 | 1.2036e-06 | -0.00067732 | 0.0055758 | 0.0055843 | 0.0055843 | 0.9901 | -0.19691 | 0.99009 | -0.19685 | 2.5383
97 | -0.17238 | -0.082809 | 0.17239 | 0.074309 | 1.4797e-05 | -0.0085001 | 0.0055758 | 0.005473 | 0.0055758 | 0.9901 | -0.19691 | 0.99018 | -0.19756 | 2.5344
98 | 0.29171 | 0.14028 | -0.2917 | -0.14128 | 5.0725e-06 | -0.00099595 | 0.0094368 | 0.0094494 | 0.0094494 | 0.99018 | -0.19756 | 0.99016 | -0.19741 | 4.2952
99 | -0.077963 | -0.036628 | 0.077965 | 0.029776 | 2.3425e-06 | -0.0068524 | 0.0025 | 0.0024221 | 0.0025 | 0.99466 | -0.22365 | 0.99468 | -0.22384 | 1.1364
100 | 0.077963 | 0.036628 | -0.077963 | -0.037759 | 4.0163e-07 | -0.0011306 | 0.0025 | 0.0025141 | 0.0025141 | 0.99466 | -0.22365 | 0.99465 | -0.2236 | 1.1428
101 | -0.077965 | -0.029776 | 0.077966 | 0.029011 | 2.527e-07 | -0.00076463 | 0.0024221 | 0.0024143 | 0.0024221 | 0.99468 | -0.22384 | 0.99469 | -0.22385 | 1.101
102 | -0.17204 | -0.074574 | 0.17204 | 0.073772 | 1.3402e-06 | -0.00080182 | 0.0054418 | 0.0054326 | 0.0054418 | 0.99469 | -0.22385 | 0.9947 | -0.2239 | 2.4735
103 | 4.5438 | 2.0704 | -4.5438 | -2.0707 | 2.9505e-05 | -0.00026619 | 0.14489 | 0.1449 | 0.1449 | 0.99482 | -0.22341 | 0.99481 | -0.22344 | 22.7113
104 | 0.54509 | 0.25232 | -0.54504 | -0.2524 | 4.9149e-05 | -7.6476e-05 | 0.01743 | 0.017431 | 0.017431 | 0.99482 | -0.22341 | 0.99472 | -0.2241 | 8.3005
105 | -0.17204 | -0.073772 | 0.17204 | 0.073464 | 5.126e-07 | -0.00030739 | 0.0054326 | 0.005429 | 0.0054326 | 0.9947 | -0.2239 | 0.9947 | -0.22392 | 2.4693
106 | 0.088541 | 0.041297 | -0.088541 | -0.041398 | 4.587e-08 | -0.00010086 | 0.0028356 | 0.0028369 | 0.0028369 | 0.9946 | -0.22447 | 0.9946 | -0.22447 | 1.2895
107 | -4.3614 | -1.9913 | 4.3619 | 1.9872 | 0.00042057 | -0.0041339 | 0.13916 | 0.1391 | 0.13916 | 0.9946 | -0.22447 | 0.9947 | -0.22398 | 21.8114
108 | 0.088541 | 0.041398 | -0.088541 | -0.042882 | 6.7957e-07 | -0.0014841 | 0.0028369 | 0.0028554 | 0.0028554 | 0.9946 | -0.22447 | 0.99459 | -0.2244 | 1.2979
109 | -4.5433 | -2.075 | 4.5438 | 2.0707 | 0.00048653 | -0.004387 | 0.14495 | 0.1449 | 0.14495 | 0.9947 | -0.22398 | 0.99481 | -0.22344 | 22.7201
110 | 0.27318 | 0.1322 | -0.27318 | -0.13231 | 4.7359e-07 | -0.00010809 | 0.0088034 | 0.0088048 | 0.0088048 | 0.99517 | -0.1845 | 0.99516 | -0.18448 | 4.0022
111 | -0.26541 | -0.11869 | 0.26542 | 0.11697 | 6.8871e-06 | -0.0017139 | 0.0084377 | 0.0084175 | 0.0084377 | 0.9947 | -0.22392 | 0.99472 | -0.2241 | 3.8353

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 13.2441 | 6.1583

## res_load
| p_mw | q_mvar
0 | 0.23792 | 0.11523
1 | 0.3656 | 0.17707
2 | 0.40182 | 0.19461
3 | 0.27375 | 0.13258
4 | 0.58394 | 0.28281
5 | 0.081998 | 0.039714
6 | 0.090027 | 0.043602
7 | 0.2189 | 0.10602
8 | 0.31465 | 0.15239
9 | 0.071525 | 0.034641
10 | 0.22461 | 0.10879
11 | 0.31998 | 0.15497
12 | 0.19812 | 0.095952
13 | 0.14608 | 0.070747
14 | 0.073276 | 0.035489
15 | 0.15383 | 0.074504
16 | 0.15212 | 0.073675
17 | 0.29167 | 0.14126
18 | 0.3213 | 0.15561
19 | 0.21618 | 0.1047
20 | 0.14795 | 0.071654
21 | 0.25997 | 0.12591
22 | 0.83087 | 0.40241
23 | 0.31366 | 0.15191
24 | 0.38804 | 0.18794
25 | 0.084402 | 0.040878
26 | 0.24462 | 0.11848
27 | 0.095886 | 0.04644
28 | 0.23396 | 0.11331
29 | 0.28582 | 0.13843
30 | 0.21087 | 0.10213
31 | 0.091706 | 0.044415
32 | 0.091436 | 0.044285
33 | 0.15779 | 0.076422
34 | 0.070707 | 0.034245
35 | 0.2907 | 0.14079
36 | 0.34812 | 0.1686
37 | 0.17238 | 0.083486
38 | 0.40384 | 0.19559
39 | 0.5055 | 0.24483
40 | 0.077573 | 0.03757
41 | 0.2917 | 0.14128
42 | 0.077963 | 0.037759
43 | 0.094074 | 0.045562
44 | 0.12866 | 0.062314
45 | 0.18146 | 0.087885
46 | 0.069861 | 0.033835
47 | 0.1091 | 0.052841
48 | 0.2078 | 0.10064
49 | 0.27318 | 0.13231
50 | 0.09337 | 0.045221
51 | 0.27962 | 0.13543
52 | 1.1133 | 0.53922
53 | 0.12258 | 0.059367
54 | 0.088541 | 0.042882

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1