## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_51_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_51_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_51_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_51_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_51_0_node_101 | 20 | n |  | TRUE
5 | bus_MV_51_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_51_0_node_100 | 20 | n |  | TRUE
7 | bus_MV_51_0_node_6 | 20 | n |  | TRUE
8 | bus_MV_51_0_node_190 | 20 | n |  | TRUE
9 | bus_MV_51_0_node_7 | 20 | n |  | TRUE
10 | bus_MV_51_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_51_0_node_8 | 20 | n |  | TRUE
12 | bus_MV_51_0_node_9 | 20 | n |  | TRUE
13 | bus_MV_51_0_node_186 | 20 | n |  | TRUE
14 | bus_MV_51_0_node_123 | 20 | n |  | TRUE
15 | bus_MV_51_0_node_187 | 20 | n |  | TRUE
16 | bus_MV_51_0_node_111 | 20 | n |  | TRUE
17 | bus_MV_51_0_node_11 | 20 | n |  | TRUE
18 | bus_MV_51_0_node_12 | 20 | n |  | TRUE
19 | bus_MV_51_0_node_13 | 20 | n |  | TRUE
20 | bus_MV_51_0_node_16 | 20 | n |  | TRUE
21 | bus_MV_51_0_node_18 | 20 | n |  | TRUE
22 | bus_MV_51_0_node_19 | 20 | n |  | TRUE
23 | bus_MV_51_0_node_21 | 20 | n |  | TRUE
24 | bus_MV_51_0_node_22 | 20 | n |  | TRUE
25 | bus_MV_51_0_node_14 | 20 | n |  | TRUE
26 | bus_MV_51_0_node_25 | 20 | n |  | TRUE
27 | bus_MV_51_0_node_17 | 20 | n |  | TRUE
28 | bus_MV_51_0_node_188 | 20 | n |  | TRUE
29 | bus_MV_51_0_node_15 | 20 | n |  | TRUE
30 | bus_MV_51_0_node_20 | 20 | n |  | TRUE
31 | bus_MV_51_0_node_134 | 20 | n |  | TRUE
32 | bus_MV_51_0_node_133 | 20 | n |  | TRUE
33 | bus_MV_51_0_node_24 | 20 | n |  | TRUE
34 | bus_MV_51_0_node_23 | 20 | n |  | TRUE
35 | bus_MV_51_0_node_189 | 20 | n |  | TRUE
36 | bus_MV_51_0_node_26 | 20 | n |  | TRUE
37 | bus_MV_51_0_node_27 | 20 | n |  | TRUE
38 | bus_MV_51_0_node_28 | 20 | n |  | TRUE
39 | bus_MV_51_0_node_46 | 20 | n |  | TRUE
40 | bus_MV_51_0_node_31 | 20 | n |  | TRUE
41 | bus_MV_51_0_node_168 | 20 | n |  | TRUE
42 | bus_MV_51_0_node_44 | 20 | n |  | TRUE
43 | bus_MV_51_0_node_29 | 20 | n |  | TRUE
44 | bus_MV_51_0_node_86 | 20 | n |  | TRUE
45 | bus_MV_51_0_node_43 | 20 | n |  | TRUE
46 | bus_MV_51_0_node_30 | 20 | n |  | TRUE
47 | bus_MV_51_0_node_32 | 20 | n |  | TRUE
48 | bus_MV_51_0_node_87 | 20 | n |  | TRUE
49 | bus_MV_51_0_node_76 | 20 | n |  | TRUE
50 | bus_MV_51_0_node_33 | 20 | n |  | TRUE
51 | bus_MV_51_0_node_135 | 20 | n |  | TRUE
52 | bus_MV_51_0_node_34 | 20 | n |  | TRUE
53 | bus_MV_51_0_node_142 | 20 | n |  | TRUE
54 | bus_MV_51_0_node_141 | 20 | n |  | TRUE
55 | bus_MV_51_0_node_140 | 20 | n |  | TRUE
56 | bus_MV_51_0_node_45 | 20 | n |  | TRUE
57 | bus_MV_51_0_node_40 | 20 | n |  | TRUE
58 | bus_MV_51_0_node_48 | 20 | n |  | TRUE
59 | bus_MV_51_0_node_39 | 20 | n |  | TRUE
60 | bus_MV_51_0_node_165 | 20 | n |  | TRUE
61 | bus_MV_51_0_node_81 | 20 | n |  | TRUE
62 | bus_MV_51_0_node_35 | 20 | n |  | TRUE
63 | bus_MV_51_0_node_37 | 20 | n |  | TRUE
64 | bus_MV_51_0_node_42 | 20 | n |  | TRUE
65 | bus_MV_51_0_node_38 | 20 | n |  | TRUE
66 | bus_MV_51_0_node_185 | 20 | n |  | TRUE
67 | bus_MV_51_0_node_41 | 20 | n |  | TRUE
68 | bus_MV_51_0_node_155 | 20 | n |  | TRUE
69 | bus_MV_51_0_node_75 | 20 | n |  | TRUE
70 | bus_MV_51_0_node_66 | 20 | n |  | TRUE
71 | bus_MV_51_0_node_67 | 20 | n |  | TRUE
72 | bus_MV_51_0_node_47 | 20 | n |  | TRUE
73 | bus_MV_51_0_node_156 | 20 | n |  | TRUE
74 | bus_MV_51_0_node_50 | 20 | n |  | TRUE
75 | bus_MV_51_0_node_51 | 20 | n |  | TRUE
76 | bus_MV_51_0_node_52 | 20 | n |  | TRUE
77 | bus_MV_51_0_node_84 | 20 | n |  | TRUE
78 | bus_MV_51_0_node_77 | 20 | n |  | TRUE
79 | bus_MV_51_0_node_53 | 20 | n |  | TRUE
80 | bus_MV_51_0_node_54 | 20 | n |  | TRUE
81 | bus_MV_51_0_node_161 | 20 | n |  | TRUE
82 | bus_MV_51_0_node_163 | 20 | n |  | TRUE
83 | bus_MV_51_0_node_82 | 20 | n |  | TRUE
84 | bus_MV_51_0_node_83 | 20 | n |  | TRUE
85 | bus_MV_51_0_node_85 | 20 | n |  | TRUE
86 | bus_MV_51_0_node_65 | 20 | n |  | TRUE
87 | bus_MV_51_0_node_79 | 20 | n |  | TRUE
88 | bus_MV_51_0_node_136 | 20 | n |  | TRUE
89 | bus_MV_51_0_node_137 | 20 | n |  | TRUE
90 | bus_MV_51_0_node_138 | 20 | n |  | TRUE
91 | bus_MV_51_0_node_139 | 20 | n |  | TRUE
92 | bus_MV_51_0_node_162 | 20 | n |  | TRUE
93 | bus_MV_51_0_node_143 | 20 | n |  | TRUE
94 | bus_MV_51_0_node_144 | 20 | n |  | TRUE
95 | bus_MV_51_0_node_145 | 20 | n |  | TRUE
96 | bus_MV_51_0_node_147 | 20 | n |  | TRUE
97 | bus_MV_51_0_node_146 | 20 | n |  | TRUE
98 | bus_MV_51_0_node_148 | 20 | n |  | TRUE
99 | bus_MV_51_0_node_158 | 20 | n |  | TRUE
100 | bus_MV_51_0_node_159 | 20 | n |  | TRUE
101 | bus_MV_51_0_node_160 | 20 | n |  | TRUE
102 | bus_MV_51_0_node_166 | 20 | n |  | TRUE
103 | bus_MV_51_0_node_164 | 20 | n |  | TRUE
104 | bus_MV_51_0_node_167 | 20 | n |  | TRUE
105 | bus_MV_51_0_node_55 | 20 | n |  | TRUE
106 | bus_MV_51_0_node_56 | 20 | n |  | TRUE
107 | bus_MV_51_0_node_149 | 20 | n |  | TRUE
108 | bus_MV_51_0_node_198 | 20 | n |  | TRUE
109 | bus_MV_51_0_node_150 | 20 | n |  | TRUE
110 | bus_MV_51_0_node_61 | 20 | n |  | TRUE
111 | bus_MV_51_0_node_112 | 20 | n |  | TRUE
112 | bus_MV_51_0_node_132 | 20 | n |  | TRUE
113 | bus_MV_51_0_node_179 | 20 | n |  | TRUE
114 | bus_MV_51_0_node_180 | 20 | n |  | TRUE
115 | bus_MV_51_0_node_178 | 20 | n |  | TRUE
116 | bus_MV_51_0_node_58 | 20 | n |  | TRUE
117 | bus_MV_51_0_node_60 | 20 | n |  | TRUE
118 | bus_MV_51_0_node_59 | 20 | n |  | TRUE
119 | bus_MV_51_0_node_64 | 20 | n |  | TRUE
120 | bus_MV_51_0_node_72 | 20 | n |  | TRUE
121 | bus_MV_51_0_node_62 | 20 | n |  | TRUE
122 | bus_MV_51_0_node_181 | 20 | n |  | TRUE
123 | bus_MV_51_0_node_197 | 20 | n |  | TRUE
124 | bus_MV_51_0_node_73 | 20 | n |  | TRUE
125 | bus_MV_51_0_node_74 | 20 | n |  | TRUE
126 | bus_MV_51_0_node_151 | 20 | n |  | TRUE
127 | bus_MV_51_0_node_152 | 20 | n |  | TRUE
128 | bus_MV_51_0_node_196 | 20 | n |  | TRUE
129 | bus_MV_51_0_node_68 | 20 | n |  | TRUE
130 | bus_MV_51_0_node_69 | 20 | n |  | TRUE
131 | bus_MV_51_0_node_70 | 20 | n |  | TRUE
132 | bus_MV_51_0_node_71 | 20 | n |  | TRUE
133 | bus_MV_51_0_node_154 | 20 | n |  | TRUE
134 | bus_MV_51_0_node_157 | 20 | n |  | TRUE
135 | bus_MV_51_0_node_153 | 20 | n |  | TRUE
136 | bus_MV_51_0_node_88 | 20 | n |  | TRUE
137 | bus_MV_51_0_node_89 | 20 | n |  | TRUE
138 | bus_MV_51_0_node_90 | 20 | n |  | TRUE
139 | bus_MV_51_0_node_91 | 20 | n |  | TRUE
140 | bus_MV_51_0_node_92 | 20 | n |  | TRUE
141 | bus_MV_51_0_node_93 | 20 | n |  | TRUE
142 | bus_MV_51_0_node_102 | 20 | n |  | TRUE
143 | bus_MV_51_0_node_96 | 20 | n |  | TRUE
144 | bus_MV_51_0_node_98 | 20 | n |  | TRUE
145 | bus_MV_51_0_node_95 | 20 | n |  | TRUE
146 | bus_MV_51_0_node_94 | 20 | n |  | TRUE
147 | bus_MV_51_0_node_97 | 20 | n |  | TRUE
148 | bus_MV_51_0_node_99 | 20 | n |  | TRUE
149 | bus_MV_51_0_node_191 | 20 | n |  | TRUE
150 | bus_MV_51_0_node_199 | 20 | n |  | TRUE
151 | bus_MV_51_0_node_103 | 20 | n |  | TRUE
152 | bus_MV_51_0_node_104 | 20 | n |  | TRUE
153 | bus_MV_51_0_node_105 | 20 | n |  | TRUE
154 | bus_MV_51_0_node_106 | 20 | n |  | TRUE
155 | bus_MV_51_0_node_129 | 20 | n |  | TRUE
156 | bus_MV_51_0_node_195 | 20 | n |  | TRUE
157 | bus_MV_51_0_node_130 | 20 | n |  | TRUE
158 | bus_MV_51_0_node_107 | 20 | n |  | TRUE
159 | bus_MV_51_0_node_109 | 20 | n |  | TRUE
160 | bus_MV_51_0_node_110 | 20 | n |  | TRUE
161 | bus_MV_51_0_node_108 | 20 | n |  | TRUE
162 | bus_MV_51_0_node_114 | 20 | n |  | TRUE
163 | bus_MV_51_0_node_115 | 20 | n |  | TRUE
164 | bus_MV_51_0_node_117 | 20 | n |  | TRUE
165 | bus_MV_51_0_node_119 | 20 | n |  | TRUE
166 | bus_MV_51_0_node_113 | 20 | n |  | TRUE
167 | bus_MV_51_0_node_125 | 20 | n |  | TRUE
168 | bus_MV_51_0_node_171 | 20 | n |  | TRUE
169 | bus_MV_51_0_node_172 | 20 | n |  | TRUE
170 | bus_MV_51_0_node_169 | 20 | n |  | TRUE
171 | bus_MV_51_0_node_121 | 20 | n |  | TRUE
172 | bus_MV_51_0_node_116 | 20 | n |  | TRUE
173 | bus_MV_51_0_node_201 | 20 | n |  | TRUE
174 | bus_MV_51_0_node_120 | 20 | n |  | TRUE
175 | bus_MV_51_0_node_118 | 20 | n |  | TRUE
176 | bus_MV_51_0_node_184 | 20 | n |  | TRUE
177 | bus_MV_51_0_node_200 | 20 | n |  | TRUE
178 | bus_MV_51_0_node_193 | 20 | n |  | TRUE
179 | bus_MV_51_0_node_122 | 20 | n |  | TRUE
180 | bus_MV_51_0_node_183 | 20 | n |  | TRUE
181 | bus_MV_51_0_node_131 | 20 | n |  | TRUE
182 | bus_MV_51_0_node_127 | 20 | n |  | TRUE
183 | bus_MV_51_0_node_175 | 20 | n |  | TRUE
184 | bus_MV_51_0_node_176 | 20 | n |  | TRUE
185 | bus_MV_51_0_node_170 | 20 | n |  | TRUE
186 | bus_MV_51_0_node_194 | 20 | n |  | TRUE
187 | bus_MV_51_0_node_182 | 20 | n |  | TRUE
188 | bus_MV_51_0_node_124 | 20 | n |  | TRUE
189 | bus_MV_51_0_node_126 | 20 | n |  | TRUE
190 | bus_MV_51_0_node_128 | 20 | n |  | TRUE
191 | bus_MV_51_0_node_173 | 20 | n |  | TRUE
192 | bus_MV_51_0_node_174 | 20 | n |  | TRUE
193 | bus_MV_51_0_node_177 | 20 | n |  | TRUE
194 | bus_HV_51_0_node_59 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_51_0_load_0 | 0 | 0.32617 | 0.15797 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_51_0_load_101 | 4 | 0.094951 | 0.045987 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_51_0_load_4 | 5 | 0.13026 | 0.063088 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_51_0_load_190 | 8 | 0.20546 | 0.099508 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_51_0_load_5 | 10 | 0.19832 | 0.09605 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_51_0_load_8 | 11 | 0.26206 | 0.12692 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_51_0_load_9 | 12 | 0.14004 | 0.067823 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_51_0_load_123 | 14 | 0.16846 | 0.081588 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_51_0_load_187 | 15 | 0.1627 | 0.078801 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_51_0_load_11 | 17 | 0.15352 | 0.074352 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_51_0_load_14 | 25 | 0.14417 | 0.069824 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_51_0_load_25 | 26 | 0.15454 | 0.074845 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_51_0_load_188 | 28 | 0.078674 | 0.038104 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_51_0_load_20 | 30 | 0.14365 | 0.069574 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_51_0_load_133 | 32 | 0.3065 | 0.14844 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_51_0_load_23 | 34 | 0.14869 | 0.072012 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_51_0_load_189 | 35 | 0.071931 | 0.034838 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_51_0_load_26 | 36 | 0.14796 | 0.071659 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_51_0_load_27 | 37 | 0.36134 | 0.17501 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_51_0_load_46 | 39 | 0.18091 | 0.08762 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_51_0_load_44 | 42 | 0.077502 | 0.037536 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_51_0_load_86 | 44 | 0.18719 | 0.090659 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_51_0_load_43 | 45 | 0.25905 | 0.12546 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_51_0_load_87 | 48 | 0.29865 | 0.14464 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_51_0_load_76 | 49 | 0.24016 | 0.11632 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_51_0_load_135 | 51 | 0.08053 | 0.039002 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_51_0_load_142 | 53 | 0.77022 | 0.37304 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_51_0_load_140 | 55 | 0.2116 | 0.10248 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_51_0_load_48 | 58 | 0.26821 | 0.1299 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_51_0_load_165 | 60 | 0.15392 | 0.074545 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_51_0_load_81 | 61 | 0.4088 | 0.19799 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_51_0_load_35 | 62 | 0.22048 | 0.10678 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_51_0_load_42 | 64 | 0.2682 | 0.1299 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_51_0_load_185 | 66 | 0.13762 | 0.066652 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_51_0_load_155 | 68 | 0.070238 | 0.034018 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_51_0_load_75 | 69 | 0.22521 | 0.10908 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_51_0_load_47 | 72 | 0.16968 | 0.082179 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_51_0_load_52 | 76 | 0.2545 | 0.12326 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_51_0_load_77 | 78 | 0.29715 | 0.14392 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_51_0_load_54 | 80 | 0.08395 | 0.040659 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_51_0_load_163 | 82 | 0.080611 | 0.039042 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_51_0_load_82 | 83 | 0.13663 | 0.066172 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_51_0_load_85 | 85 | 0.10263 | 0.049706 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_51_0_load_65 | 86 | 0.24328 | 0.11783 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_51_0_load_136 | 88 | 0.082821 | 0.040112 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_51_0_load_138 | 90 | 0.91386 | 0.4426 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_51_0_load_139 | 91 | 0.28552 | 0.13828 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_51_0_load_143 | 93 | 1.2589 | 0.60971 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_51_0_load_144 | 94 | 0.18429 | 0.089257 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_51_0_load_147 | 96 | 0.33598 | 0.16272 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_51_0_load_148 | 98 | 0.10564 | 0.051164 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_51_0_load_158 | 99 | 0.093817 | 0.045438 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_51_0_load_159 | 100 | 0.30021 | 0.1454 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_51_0_load_166 | 102 | 0.74856 | 0.36255 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_51_0_load_164 | 103 | 0.076297 | 0.036952 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_51_0_load_167 | 104 | 0.079028 | 0.038275 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_51_0_load_55 | 105 | 0.18083 | 0.087581 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_51_0_load_149 | 107 | 0.21289 | 0.10311 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_51_0_load_198 | 108 | 0.18873 | 0.091405 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_51_0_load_132 | 112 | 0.2379 | 0.11522 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_51_0_load_179 | 113 | 0.11307 | 0.054762 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_51_0_load_178 | 115 | 0.19512 | 0.094503 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_51_0_load_58 | 116 | 0.38837 | 0.1881 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_51_0_load_72 | 120 | 0.28737 | 0.13918 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_51_0_load_181 | 122 | 0.15115 | 0.073204 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_51_0_load_197 | 123 | 0.27487 | 0.13312 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_51_0_load_152 | 127 | 0.091125 | 0.044134 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_51_0_load_68 | 129 | 0.39793 | 0.19272 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_51_0_load_69 | 130 | 0.069118 | 0.033475 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_51_0_load_70 | 131 | 0.076397 | 0.037001 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_51_0_load_157 | 134 | 0.082484 | 0.039949 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_51_0_load_153 | 135 | 0.20553 | 0.099542 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_51_0_load_88 | 136 | 0.10236 | 0.049577 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_51_0_load_91 | 139 | 0.16261 | 0.078756 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_51_0_load_102 | 142 | 0.41387 | 0.20045 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_51_0_load_94 | 146 | 0.38992 | 0.18884 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_51_0_load_99 | 148 | 0.081348 | 0.039399 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_51_0_load_191 | 149 | 0.18731 | 0.090721 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_51_0_load_199 | 150 | 0.23261 | 0.11266 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_51_0_load_103 | 151 | 0.13388 | 0.064841 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_51_0_load_129 | 155 | 0.21288 | 0.1031 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_51_0_load_195 | 156 | 0.4062 | 0.19673 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_51_0_load_130 | 157 | 0.14412 | 0.069799 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_51_0_load_107 | 158 | 0.32011 | 0.15504 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_51_0_load_171 | 168 | 0.080878 | 0.039171 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_51_0_load_172 | 169 | 0.27967 | 0.13545 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_51_0_load_169 | 170 | 0.13643 | 0.066078 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_51_0_load_121 | 171 | 0.20245 | 0.098051 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_51_0_load_201 | 173 | 0.080436 | 0.038957 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_51_0_load_184 | 176 | 0.32486 | 0.15734 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_51_0_load_200 | 177 | 0.22916 | 0.11099 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_51_0_load_122 | 179 | 0.23334 | 0.11301 | 0 | 0 |  | 1 | TRUE | wye
92 | MV_51_0_load_183 | 180 | 0.24366 | 0.11801 | 0 | 0 |  | 1 | TRUE | wye
93 | MV_51_0_load_131 | 181 | 0.13015 | 0.063034 | 0 | 0 |  | 1 | TRUE | wye
94 | MV_51_0_load_175 | 183 | 0.076095 | 0.036855 | 0 | 0 |  | 1 | TRUE | wye
95 | MV_51_0_load_182 | 187 | 0.070779 | 0.03428 | 0 | 0 |  | 1 | TRUE | wye
96 | MV_51_0_load_124 | 188 | 0.19839 | 0.096085 | 0 | 0 |  | 1 | TRUE | wye
97 | MV_51_0_load_173 | 191 | 0.075115 | 0.03638 | 0 | 0 |  | 1 | TRUE | wye
98 | MV_51_0_load_174 | 192 | 0.06922 | 0.033525 | 0 | 0 |  | 1 | TRUE | wye
99 | MV_51_0_load_177 | 193 | 0.07819 | 0.037869 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 118 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_51_0_line_0 |  | 0 | 1 | 0.044837 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_51_0_line_1 |  | 1 | 2 | 0.18223 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_51_0_line_2 |  | 1 | 3 | 0.50482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_51_0_line_3 |  | 2 | 5 | 0.005249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_51_0_line_4 |  | 3 | 7 | 0.91088 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_51_0_line_5 |  | 3 | 8 | 0.1119 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_51_0_line_6 |  | 4 | 5 | 2.6859 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
7 | MV_51_0_line_7 |  | 4 | 6 | 0.2064 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
8 | MV_51_0_line_8 |  | 6 | 148 | 0.20108 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
9 | MV_51_0_line_9 |  | 7 | 9 | 0.34119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_51_0_line_10 |  | 7 | 10 | 0.040831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_51_0_line_11 |  | 9 | 11 | 0.027909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_51_0_line_12 |  | 12 | 13 | 1.2214 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_51_0_line_13 |  | 12 | 14 | 0.75789 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_51_0_line_14 |  | 13 | 15 | 0.44853 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_51_0_line_15 |  | 14 | 16 | 0.04261 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_51_0_line_16 |  | 15 | 35 | 1.0604 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_51_0_line_17 |  | 16 | 166 | 0.6308 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
18 | MV_51_0_line_18 |  | 16 | 161 | 0.21455 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
19 | MV_51_0_line_19 |  | 17 | 18 | 0.027666 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_51_0_line_20 |  | 17 | 19 | 0.032612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_51_0_line_21 |  | 17 | 20 | 0.12753 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_51_0_line_22 |  | 18 | 21 | 0.38523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_51_0_line_23 |  | 19 | 22 | 0.072821 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_51_0_line_24 |  | 20 | 23 | 0.25292 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_51_0_line_25 |  | 20 | 24 | 0.1113 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_51_0_line_26 |  | 20 | 25 | 0.033849 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_51_0_line_27 |  | 21 | 26 | 0.065423 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_51_0_line_28 |  | 22 | 30 | 0.067999 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_51_0_line_29 |  | 23 | 31 | 0.93608 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_51_0_line_30 |  | 23 | 32 | 0.050615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_51_0_line_31 |  | 24 | 33 | 0.078647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_51_0_line_32 |  | 24 | 34 | 0.026333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_51_0_line_33 |  | 25 | 29 | 0.037653 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_51_0_line_34 |  | 27 | 28 | 0.055931 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_51_0_line_35 |  | 27 | 29 | 0.047782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_51_0_line_36 |  | 31 | 35 | 0.057704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_51_0_line_37 |  | 33 | 36 | 0.027664 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_51_0_line_38 |  | 37 | 38 | 0.081507 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_51_0_line_39 |  | 37 | 39 | 0.90484 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_51_0_line_40 |  | 38 | 40 | 0.6445 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_51_0_line_41 |  | 39 | 41 | 0.24958 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
42 | MV_51_0_line_42 |  | 39 | 42 | 0.0005448 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
43 | MV_51_0_line_43 |  | 40 | 49 | 0.090058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_51_0_line_44 |  | 41 | 98 | 0.03468 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
45 | MV_51_0_line_45 |  | 41 | 104 | 0.015923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_51_0_line_46 |  | 42 | 45 | 0.080553 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
47 | MV_51_0_line_47 |  | 43 | 44 | 0.032199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_51_0_line_48 |  | 43 | 45 | 1.2152 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_51_0_line_49 |  | 45 | 56 | 0.060931 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
50 | MV_51_0_line_50 |  | 46 | 47 | 0.62814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_51_0_line_51 |  | 46 | 48 | 0.050174 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_51_0_line_52 |  | 47 | 50 | 0.11086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_51_0_line_53 |  | 47 | 51 | 0.062963 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_51_0_line_54 |  | 50 | 52 | 0.12453 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_51_0_line_55 |  | 50 | 53 | 0.0061901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_51_0_line_56 |  | 52 | 54 | 0.17137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_51_0_line_57 |  | 52 | 55 | 0.038144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_51_0_line_58 |  | 54 | 60 | 0.0010663 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
59 | MV_51_0_line_59 |  | 54 | 61 | 0.059492 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
60 | MV_51_0_line_60 |  | 56 | 72 | 0.071239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_51_0_line_61 |  | 56 | 59 | 0.27881 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
62 | MV_51_0_line_62 |  | 57 | 58 | 0.079185 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_51_0_line_63 |  | 57 | 59 | 0.23357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_51_0_line_64 |  | 59 | 67 | 0.622 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_51_0_line_65 |  | 59 | 68 | 0.028242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_51_0_line_66 |  | 59 | 65 | 0.7305 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
67 | MV_51_0_line_67 |  | 60 | 96 | 0.057214 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
68 | MV_51_0_line_68 |  | 61 | 87 | 0.0082915 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_51_0_line_69 |  | 62 | 63 | 0.057144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_51_0_line_70 |  | 63 | 64 | 0.056782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_51_0_line_71 |  | 64 | 70 | 0.40665 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_51_0_line_72 |  | 65 | 66 | 0.02234 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
73 | MV_51_0_line_73 |  | 66 | 71 | 0.12114 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
74 | MV_51_0_line_74 |  | 67 | 69 | 0.032564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_51_0_line_75 |  | 68 | 73 | 0.034395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_51_0_line_76 |  | 70 | 71 | 0.54852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_51_0_line_77 |  | 70 | 86 | 0.08187 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_51_0_line_78 |  | 71 | 128 | 0.15659 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_51_0_line_79 |  | 73 | 134 | 0.025965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_51_0_line_80 |  | 74 | 75 | 0.16206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_51_0_line_81 |  | 74 | 76 | 0.075227 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_51_0_line_82 |  | 74 | 77 | 1.014 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_51_0_line_83 |  | 75 | 78 | 0.064711 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_51_0_line_84 |  | 76 | 79 | 0.005476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_51_0_line_85 |  | 77 | 83 | 0.087732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_51_0_line_86 |  | 78 | 87 | 0.03659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_51_0_line_87 |  | 79 | 80 | 0.042365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_51_0_line_88 |  | 80 | 81 | 0.039269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_51_0_line_89 |  | 80 | 82 | 0.051117 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_51_0_line_90 |  | 81 | 100 | 0.001413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_51_0_line_91 |  | 83 | 84 | 0.19634 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_51_0_line_92 |  | 84 | 85 | 0.11852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_51_0_line_93 |  | 88 | 89 | 0.020068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_51_0_line_94 |  | 89 | 90 | 0.05232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_51_0_line_95 |  | 90 | 91 | 0.021784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_51_0_line_96 |  | 91 | 92 | 0.042634 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_51_0_line_97 |  | 92 | 102 | 0.040095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_51_0_line_98 |  | 92 | 103 | 0.049334 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_51_0_line_99 |  | 92 | 101 | 0.059248 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_51_0_line_100 |  | 93 | 94 | 0.016543 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_51_0_line_101 |  | 93 | 95 | 0.024497 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
102 | MV_51_0_line_102 |  | 94 | 96 | 0.044356 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
103 | MV_51_0_line_103 |  | 95 | 97 | 0.006552 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
104 | MV_51_0_line_104 |  | 97 | 98 | 0.016973 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
105 | MV_51_0_line_105 |  | 99 | 100 | 0.02535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_51_0_line_106 |  | 99 | 101 | 0.071444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_51_0_line_107 |  | 105 | 106 | 0.011463 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_51_0_line_108 |  | 106 | 107 | 0.27324 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
109 | MV_51_0_line_109 |  | 106 | 108 | 0.39314 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
110 | MV_51_0_line_110 |  | 107 | 109 | 0.055589 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
111 | MV_51_0_line_111 |  | 108 | 110 | 0.03512 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
112 | MV_51_0_line_112 |  | 109 | 126 | 0.012268 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
113 | MV_51_0_line_113 |  | 110 | 121 | 0.2115 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
114 | MV_51_0_line_114 |  | 111 | 112 | 0.012564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_51_0_line_115 |  | 111 | 113 | 0.10587 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_51_0_line_116 |  | 112 | 181 | 0.14944 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_51_0_line_117 |  | 113 | 114 | 0.045224 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
118 | MV_51_0_line_118 |  | 113 | 115 | 0.022596 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
119 | MV_51_0_line_119 |  | 114 | 121 | 0.013037 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
120 | MV_51_0_line_120 |  | 115 | 182 | 0.049279 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
121 | MV_51_0_line_121 |  | 116 | 117 | 0.076509 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
122 | MV_51_0_line_122 |  | 116 | 118 | 0.031706 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
123 | MV_51_0_line_123 |  | 117 | 119 | 0.26653 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
124 | MV_51_0_line_124 |  | 117 | 120 | 0.21863 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
125 | MV_51_0_line_125 |  | 119 | 123 | 0.039998 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
126 | MV_51_0_line_126 |  | 120 | 124 | 0.048767 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
127 | MV_51_0_line_127 |  | 121 | 122 | 0.055517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_51_0_line_128 |  | 123 | 128 | 0.027854 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
129 | MV_51_0_line_129 |  | 124 | 125 | 0.82858 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
130 | MV_51_0_line_130 |  | 125 | 135 | 0.017975 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
131 | MV_51_0_line_131 |  | 126 | 127 | 0.031317 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
132 | MV_51_0_line_132 |  | 127 | 135 | 0.041496 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
133 | MV_51_0_line_133 |  | 129 | 130 | 0.011463 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_51_0_line_134 |  | 129 | 131 | 0.017861 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_51_0_line_135 |  | 131 | 132 | 0.031615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_51_0_line_136 |  | 132 | 133 | 0.080938 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_51_0_line_137 |  | 133 | 134 | 0.033127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_51_0_line_138 |  | 136 | 137 | 0.058713 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
139 | MV_51_0_line_139 |  | 137 | 138 | 0.40546 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_51_0_line_140 |  | 138 | 139 | 0.049317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_51_0_line_141 |  | 139 | 140 | 0.14225 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
142 | MV_51_0_line_142 |  | 140 | 141 | 0.31079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_51_0_line_143 |  | 141 | 142 | 0.02276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_51_0_line_144 |  | 141 | 143 | 0.026895 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_51_0_line_145 |  | 143 | 144 | 0.67194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_51_0_line_146 |  | 143 | 145 | 0.3391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_51_0_line_147 |  | 144 | 149 | 0.04683 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
148 | MV_51_0_line_148 |  | 144 | 147 | 0.70171 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
149 | MV_51_0_line_149 |  | 145 | 146 | 0.013268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_51_0_line_150 |  | 147 | 148 | 0.14646 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
151 | MV_51_0_line_151 |  | 149 | 150 | 0.31169 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
152 | MV_51_0_line_152 |  | 150 | 186 | 0.086808 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
153 | MV_51_0_line_153 |  | 151 | 152 | 0.002889 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_51_0_line_154 |  | 152 | 153 | 0.43492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_51_0_line_155 |  | 153 | 154 | 0.48126 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_51_0_line_156 |  | 153 | 155 | 0.05515 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
157 | MV_51_0_line_157 |  | 154 | 156 | 0.035558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_51_0_line_158 |  | 155 | 157 | 0.035398 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_51_0_line_159 |  | 157 | 191 | 0.061334 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
160 | MV_51_0_line_160 |  | 158 | 159 | 0.038332 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_51_0_line_161 |  | 158 | 160 | 0.043527 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
162 | MV_51_0_line_162 |  | 158 | 161 | 0.030651 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
163 | MV_51_0_line_163 |  | 159 | 162 | 0.29131 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_51_0_line_164 |  | 160 | 163 | 0.7258 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_51_0_line_165 |  | 160 | 164 | 0.52098 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
166 | MV_51_0_line_166 |  | 160 | 165 | 0.58001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_51_0_line_167 |  | 162 | 168 | 0.015865 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_51_0_line_168 |  | 162 | 169 | 0.030242 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_51_0_line_169 |  | 162 | 170 | 0.015375 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_51_0_line_170 |  | 163 | 171 | 0.018997 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_51_0_line_171 |  | 164 | 175 | 0.22553 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
172 | MV_51_0_line_172 |  | 164 | 176 | 0.0628 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_51_0_line_173 |  | 165 | 179 | 0.064136 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
174 | MV_51_0_line_174 |  | 165 | 172 | 0.70439 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_51_0_line_175 |  | 166 | 167 | 0.3319 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
176 | MV_51_0_line_176 |  | 167 | 182 | 0.14719 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
177 | MV_51_0_line_177 |  | 168 | 183 | 0.024354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_51_0_line_178 |  | 169 | 184 | 0.027314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_51_0_line_179 |  | 170 | 185 | 0.024212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_51_0_line_180 |  | 172 | 173 | 0.012852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_51_0_line_181 |  | 172 | 174 | 0.54083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
182 | MV_51_0_line_182 |  | 174 | 180 | 0.016648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
183 | MV_51_0_line_183 |  | 175 | 177 | 0.017237 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
184 | MV_51_0_line_184 |  | 175 | 178 | 0.030669 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
185 | MV_51_0_line_185 |  | 178 | 186 | 0.67236 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
186 | MV_51_0_line_186 |  | 180 | 187 | 0.094936 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
187 | MV_51_0_line_187 |  | 184 | 193 | 0.013652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
188 | MV_51_0_line_188 |  | 185 | 192 | 0.031672 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
189 | MV_51_0_line_189 |  | 185 | 191 | 0.015421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
190 | MV_51_0_line_190 |  | 188 | 189 | 0.019879 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
191 | MV_51_0_line_191 |  | 189 | 190 | 0.094827 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
192 | MV_51_0_line_192 |  | 190 | 191 | 0.033426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_51_0_trafo_59 | 25 MVA 110/20 kV | 194 | 118 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2763811.0399 | 1248329.8983
1 | 2763767.6537 | 1248341.2113
2 | 2763619.4371 | 1248331.5985
3 | 2763844.7142 | 1247974.6779
4 | 2761991.2924 | 1250471.5445
5 | 2763614.1747 | 1248331.4309
6 | 2761828.4473 | 1250344.7306
7 | 2764032.2323 | 1248140.0196
8 | 2763781.0038 | 1247882.6797
9 | 2764092.2034 | 1248402.7582
10 | 2764012.586 | 1248104.1952
11 | 2764067.4281 | 1248415.7414
12 | 2761072.2481 | 1252751.5564
13 | 2761441.0128 | 1253915.9954
14 | 2761619.7877 | 1252227.5427
15 | 2761193.1007 | 1254186.5991
16 | 2761649.7787 | 1252197.2744
17 | 2759286.7785 | 1254589.9288
18 | 2759260.2003 | 1254590.7705
19 | 2759275.5075 | 1254620.2565
20 | 2759405.5799 | 1254543.5555
21 | 2759006.5567 | 1254644.733
22 | 2759259.3449 | 1254691.2608
23 | 2759538.7498 | 1254661.1829
24 | 2759512.2419 | 1254514.3861
25 | 2759373.7895 | 1254555.1785
26 | 2759019.7599 | 1254580.6557
27 | 2759311.5316 | 1254506.8767
28 | 2759332.8372 | 1254455.4419
29 | 2759355.6871 | 1254522.1467
30 | 2759320.3376 | 1254716.9718
31 | 2760220.4636 | 1254721.3125
32 | 2759536.9778 | 1254710.0447
33 | 2759507.7001 | 1254436.7292
34 | 2759538.0934 | 1254519.5098
35 | 2760274.0423 | 1254715.445
36 | 2759480.2167 | 1254439.759
37 | 2765017.5566 | 1253154.521
38 | 2765091.1259 | 1253189.6071
39 | 2764158.8621 | 1252869.2482
40 | 2765035.4391 | 1253437.1129
41 | 2764384.9746 | 1252974.9161
42 | 2764158.4209 | 1252868.9286
43 | 2765274.8684 | 1252307.3021
44 | 2765307.0924 | 1252309.4477
45 | 2764158.8956 | 1252788.377
46 | 2765135.3457 | 1252805.1955
47 | 2764601.3472 | 1252934.3814
48 | 2765184.9802 | 1252797.8604
49 | 2764969.8777 | 1253375.9678
50 | 2764542.314 | 1252934.108
51 | 2764653.8933 | 1252969.0686
52 | 2764571.4186 | 1253019.2602
53 | 2764541.7681 | 1252927.942
54 | 2764446.0127 | 1253040.5223
55 | 2764609.5377 | 1253017.8963
56 | 2764107.1166 | 1252756.0092
57 | 2764037.9124 | 1253129.1897
58 | 2764099.591 | 1253178.8492
59 | 2763922.6243 | 1252964.9735
60 | 2764445.9865 | 1253039.4564
61 | 2764448.5973 | 1253099.9581
62 | 2763761.1835 | 1252159.6673
63 | 2763715.5507 | 1252194.2308
64 | 2763682.5683 | 1252240.2448
65 | 2763820.0467 | 1252595.2769
66 | 2763798.339 | 1252589.7377
67 | 2763649.5963 | 1253033.1406
68 | 2763899.2942 | 1252949.0567
69 | 2763672.6683 | 1253056.1906
70 | 2763280.8971 | 1252176.7865
71 | 2763699.6689 | 1252519.4606
72 | 2764046.9418 | 1252717.592
73 | 2763870.8817 | 1252929.6723
74 | 2764488.4391 | 1253243.5216
75 | 2764400.0298 | 1253160.8931
76 | 2764561.9549 | 1253248.5462
77 | 2764303.5177 | 1254240.4691
78 | 2764413.6868 | 1253097.6399
79 | 2764562.0367 | 1253254.0208
80 | 2764604.3849 | 1253252.8377
81 | 2764643.6383 | 1253251.7411
82 | 2764604.9426 | 1253201.7241
83 | 2764284.4638 | 1254326.1074
84 | 2764096.5098 | 1254269.3274
85 | 2763992.9866 | 1254212.1822
86 | 2763209.2617 | 1252136.7607
87 | 2764448.7898 | 1253108.2474
88 | 2764700.7782 | 1253051.2489
89 | 2764717.6741 | 1253059.8333
90 | 2764730.0596 | 1253108.6855
91 | 2764730.3364 | 1253130.4681
92 | 2764723.7902 | 1253172.4201
93 | 2764435.3701 | 1252931.5721
94 | 2764450.3832 | 1252938.3934
95 | 2764412.242 | 1252923.4972
96 | 2764443.953 | 1252982.2804
97 | 2764409.3974 | 1252929.4022
98 | 2764401.3723 | 1252944.3576
99 | 2764668.9687 | 1253249.7524
100 | 2764643.6248 | 1253250.3282
101 | 2764724.6633 | 1253231.6615
102 | 2764763.8613 | 1253171.0279
103 | 2764682.6058 | 1253199.5803
104 | 2764378.1461 | 1252989.3005
105 | 2762603.2898 | 1252662.5516
106 | 2762593.2262 | 1252667.4249
107 | 2762522.2513 | 1252931.2877
108 | 2762413.9422 | 1252317.5491
109 | 2762466.9343 | 1252925.9815
110 | 2762398.0597 | 1252286.2262
111 | 2762240.5501 | 1252444.5846
112 | 2762236.7033 | 1252456.5471
113 | 2762275.6528 | 1252344.7039
114 | 2762308.7591 | 1252333.1496
115 | 2762253.8846 | 1252338.6445
116 | 2763247.5404 | 1252695.6679
117 | 2763283.366 | 1252763.169
118 | 2763229.2637 | 1252669.7599
119 | 2763514.9475 | 1252642.7092
120 | 2763281.9937 | 1252981.7897
121 | 2762321.6591 | 1252335.283
122 | 2762290.594 | 1252298.9652
123 | 2763552.058 | 1252627.8181
124 | 2763274.518 | 1253029.9778
125 | 2762518.7532 | 1252997.0089
126 | 2762471.8966 | 1252937.2069
127 | 2762489.4549 | 1252955.1439
128 | 2763575.9343 | 1252613.3623
129 | 2763813.0917 | 1252934.1768
130 | 2763801.9205 | 1252931.6069
131 | 2763817.8295 | 1252916.9658
132 | 2763828.1959 | 1252887.1368
133 | 2763873.8221 | 1252873.1063
134 | 2763868.5315 | 1252905.8081
135 | 2762502.8946 | 1252989.085
136 | 2760680.308 | 1250847.1255
137 | 2760623.1882 | 1250833.5412
138 | 2760436.967 | 1250939.5156
139 | 2760423.2499 | 1250986.6475
140 | 2760548.2484 | 1251054.5455
141 | 2760655.9738 | 1251153.7763
142 | 2760670.1956 | 1251135.9772
143 | 2760679.447 | 1251166.9038
144 | 2761115.5368 | 1251053.706
145 | 2760637.7137 | 1251413.0997
146 | 2760629.0053 | 1251423.1294
147 | 2761598.7748 | 1250599.6344
148 | 2761684.2153 | 1250484.5365
149 | 2761113.1652 | 1251092.8368
150 | 2761013.2604 | 1251388.0769
151 | 2762464.7548 | 1252068.6093
152 | 2762462.2734 | 1252067.1175
153 | 2762089.1522 | 1251948.1779
154 | 2762221.0419 | 1251749.4282
155 | 2762125.1486 | 1251989.9609
156 | 2762187.8698 | 1251762.478
157 | 2762134.4942 | 1252023.7326
158 | 2761818.5465 | 1252031.6895
159 | 2761842.7671 | 1252061.4592
160 | 2761821.4251 | 1251988.2682
161 | 2761807.1433 | 1252060.1405
162 | 2762044.0989 | 1252077.4889
163 | 2761442.2848 | 1251889.2479
164 | 2761537.8226 | 1251744.6153
165 | 2762150.6792 | 1251588.0599
166 | 2761916.1347 | 1252507.2636
167 | 2762097.6798 | 1252229.4209
168 | 2762056.0863 | 1252087.8812
169 | 2762021.0008 | 1252057.9756
170 | 2762056.324 | 1252068.1645
171 | 2761427.0461 | 1251877.8434
172 | 2762035.0635 | 1251390.5738
173 | 2762025.9856 | 1251381.4496
174 | 2762381.3152 | 1251566.3752
175 | 2761625.7264 | 1251643.5314
176 | 2761581.1101 | 1251786.6306
177 | 2761643.0105 | 1251643.9254
178 | 2761606.3927 | 1251619.7243
179 | 2762093.7811 | 1251558.462
180 | 2762393.0052 | 1251578.2632
181 | 2762116.2307 | 1252544.9736
182 | 2762211.2025 | 1252318.2073
183 | 2762075.1984 | 1252102.9709
184 | 2761998.9943 | 1252041.797
185 | 2762075.5754 | 1252053.4808
186 | 2761090.4277 | 1251428.2593
187 | 2762461.0156 | 1251644.5002
188 | 2762136.1729 | 1252165.3752
189 | 2762138.6508 | 1252146.8685
190 | 2762113.4959 | 1252084.2718
191 | 2762087.5471 | 1252063.2017
192 | 2762051.1044 | 1252033.3736
193 | 2762007.9571 | 1252031.4996
194 | 2763229.2637 | 1252669.7599

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98865 | -0.41189 | 0.32617 | 0.15797
1 | 0.98867 | -0.41171 | 0 | 0
2 | 0.9889 | -0.41338 | 0 | 0
3 | 0.98825 | -0.4088 | 0 | 0
4 | 0.9909 | -0.29545 | 0.094951 | 0.045987
5 | 0.98891 | -0.41343 | 0.13026 | 0.063088
6 | 0.99098 | -0.29498 | 0 | 0
7 | 0.98771 | -0.40486 | 0 | 0
8 | 0.9882 | -0.40909 | 0.20546 | 0.099508
9 | 0.9876 | -0.40387 | 0 | 0
10 | 0.9877 | -0.40476 | 0.19832 | 0.09605
11 | 0.98759 | -0.40378 | 0.26206 | 0.12692
12 | 0.99019 | -0.2839 | 0.14004 | 0.067823
13 | 0.98662 | -0.31379 | 0 | 0
14 | 0.99261 | -0.26409 | 0.16846 | 0.081588
15 | 0.98575 | -0.30714 | 0.1627 | 0.078801
16 | 0.99276 | -0.26289 | 0 | 0
17 | 0.98092 | -0.3152 | 0.15352 | 0.074352
18 | 0.98091 | -0.31516 | 0 | 0
19 | 0.98091 | -0.31515 | 0 | 0
20 | 0.98103 | -0.31432 | 0 | 0
21 | 0.98084 | -0.31454 | 0 | 0
22 | 0.9809 | -0.31503 | 0 | 0
23 | 0.98135 | -0.31695 | 0 | 0
24 | 0.98099 | -0.31394 | 0 | 0
25 | 0.98101 | -0.31442 | 0.14417 | 0.069824
26 | 0.98082 | -0.31466 | 0.15454 | 0.074845
27 | 0.98101 | -0.31435 | 0 | 0
28 | 0.981 | -0.3143 | 0.078674 | 0.038104
29 | 0.98101 | -0.3144 | 0 | 0
30 | 0.98089 | -0.31491 | 0.14365 | 0.069574
31 | 0.98288 | -0.32929 | 0 | 0
32 | 0.98133 | -0.31676 | 0.3065 | 0.14844
33 | 0.98097 | -0.31381 | 0 | 0
34 | 0.98098 | -0.31389 | 0.14869 | 0.072012
35 | 0.98298 | -0.33 | 0.071931 | 0.034838
36 | 0.98097 | -0.31375 | 0.14796 | 0.071659
37 | 0.99523 | -0.070822 | 0.36134 | 0.17501
38 | 0.9952 | -0.071183 | 0 | 0
39 | 0.99628 | -0.06279 | 0.18091 | 0.08762
40 | 0.995 | -0.069717 | 0 | 0
41 | 0.99565 | -0.097711 | 0 | 0
42 | 0.99628 | -0.062787 | 0.077502 | 0.037536
43 | 0.99606 | -0.053125 | 0 | 0
44 | 0.99605 | -0.053053 | 0.18719 | 0.090659
45 | 0.9965 | -0.050201 | 0.25905 | 0.12546
46 | 0.99463 | -0.096786 | 0 | 0
47 | 0.99487 | -0.098752 | 0 | 0
48 | 0.9946 | -0.096969 | 0.29865 | 0.14464
49 | 0.99497 | -0.069462 | 0.24016 | 0.11632
50 | 0.99492 | -0.099134 | 0 | 0
51 | 0.99486 | -0.098694 | 0.08053 | 0.039002
52 | 0.9951 | -0.1007 | 0 | 0
53 | 0.99491 | -0.099076 | 0.77022 | 0.37304
54 | 0.9954 | -0.10324 | 0 | 0
55 | 0.99509 | -0.1006 | 0.2116 | 0.10248
56 | 0.99659 | -0.049852 | 0 | 0
57 | 0.99691 | -0.047471 | 0 | 0
58 | 0.99687 | -0.04773 | 0.26821 | 0.1299
59 | 0.99699 | -0.048182 | 0 | 0
60 | 0.9954 | -0.10321 | 0.15392 | 0.074545
61 | 0.99512 | -0.11003 | 0.4088 | 0.19799
62 | 0.9977 | -0.016957 | 0.22048 | 0.10678
63 | 0.99772 | -0.017106 | 0 | 0
64 | 0.99774 | -0.017249 | 0.2682 | 0.1299
65 | 0.99818 | -0.042817 | 0 | 0
66 | 0.99822 | -0.042645 | 0.13762 | 0.066652
67 | 0.99681 | -0.046821 | 0 | 0
68 | 0.99697 | -0.047956 | 0.070238 | 0.034018
69 | 0.9968 | -0.046734 | 0.22521 | 0.10908
70 | 0.99812 | -0.014735 | 0 | 0
71 | 0.99863 | -0.019147 | 0 | 0
72 | 0.99657 | -0.04971 | 0.16968 | 0.082179
73 | 0.99694 | -0.047709 | 0 | 0
74 | 0.99387 | -0.10485 | 0 | 0
75 | 0.99453 | -0.11084 | 0 | 0
76 | 0.99359 | -0.10225 | 0.2545 | 0.12326
77 | 0.99341 | -0.10832 | 0 | 0
78 | 0.99492 | -0.10821 | 0.29715 | 0.14392
79 | 0.99357 | -0.10207 | 0 | 0
80 | 0.99343 | -0.10073 | 0.08395 | 0.040659
81 | 0.9933 | -0.09956 | 0 | 0
82 | 0.99342 | -0.10078 | 0.080611 | 0.039042
83 | 0.99338 | -0.10809 | 0.13663 | 0.066172
84 | 0.99334 | -0.10839 | 0 | 0
85 | 0.99332 | -0.10825 | 0.10263 | 0.049706
86 | 0.9981 | -0.014501 | 0.24328 | 0.11783
87 | 0.99509 | -0.10969 | 0 | 0
88 | 0.99277 | -0.094576 | 0.082821 | 0.040112
89 | 0.99277 | -0.094596 | 0 | 0
90 | 0.99278 | -0.094645 | 0.91386 | 0.4426
91 | 0.9928 | -0.094906 | 0.28552 | 0.13828
92 | 0.99287 | -0.095562 | 0 | 0
93 | 0.99555 | -0.098101 | 1.2589 | 0.60971
94 | 0.99554 | -0.098165 | 0.18429 | 0.089257
95 | 0.99558 | -0.097987 | 0 | 0
96 | 0.99545 | -0.103 | 0.33598 | 0.16272
97 | 0.99559 | -0.097956 | 0 | 0
98 | 0.99561 | -0.097877 | 0.10564 | 0.051164
99 | 0.99323 | -0.098854 | 0.093817 | 0.045438
100 | 0.9933 | -0.099518 | 0.30021 | 0.1454
101 | 0.99303 | -0.097058 | 0 | 0
102 | 0.99284 | -0.095199 | 0.74856 | 0.36255
103 | 0.99287 | -0.095608 | 0.076297 | 0.036952
104 | 0.99565 | -0.097696 | 0.079028 | 0.038275
105 | 0.99636 | -0.12068 | 0.18083 | 0.087581
106 | 0.99636 | -0.12071 | 0 | 0
107 | 0.99718 | -0.070279 | 0.21289 | 0.10311
108 | 0.99522 | -0.19205 | 0.18873 | 0.091405
109 | 0.99726 | -0.069688 | 0 | 0
110 | 0.99512 | -0.19831 | 0 | 0
111 | 0.99466 | -0.20157 | 0 | 0
112 | 0.99465 | -0.20152 | 0.2379 | 0.11522
113 | 0.99473 | -0.20109 | 0.11307 | 0.054762
114 | 0.9948 | -0.20063 | 0 | 0
115 | 0.9947 | -0.20131 | 0.19512 | 0.094503
116 | 0.99978 | -0.013331 | 0.38837 | 0.1881
117 | 0.99951 | -0.014916 | 0 | 0
118 | 1 | 0 | -21.8791 | -9.4859
119 | 0.99903 | -0.017256 | 0 | 0
120 | 0.99881 | -0.058655 | 0.28737 | 0.13918
121 | 0.99481 | -0.2005 | 0 | 0
122 | 0.9948 | -0.2004 | 0.15115 | 0.073204
123 | 0.99896 | -0.017601 | 0.27487 | 0.13312
124 | 0.99874 | -0.059225 | 0 | 0
125 | 0.99742 | -0.068579 | 0 | 0
126 | 0.99728 | -0.069557 | 0 | 0
127 | 0.99733 | -0.069222 | 0.091125 | 0.044134
128 | 0.99891 | -0.017837 | 0 | 0
129 | 0.99681 | -0.04649 | 0.39793 | 0.19272
130 | 0.9968 | -0.046481 | 0.069118 | 0.033475
131 | 0.99682 | -0.04659 | 0.076397 | 0.037001
132 | 0.99684 | -0.046795 | 0 | 0
133 | 0.99689 | -0.047312 | 0 | 0
134 | 0.99692 | -0.047521 | 0.082484 | 0.039949
135 | 0.9974 | -0.068776 | 0.20553 | 0.099542
136 | 0.99021 | -0.28451 | 0.10236 | 0.049577
137 | 0.99022 | -0.28443 | 0 | 0
138 | 0.99028 | -0.28481 | 0 | 0
139 | 0.99028 | -0.28484 | 0.16261 | 0.078756
140 | 0.99035 | -0.28424 | 0 | 0
141 | 0.99046 | -0.28495 | 0 | 0
142 | 0.99045 | -0.28484 | 0.41387 | 0.20045
143 | 0.99049 | -0.28468 | 0 | 0
144 | 0.99141 | -0.29191 | 0 | 0
145 | 0.99032 | -0.28317 | 0 | 0
146 | 0.99032 | -0.2831 | 0.38992 | 0.18884
147 | 0.99112 | -0.29409 | 0 | 0
148 | 0.99106 | -0.29449 | 0.081348 | 0.039399
149 | 0.99144 | -0.29166 | 0.18731 | 0.090721
150 | 0.9917 | -0.27596 | 0.23261 | 0.11266
151 | 0.99132 | -0.2612 | 0.13388 | 0.064841
152 | 0.99132 | -0.2612 | 0 | 0
153 | 0.99139 | -0.26177 | 0 | 0
154 | 0.99114 | -0.25959 | 0 | 0
155 | 0.99145 | -0.26129 | 0.21288 | 0.1031
156 | 0.99112 | -0.25941 | 0.4062 | 0.19673
157 | 0.99148 | -0.26156 | 0.14412 | 0.069799
158 | 0.99247 | -0.26833 | 0.32011 | 0.15504
159 | 0.99238 | -0.26755 | 0 | 0
160 | 0.99245 | -0.26858 | 0 | 0
161 | 0.99254 | -0.26447 | 0 | 0
162 | 0.99168 | -0.26151 | 0 | 0
163 | 0.99226 | -0.26721 | 0 | 0
164 | 0.99217 | -0.27088 | 0 | 0
165 | 0.99199 | -0.26553 | 0 | 0
166 | 0.99358 | -0.25702 | 0 | 0
167 | 0.99444 | -0.2032 | 0 | 0
168 | 0.99168 | -0.26148 | 0.080878 | 0.039171
169 | 0.99166 | -0.26138 | 0.27967 | 0.13545
170 | 0.99165 | -0.26128 | 0.13643 | 0.066078
171 | 0.99225 | -0.26717 | 0.20245 | 0.098051
172 | 0.99163 | -0.26314 | 0 | 0
173 | 0.99163 | -0.26313 | 0.080436 | 0.038957
174 | 0.99142 | -0.26132 | 0 | 0
175 | 0.99206 | -0.27176 | 0 | 0
176 | 0.99214 | -0.27064 | 0.32486 | 0.15734
177 | 0.99206 | -0.27171 | 0.22916 | 0.11099
178 | 0.99204 | -0.27346 | 0 | 0
179 | 0.99196 | -0.26572 | 0.23334 | 0.11301
180 | 0.99141 | -0.26125 | 0.24366 | 0.11801
181 | 0.99461 | -0.20175 | 0.13015 | 0.063034
182 | 0.99464 | -0.20179 | 0 | 0
183 | 0.99167 | -0.26145 | 0.076095 | 0.036855
184 | 0.99166 | -0.26135 | 0 | 0
185 | 0.99161 | -0.26096 | 0 | 0
186 | 0.99174 | -0.2757 | 0 | 0
187 | 0.9914 | -0.26133 | 0.070779 | 0.03428
188 | 0.99155 | -0.26042 | 0.19839 | 0.096085
189 | 0.99156 | -0.26047 | 0 | 0
190 | 0.99158 | -0.26069 | 0 | 0
191 | 0.99159 | -0.26076 | 0.075115 | 0.03638
192 | 0.99161 | -0.26093 | 0.06922 | 0.033525
193 | 0.99166 | -0.26134 | 0.07819 | 0.037869
194 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.32617 | -0.15797 | 0.32618 | 0.15792 | 8.9451e-06 | -4.6716e-05 | 0.010582 | 0.010581 | 0.010582 | 0.98865 | -0.41189 | 0.98867 | -0.41171 | 5.0391
1 | -0.99263 | -0.43791 | 0.99287 | 0.43372 | 0.00024374 | -0.0041816 | 0.031678 | 0.031628 | 0.031678 | 0.98867 | -0.41171 | 0.9889 | -0.41338 | 14.3991
2 | 0.66645 | 0.27998 | -0.66615 | -0.29167 | 0.00030214 | -0.011687 | 0.021107 | 0.021242 | 0.021242 | 0.98867 | -0.41171 | 0.98825 | -0.4088 | 9.6555
3 | -0.99287 | -0.43372 | 0.99288 | 0.4336 | 7.0094e-06 | -0.00012048 | 0.031628 | 0.031627 | 0.031628 | 0.9889 | -0.41338 | 0.98891 | -0.41343 | 14.3764
4 | 0.46068 | 0.19229 | -0.46042 | -0.21344 | 0.00026292 | -0.021151 | 0.014582 | 0.014832 | 0.014832 | 0.98825 | -0.4088 | 0.98771 | -0.40486 | 6.7418
5 | 0.20547 | 0.099383 | -0.20546 | -0.099508 | 8.8647e-06 | -0.00012491 | 0.0066671 | 0.0066687 | 0.0066687 | 0.98825 | -0.4088 | 0.9882 | -0.40909 | 3.1756
6 | 1.1244 | 0.49636 | -1.1231 | -0.49669 | 0.0012308 | -0.00032841 | 0.035806 | 0.035849 | 0.035849 | 0.9909 | -0.29545 | 0.98891 | -0.41343 | 5.5579
7 | -1.2193 | -0.54235 | 1.2194 | 0.52967 | 9.6026e-05 | -0.01268 | 0.038878 | 0.038728 | 0.038878 | 0.9909 | -0.29545 | 0.99098 | -0.29498 | 6.0937
8 | -1.2194 | -0.52967 | 1.2195 | 0.51731 | 9.2849e-05 | -0.012356 | 0.038728 | 0.038586 | 0.038728 | 0.99098 | -0.29498 | 0.99106 | -0.29449 | 6.0703
9 | 0.2621 | 0.11834 | -0.26206 | -0.12627 | 3.2548e-05 | -0.0079368 | 0.0084047 | 0.008503 | 0.008503 | 0.98771 | -0.40486 | 0.9876 | -0.40387 | 3.865
10 | 0.19832 | 0.0951 | -0.19832 | -0.09605 | 2.2567e-06 | -0.0009504 | 0.0064282 | 0.0064403 | 0.0064403 | 0.98771 | -0.40486 | 0.9877 | -0.40476 | 2.9274
11 | 0.26206 | 0.12627 | -0.26206 | -0.12692 | 2.6964e-06 | -0.00064913 | 0.008503 | 0.0085112 | 0.0085112 | 0.9876 | -0.40387 | 0.98759 | -0.40378 | 3.8687
12 | 1.5252 | 0.67363 | -1.52 | -0.67184 | 0.0051436 | 0.0017972 | 0.048608 | 0.048624 | 0.048624 | 0.99019 | -0.2839 | 0.98662 | -0.31379 | 23.1545
13 | -1.6652 | -0.74146 | 1.669 | 0.74295 | 0.0038126 | 0.0014988 | 0.053141 | 0.053131 | 0.053141 | 0.99019 | -0.2839 | 0.99261 | -0.26409 | 25.3054
14 | 1.52 | 0.67184 | -1.5186 | -0.68183 | 0.0014193 | -0.0099943 | 0.048624 | 0.048749 | 0.048749 | 0.98662 | -0.31379 | 0.98575 | -0.30714 | 22.1584
15 | -1.8375 | -0.82454 | 1.8377 | 0.82466 | 0.00026045 | 0.00011301 | 0.058572 | 0.058571 | 0.058572 | 0.99261 | -0.26409 | 0.99276 | -0.26289 | 27.8913
16 | 1.3559 | 0.60303 | -1.3523 | -0.60202 | 0.003569 | 0.0010089 | 0.043457 | 0.043471 | 0.043471 | 0.98575 | -0.30714 | 0.98298 | -0.33 | 20.7007
17 | -8.2317 | -3.4295 | 8.2382 | 3.355 | 0.0065311 | -0.074512 | 0.2593 | 0.25844 | 0.2593 | 0.99276 | -0.26289 | 0.99358 | -0.25702 | 20.3217
18 | 6.3939 | 2.6049 | -6.3926 | -2.6307 | 0.001338 | -0.025813 | 0.20076 | 0.20105 | 0.20105 | 0.99276 | -0.26289 | 0.99254 | -0.26447 | 15.7566
19 | 0.15455 | 0.065291 | -0.15455 | -0.065926 | 9.0176e-07 | -0.00063532 | 0.0049375 | 0.0049449 | 0.0049449 | 0.98092 | -0.3152 | 0.98091 | -0.31516 | 2.2477
20 | 0.14366 | 0.065591 | -0.14366 | -0.06634 | 9.4222e-07 | -0.00074893 | 0.0046475 | 0.0046567 | 0.0046567 | 0.98092 | -0.3152 | 0.98091 | -0.31515 | 2.1167
21 | -0.45173 | -0.20523 | 0.45178 | 0.20512 | 4.844e-05 | -0.00011617 | 0.014602 | 0.0146 | 0.014602 | 0.98092 | -0.3152 | 0.98103 | -0.31432 | 6.9532
22 | 0.15455 | 0.065926 | -0.15454 | -0.074772 | 1.2844e-05 | -0.0088455 | 0.0049449 | 0.0050527 | 0.0050527 | 0.98091 | -0.31516 | 0.98084 | -0.31454 | 2.2967
23 | 0.14366 | 0.06634 | -0.14365 | -0.068012 | 2.1175e-06 | -0.0016723 | 0.0046567 | 0.0046776 | 0.0046776 | 0.98091 | -0.31515 | 0.9809 | -0.31503 | 2.1262
24 | -0.97128 | -0.44783 | 0.97162 | 0.44212 | 0.00033369 | -0.0057147 | 0.031472 | 0.031401 | 0.031472 | 0.98103 | -0.31432 | 0.98135 | -0.31695 | 14.3056
25 | 0.29666 | 0.13807 | -0.29665 | -0.14062 | 1.3821e-05 | -0.0025533 | 0.0096286 | 0.0096606 | 0.0096606 | 0.98103 | -0.31432 | 0.98099 | -0.31394 | 4.3912
26 | 0.22285 | 0.10464 | -0.22284 | -0.10468 | 3.1653e-06 | -3.6907e-05 | 0.0072444 | 0.0072449 | 0.0072449 | 0.98103 | -0.31432 | 0.98101 | -0.31442 | 3.45
27 | 0.15454 | 0.074772 | -0.15454 | -0.074845 | 2.9765e-06 | -7.3272e-05 | 0.0050527 | 0.0050537 | 0.0050537 | 0.98084 | -0.31454 | 0.98082 | -0.31466 | 2.4065
28 | 0.14365 | 0.068012 | -0.14365 | -0.069574 | 1.9946e-06 | -0.0015615 | 0.0046776 | 0.0046974 | 0.0046974 | 0.9809 | -0.31503 | 0.98089 | -0.31491 | 2.1352
29 | -1.2781 | -0.5894 | 1.2803 | 0.56847 | 0.0021286 | -0.020926 | 0.041403 | 0.041141 | 0.041403 | 0.98135 | -0.31695 | 0.98288 | -0.32929 | 18.8194
30 | 0.30651 | 0.14728 | -0.3065 | -0.14844 | 6.7715e-06 | -0.0011618 | 0.010003 | 0.010018 | 0.010018 | 0.98135 | -0.31695 | 0.98133 | -0.31676 | 4.5537
31 | 0.14796 | 0.069218 | -0.14796 | -0.071024 | 2.4375e-06 | -0.0018063 | 0.0048069 | 0.0048297 | 0.0048297 | 0.98099 | -0.31394 | 0.98097 | -0.31381 | 2.1953
32 | 0.14869 | 0.071407 | -0.14869 | -0.072012 | 8.2954e-07 | -0.0006048 | 0.0048538 | 0.0048615 | 0.0048615 | 0.98099 | -0.31394 | 0.98098 | -0.31389 | 2.2098
33 | 0.078675 | 0.034856 | -0.078675 | -0.035721 | 3.2362e-07 | -0.0008651 | 0.0025321 | 0.0025426 | 0.0025426 | 0.98101 | -0.31442 | 0.98101 | -0.3144 | 1.1557
34 | 0.078675 | 0.036819 | -0.078674 | -0.038104 | 4.9094e-07 | -0.001285 | 0.0025561 | 0.0025724 | 0.0025724 | 0.98101 | -0.31435 | 0.981 | -0.3143 | 1.1693
35 | -0.078675 | -0.036819 | 0.078675 | 0.035721 | 4.1455e-07 | -0.0010978 | 0.0025561 | 0.0025426 | 0.0025561 | 0.98101 | -0.31435 | 0.98101 | -0.3144 | 1.1619
36 | -1.2803 | -0.56847 | 1.2804 | 0.56718 | 0.00013034 | -0.0012925 | 0.041141 | 0.041126 | 0.041141 | 0.98288 | -0.32929 | 0.98298 | -0.33 | 18.7007
37 | 0.14796 | 0.071024 | -0.14796 | -0.071659 | 8.6291e-07 | -0.00063535 | 0.0048297 | 0.0048378 | 0.0048378 | 0.98097 | -0.31381 | 0.98097 | -0.31375 | 2.199
38 | 0.24023 | 0.098876 | -0.24022 | -0.098967 | 8.2467e-06 | -9.1209e-05 | 0.0075352 | 0.0075363 | 0.0075363 | 0.99523 | -0.070822 | 0.9952 | -0.071183 | 3.5887
39 | -0.60157 | -0.27388 | 0.60217 | 0.27318 | 0.0005922 | -0.00070011 | 0.019172 | 0.01916 | 0.019172 | 0.99523 | -0.070822 | 0.99628 | -0.06279 | 9.1297
40 | 0.24022 | 0.098967 | -0.24017 | -0.11419 | 5.0001e-05 | -0.015223 | 0.0075363 | 0.0077155 | 0.0077155 | 0.9952 | -0.071183 | 0.995 | -0.069717 | 3.507
41 | 7.3567 | 3.4978 | -7.3542 | -3.4918 | 0.002482 | 0.0059899 | 0.23603 | 0.23604 | 0.23604 | 0.99628 | -0.06279 | 0.99565 | -0.097711 | 18.2976
42 | -8.1398 | -3.8586 | 8.1398 | 3.8585 | 5.7341e-06 | -6.4723e-05 | 0.26101 | 0.26101 | 0.26101 | 0.99628 | -0.06279 | 0.99628 | -0.062787 | 20.4554
43 | 0.24017 | 0.11419 | -0.24016 | -0.11632 | 7.1817e-06 | -0.0021266 | 0.0077155 | 0.0077422 | 0.0077422 | 0.995 | -0.069717 | 0.99497 | -0.069462 | 3.5192
44 | 7.2752 | 3.4539 | -7.2749 | -3.458 | 0.00029219 | -0.0041555 | 0.2335 | 0.23355 | 0.23355 | 0.99565 | -0.097711 | 0.99561 | -0.097877 | 18.3034
45 | 0.079028 | 0.037898 | -0.079028 | -0.038275 | 1.3752e-07 | -0.00037684 | 0.0025411 | 0.0025459 | 0.0025459 | 0.99565 | -0.097711 | 0.99565 | -0.097696 | 1.1572
46 | -8.2173 | -3.896 | 8.2183 | 3.8985 | 0.00099838 | 0.0024636 | 0.26351 | 0.2635 | 0.26351 | 0.99628 | -0.062787 | 0.9965 | -0.050201 | 20.4268
47 | 0.18719 | 0.089897 | -0.18719 | -0.090659 | 1.5594e-06 | -0.00076227 | 0.0060183 | 0.0060279 | 0.0060279 | 0.99606 | -0.053125 | 0.99605 | -0.053053 | 2.7399
48 | -0.18719 | -0.089897 | 0.18727 | 0.088506 | 7.8188e-05 | -0.001391 | 0.0060183 | 0.0060003 | 0.0060183 | 0.99606 | -0.053125 | 0.9965 | -0.050201 | 2.8658
49 | -8.6646 | -4.1125 | 8.6653 | 4.1053 | 0.00072646 | -0.0071949 | 0.27784 | 0.27775 | 0.27784 | 0.9965 | -0.050201 | 0.99659 | -0.049852 | 21.7743
50 | -0.29866 | -0.14459 | 0.29874 | 0.12977 | 7.6298e-05 | -0.014818 | 0.0096305 | 0.0094508 | 0.0096305 | 0.99463 | -0.096786 | 0.99487 | -0.098752 | 4.3775
51 | 0.29866 | 0.14459 | -0.29865 | -0.14464 | 8.2917e-06 | -5.406e-05 | 0.0096305 | 0.0096313 | 0.0096313 | 0.99463 | -0.096786 | 0.9946 | -0.096969 | 4.5863
52 | -0.37927 | -0.16729 | 0.37929 | 0.16467 | 2.1356e-05 | -0.0026135 | 0.012028 | 0.011997 | 0.012028 | 0.99487 | -0.098752 | 0.99492 | -0.099134 | 5.4673
53 | 0.08053 | 0.037515 | -0.08053 | -0.039002 | 5.6255e-07 | -0.0014877 | 0.0025778 | 0.0025963 | 0.0025963 | 0.99487 | -0.098752 | 0.99486 | -0.098694 | 1.1802
54 | -1.1495 | -0.53756 | 1.1497 | 0.53469 | 0.00022517 | -0.0028769 | 0.03682 | 0.036784 | 0.03682 | 0.99492 | -0.099134 | 0.9951 | -0.1007 | 16.7363
55 | 0.77023 | 0.37289 | -0.77022 | -0.37304 | 5.095e-06 | -0.00014479 | 0.024829 | 0.024831 | 0.024831 | 0.99492 | -0.099134 | 0.99491 | -0.099076 | 11.2869
56 | -1.3613 | -0.63627 | 1.3618 | 0.63234 | 0.00043427 | -0.0039242 | 0.043593 | 0.043543 | 0.043593 | 0.9951 | -0.1007 | 0.9954 | -0.10324 | 19.8148
57 | 0.2116 | 0.10158 | -0.2116 | -0.10248 | 2.3649e-06 | -0.00090111 | 0.0068092 | 0.0068206 | 0.0068206 | 0.9951 | -0.1007 | 0.99509 | -0.1006 | 3.1003
58 | -5.2351 | -2.4848 | 5.2351 | 2.4848 | 1.4546e-05 | -2.5674e-05 | 0.16806 | 0.16806 | 0.16806 | 0.9954 | -0.10324 | 0.9954 | -0.10321 | 46.4248
59 | 3.8734 | 1.8525 | -3.8725 | -1.8516 | 0.00084676 | 0.00089446 | 0.12452 | 0.12452 | 0.12452 | 0.9954 | -0.10324 | 0.99512 | -0.11003 | 35.5765
60 | 0.16968 | 0.08049 | -0.16968 | -0.082179 | 2.8254e-06 | -0.0016885 | 0.00544 | 0.0054611 | 0.0054611 | 0.99659 | -0.049852 | 0.99657 | -0.04971 | 2.4823
61 | -8.835 | -4.1858 | 8.8384 | 4.1529 | 0.0034492 | -0.032869 | 0.28319 | 0.28276 | 0.28319 | 0.99659 | -0.049852 | 0.99699 | -0.048182 | 22.1933
62 | 0.26822 | 0.12981 | -0.26821 | -0.1299 | 1.0506e-05 | -8.7364e-05 | 0.0086288 | 0.00863 | 0.00863 | 0.99691 | -0.047471 | 0.99687 | -0.04773 | 4.1095
63 | -0.26822 | -0.12981 | 0.26825 | 0.12428 | 2.303e-05 | -0.0055359 | 0.0086288 | 0.0085601 | 0.0086288 | 0.99691 | -0.047471 | 0.99699 | -0.048182 | 3.9222
64 | 0.22526 | 0.093557 | -0.22522 | -0.1083 | 4.2417e-05 | -0.014746 | 0.0070624 | 0.0072372 | 0.0072372 | 0.99699 | -0.048182 | 0.99681 | -0.046821 | 3.2896
65 | 0.69628 | 0.33095 | -0.69626 | -0.33161 | 1.8794e-05 | -0.00066468 | 0.022322 | 0.02233 | 0.02233 | 0.99699 | -0.048182 | 0.99697 | -0.047956 | 10.1502
66 | -10.0282 | -4.7017 | 10.0398 | 4.6168 | 0.011567 | -0.084841 | 0.32069 | 0.31958 | 0.32069 | 0.99699 | -0.048182 | 0.99818 | -0.042817 | 25.1327
67 | -5.3891 | -2.5593 | 5.3893 | 2.5523 | 0.00026448 | -0.0069752 | 0.17302 | 0.17293 | 0.17302 | 0.9954 | -0.10321 | 0.99545 | -0.103 | 13.5593
68 | 3.4637 | 1.6536 | -3.4636 | -1.6537 | 0.00013723 | -0.00015533 | 0.11134 | 0.11134 | 0.11134 | 0.99512 | -0.11003 | 0.99509 | -0.10969 | 50.6108
69 | -0.22048 | -0.10678 | 0.22049 | 0.10543 | 3.8237e-06 | -0.001357 | 0.0070883 | 0.0070712 | 0.0070883 | 0.9977 | -0.016957 | 0.99772 | -0.017106 | 3.2219
70 | -0.22049 | -0.10543 | 0.22049 | 0.10408 | 3.7814e-06 | -0.0013485 | 0.0070712 | 0.0070545 | 0.0070712 | 0.99772 | -0.017106 | 0.99774 | -0.017249 | 3.2142
71 | -0.48869 | -0.23398 | 0.48887 | 0.2336 | 0.00017799 | -0.00037197 | 0.015676 | 0.01567 | 0.015676 | 0.99774 | -0.017249 | 0.99812 | -0.014735 | 7.465
72 | -10.0398 | -4.6168 | 10.0401 | 4.6142 | 0.00035247 | -0.0025988 | 0.31958 | 0.31955 | 0.31958 | 0.99818 | -0.042817 | 0.99822 | -0.042645 | 25.0454
73 | -10.1778 | -4.6809 | 10.18 | 4.6867 | 0.0022694 | 0.0057688 | 0.32397 | 0.32396 | 0.32397 | 0.99822 | -0.042645 | 0.99863 | -0.019147 | 25.1137
74 | 0.22522 | 0.1083 | -0.22521 | -0.10908 | 2.28e-06 | -0.00077187 | 0.0072372 | 0.0072469 | 0.0072469 | 0.99681 | -0.046821 | 0.9968 | -0.046734 | 3.294
75 | 0.62602 | 0.29759 | -0.62601 | -0.29841 | 1.8506e-05 | -0.00081073 | 0.020071 | 0.020081 | 0.020081 | 0.99697 | -0.047956 | 0.99694 | -0.047709 | 9.1276
76 | -0.73216 | -0.34948 | 0.73256 | 0.33655 | 0.0004004 | -0.012935 | 0.023464 | 0.023304 | 0.023464 | 0.99812 | -0.014735 | 0.99863 | -0.019147 | 10.6655
77 | 0.24329 | 0.11588 | -0.24328 | -0.11783 | 6.6596e-06 | -0.0019454 | 0.0077937 | 0.0078181 | 0.0078181 | 0.99812 | -0.014735 | 0.9981 | -0.014501 | 3.5537
78 | -10.9126 | -5.0232 | 10.9155 | 5.0052 | 0.0029155 | -0.017987 | 0.34727 | 0.34703 | 0.34727 | 0.99863 | -0.019147 | 0.99891 | -0.017837 | 27.2153
79 | 0.62601 | 0.29841 | -0.62599 | -0.29902 | 1.3983e-05 | -0.00061198 | 0.020081 | 0.020088 | 0.020088 | 0.99694 | -0.047709 | 0.99692 | -0.047521 | 9.1311
80 | -3.1624 | -1.513 | 3.1646 | 1.5098 | 0.002242 | -0.0031595 | 0.10182 | 0.10178 | 0.10182 | 0.99387 | -0.10485 | 0.99453 | -0.11084 | 46.2836
81 | 2.923 | 1.4033 | -2.9221 | -1.4048 | 0.00089095 | -0.0015094 | 0.094177 | 0.0942 | 0.0942 | 0.99387 | -0.10485 | 0.99359 | -0.10225 | 42.8181
82 | 0.23938 | 0.10966 | -0.23927 | -0.11079 | 0.00010586 | -0.0011288 | 0.0076477 | 0.0076622 | 0.0076622 | 0.99387 | -0.10485 | 0.99341 | -0.10832 | 3.6487
83 | -3.1646 | -1.5098 | 3.1658 | 1.5105 | 0.0011943 | 0.00067161 | 0.10178 | 0.10178 | 0.10178 | 0.99453 | -0.11084 | 0.99492 | -0.10821 | 48.4648
84 | 2.6676 | 1.2816 | -2.6676 | -1.2817 | 5.4049e-05 | -0.00011304 | 0.085984 | 0.085986 | 0.085986 | 0.99359 | -0.10225 | 0.99357 | -0.10207 | 39.0844
85 | 0.23927 | 0.11079 | -0.23926 | -0.11286 | 6.899e-06 | -0.0020651 | 0.0076622 | 0.0076877 | 0.0076877 | 0.99341 | -0.10832 | 0.99338 | -0.10809 | 3.4944
86 | -3.463 | -1.6544 | 3.4636 | 1.6537 | 0.00060564 | -0.00068527 | 0.11135 | 0.11134 | 0.11135 | 0.99492 | -0.10821 | 0.99509 | -0.10969 | 50.6157
87 | 2.6676 | 1.2817 | -2.6671 | -1.2826 | 0.00041822 | -0.00087434 | 0.085986 | 0.085998 | 0.085998 | 0.99357 | -0.10207 | 0.99343 | -0.10073 | 39.0901
88 | 2.5026 | 1.2029 | -2.5022 | -1.2037 | 0.00034134 | -0.00082393 | 0.080686 | 0.080697 | 0.080697 | 0.99343 | -0.10073 | 0.9933 | -0.09956 | 36.6807
89 | 0.080611 | 0.038982 | -0.080611 | -0.039042 | 6.1677e-07 | -5.9837e-05 | 0.002602 | 0.0026027 | 0.0026027 | 0.99343 | -0.10073 | 0.99342 | -0.10078 | 1.2394
90 | 2.5022 | 1.2037 | -2.5022 | -1.2038 | 1.2284e-05 | -2.9643e-05 | 0.080697 | 0.080698 | 0.080698 | 0.9933 | -0.09956 | 0.9933 | -0.099518 | 36.6809
91 | 0.10264 | 0.046685 | -0.10263 | -0.046914 | 3.759e-06 | -0.00022894 | 0.0032766 | 0.0032794 | 0.0032794 | 0.99338 | -0.10809 | 0.99334 | -0.10839 | 1.5616
92 | 0.10263 | 0.046914 | -0.10263 | -0.049706 | 1.7194e-06 | -0.0027917 | 0.0032794 | 0.003314 | 0.003314 | 0.99334 | -0.10839 | 0.99332 | -0.10825 | 1.5064
93 | -0.082821 | -0.040112 | 0.082821 | 0.03964 | 1.9139e-07 | -0.00047218 | 0.0026758 | 0.0026699 | 0.0026758 | 0.99277 | -0.094576 | 0.99277 | -0.094596 | 1.2163
94 | -0.082821 | -0.03964 | 0.082821 | 0.038409 | 4.9503e-07 | -0.0012311 | 0.0026699 | 0.0026546 | 0.0026699 | 0.99277 | -0.094596 | 0.99278 | -0.094645 | 1.2136
95 | -0.99668 | -0.48101 | 0.99671 | 0.48051 | 3.0109e-05 | -0.00050372 | 0.03218 | 0.032173 | 0.03218 | 0.99278 | -0.094645 | 0.9928 | -0.094906 | 14.6271
96 | -1.2822 | -0.61879 | 1.2823 | 0.61782 | 9.751e-05 | -0.00097447 | 0.041398 | 0.041385 | 0.041398 | 0.9928 | -0.094906 | 0.99287 | -0.095562 | 18.8171
97 | 0.74859 | 0.36161 | -0.74856 | -0.36255 | 3.1289e-05 | -0.00093441 | 0.024171 | 0.024183 | 0.024183 | 0.99287 | -0.095562 | 0.99284 | -0.095199 | 10.9925
98 | 0.076298 | 0.036895 | -0.076297 | -0.036952 | 5.3385e-07 | -5.7724e-05 | 0.0024641 | 0.0024648 | 0.0024648 | 0.99287 | -0.095562 | 0.99287 | -0.095608 | 1.1737
99 | -2.1072 | -1.0163 | 2.1076 | 1.015 | 0.00036586 | -0.0012862 | 0.06802 | 0.068003 | 0.06802 | 0.99287 | -0.095562 | 0.99303 | -0.097058 | 30.9184
100 | 5.91 | 2.8029 | -5.9099 | -2.8049 | 9.1954e-05 | -0.0020086 | 0.18966 | 0.18969 | 0.18969 | 0.99555 | -0.098101 | 0.99554 | -0.098165 | 14.866
101 | -7.1688 | -3.4126 | 7.1691 | 3.4097 | 0.00020057 | -0.0029382 | 0.23022 | 0.23018 | 0.23022 | 0.99555 | -0.098101 | 0.99558 | -0.097987 | 18.0425
102 | 5.7256 | 2.7157 | -5.7253 | -2.7151 | 0.00026734 | 0.00059736 | 0.18375 | 0.18375 | 0.18375 | 0.99554 | -0.098165 | 0.99545 | -0.103 | 14.2445
103 | -7.1691 | -3.4097 | 7.1691 | 3.4089 | 5.3633e-05 | -0.00078589 | 0.23018 | 0.23017 | 0.23018 | 0.99558 | -0.097987 | 0.99559 | -0.097956 | 18.0395
104 | -7.1691 | -3.4089 | 7.1692 | 3.4069 | 0.00013891 | -0.0020359 | 0.23017 | 0.23015 | 0.23017 | 0.99559 | -0.097956 | 0.99561 | -0.097877 | 18.0387
105 | -2.2018 | -1.0589 | 2.202 | 1.0584 | 0.00017064 | -0.00054653 | 0.071011 | 0.071004 | 0.071011 | 0.99323 | -0.098854 | 0.9933 | -0.099518 | 32.2778
106 | 2.108 | 1.0135 | -2.1076 | -1.015 | 0.00044093 | -0.0015517 | 0.067982 | 0.068003 | 0.068003 | 0.99323 | -0.098854 | 0.99303 | -0.097058 | 30.9104
107 | -0.18083 | -0.087581 | 0.18083 | 0.087309 | 5.1831e-07 | -0.00027155 | 0.0058214 | 0.0058179 | 0.0058214 | 0.99636 | -0.12068 | 0.99636 | -0.12071 | 2.6461
108 | -9.4512 | -3.9008 | 9.4554 | 3.9115 | 0.00428 | 0.010759 | 0.29623 | 0.29623 | 0.29623 | 0.99636 | -0.12071 | 0.99718 | -0.070279 | 22.9638
109 | 9.2703 | 3.8135 | -9.2644 | -3.7986 | 0.0059193 | 0.01484 | 0.29043 | 0.29044 | 0.29044 | 0.99636 | -0.12071 | 0.99522 | -0.19205 | 22.5145
110 | -9.6683 | -4.0147 | 9.6691 | 4.0082 | 0.00078862 | -0.0065026 | 0.30306 | 0.30298 | 0.30306 | 0.99718 | -0.070279 | 0.99726 | -0.069688 | 23.7509
111 | 9.0757 | 3.7072 | -9.0752 | -3.706 | 0.00050693 | 0.001267 | 0.28437 | 0.28437 | 0.28437 | 0.99522 | -0.19205 | 0.99512 | -0.19831 | 22.044
112 | -9.6691 | -4.0082 | 9.6693 | 4.0067 | 0.00017399 | -0.0014353 | 0.30298 | 0.30297 | 0.30298 | 0.99726 | -0.069688 | 0.99728 | -0.069557 | 23.7448
113 | 9.0752 | 3.706 | -9.0725 | -3.7308 | 0.0026451 | -0.024821 | 0.28437 | 0.28466 | 0.28466 | 0.99512 | -0.19831 | 0.99481 | -0.2005 | 22.3086
114 | 0.36805 | 0.17778 | -0.36805 | -0.17808 | 2.3611e-06 | -0.00029608 | 0.011863 | 0.011867 | 0.011867 | 0.99466 | -0.20157 | 0.99465 | -0.20152 | 5.3939
115 | -0.36805 | -0.17778 | 0.36808 | 0.17768 | 2.6541e-05 | -0.00010842 | 0.011863 | 0.011861 | 0.011863 | 0.99466 | -0.20157 | 0.99473 | -0.20109 | 5.649
116 | 0.13015 | 0.06286 | -0.13015 | -0.063034 | 4.6879e-06 | -0.00017356 | 0.0041949 | 0.0041971 | 0.0041971 | 0.99465 | -0.20152 | 0.99461 | -0.20175 | 1.9986
117 | -8.9207 | -3.6657 | 8.9212 | 3.6604 | 0.00054722 | -0.0053155 | 0.27989 | 0.27983 | 0.27989 | 0.99473 | -0.20109 | 0.9948 | -0.20063 | 21.9348
118 | 8.4395 | 3.4333 | -8.4393 | -3.436 | 0.0002441 | -0.0026721 | 0.26441 | 0.26444 | 0.26444 | 0.99473 | -0.20109 | 0.9947 | -0.20131 | 20.7242
119 | -8.9212 | -3.6604 | 8.9214 | 3.6589 | 0.00015771 | -0.0015325 | 0.27983 | 0.27981 | 0.27983 | 0.9948 | -0.20063 | 0.99481 | -0.2005 | 21.9299
120 | 8.2442 | 3.3415 | -8.2437 | -3.3473 | 0.00050756 | -0.0058409 | 0.25816 | 0.25823 | 0.25823 | 0.9947 | -0.20131 | 0.99464 | -0.20179 | 20.2374
121 | 21.4741 | 9.2802 | -21.4687 | -9.2868 | 0.0053941 | -0.0065701 | 0.67546 | 0.67557 | 0.67557 | 0.99978 | -0.013331 | 0.99951 | -0.014916 | 52.9447
122 | -21.8625 | -9.4683 | 21.8651 | 9.4754 | 0.0026782 | 0.0071143 | 0.68791 | 0.68791 | 0.68791 | 0.99978 | -0.013331 | 1 | 0 | 53.3266
123 | 11.1969 | 5.1001 | -11.1917 | -5.1306 | 0.0052056 | -0.030513 | 0.35535 | 0.35575 | 0.35575 | 0.99951 | -0.014916 | 0.99903 | -0.017256 | 27.8802
124 | 10.2718 | 4.1867 | -10.2678 | -4.1765 | 0.0040053 | 0.010167 | 0.32036 | 0.32037 | 0.32037 | 0.99951 | -0.014916 | 0.99881 | -0.058655 | 24.8348
125 | 11.1917 | 5.1306 | -11.1909 | -5.1351 | 0.00078223 | -0.0045757 | 0.35575 | 0.35581 | 0.35581 | 0.99903 | -0.017256 | 0.99896 | -0.017601 | 27.8849
126 | 9.9804 | 4.0374 | -9.9797 | -4.0431 | 0.00072965 | -0.0057024 | 0.31116 | 0.31123 | 0.31123 | 0.99881 | -0.058655 | 0.99874 | -0.059225 | 24.3908
127 | 0.15115 | 0.071892 | -0.15115 | -0.073204 | 1.7542e-06 | -0.0013113 | 0.0048569 | 0.0048734 | 0.0048734 | 0.99481 | -0.2005 | 0.9948 | -0.2004 | 2.2152
128 | 10.916 | 5.002 | -10.9155 | -5.0052 | 0.0005182 | -0.003201 | 0.34699 | 0.34703 | 0.34703 | 0.99896 | -0.017601 | 0.99891 | -0.017837 | 27.1967
129 | 9.9797 | 4.0431 | -9.9673 | -4.1398 | 0.012445 | -0.096715 | 0.31123 | 0.31237 | 0.31237 | 0.99874 | -0.059225 | 0.99742 | -0.068579 | 24.4801
130 | 9.9673 | 4.1398 | -9.967 | -4.1419 | 0.000271 | -0.0020946 | 0.31237 | 0.31239 | 0.31239 | 0.99742 | -0.068579 | 0.9974 | -0.068776 | 24.482
131 | -9.6693 | -4.0067 | 9.6697 | 4.0031 | 0.00044406 | -0.0036642 | 0.30297 | 0.30292 | 0.30297 | 0.99728 | -0.069557 | 0.99733 | -0.069222 | 23.7435
132 | -9.7609 | -4.0472 | 9.7615 | 4.0423 | 0.00059961 | -0.0048494 | 0.30585 | 0.30579 | 0.30585 | 0.99733 | -0.069222 | 0.9974 | -0.068776 | 23.9694
133 | 0.069118 | 0.033203 | -0.069118 | -0.033475 | 7.5572e-08 | -0.00027192 | 0.0022206 | 0.0022241 | 0.0022241 | 0.99681 | -0.04649 | 0.9968 | -0.046481 | 1.0109
134 | -0.46705 | -0.22593 | 0.46705 | 0.22551 | 5.381e-06 | -0.00042214 | 0.015025 | 0.01502 | 0.015025 | 0.99681 | -0.04649 | 0.99682 | -0.04659 | 6.8296
135 | -0.54345 | -0.26251 | 0.54346 | 0.26176 | 1.2886e-05 | -0.00074624 | 0.017478 | 0.017469 | 0.017478 | 0.99682 | -0.04659 | 0.99684 | -0.046795 | 7.9445
136 | -0.54346 | -0.26176 | 0.54349 | 0.25985 | 3.2927e-05 | -0.0019106 | 0.017469 | 0.017444 | 0.017469 | 0.99684 | -0.046795 | 0.99689 | -0.047312 | 7.9402
137 | -0.54349 | -0.25985 | 0.54351 | 0.25907 | 1.345e-05 | -0.00078207 | 0.017444 | 0.017435 | 0.017444 | 0.99689 | -0.047312 | 0.99692 | -0.047521 | 7.9293
138 | -0.10236 | -0.049577 | 0.10236 | 0.049509 | 1.1498e-06 | -6.8007e-05 | 0.0033158 | 0.0033149 | 0.0033158 | 0.99021 | -0.28451 | 0.99022 | -0.28443 | 1.5789
139 | -0.10236 | -0.049509 | 0.10237 | 0.040018 | 5.7421e-06 | -0.0094912 | 0.0033149 | 0.0032041 | 0.0033149 | 0.99022 | -0.28443 | 0.99028 | -0.28481 | 1.5068
140 | -0.10237 | -0.040018 | 0.10237 | 0.038863 | 6.7334e-07 | -0.0011545 | 0.0032041 | 0.003192 | 0.0032041 | 0.99028 | -0.28481 | 0.99028 | -0.28484 | 1.4564
141 | -0.26498 | -0.11762 | 0.265 | 0.11746 | 1.8098e-05 | -0.00015521 | 0.0084512 | 0.0084492 | 0.0084512 | 0.99028 | -0.28484 | 0.99035 | -0.28424 | 4.0244
142 | -0.265 | -0.11746 | 0.26503 | 0.11019 | 2.9323e-05 | -0.0072701 | 0.0084492 | 0.0083655 | 0.0084492 | 0.99035 | -0.28424 | 0.99046 | -0.28495 | 3.8406
143 | 0.41388 | 0.19992 | -0.41387 | -0.20045 | 5.4555e-06 | -0.00053147 | 0.013396 | 0.013403 | 0.013403 | 0.99046 | -0.28495 | 0.99045 | -0.28484 | 6.0923
144 | -0.67891 | -0.31011 | 0.67893 | 0.31009 | 2.2676e-05 | -1.7295e-05 | 0.021754 | 0.021753 | 0.021754 | 0.99046 | -0.28495 | 0.99049 | -0.28468 | 10.3589
145 | -1.0689 | -0.49071 | 1.07 | 0.47526 | 0.0010482 | -0.015443 | 0.034279 | 0.03409 | 0.034279 | 0.99049 | -0.28468 | 0.99141 | -0.29191 | 15.5814
146 | 0.38999 | 0.18061 | -0.38992 | -0.18853 | 7.1584e-05 | -0.0079205 | 0.012526 | 0.012625 | 0.012625 | 0.99049 | -0.28468 | 0.99032 | -0.28317 | 5.7386
147 | -2.3713 | -0.97986 | 2.3713 | 0.97701 | 8.073e-05 | -0.0028467 | 0.074708 | 0.074676 | 0.074708 | 0.99141 | -0.29191 | 0.99144 | -0.29166 | 11.7098
148 | 1.3013 | 0.5046 | -1.3009 | -0.54772 | 0.00036222 | -0.043119 | 0.04064 | 0.041113 | 0.041113 | 0.99141 | -0.29191 | 0.99112 | -0.29409 | 6.444
149 | 0.38992 | 0.18853 | -0.38992 | -0.18884 | 2.8241e-06 | -0.00030985 | 0.012625 | 0.012629 | 0.012629 | 0.99032 | -0.28317 | 0.99032 | -0.2831 | 5.7404
150 | 1.3009 | 0.54772 | -1.3009 | -0.55671 | 7.6685e-05 | -0.0089959 | 0.041113 | 0.041216 | 0.041216 | 0.99112 | -0.29409 | 0.99106 | -0.29449 | 6.4601
151 | -2.5587 | -1.0677 | 2.559 | 1.0679 | 0.00036252 | 0.00012762 | 0.080726 | 0.080717 | 0.080726 | 0.99144 | -0.29166 | 0.9917 | -0.27596 | 6.2578
152 | -2.7916 | -1.1805 | 2.7917 | 1.1698 | 0.00010426 | -0.01067 | 0.088229 | 0.088108 | 0.088229 | 0.9917 | -0.27596 | 0.99174 | -0.2757 | 6.9145
153 | -0.13388 | -0.064841 | 0.13388 | 0.064774 | 7.2333e-08 | -6.7764e-05 | 0.0043318 | 0.004331 | 0.0043318 | 0.99132 | -0.2612 | 0.99132 | -0.2612 | 1.969
154 | -0.13388 | -0.064774 | 0.13389 | 0.054571 | 1.0578e-05 | -0.010202 | 0.004331 | 0.00421 | 0.004331 | 0.99132 | -0.2612 | 0.99139 | -0.26177 | 1.9686
155 | 0.40632 | 0.18464 | -0.40621 | -0.1959 | 0.00010966 | -0.011258 | 0.012995 | 0.013135 | 0.013135 | 0.99139 | -0.26177 | 0.99114 | -0.25959 | 5.9704
156 | -0.54021 | -0.23921 | 0.54024 | 0.23917 | 2.9079e-05 | -4.65e-05 | 0.017203 | 0.017202 | 0.017203 | 0.99139 | -0.26177 | 0.99145 | -0.26129 | 8.1919
157 | 0.40621 | 0.1959 | -0.4062 | -0.19673 | 8.1964e-06 | -0.00083157 | 0.013135 | 0.013145 | 0.013145 | 0.99114 | -0.25959 | 0.99112 | -0.25941 | 5.9752
158 | -0.75312 | -0.34227 | 0.75314 | 0.34145 | 2.7404e-05 | -0.00082267 | 0.024086 | 0.024076 | 0.024086 | 0.99145 | -0.26129 | 0.99148 | -0.26156 | 10.9484
159 | -0.89726 | -0.41124 | 0.89735 | 0.41123 | 9.0244e-05 | -1.5461e-05 | 0.028737 | 0.028737 | 0.028737 | 0.99148 | -0.26156 | 0.99159 | -0.26076 | 13.6845
160 | 1.8931 | 0.87729 | -1.8929 | -0.87814 | 0.00018851 | -0.00084549 | 0.060689 | 0.0607 | 0.0607 | 0.99247 | -0.26833 | 0.99238 | -0.26755 | 27.5909
161 | 4.1792 | 1.5979 | -4.179 | -1.6032 | 0.00011394 | -0.0053234 | 0.13014 | 0.13019 | 0.13019 | 0.99247 | -0.26833 | 0.99245 | -0.26858 | 10.2033
162 | -6.3924 | -2.6302 | 6.3926 | 2.6307 | 0.00022116 | 0.00051125 | 0.20105 | 0.20105 | 0.20105 | 0.99247 | -0.26833 | 0.99254 | -0.26447 | 15.5856
163 | 1.8929 | 0.87814 | -1.8915 | -0.88456 | 0.0014349 | -0.0064192 | 0.0607 | 0.060784 | 0.060784 | 0.99238 | -0.26755 | 0.99168 | -0.26151 | 27.6291
164 | 0.20249 | 0.080552 | -0.20245 | -0.097605 | 4.012e-05 | -0.017053 | 0.0063389 | 0.0065386 | 0.0065386 | 0.99245 | -0.26858 | 0.99226 | -0.26721 | 2.9721
165 | 3.3478 | 1.262 | -3.3469 | -1.3259 | 0.00087733 | -0.063971 | 0.10407 | 0.10474 | 0.10474 | 0.99245 | -0.26858 | 0.99217 | -0.27088 | 8.2087
166 | 0.62875 | 0.26067 | -0.62845 | -0.27421 | 0.00030586 | -0.013543 | 0.019798 | 0.019953 | 0.019953 | 0.99245 | -0.26858 | 0.99199 | -0.26553 | 9.0697
167 | 0.15697 | 0.075081 | -0.15697 | -0.075454 | 5.4391e-07 | -0.00037235 | 0.0050653 | 0.0050699 | 0.0050699 | 0.99168 | -0.26151 | 0.99168 | -0.26148 | 2.3045
168 | 0.35787 | 0.17165 | -0.35786 | -0.17236 | 5.3937e-06 | -0.00070849 | 0.011554 | 0.011563 | 0.011563 | 0.99168 | -0.26151 | 0.99166 | -0.26138 | 5.2558
169 | 1.3766 | 0.63782 | -1.3766 | -0.63817 | 4.0042e-05 | -0.00034913 | 0.044166 | 0.04417 | 0.04417 | 0.99168 | -0.26151 | 0.99165 | -0.26128 | 20.0774
170 | 0.20245 | 0.097605 | -0.20245 | -0.098051 | 1.0852e-06 | -0.00044626 | 0.0065386 | 0.0065443 | 0.0065443 | 0.99226 | -0.26721 | 0.99225 | -0.26717 | 2.9747
171 | 3.022 | 1.1701 | -3.0217 | -1.1978 | 0.00031074 | -0.02772 | 0.094288 | 0.094584 | 0.094584 | 0.99217 | -0.27088 | 0.99206 | -0.27176 | 7.4125
172 | 0.32487 | 0.15586 | -0.32486 | -0.15734 | 9.2309e-06 | -0.0014732 | 0.010484 | 0.010502 | 0.010502 | 0.99217 | -0.27088 | 0.99214 | -0.27064 | 4.7738
173 | 0.23335 | 0.11294 | -0.23334 | -0.11301 | 6.5045e-06 | -7.1267e-05 | 0.0075442 | 0.0075451 | 0.0075451 | 0.99199 | -0.26553 | 0.99196 | -0.26572 | 3.5929
174 | 0.3951 | 0.16127 | -0.39495 | -0.17777 | 0.0001472 | -0.0165 | 0.012419 | 0.012609 | 0.012609 | 0.99199 | -0.26553 | 0.99163 | -0.26314 | 5.7312
175 | -8.2382 | -3.355 | 8.2421 | 3.3648 | 0.0039568 | 0.0097334 | 0.25844 | 0.25843 | 0.25844 | 0.99358 | -0.25702 | 0.99444 | -0.2032 | 20.034
176 | -8.2421 | -3.3648 | 8.2437 | 3.3473 | 0.0015176 | -0.01744 | 0.25843 | 0.25823 | 0.25843 | 0.99444 | -0.2032 | 0.99464 | -0.20179 | 20.2531
177 | 0.076095 | 0.036283 | -0.076095 | -0.036855 | 1.9637e-07 | -0.00057177 | 0.002454 | 0.0024612 | 0.0024612 | 0.99168 | -0.26148 | 0.99167 | -0.26145 | 1.1187
178 | 0.078191 | 0.036908 | -0.07819 | -0.037549 | 2.3174e-07 | -0.00064125 | 0.002517 | 0.002525 | 0.002525 | 0.99166 | -0.26138 | 0.99166 | -0.26135 | 1.1477
179 | 1.2402 | 0.57209 | -1.2401 | -0.57265 | 5.1102e-05 | -0.0005533 | 0.039758 | 0.039765 | 0.039765 | 0.99165 | -0.26128 | 0.99161 | -0.26096 | 18.075
180 | 0.080436 | 0.038655 | -0.080436 | -0.038957 | 1.1597e-07 | -0.00030171 | 0.0025979 | 0.0026017 | 0.0026017 | 0.99163 | -0.26314 | 0.99163 | -0.26313 | 1.1826
181 | 0.31452 | 0.13912 | -0.31444 | -0.15179 | 7.3475e-05 | -0.012673 | 0.010012 | 0.010167 | 0.010167 | 0.99163 | -0.26314 | 0.99142 | -0.26132 | 4.6213
182 | 0.31444 | 0.15179 | -0.31444 | -0.15218 | 2.2984e-06 | -0.00039001 | 0.010167 | 0.010172 | 0.010172 | 0.99142 | -0.26132 | 0.99141 | -0.26125 | 4.6235
183 | 0.22916 | 0.11058 | -0.22916 | -0.11099 | 1.2624e-06 | -0.00040467 | 0.0074041 | 0.0074092 | 0.0074092 | 0.99206 | -0.27176 | 0.99206 | -0.27171 | 3.3678
184 | 2.7926 | 1.0872 | -2.7925 | -1.0872 | 4.1627e-05 | 2.8495e-05 | 0.087201 | 0.087202 | 0.087202 | 0.99206 | -0.27176 | 0.99204 | -0.27346 | 6.7598
185 | 2.7925 | 1.0872 | -2.7917 | -1.1698 | 0.00079801 | -0.082676 | 0.087202 | 0.088108 | 0.088108 | 0.99204 | -0.27346 | 0.99174 | -0.2757 | 6.905
186 | 0.07078 | 0.034169 | -0.070779 | -0.03428 | 8.8643e-07 | -0.00011084 | 0.0022885 | 0.0022899 | 0.0022899 | 0.99141 | -0.26125 | 0.9914 | -0.26133 | 1.0904
187 | 0.07819 | 0.037549 | -0.07819 | -0.037869 | 1.1638e-07 | -0.0003205 | 0.002525 | 0.002529 | 0.002529 | 0.99166 | -0.26135 | 0.99166 | -0.26134 | 1.1496
188 | 0.069221 | 0.032781 | -0.06922 | -0.033525 | 2.1108e-07 | -0.00074351 | 0.0022297 | 0.002239 | 0.002239 | 0.99161 | -0.26096 | 0.99161 | -0.26093 | 1.0177
189 | 1.1709 | 0.53987 | -1.1709 | -0.54022 | 2.9009e-05 | -0.00035344 | 0.037535 | 0.03754 | 0.03754 | 0.99161 | -0.26096 | 0.99159 | -0.26076 | 17.0635
190 | -0.19839 | -0.096085 | 0.19839 | 0.095618 | 1.092e-06 | -0.00046633 | 0.0064176 | 0.0064117 | 0.0064176 | 0.99155 | -0.26042 | 0.99156 | -0.26047 | 2.9171
191 | -0.19839 | -0.095618 | 0.1984 | 0.093394 | 5.1815e-06 | -0.0022246 | 0.0064117 | 0.0063838 | 0.0064117 | 0.99156 | -0.26047 | 0.99158 | -0.26069 | 2.9144
192 | -0.1984 | -0.093394 | 0.1984 | 0.09261 | 1.8158e-06 | -0.00078417 | 0.0063838 | 0.0063741 | 0.0063838 | 0.99158 | -0.26069 | 0.99159 | -0.26076 | 2.9017

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.8791 | 9.4859

## res_load
| p_mw | q_mvar
0 | 0.32617 | 0.15797
1 | 0.094951 | 0.045987
2 | 0.13026 | 0.063088
3 | 0.20546 | 0.099508
4 | 0.19832 | 0.09605
5 | 0.26206 | 0.12692
6 | 0.14004 | 0.067823
7 | 0.16846 | 0.081588
8 | 0.1627 | 0.078801
9 | 0.15352 | 0.074352
10 | 0.14417 | 0.069824
11 | 0.15454 | 0.074845
12 | 0.078674 | 0.038104
13 | 0.14365 | 0.069574
14 | 0.3065 | 0.14844
15 | 0.14869 | 0.072012
16 | 0.071931 | 0.034838
17 | 0.14796 | 0.071659
18 | 0.36134 | 0.17501
19 | 0.18091 | 0.08762
20 | 0.077502 | 0.037536
21 | 0.18719 | 0.090659
22 | 0.25905 | 0.12546
23 | 0.29865 | 0.14464
24 | 0.24016 | 0.11632
25 | 0.08053 | 0.039002
26 | 0.77022 | 0.37304
27 | 0.2116 | 0.10248
28 | 0.26821 | 0.1299
29 | 0.15392 | 0.074545
30 | 0.4088 | 0.19799
31 | 0.22048 | 0.10678
32 | 0.2682 | 0.1299
33 | 0.13762 | 0.066652
34 | 0.070238 | 0.034018
35 | 0.22521 | 0.10908
36 | 0.16968 | 0.082179
37 | 0.2545 | 0.12326
38 | 0.29715 | 0.14392
39 | 0.08395 | 0.040659
40 | 0.080611 | 0.039042
41 | 0.13663 | 0.066172
42 | 0.10263 | 0.049706
43 | 0.24328 | 0.11783
44 | 0.082821 | 0.040112
45 | 0.91386 | 0.4426
46 | 0.28552 | 0.13828
47 | 1.2589 | 0.60971
48 | 0.18429 | 0.089257
49 | 0.33598 | 0.16272
50 | 0.10564 | 0.051164
51 | 0.093817 | 0.045438
52 | 0.30021 | 0.1454
53 | 0.74856 | 0.36255
54 | 0.076297 | 0.036952
55 | 0.079028 | 0.038275
56 | 0.18083 | 0.087581
57 | 0.21289 | 0.10311
58 | 0.18873 | 0.091405
59 | 0.2379 | 0.11522
60 | 0.11307 | 0.054762
61 | 0.19512 | 0.094503
62 | 0.38837 | 0.1881
63 | 0.28737 | 0.13918
64 | 0.15115 | 0.073204
65 | 0.27487 | 0.13312
66 | 0.091125 | 0.044134
67 | 0.39793 | 0.19272
68 | 0.069118 | 0.033475
69 | 0.076397 | 0.037001
70 | 0.082484 | 0.039949
71 | 0.20553 | 0.099542
72 | 0.10236 | 0.049577
73 | 0.16261 | 0.078756
74 | 0.41387 | 0.20045
75 | 0.38992 | 0.18884
76 | 0.081348 | 0.039399
77 | 0.18731 | 0.090721
78 | 0.23261 | 0.11266
79 | 0.13388 | 0.064841
80 | 0.21288 | 0.1031
81 | 0.4062 | 0.19673
82 | 0.14412 | 0.069799
83 | 0.32011 | 0.15504
84 | 0.080878 | 0.039171
85 | 0.27967 | 0.13545
86 | 0.13643 | 0.066078
87 | 0.20245 | 0.098051
88 | 0.080436 | 0.038957
89 | 0.32486 | 0.15734
90 | 0.22916 | 0.11099
91 | 0.23334 | 0.11301
92 | 0.24366 | 0.11801
93 | 0.13015 | 0.063034
94 | 0.076095 | 0.036855
95 | 0.070779 | 0.03428
96 | 0.19839 | 0.096085
97 | 0.075115 | 0.03638
98 | 0.06922 | 0.033525
99 | 0.07819 | 0.037869

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1