## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_522_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_522_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_522_0_node_109 | 20 | n |  | TRUE
3 | bus_MV_522_0_node_53 | 20 | n |  | TRUE
4 | bus_MV_522_0_node_52 | 20 | n |  | TRUE
5 | bus_MV_522_0_node_29 | 20 | n |  | TRUE
6 | bus_MV_522_0_node_2 | 20 | n |  | TRUE
7 | bus_MV_522_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_522_0_node_7 | 20 | n |  | TRUE
9 | bus_MV_522_0_node_10 | 20 | n |  | TRUE
10 | bus_MV_522_0_node_136 | 20 | n |  | TRUE
11 | bus_MV_522_0_node_4 | 20 | n |  | TRUE
12 | bus_MV_522_0_node_5 | 20 | n |  | TRUE
13 | bus_MV_522_0_node_6 | 20 | n |  | TRUE
14 | bus_MV_522_0_node_8 | 20 | n |  | TRUE
15 | bus_MV_522_0_node_152 | 20 | n |  | TRUE
16 | bus_MV_522_0_node_9 | 20 | n |  | TRUE
17 | bus_MV_522_0_node_11 | 20 | n |  | TRUE
18 | bus_MV_522_0_node_176 | 20 | n |  | TRUE
19 | bus_MV_522_0_node_171 | 20 | n |  | TRUE
20 | bus_MV_522_0_node_151 | 20 | n |  | TRUE
21 | bus_MV_522_0_node_150 | 20 | n |  | TRUE
22 | bus_MV_522_0_node_172 | 20 | n |  | TRUE
23 | bus_MV_522_0_node_12 | 20 | n |  | TRUE
24 | bus_MV_522_0_node_13 | 20 | n |  | TRUE
25 | bus_MV_522_0_node_14 | 20 | n |  | TRUE
26 | bus_MV_522_0_node_15 | 20 | n |  | TRUE
27 | bus_MV_522_0_node_20 | 20 | n |  | TRUE
28 | bus_MV_522_0_node_149 | 20 | n |  | TRUE
29 | bus_MV_522_0_node_140 | 20 | n |  | TRUE
30 | bus_MV_522_0_node_144 | 20 | n |  | TRUE
31 | bus_MV_522_0_node_16 | 20 | n |  | TRUE
32 | bus_MV_522_0_node_21 | 20 | n |  | TRUE
33 | bus_MV_522_0_node_163 | 20 | n |  | TRUE
34 | bus_MV_522_0_node_17 | 20 | n |  | TRUE
35 | bus_MV_522_0_node_174 | 20 | n |  | TRUE
36 | bus_MV_522_0_node_19 | 20 | n |  | TRUE
37 | bus_MV_522_0_node_100 | 20 | n |  | TRUE
38 | bus_MV_522_0_node_47 | 20 | n |  | TRUE
39 | bus_MV_522_0_node_46 | 20 | n |  | TRUE
40 | bus_MV_522_0_node_193 | 20 | n |  | TRUE
41 | bus_MV_522_0_node_23 | 20 | n |  | TRUE
42 | bus_MV_522_0_node_148 | 20 | n |  | TRUE
43 | bus_MV_522_0_node_162 | 20 | n |  | TRUE
44 | bus_MV_522_0_node_22 | 20 | n |  | TRUE
45 | bus_MV_522_0_node_184 | 20 | n |  | TRUE
46 | bus_MV_522_0_node_196 | 20 | n |  | TRUE
47 | bus_MV_522_0_node_124 | 20 | n |  | TRUE
48 | bus_MV_522_0_node_141 | 20 | n |  | TRUE
49 | bus_MV_522_0_node_142 | 20 | n |  | TRUE
50 | bus_MV_522_0_node_177 | 20 | n |  | TRUE
51 | bus_MV_522_0_node_139 | 20 | n |  | TRUE
52 | bus_MV_522_0_node_143 | 20 | n |  | TRUE
53 | bus_MV_522_0_node_145 | 20 | n |  | TRUE
54 | bus_MV_522_0_node_183 | 20 | n |  | TRUE
55 | bus_MV_522_0_node_173 | 20 | n |  | TRUE
56 | bus_MV_522_0_node_175 | 20 | n |  | TRUE
57 | bus_MV_522_0_node_118 | 20 | n |  | TRUE
58 | bus_MV_522_0_node_128 | 20 | n |  | TRUE
59 | bus_MV_522_0_node_165 | 20 | n |  | TRUE
60 | bus_MV_522_0_node_168 | 20 | n |  | TRUE
61 | bus_MV_522_0_node_24 | 20 | n |  | TRUE
62 | bus_MV_522_0_node_25 | 20 | n |  | TRUE
63 | bus_MV_522_0_node_87 | 20 | n |  | TRUE
64 | bus_MV_522_0_node_26 | 20 | n |  | TRUE
65 | bus_MV_522_0_node_34 | 20 | n |  | TRUE
66 | bus_MV_522_0_node_27 | 20 | n |  | TRUE
67 | bus_MV_522_0_node_33 | 20 | n |  | TRUE
68 | bus_MV_522_0_node_35 | 20 | n |  | TRUE
69 | bus_MV_522_0_node_32 | 20 | n |  | TRUE
70 | bus_MV_522_0_node_75 | 20 | n |  | TRUE
71 | bus_MV_522_0_node_72 | 20 | n |  | TRUE
72 | bus_MV_522_0_node_28 | 20 | n |  | TRUE
73 | bus_MV_522_0_node_30 | 20 | n |  | TRUE
74 | bus_MV_522_0_node_192 | 20 | n |  | TRUE
75 | bus_MV_522_0_node_77 | 20 | n |  | TRUE
76 | bus_MV_522_0_node_186 | 20 | n |  | TRUE
77 | bus_MV_522_0_node_39 | 20 | n |  | TRUE
78 | bus_MV_522_0_node_185 | 20 | n |  | TRUE
79 | bus_MV_522_0_node_38 | 20 | n |  | TRUE
80 | bus_MV_522_0_node_56 | 20 | n |  | TRUE
81 | bus_MV_522_0_node_191 | 20 | n |  | TRUE
82 | bus_MV_522_0_node_37 | 20 | n |  | TRUE
83 | bus_MV_522_0_node_78 | 20 | n |  | TRUE
84 | bus_MV_522_0_node_129 | 20 | n |  | TRUE
85 | bus_MV_522_0_node_76 | 20 | n |  | TRUE
86 | bus_MV_522_0_node_189 | 20 | n |  | TRUE
87 | bus_MV_522_0_node_43 | 20 | n |  | TRUE
88 | bus_MV_522_0_node_156 | 20 | n |  | TRUE
89 | bus_MV_522_0_node_73 | 20 | n |  | TRUE
90 | bus_MV_522_0_node_36 | 20 | n |  | TRUE
91 | bus_MV_522_0_node_40 | 20 | n |  | TRUE
92 | bus_MV_522_0_node_41 | 20 | n |  | TRUE
93 | bus_MV_522_0_node_45 | 20 | n |  | TRUE
94 | bus_MV_522_0_node_42 | 20 | n |  | TRUE
95 | bus_MV_522_0_node_112 | 20 | n |  | TRUE
96 | bus_MV_522_0_node_54 | 20 | n |  | TRUE
97 | bus_MV_522_0_node_44 | 20 | n |  | TRUE
98 | bus_MV_522_0_node_110 | 20 | n |  | TRUE
99 | bus_MV_522_0_node_111 | 20 | n |  | TRUE
100 | bus_MV_522_0_node_113 | 20 | n |  | TRUE
101 | bus_MV_522_0_node_55 | 20 | n |  | TRUE
102 | bus_MV_522_0_node_48 | 20 | n |  | TRUE
103 | bus_MV_522_0_node_49 | 20 | n |  | TRUE
104 | bus_MV_522_0_node_50 | 20 | n |  | TRUE
105 | bus_MV_522_0_node_51 | 20 | n |  | TRUE
106 | bus_MV_522_0_node_138 | 20 | n |  | TRUE
107 | bus_MV_522_0_node_153 | 20 | n |  | TRUE
108 | bus_MV_522_0_node_154 | 20 | n |  | TRUE
109 | bus_MV_522_0_node_114 | 20 | n |  | TRUE
110 | bus_MV_522_0_node_195 | 20 | n |  | TRUE
111 | bus_MV_522_0_node_57 | 20 | n |  | TRUE
112 | bus_MV_522_0_node_59 | 20 | n |  | TRUE
113 | bus_MV_522_0_node_62 | 20 | n |  | TRUE
114 | bus_MV_522_0_node_63 | 20 | n |  | TRUE
115 | bus_MV_522_0_node_60 | 20 | n |  | TRUE
116 | bus_MV_522_0_node_197 | 20 | n |  | TRUE
117 | bus_MV_522_0_node_61 | 20 | n |  | TRUE
118 | bus_MV_522_0_node_182 | 20 | n |  | TRUE
119 | bus_MV_522_0_node_187 | 20 | n |  | TRUE
120 | bus_MV_522_0_node_161 | 20 | n |  | TRUE
121 | bus_MV_522_0_node_64 | 20 | n |  | TRUE
122 | bus_MV_522_0_node_71 | 20 | n |  | TRUE
123 | bus_MV_522_0_node_90 | 20 | n |  | TRUE
124 | bus_MV_522_0_node_91 | 20 | n |  | TRUE
125 | bus_MV_522_0_node_89 | 20 | n |  | TRUE
126 | bus_MV_522_0_node_188 | 20 | n |  | TRUE
127 | bus_MV_522_0_node_180 | 20 | n |  | TRUE
128 | bus_MV_522_0_node_65 | 20 | n |  | TRUE
129 | bus_MV_522_0_node_66 | 20 | n |  | TRUE
130 | bus_MV_522_0_node_68 | 20 | n |  | TRUE
131 | bus_MV_522_0_node_70 | 20 | n |  | TRUE
132 | bus_MV_522_0_node_69 | 20 | n |  | TRUE
133 | bus_MV_522_0_node_155 | 20 | n |  | TRUE
134 | bus_MV_522_0_node_194 | 20 | n |  | TRUE
135 | bus_MV_522_0_node_84 | 20 | n |  | TRUE
136 | bus_MV_522_0_node_108 | 20 | n |  | TRUE
137 | bus_MV_522_0_node_104 | 20 | n |  | TRUE
138 | bus_MV_522_0_node_74 | 20 | n |  | TRUE
139 | bus_MV_522_0_node_101 | 20 | n |  | TRUE
140 | bus_MV_522_0_node_82 | 20 | n |  | TRUE
141 | bus_MV_522_0_node_157 | 20 | n |  | TRUE
142 | bus_MV_522_0_node_79 | 20 | n |  | TRUE
143 | bus_MV_522_0_node_81 | 20 | n |  | TRUE
144 | bus_MV_522_0_node_83 | 20 | n |  | TRUE
145 | bus_MV_522_0_node_86 | 20 | n |  | TRUE
146 | bus_MV_522_0_node_80 | 20 | n |  | TRUE
147 | bus_MV_522_0_node_98 | 20 | n |  | TRUE
148 | bus_MV_522_0_node_85 | 20 | n |  | TRUE
149 | bus_MV_522_0_node_88 | 20 | n |  | TRUE
150 | bus_MV_522_0_node_178 | 20 | n |  | TRUE
151 | bus_MV_522_0_node_159 | 20 | n |  | TRUE
152 | bus_MV_522_0_node_160 | 20 | n |  | TRUE
153 | bus_MV_522_0_node_92 | 20 | n |  | TRUE
154 | bus_MV_522_0_node_93 | 20 | n |  | TRUE
155 | bus_MV_522_0_node_95 | 20 | n |  | TRUE
156 | bus_MV_522_0_node_96 | 20 | n |  | TRUE
157 | bus_MV_522_0_node_97 | 20 | n |  | TRUE
158 | bus_MV_522_0_node_190 | 20 | n |  | TRUE
159 | bus_MV_522_0_node_167 | 20 | n |  | TRUE
160 | bus_MV_522_0_node_102 | 20 | n |  | TRUE
161 | bus_MV_522_0_node_103 | 20 | n |  | TRUE
162 | bus_MV_522_0_node_105 | 20 | n |  | TRUE
163 | bus_MV_522_0_node_106 | 20 | n |  | TRUE
164 | bus_MV_522_0_node_170 | 20 | n |  | TRUE
165 | bus_MV_522_0_node_137 | 20 | n |  | TRUE
166 | bus_MV_522_0_node_158 | 20 | n |  | TRUE
167 | bus_MV_522_0_node_179 | 20 | n |  | TRUE
168 | bus_MV_522_0_node_132 | 20 | n |  | TRUE
169 | bus_MV_522_0_node_181 | 20 | n |  | TRUE
170 | bus_MV_522_0_node_115 | 20 | n |  | TRUE
171 | bus_MV_522_0_node_116 | 20 | n |  | TRUE
172 | bus_MV_522_0_node_117 | 20 | n |  | TRUE
173 | bus_MV_522_0_node_119 | 20 | n |  | TRUE
174 | bus_MV_522_0_node_120 | 20 | n |  | TRUE
175 | bus_MV_522_0_node_135 | 20 | n |  | TRUE
176 | bus_MV_522_0_node_134 | 20 | n |  | TRUE
177 | bus_MV_522_0_node_121 | 20 | n |  | TRUE
178 | bus_MV_522_0_node_133 | 20 | n |  | TRUE
179 | bus_MV_522_0_node_122 | 20 | n |  | TRUE
180 | bus_MV_522_0_node_123 | 20 | n |  | TRUE
181 | bus_MV_522_0_node_125 | 20 | n |  | TRUE
182 | bus_MV_522_0_node_126 | 20 | n |  | TRUE
183 | bus_MV_522_0_node_127 | 20 | n |  | TRUE
184 | bus_MV_522_0_node_130 | 20 | n |  | TRUE
185 | bus_MV_522_0_node_131 | 20 | n |  | TRUE
186 | bus_MV_522_0_node_146 | 20 | n |  | TRUE
187 | bus_MV_522_0_node_147 | 20 | n |  | TRUE
188 | bus_MV_522_0_node_166 | 20 | n |  | TRUE
189 | bus_MV_522_0_node_169 | 20 | n |  | TRUE
190 | bus_HV_522_0_node_80 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_522_0_load_0 | 0 | 0.27712 | 0.13422 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_522_0_load_109 | 2 | 0.30393 | 0.1472 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_522_0_load_53 | 3 | 0.20584 | 0.099694 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_522_0_load_2 | 6 | 0.40411 | 0.19572 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_522_0_load_136 | 10 | 0.19908 | 0.096417 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_522_0_load_4 | 11 | 0.07305 | 0.03538 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_522_0_load_8 | 14 | 0.31997 | 0.15497 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_522_0_load_152 | 15 | 0.19272 | 0.093338 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_522_0_load_176 | 18 | 0.13415 | 0.064974 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_522_0_load_171 | 19 | 0.39333 | 0.1905 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_522_0_load_150 | 21 | 0.094169 | 0.045608 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_522_0_load_12 | 23 | 0.29327 | 0.14204 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_522_0_load_149 | 28 | 0.17975 | 0.087057 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_522_0_load_144 | 30 | 0.089425 | 0.043311 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_522_0_load_163 | 33 | 0.38366 | 0.18582 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_522_0_load_174 | 35 | 0.28931 | 0.14012 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_522_0_load_47 | 38 | 0.087169 | 0.042218 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_522_0_load_46 | 39 | 0.22566 | 0.10929 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_522_0_load_193 | 40 | 0.24953 | 0.12085 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_522_0_load_162 | 43 | 0.14217 | 0.068857 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_522_0_load_184 | 45 | 0.37082 | 0.1796 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_522_0_load_196 | 46 | 0.1057 | 0.051193 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_522_0_load_177 | 50 | 0.12961 | 0.062774 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_522_0_load_139 | 51 | 0.10607 | 0.051374 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_522_0_load_143 | 52 | 0.081156 | 0.039306 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_522_0_load_183 | 54 | 0.37474 | 0.18149 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_522_0_load_173 | 55 | 0.34204 | 0.16566 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_522_0_load_175 | 56 | 0.072079 | 0.03491 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_522_0_load_128 | 58 | 0.27217 | 0.13182 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_522_0_load_168 | 60 | 0.19002 | 0.092031 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_522_0_load_24 | 61 | 0.21127 | 0.10232 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_522_0_load_87 | 63 | 0.22287 | 0.10794 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_522_0_load_26 | 64 | 0.24166 | 0.11704 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_522_0_load_32 | 69 | 0.32674 | 0.15825 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_522_0_load_72 | 71 | 0.19821 | 0.095998 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_522_0_load_28 | 72 | 0.21398 | 0.10363 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_522_0_load_192 | 74 | 0.29202 | 0.14143 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_522_0_load_186 | 76 | 0.1429 | 0.069212 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_522_0_load_185 | 78 | 0.23534 | 0.11398 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_522_0_load_191 | 81 | 0.29403 | 0.1424 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_522_0_load_129 | 84 | 0.1451 | 0.070277 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_522_0_load_189 | 86 | 0.13179 | 0.06383 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_522_0_load_156 | 88 | 0.08952 | 0.043356 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_522_0_load_36 | 90 | 0.36182 | 0.17524 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_522_0_load_40 | 91 | 0.13306 | 0.064444 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_522_0_load_112 | 95 | 0.19848 | 0.09613 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_522_0_load_54 | 96 | 0.23484 | 0.11374 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_522_0_load_110 | 98 | 0.23341 | 0.11305 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_522_0_load_111 | 99 | 0.32177 | 0.15584 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_522_0_load_48 | 102 | 0.29719 | 0.14394 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_522_0_load_138 | 106 | 0.25135 | 0.12173 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_522_0_load_153 | 107 | 0.11115 | 0.053832 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_522_0_load_154 | 108 | 0.11775 | 0.05703 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_522_0_load_195 | 110 | 0.27778 | 0.13453 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_522_0_load_57 | 111 | 0.38722 | 0.18754 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_522_0_load_197 | 116 | 0.26946 | 0.13051 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_522_0_load_182 | 118 | 0.30024 | 0.14541 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_522_0_load_187 | 119 | 0.10295 | 0.049859 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_522_0_load_161 | 120 | 0.23533 | 0.11398 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_522_0_load_71 | 122 | 0.20845 | 0.10096 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_522_0_load_89 | 125 | 0.27429 | 0.13285 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_522_0_load_188 | 126 | 0.21343 | 0.10337 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_522_0_load_180 | 127 | 0.25675 | 0.12435 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_522_0_load_65 | 128 | 0.18368 | 0.088961 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_522_0_load_155 | 133 | 0.2591 | 0.12549 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_522_0_load_194 | 134 | 0.082865 | 0.040133 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_522_0_load_101 | 139 | 0.094727 | 0.045878 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_522_0_load_79 | 142 | 0.34598 | 0.16757 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_522_0_load_98 | 147 | 0.36014 | 0.17442 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_522_0_load_88 | 149 | 0.36728 | 0.17788 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_522_0_load_178 | 150 | 0.50054 | 0.24242 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_522_0_load_159 | 151 | 0.0833 | 0.040344 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_522_0_load_160 | 152 | 0.089126 | 0.043166 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_522_0_load_92 | 153 | 0.25541 | 0.1237 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_522_0_load_97 | 157 | 0.1632 | 0.079042 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_522_0_load_190 | 158 | 0.40742 | 0.19732 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_522_0_load_102 | 160 | 0.33277 | 0.16117 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_522_0_load_170 | 164 | 0.097915 | 0.047422 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_522_0_load_137 | 165 | 0.10806 | 0.052335 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_522_0_load_179 | 167 | 0.311 | 0.15062 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_522_0_load_181 | 169 | 0.29448 | 0.14262 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_522_0_load_115 | 170 | 0.22633 | 0.10962 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_522_0_load_135 | 175 | 0.09027 | 0.04372 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_522_0_load_121 | 177 | 0.31428 | 0.15221 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_522_0_load_133 | 178 | 0.073919 | 0.0358 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_522_0_load_122 | 179 | 0.09701 | 0.046984 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_522_0_load_126 | 182 | 0.09967 | 0.048272 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_522_0_load_127 | 183 | 0.19082 | 0.092419 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_522_0_load_130 | 184 | 0.11204 | 0.054263 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_522_0_load_147 | 187 | 0.072583 | 0.035153 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_522_0_load_169 | 189 | 0.085093 | 0.041213 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 146 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_522_0_line_0 |  | 0 | 1 | 0.024939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_522_0_line_1 |  | 0 | 2 | 1.4279 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
2 | MV_522_0_line_2 |  | 1 | 3 | 0.58782 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_522_0_line_3 |  | 2 | 5 | 0.97539 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
4 | MV_522_0_line_4 |  | 3 | 4 | 0.036449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_522_0_line_5 |  | 4 | 103 | 0.35801 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_522_0_line_6 |  | 5 | 73 | 0.39873 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
7 | MV_522_0_line_7 |  | 5 | 72 | 0.080439 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_522_0_line_8 |  | 6 | 7 | 0.017369 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_522_0_line_9 |  | 7 | 8 | 0.1249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_522_0_line_10 |  | 8 | 9 | 0.055409 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_522_0_line_11 |  | 8 | 10 | 0.026397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_522_0_line_12 |  | 9 | 15 | 0.018154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_522_0_line_13 |  | 11 | 12 | 0.037977 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_522_0_line_14 |  | 12 | 13 | 0.008426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_522_0_line_15 |  | 13 | 14 | 0.054329 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_522_0_line_16 |  | 14 | 16 | 0.01026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_522_0_line_17 |  | 15 | 20 | 0.01434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_522_0_line_18 |  | 16 | 17 | 0.023624 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_522_0_line_19 |  | 17 | 18 | 0.026867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_522_0_line_20 |  | 17 | 19 | 0.067978 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_522_0_line_21 |  | 18 | 21 | 0.055063 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_522_0_line_22 |  | 19 | 22 | 0.011364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_522_0_line_23 |  | 20 | 21 | 0.011486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_522_0_line_24 |  | 20 | 175 | 0.020418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_522_0_line_25 |  | 22 | 55 | 0.029422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_522_0_line_26 |  | 23 | 24 | 0.007585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_522_0_line_27 |  | 24 | 25 | 0.064183 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
28 | MV_522_0_line_28 |  | 24 | 26 | 0.04113 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
29 | MV_522_0_line_29 |  | 25 | 27 | 0.14552 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
30 | MV_522_0_line_30 |  | 25 | 28 | 0.028116 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_522_0_line_31 |  | 26 | 29 | 0.042527 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
32 | MV_522_0_line_32 |  | 26 | 30 | 0.022329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_522_0_line_33 |  | 27 | 40 | 0.031985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_522_0_line_34 |  | 27 | 41 | 0.48961 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_522_0_line_35 |  | 27 | 42 | 0.035877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_522_0_line_36 |  | 27 | 34 | 0.15501 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
37 | MV_522_0_line_37 |  | 28 | 47 | 0.013043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_522_0_line_38 |  | 29 | 51 | 0.017122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_522_0_line_39 |  | 29 | 48 | 0.076207 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
40 | MV_522_0_line_40 |  | 30 | 53 | 0.0061447 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_522_0_line_41 |  | 31 | 32 | 0.026644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_522_0_line_42 |  | 31 | 33 | 0.022035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_522_0_line_43 |  | 32 | 43 | 0.0094854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_522_0_line_44 |  | 32 | 34 | 0.25894 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_522_0_line_45 |  | 34 | 35 | 0.020878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_522_0_line_46 |  | 34 | 36 | 0.079444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_522_0_line_47 |  | 34 | 37 | 0.026469 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_522_0_line_48 |  | 35 | 54 | 0.036556 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_522_0_line_49 |  | 36 | 38 | 0.036759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_522_0_line_50 |  | 36 | 39 | 0.021947 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_522_0_line_51 |  | 37 | 55 | 0.031499 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_522_0_line_52 |  | 41 | 46 | 0.027625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_522_0_line_53 |  | 41 | 44 | 0.53322 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_522_0_line_54 |  | 42 | 58 | 0.031004 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_522_0_line_55 |  | 44 | 45 | 0.018958 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_522_0_line_56 |  | 46 | 59 | 0.040017 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_522_0_line_57 |  | 46 | 60 | 0.023858 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_522_0_line_58 |  | 47 | 180 | 0.16266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_522_0_line_59 |  | 48 | 49 | 0.058166 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_522_0_line_60 |  | 48 | 50 | 0.033814 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
61 | MV_522_0_line_61 |  | 49 | 52 | 0.032881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_522_0_line_62 |  | 50 | 121 | 0.017971 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_522_0_line_63 |  | 53 | 186 | 0.017834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_522_0_line_64 |  | 56 | 57 | 0.02367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_522_0_line_65 |  | 57 | 173 | 0.058837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_522_0_line_66 |  | 58 | 182 | 0.032231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_522_0_line_67 |  | 59 | 188 | 0.039103 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_522_0_line_68 |  | 59 | 159 | 0.041803 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_522_0_line_69 |  | 61 | 62 | 0.039067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_522_0_line_70 |  | 61 | 63 | 0.06034 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_522_0_line_71 |  | 62 | 64 | 0.056051 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_522_0_line_72 |  | 63 | 65 | 0.021695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_522_0_line_73 |  | 64 | 66 | 0.036121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_522_0_line_74 |  | 65 | 67 | 0.061485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_522_0_line_75 |  | 66 | 68 | 0.020338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_522_0_line_76 |  | 67 | 69 | 0.032323 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_522_0_line_77 |  | 68 | 70 | 0.34776 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
78 | MV_522_0_line_78 |  | 68 | 71 | 0.029883 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_522_0_line_79 |  | 70 | 75 | 0.54148 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_522_0_line_80 |  | 70 | 83 | 0.19965 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_522_0_line_81 |  | 70 | 84 | 0.016071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_522_0_line_82 |  | 71 | 89 | 0.006137 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
83 | MV_522_0_line_83 |  | 73 | 76 | 0.069418 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
84 | MV_522_0_line_84 |  | 74 | 75 | 0.021105 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_522_0_line_85 |  | 75 | 79 | 0.58428 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
86 | MV_522_0_line_86 |  | 76 | 80 | 0.18121 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
87 | MV_522_0_line_87 |  | 77 | 78 | 0.00743 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
88 | MV_522_0_line_88 |  | 77 | 79 | 0.16434 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
89 | MV_522_0_line_89 |  | 78 | 80 | 0.006704 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
90 | MV_522_0_line_90 |  | 79 | 82 | 0.48155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_522_0_line_91 |  | 79 | 81 | 0.03162 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_522_0_line_92 |  | 80 | 101 | 0.43198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_522_0_line_93 |  | 82 | 90 | 0.008676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_522_0_line_94 |  | 83 | 88 | 0.0039434 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
95 | MV_522_0_line_95 |  | 85 | 86 | 0.041722 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_522_0_line_96 |  | 85 | 87 | 0.46656 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
97 | MV_522_0_line_97 |  | 86 | 93 | 0.040402 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_522_0_line_98 |  | 87 | 97 | 0.25661 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_522_0_line_99 |  | 87 | 98 | 0.026104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_522_0_line_100 |  | 88 | 141 | 0.03033 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_522_0_line_101 |  | 89 | 138 | 0.12211 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
102 | MV_522_0_line_102 |  | 91 | 92 | 0.04864 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
103 | MV_522_0_line_103 |  | 92 | 93 | 0.16934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_522_0_line_104 |  | 94 | 95 | 0.082512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_522_0_line_105 |  | 94 | 96 | 0.05877 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_522_0_line_106 |  | 95 | 100 | 0.065589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_522_0_line_107 |  | 96 | 101 | 0.085459 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_522_0_line_108 |  | 97 | 99 | 0.021577 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_522_0_line_109 |  | 98 | 101 | 0.45777 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_522_0_line_110 |  | 100 | 109 | 0.1833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_522_0_line_111 |  | 102 | 103 | 0.06386 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
112 | MV_522_0_line_112 |  | 103 | 104 | 0.21789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_522_0_line_113 |  | 104 | 105 | 0.092744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_522_0_line_114 |  | 104 | 106 | 0.004163 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_522_0_line_115 |  | 105 | 107 | 0.016824 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_522_0_line_116 |  | 107 | 108 | 0.019855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_522_0_line_117 |  | 108 | 132 | 0.037778 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_522_0_line_118 |  | 109 | 110 | 0.18631 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_522_0_line_119 |  | 111 | 112 | 0.005815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_522_0_line_120 |  | 112 | 113 | 0.17355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_522_0_line_121 |  | 112 | 114 | 0.13537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_522_0_line_122 |  | 113 | 120 | 0.04017 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_522_0_line_123 |  | 113 | 115 | 0.080315 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
124 | MV_522_0_line_124 |  | 114 | 121 | 0.1318 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
125 | MV_522_0_line_125 |  | 114 | 122 | 0.049052 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
126 | MV_522_0_line_126 |  | 115 | 116 | 0.036174 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
127 | MV_522_0_line_127 |  | 117 | 118 | 0.041651 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_522_0_line_128 |  | 117 | 119 | 0.12539 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
129 | MV_522_0_line_129 |  | 119 | 123 | 0.5147 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
130 | MV_522_0_line_130 |  | 122 | 127 | 0.19505 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
131 | MV_522_0_line_131 |  | 123 | 124 | 0.19443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_522_0_line_132 |  | 123 | 125 | 0.05148 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_522_0_line_133 |  | 124 | 126 | 0.034112 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_522_0_line_134 |  | 126 | 153 | 0.42928 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
135 | MV_522_0_line_135 |  | 127 | 136 | 0.0070168 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
136 | MV_522_0_line_136 |  | 128 | 129 | 0.057845 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_522_0_line_137 |  | 129 | 130 | 0.16449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_522_0_line_138 |  | 130 | 131 | 0.069149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_522_0_line_139 |  | 130 | 132 | 0.10822 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_522_0_line_140 |  | 130 | 133 | 0.03488 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_522_0_line_141 |  | 131 | 134 | 0.059634 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_522_0_line_142 |  | 133 | 135 | 0.036277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_522_0_line_143 |  | 135 | 148 | 0.11081 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_522_0_line_144 |  | 136 | 137 | 0.23924 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
145 | MV_522_0_line_145 |  | 137 | 160 | 0.023775 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
146 | MV_522_0_line_146 |  | 138 | 139 | 0.031251 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
147 | MV_522_0_line_147 |  | 139 | 140 | 0.033016 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
148 | MV_522_0_line_148 |  | 140 | 147 | 0.005478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_522_0_line_149 |  | 140 | 146 | 0.056133 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
150 | MV_522_0_line_150 |  | 141 | 166 | 0.13795 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
151 | MV_522_0_line_151 |  | 142 | 143 | 0.021683 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_522_0_line_152 |  | 143 | 144 | 0.13989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_522_0_line_153 |  | 143 | 145 | 0.12479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_522_0_line_154 |  | 144 | 148 | 0.11144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_522_0_line_155 |  | 144 | 149 | 0.028201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_522_0_line_156 |  | 145 | 151 | 0.020016 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_522_0_line_157 |  | 148 | 150 | 0.055585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_522_0_line_158 |  | 151 | 152 | 0.029407 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_522_0_line_159 |  | 153 | 154 | 0.067129 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
160 | MV_522_0_line_160 |  | 154 | 155 | 0.69241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_522_0_line_161 |  | 155 | 156 | 0.63978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_522_0_line_162 |  | 155 | 157 | 0.03334 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
163 | MV_522_0_line_163 |  | 156 | 158 | 0.034207 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_522_0_line_164 |  | 158 | 159 | 0.03466 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
165 | MV_522_0_line_165 |  | 160 | 161 | 0.028994 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
166 | MV_522_0_line_166 |  | 161 | 162 | 0.22305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_522_0_line_167 |  | 161 | 163 | 0.38726 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
168 | MV_522_0_line_168 |  | 161 | 164 | 0.074801 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
169 | MV_522_0_line_169 |  | 162 | 165 | 0.025597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_522_0_line_170 |  | 163 | 166 | 0.25222 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
171 | MV_522_0_line_171 |  | 163 | 167 | 0.00666 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_522_0_line_172 |  | 165 | 168 | 0.032264 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_522_0_line_173 |  | 166 | 169 | 0.022144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_522_0_line_174 |  | 168 | 185 | 0.024667 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_522_0_line_175 |  | 170 | 171 | 0.036479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_522_0_line_176 |  | 170 | 172 | 0.04395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_522_0_line_177 |  | 171 | 173 | 0.062323 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_522_0_line_178 |  | 172 | 174 | 0.005182 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_522_0_line_179 |  | 173 | 175 | 0.019279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_522_0_line_180 |  | 173 | 176 | 0.031444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_522_0_line_181 |  | 174 | 177 | 0.032437 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
182 | MV_522_0_line_182 |  | 176 | 178 | 0.020261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
183 | MV_522_0_line_183 |  | 179 | 180 | 0.021867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
184 | MV_522_0_line_184 |  | 181 | 182 | 0.0046542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
185 | MV_522_0_line_185 |  | 181 | 183 | 0.0063219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
186 | MV_522_0_line_186 |  | 184 | 185 | 0.020377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
187 | MV_522_0_line_187 |  | 186 | 187 | 0.043059 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
188 | MV_522_0_line_188 |  | 188 | 189 | 0.011251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_522_0_trafo_80 | 25 MVA 110/20 kV | 190 | 146 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2644328.4858 | 1248405.0252
1 | 2644341.3319 | 1248383.6291
2 | 2643896.4959 | 1249766.0261
3 | 2644916.0486 | 1248507.0677
4 | 2644950.9278 | 1248517.9836
5 | 2644864.3075 | 1249644.6513
6 | 2646092.495 | 1249288.4491
7 | 2646095.2708 | 1249271.3035
8 | 2646019.601 | 1249212.1763
9 | 2646016.0066 | 1249171.3876
10 | 2646036.5684 | 1249192.2854
11 | 2646020.0441 | 1249252.3623
12 | 2645983.2181 | 1249243.0816
13 | 2645975.1745 | 1249240.4953
14 | 2645924.8676 | 1249219.9807
15 | 2645998.8808 | 1249165.3659
16 | 2645928.3701 | 1249210.3347
17 | 2645906.9055 | 1249200.473
18 | 2645928.5084 | 1249184.499
19 | 2645889.2786 | 1249134.8206
20 | 2645985.3528 | 1249160.6093
21 | 2645975.1788 | 1249155.2788
22 | 2645884.7831 | 1249124.384
23 | 2645942.1583 | 1248925.6388
24 | 2645946.5653 | 1248931.8215
25 | 2645978.9121 | 1248962.0258
26 | 2645964.9857 | 1248900.0873
27 | 2645884.549 | 1248987.8125
28 | 2646006.1786 | 1248955.1661
29 | 2645995.4594 | 1248902.1471
30 | 2645951.2246 | 1248882.5029
31 | 2645690.1059 | 1248980.0845
32 | 2645696.7493 | 1249002.762
33 | 2645675.8062 | 1248963.2853
34 | 2645840.6925 | 1249073.1309
35 | 2645826.0071 | 1249058.4409
36 | 2645888.2989 | 1249059.3786
37 | 2645830.153 | 1249097.4214
38 | 2645921.4158 | 1249075.2483
39 | 2645895.7148 | 1249038.722
40 | 2645870.7728 | 1249016.6254
41 | 2645683.9656 | 1248890.1545
42 | 2645918.486 | 1248983.2943
43 | 2645691.8204 | 1248994.6586
44 | 2645764.3503 | 1248618.1913
45 | 2645772.78 | 1248601.2005
46 | 2645669.393 | 1248913.647
47 | 2646018.827 | 1248951.984
48 | 2646021.7735 | 1248860.323
49 | 2646026.0814 | 1248895.8025
50 | 2646048.8165 | 1248840.0234
51 | 2645981.7659 | 1248912.4252
52 | 2646057.5676 | 1248886.353
53 | 2645947.4305 | 1248877.6696
54 | 2645807.1665 | 1249082.178
55 | 2645858.3992 | 1249111.3622
56 | 2645942.6627 | 1249101.3221
57 | 2645963.864 | 1249110.9983
58 | 2645944.1101 | 1248999.5805
59 | 2645632.6912 | 1248897.6983
60 | 2645668.8165 | 1248937.4984
61 | 2645653.035 | 1249262.8299
62 | 2645685.2347 | 1249284.9521
63 | 2645633.1421 | 1249319.7968
64 | 2645734.0666 | 1249312.7137
65 | 2645645.1965 | 1249337.8573
66 | 2645765.0973 | 1249331.3544
67 | 2645692.1251 | 1249376.4445
68 | 2645783.3666 | 1249340.4015
69 | 2645714.2961 | 1249398.4412
70 | 2645863.0796 | 1249528.9109
71 | 2645795.1297 | 1249313.0405
72 | 2644873.5481 | 1249564.8898
73 | 2645222.5196 | 1249736.5776
74 | 2645439.8542 | 1249352.8688
75 | 2645457.5458 | 1249364.4566
76 | 2645269.7996 | 1249787.4058
77 | 2645453.0474 | 1249787.685
78 | 2645456.409 | 1249794.3152
79 | 2645468.8107 | 1249706.9958
80 | 2645450.7045 | 1249797.8628
81 | 2645441.2066 | 1249691.5739
82 | 2645739.6835 | 1249879.3278
83 | 2645966.0541 | 1249517.9783
84 | 2645871.3254 | 1249515.1184
85 | 2646038.7993 | 1249961.9754
86 | 2646062.9494 | 1249995.9969
87 | 2645859.5146 | 1250392.711
88 | 2645966.1201 | 1249514.0354
89 | 2645797.6569 | 1249307.4451
90 | 2645743.4957 | 1249871.5297
91 | 2645998.7135 | 1250161.2657
92 | 2645965.0602 | 1250126.1478
93 | 2646030.5044 | 1250020.0725
94 | 2645534.3055 | 1250178.5386
95 | 2645579.5541 | 1250247.3104
96 | 2645515.7327 | 1250122.7806
97 | 2646011.4403 | 1250570.7971
98 | 2645838.7882 | 1250376.7623
99 | 2646030.6965 | 1250580.5308
100 | 2645552.6606 | 1250301.874
101 | 2645530.2774 | 1250038.5687
102 | 2645268.0422 | 1248594.6348
103 | 2645265.9767 | 1248658.4619
104 | 2645394.5439 | 1248828.5361
105 | 2645443.6095 | 1248847.1464
106 | 2645396.6406 | 1248832.1326
107 | 2645452.9055 | 1248860.988
108 | 2645464.755 | 1248876.9158
109 | 2645447.1215 | 1250357.7466
110 | 2645262.4193 | 1250382.1842
111 | 2646086.3845 | 1248770.0639
112 | 2646087.1466 | 1248764.2992
113 | 2646147.3389 | 1248638.5826
114 | 2646154.9937 | 1248798.8833
115 | 2646202.321 | 1248580.0379
116 | 2646233.4767 | 1248561.6571
117 | 2646062.9394 | 1248250.0104
118 | 2646027.4135 | 1248228.0978
119 | 2645982.7724 | 1248346.431
120 | 2646140.0544 | 1248678.0127
121 | 2646063.1892 | 1248829.2346
122 | 2646202.9189 | 1248788.4289
123 | 2646251.3641 | 1247907.3686
124 | 2646089.9023 | 1247861.8373
125 | 2646302.9931 | 1247906.8709
126 | 2646066.6017 | 1247836.9064
127 | 2646316.6253 | 1248946.9091
128 | 2645368.869 | 1249181.0988
129 | 2645394.4916 | 1249129.2377
130 | 2645453.4586 | 1248984.6587
131 | 2645489.7994 | 1248947.2677
132 | 2645465.654 | 1248904.7429
133 | 2645471.8661 | 1249014.2863
134 | 2645502.7126 | 1248905.7277
135 | 2645489.4496 | 1249045.998
136 | 2646319.0354 | 1248953.499
137 | 2646297.7547 | 1249182.0646
138 | 2645838.7651 | 1249223.7841
139 | 2645813.5035 | 1249205.6103
140 | 2645784.8361 | 1249189.2332
141 | 2645965.488 | 1249483.8731
142 | 2645686.7262 | 1249147.2598
143 | 2645665.4381 | 1249142.8262
144 | 2645541.9586 | 1249166.5263
145 | 2645632.7607 | 1249048.5781
146 | 2645746.1833 | 1249156.324
147 | 2645787.7261 | 1249184.5746
148 | 2645552.2507 | 1249098.593
149 | 2645534.6492 | 1249192.1764
150 | 2645591.5289 | 1249059.1904
151 | 2645642.3876 | 1249062.1633
152 | 2645651.8957 | 1249089.9676
153 | 2645731.0241 | 1248104.6122
154 | 2645744.7218 | 1248170.3285
155 | 2645510.3081 | 1248447.356
156 | 2645602.009 | 1248817.6976
157 | 2645477.2197 | 1248443.2662
158 | 2645627.4141 | 1248840.6861
159 | 2645609.9154 | 1248870.605
160 | 2646275.4869 | 1249173.5963
161 | 2646264.7817 | 1249200.5421
162 | 2646175.3338 | 1249249.9118
163 | 2646245.5171 | 1249433.3154
164 | 2646337.0534 | 1249219.8286
165 | 2646192.3287 | 1249233.431
166 | 2646044.9485 | 1249433.6666
167 | 2646239.6606 | 1249430.112
168 | 2646204.5216 | 1249203.5856
169 | 2646041.3059 | 1249455.5086
170 | 2646049.3001 | 1249124.3134
171 | 2646015.0036 | 1249111.8842
172 | 2646091.0247 | 1249137.6583
173 | 2646000.9782 | 1249124.117
174 | 2646089.1524 | 1249142.4915
175 | 2645993.3897 | 1249141.8396
176 | 2646030.3125 | 1249135.6634
177 | 2646118.5165 | 1249156.2302
178 | 2646049.1156 | 1249143.2088
179 | 2646010.3109 | 1249030.2382
180 | 2646030.6457 | 1249038.2782
181 | 2645974.3822 | 1249016.494
182 | 2645973.7894 | 1249012.1222
183 | 2645980.4294 | 1249014.6507
184 | 2646180.4014 | 1249180.4008
185 | 2646199.683 | 1249186.97
186 | 2645932.7784 | 1248887.8963
187 | 2645902.37 | 1248865.6794
188 | 2645622.8838 | 1248915.2347
189 | 2645614.3181 | 1248922.5293
190 | 2645746.1833 | 1249156.324

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98868 | -0.33992 | 0.27712 | 0.13422
1 | 0.98859 | -0.3391 | 0 | 0
2 | 0.99328 | -0.18553 | 0.30393 | 0.1472
3 | 0.98526 | -0.36263 | 0.20584 | 0.099694
4 | 0.98514 | -0.36152 | 0 | 0
5 | 0.99561 | -0.054993 | 0 | 0
6 | 0.99281 | -0.070248 | 0.40411 | 0.19572
7 | 0.99281 | -0.070333 | 0 | 0
8 | 0.99288 | -0.070931 | 0 | 0
9 | 0.99292 | -0.07132 | 0 | 0
10 | 0.99287 | -0.070868 | 0.19908 | 0.096417
11 | 0.99318 | -0.07101 | 0.07305 | 0.03538
12 | 0.99319 | -0.071043 | 0 | 0
13 | 0.99319 | -0.07105 | 0 | 0
14 | 0.9932 | -0.070996 | 0.31997 | 0.15497
15 | 0.99294 | -0.071446 | 0.19272 | 0.093338
16 | 0.9932 | -0.071044 | 0 | 0
17 | 0.99321 | -0.071154 | 0 | 0
18 | 0.99315 | -0.070593 | 0.13415 | 0.064974
19 | 0.9935 | -0.069225 | 0.39333 | 0.1905
20 | 0.99295 | -0.071579 | 0 | 0
21 | 0.99297 | -0.071788 | 0.094169 | 0.045608
22 | 0.99354 | -0.069569 | 0 | 0
23 | 0.99449 | -0.067249 | 0.29327 | 0.14204
24 | 0.9945 | -0.067276 | 0 | 0
25 | 0.99441 | -0.067644 | 0 | 0
26 | 0.99455 | -0.067032 | 0 | 0
27 | 0.99423 | -0.068433 | 0 | 0
28 | 0.9944 | -0.067558 | 0.17975 | 0.087057
29 | 0.99461 | -0.066773 | 0 | 0
30 | 0.99455 | -0.066991 | 0.089425 | 0.043311
31 | 0.99367 | -0.070747 | 0 | 0
32 | 0.99368 | -0.07087 | 0 | 0
33 | 0.99366 | -0.070645 | 0.38366 | 0.18582
34 | 0.99385 | -0.072445 | 0 | 0
35 | 0.99384 | -0.072279 | 0.28931 | 0.14012
36 | 0.99382 | -0.072153 | 0 | 0
37 | 0.99376 | -0.071538 | 0 | 0
38 | 0.99382 | -0.072116 | 0.087169 | 0.042218
39 | 0.99381 | -0.072214 | 0.22566 | 0.10929
40 | 0.99422 | -0.068337 | 0.24953 | 0.12085
41 | 0.99269 | -0.055747 | 0 | 0
42 | 0.9942 | -0.068194 | 0 | 0
43 | 0.99368 | -0.070853 | 0.14217 | 0.068857
44 | 0.99244 | -0.053577 | 0 | 0
45 | 0.99243 | -0.053492 | 0.37082 | 0.1796
46 | 0.99261 | -0.05512 | 0.1057 | 0.051193
47 | 0.9944 | -0.067547 | 0 | 0
48 | 0.99472 | -0.066299 | 0 | 0
49 | 0.99471 | -0.066248 | 0 | 0
50 | 0.99477 | -0.066085 | 0.12961 | 0.062774
51 | 0.99461 | -0.066751 | 0.10607 | 0.051374
52 | 0.99471 | -0.066216 | 0.081156 | 0.039306
53 | 0.99455 | -0.066986 | 0 | 0
54 | 0.99382 | -0.072114 | 0.37474 | 0.18149
55 | 0.99364 | -0.070458 | 0.34204 | 0.16566
56 | 0.99291 | -0.071179 | 0.072079 | 0.03491
57 | 0.99291 | -0.0712 | 0 | 0
58 | 0.99418 | -0.067985 | 0.27217 | 0.13182
59 | 0.99247 | -0.056158 | 0 | 0
60 | 0.9926 | -0.055176 | 0.19002 | 0.092031
61 | 0.99896 | -0.0030718 | 0.21127 | 0.10232
62 | 0.99899 | -0.00342 | 0 | 0
63 | 0.99889 | -0.0034878 | 0.22287 | 0.10794
64 | 0.99905 | -0.0039154 | 0.24166 | 0.11704
65 | 0.99888 | -0.0034063 | 0 | 0
66 | 0.99909 | -0.0043368 | 0 | 0
67 | 0.99886 | -0.0031713 | 0 | 0
68 | 0.99912 | -0.0045731 | 0 | 0
69 | 0.99884 | -0.0030454 | 0.32674 | 0.15825
70 | 0.99809 | -0.0099161 | 0 | 0
71 | 0.99921 | -0.0040904 | 0.19821 | 0.095998
72 | 0.99559 | -0.05479 | 0.21398 | 0.10363
73 | 0.9961 | -0.052999 | 0 | 0
74 | 0.99751 | -0.012823 | 0.29202 | 0.14143
75 | 0.99752 | -0.012896 | 0 | 0
76 | 0.99628 | -0.043142 | 0.1429 | 0.069212
77 | 0.99677 | -0.016366 | 0 | 0
78 | 0.99676 | -0.016396 | 0.23534 | 0.11398
79 | 0.99692 | -0.015709 | 0 | 0
80 | 0.99675 | -0.016446 | 0 | 0
81 | 0.9969 | -0.015822 | 0.29403 | 0.1424
82 | 0.9967 | -0.013794 | 0 | 0
83 | 0.99772 | -0.011771 | 0 | 0
84 | 0.99809 | -0.0098883 | 0.1451 | 0.070277
85 | 0.99492 | -0.015726 | 0 | 0
86 | 0.9949 | -0.015876 | 0.13179 | 0.06383
87 | 0.99516 | -0.01404 | 0 | 0
88 | 0.99771 | -0.011807 | 0.08952 | 0.043356
89 | 0.99923 | -0.0039905 | 0 | 0
90 | 0.99669 | -0.013756 | 0.36182 | 0.17524
91 | 0.99485 | -0.015785 | 0.13306 | 0.064444
92 | 0.99486 | -0.015706 | 0 | 0
93 | 0.99489 | -0.015955 | 0 | 0
94 | 0.99574 | -0.010352 | 0 | 0
95 | 0.99569 | -0.0099157 | 0.19848 | 0.09613
96 | 0.99579 | -0.0099704 | 0.23484 | 0.11374
97 | 0.99506 | -0.013093 | 0 | 0
98 | 0.99518 | -0.014207 | 0.23341 | 0.11305
99 | 0.99504 | -0.013178 | 0.32177 | 0.15584
100 | 0.99566 | -0.0097183 | 0 | 0
101 | 0.99591 | -0.0091698 | 0 | 0
102 | 0.98386 | -0.35079 | 0.29719 | 0.14394
103 | 0.98389 | -0.35055 | 0 | 0
104 | 0.98322 | -0.34457 | 0 | 0
105 | 0.98296 | -0.34229 | 0 | 0
106 | 0.98322 | -0.34456 | 0.25135 | 0.12173
107 | 0.98292 | -0.34187 | 0.11115 | 0.053832
108 | 0.98287 | -0.34141 | 0.11775 | 0.05703
109 | 0.9956 | -0.0091319 | 0 | 0
110 | 0.9955 | -0.0097646 | 0.27778 | 0.13453
111 | 0.99482 | -0.063687 | 0.38722 | 0.18754
112 | 0.99483 | -0.063715 | 0 | 0
113 | 0.99472 | -0.06269 | 0 | 0
114 | 0.99498 | -0.065114 | 0 | 0
115 | 0.99467 | -0.062955 | 0 | 0
116 | 0.99465 | -0.063075 | 0.26946 | 0.13051
117 | 0.98855 | -0.045348 | 0 | 0
118 | 0.98853 | -0.045196 | 0.30024 | 0.14541
119 | 0.98862 | -0.044871 | 0.10295 | 0.049859
120 | 0.9947 | -0.062577 | 0.23533 | 0.11398
121 | 0.99479 | -0.06597 | 0 | 0
122 | 0.99506 | -0.064762 | 0.20845 | 0.10096
123 | 0.98903 | -0.042243 | 0 | 0
124 | 0.9892 | -0.043788 | 0 | 0
125 | 0.98901 | -0.042072 | 0.27429 | 0.13285
126 | 0.98923 | -0.044054 | 0.21343 | 0.10337
127 | 0.99571 | -0.027866 | 0.25675 | 0.12435
128 | 0.98245 | -0.33797 | 0.18368 | 0.088961
129 | 0.98247 | -0.33784 | 0 | 0
130 | 0.98251 | -0.33819 | 0 | 0
131 | 0.9825 | -0.33813 | 0 | 0
132 | 0.98277 | -0.34058 | 0 | 0
133 | 0.98243 | -0.33752 | 0.2591 | 0.12549
134 | 0.98249 | -0.33807 | 0.082865 | 0.040133
135 | 0.98237 | -0.33693 | 0 | 0
136 | 0.99573 | -0.026505 | 0 | 0
137 | 0.99613 | -0.02471 | 0 | 0
138 | 0.99962 | -0.0019956 | 0 | 0
139 | 0.99972 | -0.0014831 | 0.094727 | 0.045878
140 | 0.99982 | -0.000939 | 0 | 0
141 | 0.99766 | -0.012084 | 0 | 0
142 | 0.98194 | -0.33303 | 0.34598 | 0.16757
143 | 0.98195 | -0.33313 | 0 | 0
144 | 0.98204 | -0.33397 | 0 | 0
145 | 0.98192 | -0.33288 | 0 | 0
146 | 1 | 0 | -19.9563 | -8.9694
147 | 0.99982 | -0.00091541 | 0.36014 | 0.17442
148 | 0.98217 | -0.33512 | 0 | 0
149 | 0.98203 | -0.33384 | 0.36728 | 0.17788
150 | 0.98213 | -0.33478 | 0.50054 | 0.24242
151 | 0.98191 | -0.33284 | 0.0833 | 0.040344
152 | 0.98191 | -0.33281 | 0.089126 | 0.043166
153 | 0.98997 | -0.039015 | 0.25541 | 0.1237
154 | 0.99012 | -0.038015 | 0 | 0
155 | 0.99114 | -0.046944 | 0 | 0
156 | 0.99221 | -0.055797 | 0 | 0
157 | 0.99113 | -0.047011 | 0.1632 | 0.079042
158 | 0.99227 | -0.056253 | 0.40742 | 0.19732
159 | 0.99238 | -0.055397 | 0 | 0
160 | 0.99617 | -0.024529 | 0.33277 | 0.16117
161 | 0.99627 | -0.018719 | 0 | 0
162 | 0.99621 | -0.0182 | 0 | 0
163 | 0.99695 | -0.015529 | 0 | 0
164 | 0.99625 | -0.018808 | 0.097915 | 0.047422
165 | 0.9962 | -0.018136 | 0.10806 | 0.052335
166 | 0.9974 | -0.013333 | 0 | 0
167 | 0.99695 | -0.015504 | 0.311 | 0.15062
168 | 0.99619 | -0.018095 | 0 | 0
169 | 0.9974 | -0.013255 | 0.29448 | 0.14262
170 | 0.99284 | -0.070618 | 0.22633 | 0.10962
171 | 0.99287 | -0.070852 | 0 | 0
172 | 0.99283 | -0.070454 | 0 | 0
173 | 0.99291 | -0.071246 | 0 | 0
174 | 0.99282 | -0.070435 | 0 | 0
175 | 0.99293 | -0.071397 | 0.09027 | 0.04372
176 | 0.99291 | -0.07122 | 0 | 0
177 | 0.99281 | -0.070312 | 0.31428 | 0.15221
178 | 0.99291 | -0.071202 | 0.073919 | 0.0358
179 | 0.99438 | -0.067356 | 0.09701 | 0.046984
180 | 0.99438 | -0.067382 | 0 | 0
181 | 0.99417 | -0.067863 | 0 | 0
182 | 0.99417 | -0.067873 | 0.09967 | 0.048272
183 | 0.99417 | -0.067848 | 0.19082 | 0.092419
184 | 0.99619 | -0.018036 | 0.11204 | 0.054263
185 | 0.99619 | -0.018063 | 0 | 0
186 | 0.99455 | -0.066972 | 0 | 0
187 | 0.99454 | -0.066935 | 0.072583 | 0.035153
188 | 0.99247 | -0.056119 | 0 | 0
189 | 0.99247 | -0.056108 | 0.085093 | 0.041213
190 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 2.9128 | 1.3653 | -2.9125 | -1.3658 | 0.00029375 | -0.00049486 | 0.093927 | 0.093934 | 0.093934 | 0.98868 | -0.33992 | 0.98859 | -0.3391 | 42.6975
1 | -3.1899 | -1.4995 | 3.2007 | 1.5133 | 0.010778 | 0.01379 | 0.10292 | 0.10289 | 0.10292 | 0.98868 | -0.33992 | 0.99328 | -0.18553 | 25.1017
2 | 2.9125 | 1.3658 | -2.9033 | -1.3607 | 0.0092421 | 0.0051054 | 0.093934 | 0.093943 | 0.093943 | 0.98859 | -0.3391 | 0.98526 | -0.36263 | 44.7347
3 | -3.5046 | -1.6605 | 3.5091 | 1.6711 | 0.0044228 | 0.01056 | 0.11271 | 0.11269 | 0.11271 | 0.99328 | -0.18553 | 0.99561 | -0.054993 | 17.4742
4 | 2.6974 | 1.261 | -2.6971 | -1.2617 | 0.0003704 | -0.00073482 | 0.087242 | 0.087253 | 0.087253 | 0.98526 | -0.36263 | 0.98514 | -0.36152 | 39.6604
5 | 2.6971 | 1.2617 | -2.6934 | -1.2689 | 0.003643 | -0.0072047 | 0.087253 | 0.087356 | 0.087356 | 0.98514 | -0.36152 | 0.98389 | -0.35055 | 39.7073
6 | -3.7231 | -1.7728 | 3.7248 | 1.7489 | 0.0017567 | -0.023856 | 0.11956 | 0.11925 | 0.11956 | 0.99561 | -0.054993 | 0.9961 | -0.052999 | 18.7401
7 | 0.21398 | 0.10173 | -0.21398 | -0.10363 | 5.0856e-06 | -0.0019022 | 0.0068698 | 0.0068937 | 0.0068937 | 0.99561 | -0.054993 | 0.99559 | -0.05479 | 3.1335
8 | -0.40411 | -0.19572 | 0.40411 | 0.19531 | 3.9508e-06 | -0.00040759 | 0.013056 | 0.013051 | 0.013056 | 0.99281 | -0.070248 | 0.99281 | -0.070333 | 5.9344
9 | -0.40411 | -0.19531 | 0.40414 | 0.19238 | 2.8319e-05 | -0.0029313 | 0.013051 | 0.013014 | 0.013051 | 0.99281 | -0.070333 | 0.99288 | -0.070931 | 5.9321
10 | -0.60322 | -0.28818 | 0.60325 | 0.28688 | 2.7923e-05 | -0.001296 | 0.019437 | 0.019421 | 0.019437 | 0.99288 | -0.070931 | 0.99292 | -0.07132 | 8.835
11 | 0.19908 | 0.095797 | -0.19908 | -0.096417 | 1.4558e-06 | -0.00062088 | 0.0064234 | 0.0064312 | 0.0064312 | 0.99288 | -0.070931 | 0.99287 | -0.070868 | 2.9233
12 | -0.60325 | -0.28688 | 0.60326 | 0.28646 | 9.138e-06 | -0.00042462 | 0.019421 | 0.019415 | 0.019421 | 0.99292 | -0.07132 | 0.99294 | -0.071446 | 8.8276
13 | -0.07305 | -0.03538 | 0.07305 | 0.034485 | 2.8083e-07 | -0.00089435 | 0.0023591 | 0.0023479 | 0.0023591 | 0.99318 | -0.07101 | 0.99319 | -0.071043 | 1.0723
14 | -0.07305 | -0.034485 | 0.07305 | 0.034287 | 6.196e-08 | -0.00019843 | 0.0023479 | 0.0023455 | 0.0023479 | 0.99319 | -0.071043 | 0.99319 | -0.07105 | 1.0672
15 | -0.07305 | -0.034287 | 0.07305 | 0.034223 | 5.3233e-07 | -6.3645e-05 | 0.0023455 | 0.0023447 | 0.0023455 | 0.99319 | -0.07105 | 0.9932 | -0.070996 | 1.1169
16 | -0.39302 | -0.18919 | 0.39302 | 0.18895 | 2.201e-06 | -0.000241 | 0.012678 | 0.012675 | 0.012678 | 0.9932 | -0.070996 | 0.9932 | -0.071044 | 5.7627
17 | -0.79598 | -0.37979 | 0.79599 | 0.37946 | 1.2584e-05 | -0.00033383 | 0.025641 | 0.025636 | 0.025641 | 0.99294 | -0.071446 | 0.99295 | -0.071579 | 11.6548
18 | -0.39302 | -0.18895 | 0.39303 | 0.1884 | 5.0638e-06 | -0.00055491 | 0.012675 | 0.012668 | 0.012675 | 0.9932 | -0.071044 | 0.99321 | -0.071154 | 5.7613
19 | 1.8017 | 0.85725 | -1.8016 | -0.85784 | 0.00012064 | -0.00059698 | 0.057992 | 0.058 | 0.058 | 0.99321 | -0.071154 | 0.99315 | -0.070593 | 26.3635
20 | -2.1947 | -1.0456 | 2.1953 | 1.0459 | 0.00060469 | 0.00029868 | 0.07066 | 0.070659 | 0.07066 | 0.99321 | -0.071154 | 0.9935 | -0.069225 | 33.6474
21 | 1.6674 | 0.79287 | -1.6672 | -0.79276 | 0.00028256 | 0.00011216 | 0.053667 | 0.053668 | 0.053668 | 0.99315 | -0.070593 | 0.99297 | -0.071788 | 25.5561
22 | -2.5887 | -1.2364 | 2.5888 | 1.2362 | 0.00010541 | -0.00023655 | 0.083357 | 0.083354 | 0.083357 | 0.9935 | -0.069225 | 0.99354 | -0.069569 | 37.8895
23 | -1.573 | -0.74741 | 1.573 | 0.74715 | 3.9302e-05 | -0.00025873 | 0.050629 | 0.050626 | 0.050629 | 0.99295 | -0.071579 | 0.99297 | -0.071788 | 23.0134
24 | 0.77696 | 0.36795 | -0.77695 | -0.36842 | 1.7031e-05 | -0.00047559 | 0.024993 | 0.024999 | 0.024999 | 0.99295 | -0.071579 | 0.99293 | -0.071397 | 11.3632
25 | -2.5888 | -1.2362 | 2.5891 | 1.2356 | 0.00027287 | -0.00061257 | 0.083354 | 0.083345 | 0.083354 | 0.99354 | -0.069569 | 0.99364 | -0.070458 | 37.888
26 | -0.29327 | -0.14204 | 0.29327 | 0.14186 | 9.0575e-07 | -0.00017884 | 0.0094588 | 0.0094565 | 0.0094588 | 0.99449 | -0.067249 | 0.9945 | -0.067276 | 4.2995
27 | 8.0047 | 3.7363 | -8.0041 | -3.7439 | 0.00065226 | -0.007609 | 0.25642 | 0.25652 | 0.25652 | 0.9945 | -0.067276 | 0.99441 | -0.067644 | 20.1033
28 | -8.298 | -3.8782 | 8.2984 | 3.8733 | 0.0004491 | -0.0048593 | 0.26588 | 0.26581 | 0.26588 | 0.9945 | -0.067276 | 0.99455 | -0.067032 | 20.8367
29 | 7.7273 | 3.6152 | -7.7259 | -3.6325 | 0.0013802 | -0.017303 | 0.24766 | 0.24788 | 0.24788 | 0.99441 | -0.067644 | 0.99423 | -0.068433 | 19.4263
30 | 0.27677 | 0.12871 | -0.27676 | -0.12938 | 2.9497e-06 | -0.00066294 | 0.0088608 | 0.0088689 | 0.0088689 | 0.99441 | -0.067644 | 0.9944 | -0.067558 | 4.0313
31 | -8.4605 | -3.9497 | 8.4609 | 3.9447 | 0.00048246 | -0.0050147 | 0.27101 | 0.27095 | 0.27101 | 0.99455 | -0.067032 | 0.99461 | -0.066773 | 21.2391
32 | 0.16201 | 0.076354 | -0.16201 | -0.076881 | 8.0658e-07 | -0.00052709 | 0.0051985 | 0.005205 | 0.005205 | 0.99455 | -0.067032 | 0.99455 | -0.066991 | 2.3659
33 | 0.24953 | 0.1201 | -0.24953 | -0.12085 | 2.7639e-06 | -0.00075406 | 0.0080406 | 0.0080502 | 0.0080502 | 0.99423 | -0.068433 | 0.99422 | -0.068337 | 3.6592
34 | 2.4775 | 1.1303 | -2.4734 | -1.1406 | 0.0040936 | -0.010323 | 0.079068 | 0.079208 | 0.079208 | 0.99423 | -0.068433 | 0.99269 | -0.055747 | 36.0036
35 | 0.56269 | 0.26992 | -0.56268 | -0.27076 | 1.5735e-05 | -0.00084206 | 0.01812 | 0.018131 | 0.018131 | 0.99423 | -0.068433 | 0.9942 | -0.068194 | 8.2413
36 | 4.4362 | 2.1122 | -4.4346 | -2.1163 | 0.0015245 | -0.0041469 | 0.14266 | 0.14272 | 0.14272 | 0.99423 | -0.068433 | 0.99385 | -0.072445 | 39.4267
37 | 0.097012 | 0.04232 | -0.097012 | -0.042628 | 1.6457e-07 | -0.00030788 | 0.0030726 | 0.0030761 | 0.0030761 | 0.9944 | -0.067558 | 0.9944 | -0.067547 | 1.3982
38 | 0.10608 | 0.05097 | -0.10607 | -0.051374 | 2.6707e-07 | -0.00040433 | 0.0034157 | 0.0034208 | 0.0034208 | 0.99461 | -0.066773 | 0.99461 | -0.066751 | 1.5549
39 | -8.567 | -3.9956 | 8.5679 | 3.9867 | 0.00088591 | -0.0089757 | 0.27436 | 0.27425 | 0.27436 | 0.99461 | -0.066773 | 0.99472 | -0.066299 | 21.5017
40 | 0.072583 | 0.03357 | -0.072583 | -0.033715 | 4.4245e-08 | -0.0001451 | 0.0023212 | 0.002323 | 0.002323 | 0.99455 | -0.066991 | 0.99455 | -0.066986 | 1.0559
41 | -0.38367 | -0.1853 | 0.38367 | 0.18467 | 5.4462e-06 | -0.00062651 | 0.012378 | 0.01237 | 0.012378 | 0.99367 | -0.070747 | 0.99368 | -0.07087 | 5.6263
42 | 0.38367 | 0.1853 | -0.38366 | -0.18582 | 4.5094e-06 | -0.00051812 | 0.012378 | 0.012384 | 0.012384 | 0.99367 | -0.070747 | 0.99366 | -0.070645 | 5.6293
43 | 0.14217 | 0.068633 | -0.14217 | -0.068857 | 2.6652e-07 | -0.00022354 | 0.0045863 | 0.0045892 | 0.0045892 | 0.99368 | -0.07087 | 0.99368 | -0.070853 | 2.086
44 | -0.52584 | -0.2533 | 0.52594 | 0.24723 | 9.8941e-05 | -0.0060762 | 0.016956 | 0.01688 | 0.016956 | 0.99368 | -0.07087 | 0.99385 | -0.072445 | 7.7074
45 | 0.66407 | 0.32027 | -0.66406 | -0.32076 | 1.2786e-05 | -0.00048858 | 0.021415 | 0.021421 | 0.021421 | 0.99385 | -0.072445 | 0.99384 | -0.072279 | 9.7368
46 | 0.31284 | 0.14875 | -0.31283 | -0.15062 | 1.0762e-05 | -0.0018703 | 0.010062 | 0.010085 | 0.010085 | 0.99385 | -0.072445 | 0.99382 | -0.072153 | 4.5841
47 | 2.9318 | 1.4001 | -2.9315 | -1.4006 | 0.00031471 | -0.00053082 | 0.094369 | 0.094376 | 0.094376 | 0.99385 | -0.072445 | 0.99376 | -0.071538 | 42.8984
48 | 0.37475 | 0.18063 | -0.37474 | -0.18149 | 7.1322e-06 | -0.00085996 | 0.012084 | 0.012095 | 0.012095 | 0.99384 | -0.072279 | 0.99382 | -0.072114 | 5.4975
49 | 0.087169 | 0.041351 | -0.087169 | -0.042218 | 3.869e-07 | -0.00086675 | 0.0028024 | 0.0028133 | 0.0028133 | 0.99382 | -0.072153 | 0.99382 | -0.072116 | 1.2788
50 | 0.22566 | 0.10927 | -0.22566 | -0.10929 | 2.0741e-06 | -2.4579e-05 | 0.0072827 | 0.007283 | 0.007283 | 0.99382 | -0.072153 | 0.99381 | -0.072214 | 3.4681
51 | 2.9315 | 1.4006 | -2.9311 | -1.4012 | 0.00037458 | -0.00063151 | 0.094376 | 0.094386 | 0.094386 | 0.99376 | -0.071538 | 0.99364 | -0.070458 | 42.9026
52 | 2.1025 | 0.974 | -2.1023 | -0.9746 | 0.00016747 | -0.00060024 | 0.067383 | 0.067391 | 0.067391 | 0.99269 | -0.055747 | 0.99261 | -0.05512 | 30.6325
53 | 0.37093 | 0.16664 | -0.37083 | -0.17915 | 0.00010082 | -0.012513 | 0.011825 | 0.011979 | 0.011979 | 0.99269 | -0.055747 | 0.99244 | -0.053577 | 5.4451
54 | 0.56268 | 0.27076 | -0.56266 | -0.27149 | 1.3613e-05 | -0.00072765 | 0.018131 | 0.01814 | 0.01814 | 0.9942 | -0.068194 | 0.99418 | -0.067985 | 8.2455
55 | 0.37083 | 0.17915 | -0.37082 | -0.1796 | 3.6336e-06 | -0.00044474 | 0.011979 | 0.011985 | 0.011985 | 0.99244 | -0.053577 | 0.99243 | -0.053492 | 5.4477
56 | 1.8066 | 0.83141 | -1.8064 | -0.8313 | 0.00023851 | 0.00010233 | 0.057838 | 0.057838 | 0.057838 | 0.99261 | -0.05512 | 0.99247 | -0.056158 | 27.542
57 | 0.19002 | 0.092004 | -0.19002 | -0.092031 | 1.6026e-06 | -2.7059e-05 | 0.0061399 | 0.0061403 | 0.0061403 | 0.99261 | -0.05512 | 0.9926 | -0.055176 | 2.9239
58 | 0.097012 | 0.042628 | -0.09701 | -0.046468 | 2.0854e-06 | -0.0038396 | 0.0030761 | 0.0031227 | 0.0031227 | 0.9944 | -0.067547 | 0.99438 | -0.067382 | 1.4194
59 | 0.081157 | 0.037155 | -0.081157 | -0.038529 | 5.244e-07 | -0.001374 | 0.0025903 | 0.0026072 | 0.0026072 | 0.99472 | -0.066299 | 0.99471 | -0.066248 | 1.1851
60 | -8.6491 | -4.0238 | 8.6495 | 4.0198 | 0.00040031 | -0.0039792 | 0.27684 | 0.27678 | 0.27684 | 0.99472 | -0.066299 | 0.99477 | -0.066085 | 21.6956
61 | 0.081157 | 0.038529 | -0.081156 | -0.039306 | 2.9949e-07 | -0.0007767 | 0.0026072 | 0.0026169 | 0.0026169 | 0.99471 | -0.066248 | 0.99471 | -0.066216 | 1.1895
62 | -8.7791 | -4.0826 | 8.7793 | 4.0805 | 0.00021916 | -0.0021114 | 0.28096 | 0.28094 | 0.28096 | 0.99477 | -0.066085 | 0.99479 | -0.06597 | 22.0191
63 | 0.072583 | 0.033715 | -0.072583 | -0.034137 | 1.2876e-07 | -0.00042114 | 0.002323 | 0.0023281 | 0.0023281 | 0.99455 | -0.066986 | 0.99455 | -0.066972 | 1.0582
64 | -0.072079 | -0.03491 | 0.07208 | 0.034353 | 1.7081e-07 | -0.00055711 | 0.0023285 | 0.0023215 | 0.0023285 | 0.99291 | -0.071179 | 0.99291 | -0.0712 | 1.0584
65 | -0.07208 | -0.034353 | 0.07208 | 0.032968 | 4.2017e-07 | -0.0013848 | 0.0023215 | 0.0023044 | 0.0023215 | 0.99291 | -0.0712 | 0.99291 | -0.071246 | 1.0552
66 | 0.2905 | 0.13967 | -0.29049 | -0.14043 | 3.773e-06 | -0.00075949 | 0.0093593 | 0.0093689 | 0.0093689 | 0.99418 | -0.067985 | 0.99417 | -0.067873 | 4.2586
67 | 0.085094 | 0.040029 | -0.085093 | -0.040948 | 3.9219e-07 | -0.00091951 | 0.0027352 | 0.0027467 | 0.0027467 | 0.99247 | -0.056158 | 0.99247 | -0.056119 | 1.2485
68 | 1.7213 | 0.79128 | -1.7211 | -0.79221 | 0.00016949 | -0.00093277 | 0.055103 | 0.055115 | 0.055115 | 0.99247 | -0.056158 | 0.99238 | -0.055397 | 25.0522
69 | -0.76093 | -0.36571 | 0.76096 | 0.36479 | 3.1028e-05 | -0.00092165 | 0.024397 | 0.024385 | 0.024397 | 0.99896 | -0.0030718 | 0.99899 | -0.00342 | 11.0895
70 | 0.54966 | 0.26339 | -0.54963 | -0.26344 | 3.3354e-05 | -5.0988e-05 | 0.017613 | 0.017614 | 0.017614 | 0.99896 | -0.0030718 | 0.99889 | -0.0034878 | 8.3878
71 | -0.76096 | -0.36479 | 0.76101 | 0.36347 | 4.4465e-05 | -0.0013225 | 0.024385 | 0.024369 | 0.024385 | 0.99899 | -0.00342 | 0.99905 | -0.0039154 | 11.0842
72 | 0.32676 | 0.1555 | -0.32676 | -0.15602 | 3.1696e-06 | -0.0005159 | 0.010458 | 0.010464 | 0.010464 | 0.99889 | -0.0034878 | 0.99888 | -0.0034063 | 4.7565
73 | -1.0027 | -0.48051 | 1.0027 | 0.47966 | 4.9755e-05 | -0.00084607 | 0.032127 | 0.032116 | 0.032127 | 0.99905 | -0.0039154 | 0.99909 | -0.0043368 | 14.6032
74 | 0.32676 | 0.15602 | -0.32675 | -0.15748 | 9.004e-06 | -0.001462 | 0.010464 | 0.010483 | 0.010483 | 0.99888 | -0.0034063 | 0.99886 | -0.0031713 | 4.7649
75 | -1.0027 | -0.47966 | 1.0027 | 0.47919 | 2.8e-05 | -0.00047642 | 0.032116 | 0.03211 | 0.032116 | 0.99909 | -0.0043368 | 0.99912 | -0.0045731 | 14.5983
76 | 0.32675 | 0.15748 | -0.32674 | -0.15825 | 4.7461e-06 | -0.00076857 | 0.010483 | 0.010492 | 0.010492 | 0.99886 | -0.0031713 | 0.99884 | -0.0030454 | 4.7693
77 | 18.27 | 8.1892 | -18.252 | -8.2227 | 0.017996 | -0.033446 | 0.57848 | 0.57899 | 0.57899 | 0.99912 | -0.0045731 | 0.99809 | -0.0099161 | 45.3756
78 | -19.2727 | -8.6684 | 19.2745 | 8.6656 | 0.0017211 | -0.0027798 | 0.61058 | 0.61053 | 0.61058 | 0.99912 | -0.0045731 | 0.99921 | -0.0040904 | 47.8509
79 | 6.594 | 2.9364 | -6.5903 | -3.0021 | 0.0036603 | -0.065685 | 0.20877 | 0.20958 | 0.20958 | 0.99809 | -0.0099161 | 0.99752 | -0.012896 | 16.4244
80 | 11.5129 | 5.2164 | -11.5088 | -5.2391 | 0.0041257 | -0.022661 | 0.36557 | 0.36587 | 0.36587 | 0.99809 | -0.0099161 | 0.99772 | -0.011771 | 28.673
81 | 0.1451 | 0.069895 | -0.1451 | -0.070277 | 4.6604e-07 | -0.00038211 | 0.0046583 | 0.0046631 | 0.0046631 | 0.99809 | -0.0099161 | 0.99809 | -0.0098883 | 2.1196
82 | -19.4727 | -8.7616 | 19.473 | 8.7611 | 0.00036083 | -0.00056682 | 0.61689 | 0.61688 | 0.61689 | 0.99921 | -0.0040904 | 0.99923 | -0.0039905 | 48.3459
83 | -3.7248 | -1.7489 | 3.7252 | 1.7498 | 0.00035244 | 0.00085251 | 0.11925 | 0.11925 | 0.11925 | 0.9961 | -0.052999 | 0.99628 | -0.043142 | 18.489
84 | -0.29202 | -0.14143 | 0.29202 | 0.14093 | 2.4826e-06 | -0.00050067 | 0.00939 | 0.0093836 | 0.00939 | 0.99751 | -0.012823 | 0.99752 | -0.012896 | 4.2682
85 | 6.2983 | 2.8611 | -6.2947 | -2.9321 | 0.0036337 | -0.070968 | 0.20019 | 0.20108 | 0.20108 | 0.99752 | -0.012896 | 0.99692 | -0.015709 | 15.7584
86 | -3.8681 | -1.819 | 3.8691 | 1.8214 | 0.00099231 | 0.0024197 | 0.12385 | 0.12385 | 0.12385 | 0.99628 | -0.043142 | 0.99675 | -0.016446 | 19.202
87 | 5.6379 | 2.6462 | -5.6379 | -2.6471 | 3.7348e-05 | -0.00090662 | 0.18037 | 0.18038 | 0.18038 | 0.99677 | -0.016366 | 0.99676 | -0.016396 | 14.1365
88 | -5.6379 | -2.6462 | 5.6387 | 2.6261 | 0.00082491 | -0.020057 | 0.18037 | 0.18012 | 0.18037 | 0.99677 | -0.016366 | 0.99692 | -0.015709 | 14.1356
89 | 5.4025 | 2.5331 | -5.4025 | -2.5335 | 6.1864e-05 | -0.00038366 | 0.17281 | 0.17281 | 0.17281 | 0.99676 | -0.016396 | 0.99675 | -0.016446 | 27.0868
90 | 0.36191 | 0.16364 | -0.36183 | -0.17503 | 8.6063e-05 | -0.011399 | 0.011501 | 0.011641 | 0.011641 | 0.99692 | -0.015709 | 0.9967 | -0.013794 | 5.2916
91 | 0.29403 | 0.14237 | -0.29403 | -0.1424 | 5.0417e-06 | -3.4357e-05 | 0.0094597 | 0.0094602 | 0.0094602 | 0.99692 | -0.015709 | 0.9969 | -0.015822 | 4.5049
92 | 1.5334 | 0.71205 | -1.532 | -0.72188 | 0.0013861 | -0.0098271 | 0.048964 | 0.04909 | 0.04909 | 0.99675 | -0.016446 | 0.99591 | -0.0091698 | 22.3136
93 | 0.36183 | 0.17503 | -0.36182 | -0.17524 | 1.57e-06 | -0.00020532 | 0.011641 | 0.011644 | 0.011644 | 0.9967 | -0.013794 | 0.99669 | -0.013756 | 5.2927
94 | 11.5088 | 5.2391 | -11.5087 | -5.2395 | 8.1557e-05 | -0.00044736 | 0.36587 | 0.36587 | 0.36587 | 0.99772 | -0.011771 | 0.99771 | -0.011807 | 28.6735
95 | 0.26487 | 0.12412 | -0.26486 | -0.12417 | 5.3548e-06 | -4.5948e-05 | 0.0084871 | 0.0084877 | 0.0084877 | 0.99492 | -0.015726 | 0.9949 | -0.015876 | 4.0417
96 | -0.26487 | -0.12412 | 0.26493 | 0.12361 | 5.9828e-05 | -0.000514 | 0.0084871 | 0.0084803 | 0.0084871 | 0.99492 | -0.015726 | 0.99516 | -0.01404 | 4.0415
97 | 0.13307 | 0.06034 | -0.13307 | -0.060387 | 1.2939e-06 | -4.6931e-05 | 0.0042394 | 0.00424 | 0.00424 | 0.9949 | -0.015876 | 0.99489 | -0.015955 | 2.019
98 | 0.32181 | 0.14976 | -0.32177 | -0.15582 | 3.6582e-05 | -0.0060561 | 0.010296 | 0.010372 | 0.010372 | 0.99516 | -0.01404 | 0.99506 | -0.013093 | 4.7144
99 | -0.58673 | -0.27337 | 0.58675 | 0.27276 | 1.2281e-05 | -0.00061362 | 0.018777 | 0.018769 | 0.018777 | 0.99516 | -0.01404 | 0.99518 | -0.014207 | 8.5348
100 | 11.4192 | 5.1962 | -11.4186 | -5.1996 | 0.00061753 | -0.003446 | 0.363 | 0.36304 | 0.36304 | 0.99771 | -0.011807 | 0.99766 | -0.012084 | 28.4516
101 | -19.473 | -8.7611 | 19.4802 | 8.7498 | 0.0071775 | -0.011286 | 0.61688 | 0.6167 | 0.61688 | 0.99923 | -0.0039905 | 0.99962 | -0.0019956 | 48.3452
102 | -0.13306 | -0.064444 | 0.13306 | 0.064388 | 1.5947e-06 | -5.6472e-05 | 0.00429 | 0.0042893 | 0.00429 | 0.99485 | -0.015785 | 0.99486 | -0.015706 | 2.0429
103 | -0.13306 | -0.064388 | 0.13307 | 0.060387 | 4.1109e-06 | -0.0040006 | 0.0042893 | 0.00424 | 0.0042893 | 0.99486 | -0.015706 | 0.99489 | -0.015955 | 1.9497
104 | 0.47634 | 0.22263 | -0.47632 | -0.22458 | 2.5636e-05 | -0.0019456 | 0.015244 | 0.015268 | 0.015268 | 0.99574 | -0.010352 | 0.99569 | -0.0099157 | 6.9398
105 | -0.47634 | -0.22263 | 0.47637 | 0.22258 | 2.433e-05 | -5.4327e-05 | 0.015244 | 0.015243 | 0.015244 | 0.99574 | -0.010352 | 0.99579 | -0.0099704 | 7.2588
106 | 0.27783 | 0.12845 | -0.27782 | -0.13 | 6.9104e-06 | -0.0015504 | 0.0088742 | 0.0088932 | 0.0088932 | 0.99569 | -0.0099157 | 0.99566 | -0.0097183 | 4.0424
107 | -0.71121 | -0.33632 | 0.71129 | 0.33627 | 7.9194e-05 | -5.1571e-05 | 0.022807 | 0.022805 | 0.022807 | 0.99579 | -0.0099704 | 0.99591 | -0.0091698 | 10.8603
108 | 0.32177 | 0.15582 | -0.32177 | -0.15584 | 4.1356e-06 | -2.2914e-05 | 0.010372 | 0.010372 | 0.010372 | 0.99506 | -0.013093 | 0.99504 | -0.013178 | 4.9391
109 | -0.82016 | -0.3858 | 0.82072 | 0.38561 | 0.00056363 | -0.00018859 | 0.026291 | 0.026285 | 0.026291 | 0.99518 | -0.014207 | 0.99591 | -0.0091698 | 12.5196
110 | 0.27782 | 0.13 | -0.27781 | -0.13433 | 1.947e-05 | -0.0043324 | 0.0088932 | 0.0089473 | 0.0089473 | 0.99566 | -0.0097183 | 0.9956 | -0.0091319 | 4.0669
111 | -0.29719 | -0.14394 | 0.2972 | 0.14387 | 1.068e-05 | -6.7109e-05 | 0.0096889 | 0.009688 | 0.0096889 | 0.98386 | -0.35079 | 0.98389 | -0.35055 | 4.6138
112 | 2.3962 | 1.1251 | -2.3945 | -1.1296 | 0.0017561 | -0.0045117 | 0.077669 | 0.077732 | 0.077732 | 0.98389 | -0.35055 | 0.98322 | -0.34457 | 35.3326
113 | 2.1431 | 1.0079 | -2.1425 | -1.0099 | 0.00059886 | -0.0019625 | 0.069534 | 0.069561 | 0.069561 | 0.98322 | -0.34457 | 0.98296 | -0.34229 | 31.6184
114 | 0.25135 | 0.12164 | -0.25135 | -0.12173 | 3.7357e-07 | -9.5978e-05 | 0.0081983 | 0.0081995 | 0.0081995 | 0.98322 | -0.34457 | 0.98322 | -0.34456 | 3.7271
115 | 2.1425 | 1.0099 | -2.1424 | -1.0102 | 0.00010868 | -0.00035587 | 0.069561 | 0.069565 | 0.069565 | 0.98296 | -0.34229 | 0.98292 | -0.34187 | 31.6206
116 | 2.0313 | 0.95641 | -2.0311 | -0.95684 | 0.00011526 | -0.00042379 | 0.065939 | 0.065944 | 0.065944 | 0.98292 | -0.34187 | 0.98287 | -0.34141 | 29.9747
117 | 1.9134 | 0.89981 | -1.9132 | -0.90062 | 0.00019454 | -0.00081356 | 0.062102 | 0.062113 | 0.062113 | 0.98287 | -0.34141 | 0.98277 | -0.34058 | 28.233
118 | 0.27781 | 0.13433 | -0.27778 | -0.13453 | 2.6582e-05 | -0.00020379 | 0.0089473 | 0.0089501 | 0.0089501 | 0.9956 | -0.0091319 | 0.9955 | -0.0097646 | 4.2619
119 | -0.38722 | -0.18754 | 0.38722 | 0.1874 | 1.2098e-06 | -0.00013705 | 0.012485 | 0.012483 | 0.012485 | 0.99482 | -0.063687 | 0.99483 | -0.063715 | 5.6748
120 | 0.50487 | 0.23932 | -0.50481 | -0.24341 | 6.1094e-05 | -0.0040825 | 0.016213 | 0.016264 | 0.016264 | 0.99483 | -0.063715 | 0.99472 | -0.06269 | 7.3928
121 | -0.89209 | -0.42672 | 0.89224 | 0.42357 | 0.0001486 | -0.0031551 | 0.028695 | 0.028655 | 0.028695 | 0.99483 | -0.063715 | 0.99498 | -0.065114 | 13.0434
122 | 0.23533 | 0.11303 | -0.23533 | -0.11398 | 3.0832e-06 | -0.00094807 | 0.0075765 | 0.0075884 | 0.0075884 | 0.99472 | -0.06269 | 0.9947 | -0.062577 | 3.4493
123 | 0.26948 | 0.13038 | -0.26947 | -0.13047 | 1.0802e-05 | -8.81e-05 | 0.0086877 | 0.0086889 | 0.0086889 | 0.99472 | -0.06269 | 0.99467 | -0.062955 | 4.1376
124 | 8.7809 | 4.065 | -8.7793 | -4.0805 | 0.001606 | -0.015489 | 0.28074 | 0.28094 | 0.28094 | 0.99498 | -0.065114 | 0.99479 | -0.06597 | 22.0169
125 | -9.6731 | -4.4886 | 9.6739 | 4.4829 | 0.00072526 | -0.0056945 | 0.30939 | 0.30932 | 0.30939 | 0.99498 | -0.065114 | 0.99506 | -0.064762 | 24.2469
126 | 0.26947 | 0.13047 | -0.26946 | -0.13051 | 4.8661e-06 | -3.9677e-05 | 0.0086889 | 0.0086894 | 0.0086894 | 0.99467 | -0.062955 | 0.99465 | -0.063075 | 4.1378
127 | 0.30025 | 0.14444 | -0.30024 | -0.14541 | 5.2705e-06 | -0.00097024 | 0.0097297 | 0.009742 | 0.009742 | 0.98855 | -0.045348 | 0.98853 | -0.045196 | 4.4282
128 | -0.30025 | -0.14444 | 0.30027 | 0.14431 | 2.1146e-05 | -0.00013305 | 0.0097297 | 0.0097278 | 0.0097297 | 0.98855 | -0.045348 | 0.98862 | -0.044871 | 4.6332
129 | -0.40321 | -0.19417 | 0.40337 | 0.19367 | 0.00015651 | -0.00050277 | 0.013068 | 0.01306 | 0.013068 | 0.98862 | -0.044871 | 0.98903 | -0.042243 | 6.2227
130 | -9.8823 | -4.5838 | 9.8858 | 4.5927 | 0.0034773 | 0.0088165 | 0.31603 | 0.31603 | 0.31603 | 0.99506 | -0.064762 | 0.99571 | -0.027866 | 24.4988
131 | -0.67767 | -0.32531 | 0.6778 | 0.32081 | 0.00012462 | -0.0045047 | 0.021941 | 0.021884 | 0.021941 | 0.98903 | -0.042243 | 0.9892 | -0.043788 | 9.973
132 | 0.2743 | 0.13165 | -0.27429 | -0.13285 | 5.4292e-06 | -0.0012007 | 0.0088805 | 0.0088957 | 0.0088957 | 0.98903 | -0.042243 | 0.98901 | -0.042072 | 4.0435
133 | -0.6778 | -0.32081 | 0.67782 | 0.32002 | 2.1799e-05 | -0.00079052 | 0.021884 | 0.021874 | 0.021884 | 0.9892 | -0.043788 | 0.98923 | -0.044054 | 9.9471
134 | -0.89125 | -0.42339 | 0.89188 | 0.42328 | 0.00063398 | -0.00010477 | 0.028794 | 0.028787 | 0.028794 | 0.98923 | -0.044054 | 0.98997 | -0.039015 | 13.7113
135 | -10.1425 | -4.717 | 10.1427 | 4.7173 | 0.00013172 | 0.00033498 | 0.3243 | 0.3243 | 0.3243 | 0.99571 | -0.027866 | 0.99573 | -0.026505 | 25.1393
136 | -0.18368 | -0.088961 | 0.18369 | 0.088897 | 3.7059e-06 | -6.4333e-05 | 0.0059969 | 0.005996 | 0.0059969 | 0.98245 | -0.33797 | 0.98247 | -0.33784 | 2.8557
137 | -0.18369 | -0.088897 | 0.18369 | 0.085109 | 7.8315e-06 | -0.0037886 | 0.005996 | 0.0059484 | 0.005996 | 0.98247 | -0.33784 | 0.98251 | -0.33819 | 2.7255
138 | 0.082866 | 0.037165 | -0.082865 | -0.038759 | 6.6207e-07 | -0.0015935 | 0.0026684 | 0.0026879 | 0.0026879 | 0.98251 | -0.33819 | 0.9825 | -0.33813 | 1.2218
139 | -1.9126 | -0.90295 | 1.9132 | 0.90062 | 0.00055764 | -0.0023294 | 0.062144 | 0.062113 | 0.062144 | 0.98251 | -0.33819 | 0.98277 | -0.34058 | 28.2472
140 | 1.6461 | 0.78067 | -1.6459 | -0.78144 | 0.00013345 | -0.00076428 | 0.053528 | 0.053538 | 0.053538 | 0.98251 | -0.33819 | 0.98243 | -0.33752 | 24.3355
141 | 0.082865 | 0.038759 | -0.082865 | -0.040133 | 5.7887e-07 | -0.0013742 | 0.0026879 | 0.0027053 | 0.0027053 | 0.9825 | -0.33813 | 0.98249 | -0.33807 | 1.2297
142 | 1.3868 | 0.65595 | -1.3867 | -0.65676 | 9.8437e-05 | -0.00080673 | 0.045079 | 0.04509 | 0.04509 | 0.98243 | -0.33752 | 0.98237 | -0.33693 | 20.4952
143 | 1.3867 | 0.65676 | -1.3864 | -0.65922 | 0.00030097 | -0.0024634 | 0.04509 | 0.045122 | 0.045122 | 0.98237 | -0.33693 | 0.98217 | -0.33512 | 20.5099
144 | -10.1427 | -4.7173 | 10.1465 | 4.6897 | 0.0038829 | -0.027633 | 0.3243 | 0.32393 | 0.3243 | 0.99573 | -0.026505 | 0.99613 | -0.02471 | 25.4151
145 | -10.1465 | -4.6897 | 10.1469 | 4.687 | 0.0003854 | -0.0027476 | 0.32393 | 0.3239 | 0.32393 | 0.99613 | -0.02471 | 0.99617 | -0.024529 | 25.3866
146 | -19.4802 | -8.7498 | 19.4821 | 8.7469 | 0.0018362 | -0.0028906 | 0.6167 | 0.61666 | 0.6167 | 0.99962 | -0.0019956 | 0.99972 | -0.0014831 | 48.331
147 | -19.5768 | -8.7928 | 19.5787 | 8.7897 | 0.0019587 | -0.003044 | 0.61969 | 0.61965 | 0.61969 | 0.99972 | -0.0014831 | 0.99982 | -0.000939 | 48.5654
148 | 0.36014 | 0.17429 | -0.36014 | -0.17442 | 9.7602e-07 | -0.00013046 | 0.011552 | 0.011554 | 0.011554 | 0.99982 | -0.000939 | 0.99982 | -0.00091541 | 5.2516
149 | -19.9389 | -8.964 | 19.9423 | 8.9589 | 0.0034548 | -0.0051073 | 0.63119 | 0.63111 | 0.63119 | 0.99982 | -0.000939 | 1 | 0 | 49.4665
150 | 11.4186 | 5.1996 | -11.4158 | -5.2153 | 0.0028107 | -0.015667 | 0.36304 | 0.36325 | 0.36325 | 0.99766 | -0.012084 | 0.9974 | -0.013333 | 28.4678
151 | -0.34598 | -0.16757 | 0.34599 | 0.16707 | 3.6952e-06 | -0.00049808 | 0.011302 | 0.011295 | 0.011302 | 0.98194 | -0.33303 | 0.98195 | -0.33313 | 5.1371
152 | -0.51842 | -0.24657 | 0.51847 | 0.24337 | 5.3062e-05 | -0.003205 | 0.016877 | 0.016836 | 0.016877 | 0.98195 | -0.33313 | 0.98204 | -0.33397 | 7.6712
153 | 0.17243 | 0.079501 | -0.17243 | -0.082372 | 5.2243e-06 | -0.0028713 | 0.005582 | 0.0056179 | 0.0056179 | 0.98195 | -0.33313 | 0.98192 | -0.33288 | 2.5536
154 | -0.88576 | -0.4206 | 0.88588 | 0.41807 | 0.00012346 | -0.0025298 | 0.028824 | 0.028791 | 0.028824 | 0.98204 | -0.33397 | 0.98217 | -0.33512 | 13.1016
155 | 0.36729 | 0.17723 | -0.36728 | -0.17788 | 5.4141e-06 | -0.00064775 | 0.011988 | 0.011996 | 0.011996 | 0.98204 | -0.33397 | 0.98203 | -0.33384 | 5.4528
156 | 0.17243 | 0.082372 | -0.17243 | -0.082833 | 8.4423e-07 | -0.00046052 | 0.0056179 | 0.0056238 | 0.0056238 | 0.98192 | -0.33288 | 0.98191 | -0.33284 | 2.5563
157 | 0.50056 | 0.24115 | -0.50054 | -0.24242 | 1.981e-05 | -0.0012743 | 0.016331 | 0.016347 | 0.016347 | 0.98217 | -0.33512 | 0.98213 | -0.33478 | 7.4305
158 | 0.089126 | 0.042489 | -0.089126 | -0.043166 | 3.3177e-07 | -0.00067687 | 0.0029028 | 0.0029114 | 0.0029114 | 0.98191 | -0.33284 | 0.98191 | -0.33281 | 1.3234
159 | -1.1473 | -0.54698 | 1.1475 | 0.54701 | 0.00016429 | 2.4352e-05 | 0.037063 | 0.037062 | 0.037063 | 0.98997 | -0.039015 | 0.99012 | -0.038015 | 17.6488
160 | -1.1475 | -0.54701 | 1.1487 | 0.53116 | 0.0012628 | -0.015849 | 0.037062 | 0.036861 | 0.037062 | 0.99012 | -0.038015 | 0.99114 | -0.046944 | 16.8462
161 | -1.3119 | -0.61016 | 1.3134 | 0.59559 | 0.0015102 | -0.014574 | 0.042141 | 0.041958 | 0.042141 | 0.99114 | -0.046944 | 0.99221 | -0.055797 | 19.155
162 | 0.1632 | 0.079004 | -0.1632 | -0.079042 | 1.6569e-06 | -3.8061e-05 | 0.0052811 | 0.0052816 | 0.0052816 | 0.99114 | -0.046944 | 0.99113 | -0.047011 | 2.515
163 | -1.3134 | -0.59559 | 1.3135 | 0.59481 | 8.0378e-05 | -0.00078026 | 0.041958 | 0.041949 | 0.041958 | 0.99221 | -0.055797 | 0.99227 | -0.056253 | 19.072
164 | -1.7209 | -0.79213 | 1.7211 | 0.79221 | 0.00018759 | 7.6756e-05 | 0.055115 | 0.055115 | 0.055115 | 0.99227 | -0.056253 | 0.99238 | -0.055397 | 26.2454
165 | -10.4797 | -4.8481 | 10.4803 | 4.8496 | 0.00057947 | 0.0014787 | 0.33461 | 0.33461 | 0.33461 | 0.99617 | -0.024529 | 0.99627 | -0.018719 | 25.9388
166 | 0.22012 | 0.09888 | -0.2201 | -0.10416 | 1.469e-05 | -0.0052811 | 0.006992 | 0.0070561 | 0.0070561 | 0.99627 | -0.018719 | 0.99621 | -0.0182 | 3.2073
167 | -10.7983 | -4.9958 | 10.8054 | 4.9515 | 0.0070992 | -0.044338 | 0.34475 | 0.34417 | 0.34475 | 0.99627 | -0.018719 | 0.99695 | -0.015529 | 27.0181
168 | 0.097916 | 0.047334 | -0.097915 | -0.047422 | 1.324e-06 | -8.7802e-05 | 0.0031513 | 0.0031524 | 0.0031524 | 0.99627 | -0.018719 | 0.99625 | -0.018808 | 1.5012
169 | 0.2201 | 0.10416 | -0.2201 | -0.10477 | 1.7032e-06 | -0.00060603 | 0.0070561 | 0.0070636 | 0.0070636 | 0.99621 | -0.0182 | 0.9962 | -0.018136 | 3.2107
170 | -11.1164 | -5.1019 | 11.1213 | 5.0732 | 0.0048827 | -0.028767 | 0.35417 | 0.35379 | 0.35417 | 0.99695 | -0.015529 | 0.9974 | -0.013333 | 27.7561
171 | 0.311 | 0.15047 | -0.311 | -0.15062 | 8.8999e-07 | -0.00015778 | 0.010004 | 0.010006 | 0.010006 | 0.99695 | -0.015529 | 0.99695 | -0.015504 | 4.5481
172 | 0.11204 | 0.052431 | -0.11204 | -0.053196 | 5.549e-07 | -0.00076432 | 0.0035846 | 0.003594 | 0.003594 | 0.9962 | -0.018136 | 0.99619 | -0.018095 | 1.6336
173 | 0.29448 | 0.1421 | -0.29448 | -0.14262 | 2.6494e-06 | -0.00052518 | 0.0094636 | 0.0094702 | 0.0094702 | 0.9974 | -0.013333 | 0.9974 | -0.013255 | 4.3046
174 | 0.11204 | 0.053196 | -0.11204 | -0.05378 | 4.2623e-07 | -0.00058435 | 0.003594 | 0.0036013 | 0.0036013 | 0.99619 | -0.018095 | 0.99619 | -0.018063 | 1.637
175 | -0.54062 | -0.25991 | 0.54064 | 0.25906 | 1.4805e-05 | -0.00085419 | 0.017441 | 0.01743 | 0.017441 | 0.99284 | -0.070618 | 0.99287 | -0.070852 | 7.9278
176 | 0.31429 | 0.1503 | -0.31428 | -0.15133 | 6.0277e-06 | -0.0010326 | 0.010129 | 0.010142 | 0.010142 | 0.99284 | -0.070618 | 0.99283 | -0.070454 | 4.6101
177 | -0.54064 | -0.25906 | 0.54066 | 0.2576 | 2.5251e-05 | -0.0014595 | 0.01743 | 0.017412 | 0.01743 | 0.99287 | -0.070852 | 0.99291 | -0.071246 | 7.9229
178 | 0.31428 | 0.15133 | -0.31428 | -0.15145 | 7.1173e-07 | -0.00012175 | 0.010142 | 0.010144 | 0.010144 | 0.99283 | -0.070454 | 0.99282 | -0.070435 | 4.6108
179 | -0.68666 | -0.32515 | 0.68668 | 0.3247 | 1.2554e-05 | -0.00045009 | 0.022089 | 0.022083 | 0.022089 | 0.99291 | -0.071246 | 0.99293 | -0.071397 | 10.0404
180 | 0.073919 | 0.034584 | -0.073919 | -0.035324 | 2.3723e-07 | -0.00074008 | 0.0023727 | 0.0023819 | 0.0023819 | 0.99291 | -0.071246 | 0.99291 | -0.07122 | 1.0827
181 | 0.31428 | 0.15145 | -0.31428 | -0.15221 | 4.46e-06 | -0.00076206 | 0.010144 | 0.010154 | 0.010154 | 0.99282 | -0.070435 | 0.99281 | -0.070312 | 4.6152
182 | 0.073919 | 0.035324 | -0.073919 | -0.0358 | 1.5383e-07 | -0.00047686 | 0.0023819 | 0.0023879 | 0.0023879 | 0.99291 | -0.07122 | 0.99291 | -0.071202 | 1.0854
183 | -0.09701 | -0.046984 | 0.09701 | 0.046468 | 2.8524e-07 | -0.00051615 | 0.0031292 | 0.0031227 | 0.0031292 | 0.99438 | -0.067356 | 0.99438 | -0.067382 | 1.4223
184 | -0.19082 | -0.09227 | 0.19082 | 0.09216 | 2.3532e-07 | -0.00010976 | 0.0061546 | 0.0061532 | 0.0061546 | 0.99417 | -0.067863 | 0.99417 | -0.067873 | 2.7976
185 | 0.19082 | 0.09227 | -0.19082 | -0.092419 | 3.1979e-07 | -0.00014909 | 0.0061546 | 0.0061565 | 0.0061565 | 0.99417 | -0.067863 | 0.99417 | -0.067848 | 2.7984
186 | -0.11204 | -0.054263 | 0.11204 | 0.05378 | 3.5341e-07 | -0.00048272 | 0.0036074 | 0.0036013 | 0.0036074 | 0.99619 | -0.018036 | 0.99619 | -0.018063 | 1.6397
187 | 0.072583 | 0.034137 | -0.072583 | -0.035153 | 3.1327e-07 | -0.0010168 | 0.0023281 | 0.0023409 | 0.0023409 | 0.99455 | -0.066972 | 0.99454 | -0.066935 | 1.064
188 | 0.085093 | 0.040948 | -0.085093 | -0.041213 | 1.1346e-07 | -0.00026456 | 0.0027467 | 0.0027501 | 0.0027501 | 0.99247 | -0.056119 | 0.99247 | -0.056108 | 1.25

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 19.9563 | 8.9694

## res_load
| p_mw | q_mvar
0 | 0.27712 | 0.13422
1 | 0.30393 | 0.1472
2 | 0.20584 | 0.099694
3 | 0.40411 | 0.19572
4 | 0.19908 | 0.096417
5 | 0.07305 | 0.03538
6 | 0.31997 | 0.15497
7 | 0.19272 | 0.093338
8 | 0.13415 | 0.064974
9 | 0.39333 | 0.1905
10 | 0.094169 | 0.045608
11 | 0.29327 | 0.14204
12 | 0.17975 | 0.087057
13 | 0.089425 | 0.043311
14 | 0.38366 | 0.18582
15 | 0.28931 | 0.14012
16 | 0.087169 | 0.042218
17 | 0.22566 | 0.10929
18 | 0.24953 | 0.12085
19 | 0.14217 | 0.068857
20 | 0.37082 | 0.1796
21 | 0.1057 | 0.051193
22 | 0.12961 | 0.062774
23 | 0.10607 | 0.051374
24 | 0.081156 | 0.039306
25 | 0.37474 | 0.18149
26 | 0.34204 | 0.16566
27 | 0.072079 | 0.03491
28 | 0.27217 | 0.13182
29 | 0.19002 | 0.092031
30 | 0.21127 | 0.10232
31 | 0.22287 | 0.10794
32 | 0.24166 | 0.11704
33 | 0.32674 | 0.15825
34 | 0.19821 | 0.095998
35 | 0.21398 | 0.10363
36 | 0.29202 | 0.14143
37 | 0.1429 | 0.069212
38 | 0.23534 | 0.11398
39 | 0.29403 | 0.1424
40 | 0.1451 | 0.070277
41 | 0.13179 | 0.06383
42 | 0.08952 | 0.043356
43 | 0.36182 | 0.17524
44 | 0.13306 | 0.064444
45 | 0.19848 | 0.09613
46 | 0.23484 | 0.11374
47 | 0.23341 | 0.11305
48 | 0.32177 | 0.15584
49 | 0.29719 | 0.14394
50 | 0.25135 | 0.12173
51 | 0.11115 | 0.053832
52 | 0.11775 | 0.05703
53 | 0.27778 | 0.13453
54 | 0.38722 | 0.18754
55 | 0.26946 | 0.13051
56 | 0.30024 | 0.14541
57 | 0.10295 | 0.049859
58 | 0.23533 | 0.11398
59 | 0.20845 | 0.10096
60 | 0.27429 | 0.13285
61 | 0.21343 | 0.10337
62 | 0.25675 | 0.12435
63 | 0.18368 | 0.088961
64 | 0.2591 | 0.12549
65 | 0.082865 | 0.040133
66 | 0.094727 | 0.045878
67 | 0.34598 | 0.16757
68 | 0.36014 | 0.17442
69 | 0.36728 | 0.17788
70 | 0.50054 | 0.24242
71 | 0.0833 | 0.040344
72 | 0.089126 | 0.043166
73 | 0.25541 | 0.1237
74 | 0.1632 | 0.079042
75 | 0.40742 | 0.19732
76 | 0.33277 | 0.16117
77 | 0.097915 | 0.047422
78 | 0.10806 | 0.052335
79 | 0.311 | 0.15062
80 | 0.29448 | 0.14262
81 | 0.22633 | 0.10962
82 | 0.09027 | 0.04372
83 | 0.31428 | 0.15221
84 | 0.073919 | 0.0358
85 | 0.09701 | 0.046984
86 | 0.09967 | 0.048272
87 | 0.19082 | 0.092419
88 | 0.11204 | 0.054263
89 | 0.072583 | 0.035153
90 | 0.085093 | 0.041213

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1