## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_524_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_524_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_524_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_524_0_node_7 | 20 | n |  | TRUE
4 | bus_MV_524_0_node_63 | 20 | n |  | TRUE
5 | bus_MV_524_0_node_153 | 20 | n |  | TRUE
6 | bus_MV_524_0_node_62 | 20 | n |  | TRUE
7 | bus_MV_524_0_node_22 | 20 | n |  | TRUE
8 | bus_MV_524_0_node_23 | 20 | n |  | TRUE
9 | bus_MV_524_0_node_24 | 20 | n |  | TRUE
10 | bus_MV_524_0_node_152 | 20 | n |  | TRUE
11 | bus_MV_524_0_node_3 | 20 | n |  | TRUE
12 | bus_MV_524_0_node_4 | 20 | n |  | TRUE
13 | bus_MV_524_0_node_169 | 20 | n |  | TRUE
14 | bus_MV_524_0_node_20 | 20 | n |  | TRUE
15 | bus_MV_524_0_node_168 | 20 | n |  | TRUE
16 | bus_MV_524_0_node_5 | 20 | n |  | TRUE
17 | bus_MV_524_0_node_6 | 20 | n |  | TRUE
18 | bus_MV_524_0_node_161 | 20 | n |  | TRUE
19 | bus_MV_524_0_node_8 | 20 | n |  | TRUE
20 | bus_MV_524_0_node_15 | 20 | n |  | TRUE
21 | bus_MV_524_0_node_133 | 20 | n |  | TRUE
22 | bus_MV_524_0_node_164 | 20 | n |  | TRUE
23 | bus_MV_524_0_node_9 | 20 | n |  | TRUE
24 | bus_MV_524_0_node_73 | 20 | n |  | TRUE
25 | bus_MV_524_0_node_10 | 20 | n |  | TRUE
26 | bus_MV_524_0_node_52 | 20 | n |  | TRUE
27 | bus_MV_524_0_node_46 | 20 | n |  | TRUE
28 | bus_MV_524_0_node_47 | 20 | n |  | TRUE
29 | bus_MV_524_0_node_162 | 20 | n |  | TRUE
30 | bus_MV_524_0_node_11 | 20 | n |  | TRUE
31 | bus_MV_524_0_node_165 | 20 | n |  | TRUE
32 | bus_MV_524_0_node_34 | 20 | n |  | TRUE
33 | bus_MV_524_0_node_13 | 20 | n |  | TRUE
34 | bus_MV_524_0_node_44 | 20 | n |  | TRUE
35 | bus_MV_524_0_node_14 | 20 | n |  | TRUE
36 | bus_MV_524_0_node_167 | 20 | n |  | TRUE
37 | bus_MV_524_0_node_80 | 20 | n |  | TRUE
38 | bus_MV_524_0_node_16 | 20 | n |  | TRUE
39 | bus_MV_524_0_node_158 | 20 | n |  | TRUE
40 | bus_MV_524_0_node_78 | 20 | n |  | TRUE
41 | bus_MV_524_0_node_17 | 20 | n |  | TRUE
42 | bus_MV_524_0_node_18 | 20 | n |  | TRUE
43 | bus_MV_524_0_node_19 | 20 | n |  | TRUE
44 | bus_MV_524_0_node_53 | 20 | n |  | TRUE
45 | bus_MV_524_0_node_26 | 20 | n |  | TRUE
46 | bus_MV_524_0_node_27 | 20 | n |  | TRUE
47 | bus_MV_524_0_node_21 | 20 | n |  | TRUE
48 | bus_MV_524_0_node_28 | 20 | n |  | TRUE
49 | bus_MV_524_0_node_29 | 20 | n |  | TRUE
50 | bus_MV_524_0_node_163 | 20 | n |  | TRUE
51 | bus_MV_524_0_node_45 | 20 | n |  | TRUE
52 | bus_MV_524_0_node_54 | 20 | n |  | TRUE
53 | bus_MV_524_0_node_154 | 20 | n |  | TRUE
54 | bus_MV_524_0_node_60 | 20 | n |  | TRUE
55 | bus_MV_524_0_node_150 | 20 | n |  | TRUE
56 | bus_MV_524_0_node_58 | 20 | n |  | TRUE
57 | bus_MV_524_0_node_95 | 20 | n |  | TRUE
58 | bus_MV_524_0_node_33 | 20 | n |  | TRUE
59 | bus_MV_524_0_node_40 | 20 | n |  | TRUE
60 | bus_MV_524_0_node_37 | 20 | n |  | TRUE
61 | bus_MV_524_0_node_43 | 20 | n |  | TRUE
62 | bus_MV_524_0_node_38 | 20 | n |  | TRUE
63 | bus_MV_524_0_node_77 | 20 | n |  | TRUE
64 | bus_MV_524_0_node_142 | 20 | n |  | TRUE
65 | bus_MV_524_0_node_139 | 20 | n |  | TRUE
66 | bus_MV_524_0_node_89 | 20 | n |  | TRUE
67 | bus_MV_524_0_node_90 | 20 | n |  | TRUE
68 | bus_MV_524_0_node_30 | 20 | n |  | TRUE
69 | bus_MV_524_0_node_31 | 20 | n |  | TRUE
70 | bus_MV_524_0_node_74 | 20 | n |  | TRUE
71 | bus_MV_524_0_node_32 | 20 | n |  | TRUE
72 | bus_MV_524_0_node_79 | 20 | n |  | TRUE
73 | bus_MV_524_0_node_76 | 20 | n |  | TRUE
74 | bus_MV_524_0_node_75 | 20 | n |  | TRUE
75 | bus_MV_524_0_node_35 | 20 | n |  | TRUE
76 | bus_MV_524_0_node_36 | 20 | n |  | TRUE
77 | bus_MV_524_0_node_41 | 20 | n |  | TRUE
78 | bus_MV_524_0_node_42 | 20 | n |  | TRUE
79 | bus_MV_524_0_node_143 | 20 | n |  | TRUE
80 | bus_MV_524_0_node_48 | 20 | n |  | TRUE
81 | bus_MV_524_0_node_49 | 20 | n |  | TRUE
82 | bus_MV_524_0_node_50 | 20 | n |  | TRUE
83 | bus_MV_524_0_node_64 | 20 | n |  | TRUE
84 | bus_MV_524_0_node_51 | 20 | n |  | TRUE
85 | bus_MV_524_0_node_117 | 20 | n |  | TRUE
86 | bus_MV_524_0_node_118 | 20 | n |  | TRUE
87 | bus_MV_524_0_node_116 | 20 | n |  | TRUE
88 | bus_MV_524_0_node_65 | 20 | n |  | TRUE
89 | bus_MV_524_0_node_148 | 20 | n |  | TRUE
90 | bus_MV_524_0_node_137 | 20 | n |  | TRUE
91 | bus_MV_524_0_node_138 | 20 | n |  | TRUE
92 | bus_MV_524_0_node_135 | 20 | n |  | TRUE
93 | bus_MV_524_0_node_55 | 20 | n |  | TRUE
94 | bus_MV_524_0_node_56 | 20 | n |  | TRUE
95 | bus_MV_524_0_node_57 | 20 | n |  | TRUE
96 | bus_MV_524_0_node_59 | 20 | n |  | TRUE
97 | bus_MV_524_0_node_147 | 20 | n |  | TRUE
98 | bus_MV_524_0_node_61 | 20 | n |  | TRUE
99 | bus_MV_524_0_node_92 | 20 | n |  | TRUE
100 | bus_MV_524_0_node_88 | 20 | n |  | TRUE
101 | bus_MV_524_0_node_85 | 20 | n |  | TRUE
102 | bus_MV_524_0_node_155 | 20 | n |  | TRUE
103 | bus_MV_524_0_node_83 | 20 | n |  | TRUE
104 | bus_MV_524_0_node_66 | 20 | n |  | TRUE
105 | bus_MV_524_0_node_67 | 20 | n |  | TRUE
106 | bus_MV_524_0_node_93 | 20 | n |  | TRUE
107 | bus_MV_524_0_node_96 | 20 | n |  | TRUE
108 | bus_MV_524_0_node_94 | 20 | n |  | TRUE
109 | bus_MV_524_0_node_166 | 20 | n |  | TRUE
110 | bus_MV_524_0_node_151 | 20 | n |  | TRUE
111 | bus_MV_524_0_node_84 | 20 | n |  | TRUE
112 | bus_MV_524_0_node_170 | 20 | n |  | TRUE
113 | bus_MV_524_0_node_82 | 20 | n |  | TRUE
114 | bus_MV_524_0_node_69 | 20 | n |  | TRUE
115 | bus_MV_524_0_node_70 | 20 | n |  | TRUE
116 | bus_MV_524_0_node_71 | 20 | n |  | TRUE
117 | bus_MV_524_0_node_105 | 20 | n |  | TRUE
118 | bus_MV_524_0_node_72 | 20 | n |  | TRUE
119 | bus_MV_524_0_node_103 | 20 | n |  | TRUE
120 | bus_MV_524_0_node_115 | 20 | n |  | TRUE
121 | bus_MV_524_0_node_110 | 20 | n |  | TRUE
122 | bus_MV_524_0_node_104 | 20 | n |  | TRUE
123 | bus_MV_524_0_node_134 | 20 | n |  | TRUE
124 | bus_MV_524_0_node_81 | 20 | n |  | TRUE
125 | bus_MV_524_0_node_86 | 20 | n |  | TRUE
126 | bus_MV_524_0_node_87 | 20 | n |  | TRUE
127 | bus_MV_524_0_node_113 | 20 | n |  | TRUE
128 | bus_MV_524_0_node_160 | 20 | n |  | TRUE
129 | bus_MV_524_0_node_156 | 20 | n |  | TRUE
130 | bus_MV_524_0_node_112 | 20 | n |  | TRUE
131 | bus_MV_524_0_node_91 | 20 | n |  | TRUE
132 | bus_MV_524_0_node_131 | 20 | n |  | TRUE
133 | bus_MV_524_0_node_102 | 20 | n |  | TRUE
134 | bus_MV_524_0_node_130 | 20 | n |  | TRUE
135 | bus_MV_524_0_node_100 | 20 | n |  | TRUE
136 | bus_MV_524_0_node_101 | 20 | n |  | TRUE
137 | bus_MV_524_0_node_98 | 20 | n |  | TRUE
138 | bus_MV_524_0_node_114 | 20 | n |  | TRUE
139 | bus_MV_524_0_node_97 | 20 | n |  | TRUE
140 | bus_MV_524_0_node_99 | 20 | n |  | TRUE
141 | bus_MV_524_0_node_106 | 20 | n |  | TRUE
142 | bus_MV_524_0_node_107 | 20 | n |  | TRUE
143 | bus_MV_524_0_node_108 | 20 | n |  | TRUE
144 | bus_MV_524_0_node_109 | 20 | n |  | TRUE
145 | bus_MV_524_0_node_111 | 20 | n |  | TRUE
146 | bus_MV_524_0_node_141 | 20 | n |  | TRUE
147 | bus_MV_524_0_node_136 | 20 | n |  | TRUE
148 | bus_MV_524_0_node_119 | 20 | n |  | TRUE
149 | bus_MV_524_0_node_120 | 20 | n |  | TRUE
150 | bus_MV_524_0_node_121 | 20 | n |  | TRUE
151 | bus_MV_524_0_node_122 | 20 | n |  | TRUE
152 | bus_MV_524_0_node_123 | 20 | n |  | TRUE
153 | bus_MV_524_0_node_126 | 20 | n |  | TRUE
154 | bus_MV_524_0_node_157 | 20 | n |  | TRUE
155 | bus_MV_524_0_node_125 | 20 | n |  | TRUE
156 | bus_MV_524_0_node_146 | 20 | n |  | TRUE
157 | bus_MV_524_0_node_124 | 20 | n |  | TRUE
158 | bus_MV_524_0_node_149 | 20 | n |  | TRUE
159 | bus_MV_524_0_node_144 | 20 | n |  | TRUE
160 | bus_MV_524_0_node_145 | 20 | n |  | TRUE
161 | bus_MV_524_0_node_127 | 20 | n |  | TRUE
162 | bus_MV_524_0_node_128 | 20 | n |  | TRUE
163 | bus_MV_524_0_node_129 | 20 | n |  | TRUE
164 | bus_MV_524_0_node_159 | 20 | n |  | TRUE
165 | bus_HV_524_0_node_58 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_524_0_load_0 | 0 | 0.33656 | 0.163 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_524_0_load_153 | 5 | 0.20763 | 0.10056 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_524_0_load_152 | 10 | 0.16193 | 0.078426 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_524_0_load_169 | 13 | 0.13912 | 0.067381 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_524_0_load_20 | 14 | 0.30127 | 0.14591 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_524_0_load_168 | 15 | 0.16054 | 0.077752 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_524_0_load_161 | 18 | 0.37063 | 0.17951 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_524_0_load_133 | 21 | 0.11612 | 0.05624 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_524_0_load_164 | 22 | 0.37281 | 0.18056 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_524_0_load_73 | 24 | 0.27449 | 0.13294 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_524_0_load_52 | 26 | 0.27173 | 0.1316 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_524_0_load_162 | 29 | 0.22825 | 0.11055 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_524_0_load_165 | 31 | 0.093244 | 0.04516 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_524_0_load_44 | 34 | 0.37577 | 0.182 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_524_0_load_167 | 36 | 0.35524 | 0.17205 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_524_0_load_80 | 37 | 0.13636 | 0.06604 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_524_0_load_158 | 39 | 0.27505 | 0.13321 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_524_0_load_17 | 41 | 0.26718 | 0.1294 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_524_0_load_53 | 44 | 0.32618 | 0.15798 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_524_0_load_26 | 45 | 0.35407 | 0.17148 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_524_0_load_27 | 46 | 0.25601 | 0.12399 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_524_0_load_163 | 50 | 0.21623 | 0.10473 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_524_0_load_45 | 51 | 0.35101 | 0.17 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_524_0_load_54 | 52 | 0.24394 | 0.11815 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_524_0_load_150 | 55 | 0.27653 | 0.13393 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_524_0_load_33 | 58 | 0.34772 | 0.16841 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_524_0_load_40 | 59 | 0.14845 | 0.071899 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_524_0_load_142 | 64 | 0.076179 | 0.036895 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_524_0_load_139 | 65 | 0.086285 | 0.04179 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_524_0_load_89 | 66 | 0.072988 | 0.03535 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_524_0_load_30 | 68 | 0.19094 | 0.092476 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_524_0_load_74 | 70 | 0.17943 | 0.0869 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_524_0_load_79 | 72 | 0.33607 | 0.16277 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_524_0_load_75 | 74 | 0.10877 | 0.052679 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_524_0_load_35 | 75 | 0.17498 | 0.084747 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_524_0_load_41 | 77 | 0.25291 | 0.12249 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_524_0_load_143 | 79 | 0.10444 | 0.050584 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_524_0_load_48 | 80 | 0.38745 | 0.18765 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_524_0_load_64 | 83 | 0.4019 | 0.19465 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_524_0_load_116 | 87 | 0.097045 | 0.047001 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_524_0_load_148 | 89 | 0.40874 | 0.19796 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_524_0_load_137 | 90 | 0.12028 | 0.058254 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_524_0_load_135 | 92 | 0.071072 | 0.034422 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_524_0_load_57 | 95 | 0.36643 | 0.17747 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_524_0_load_147 | 97 | 0.19216 | 0.093065 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_524_0_load_61 | 98 | 0.232 | 0.11236 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_524_0_load_92 | 99 | 0.1055 | 0.051095 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_524_0_load_93 | 106 | 0.098707 | 0.047806 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_524_0_load_96 | 107 | 0.09073 | 0.043943 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_524_0_load_166 | 109 | 0.3685 | 0.17847 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_524_0_load_151 | 110 | 0.29749 | 0.14408 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_524_0_load_170 | 112 | 0.34475 | 0.16697 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_524_0_load_69 | 114 | 0.29632 | 0.14351 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_524_0_load_105 | 117 | 0.10367 | 0.050211 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_524_0_load_103 | 119 | 0.15092 | 0.073093 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_524_0_load_115 | 120 | 0.30182 | 0.14618 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_524_0_load_110 | 121 | 0.11075 | 0.053641 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_524_0_load_104 | 122 | 0.10936 | 0.052966 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_524_0_load_134 | 123 | 0.068767 | 0.033306 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_524_0_load_81 | 124 | 0.083135 | 0.040264 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_524_0_load_113 | 127 | 0.1046 | 0.050659 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_524_0_load_160 | 128 | 0.22955 | 0.11118 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_524_0_load_156 | 129 | 0.25279 | 0.12243 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_524_0_load_112 | 130 | 0.11684 | 0.05659 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_524_0_load_131 | 132 | 0.071059 | 0.034415 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_524_0_load_130 | 134 | 0.092391 | 0.044747 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_524_0_load_101 | 136 | 0.12296 | 0.059551 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_524_0_load_114 | 138 | 0.58208 | 0.28191 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_524_0_load_97 | 139 | 0.12883 | 0.062394 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_524_0_load_99 | 140 | 0.10325 | 0.050006 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_524_0_load_107 | 142 | 0.12243 | 0.059295 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_524_0_load_111 | 145 | 0.11152 | 0.05401 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_524_0_load_141 | 146 | 0.071283 | 0.034524 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_524_0_load_136 | 147 | 0.076166 | 0.036889 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_524_0_load_119 | 148 | 0.093606 | 0.045335 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_524_0_load_157 | 154 | 0.077166 | 0.037373 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_524_0_load_146 | 156 | 0.08815 | 0.042693 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_524_0_load_149 | 158 | 0.45192 | 0.21887 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_524_0_load_144 | 159 | 0.069947 | 0.033877 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_524_0_load_127 | 161 | 0.074144 | 0.035909 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_524_0_load_159 | 164 | 0.39412 | 0.19088 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_524_0_line_0 |  | 0 | 1 | 0.006475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_524_0_line_1 |  | 1 | 2 | 0.54456 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
2 | MV_524_0_line_2 |  | 1 | 3 | 0.36249 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
3 | MV_524_0_line_3 |  | 2 | 7 | 0.19812 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_524_0_line_4 |  | 2 | 8 | 0.3232 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_524_0_line_5 |  | 2 | 9 | 0.61551 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
6 | MV_524_0_line_6 |  | 2 | 10 | 0.036045 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_524_0_line_7 |  | 3 | 22 | 0.007102 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_524_0_line_8 |  | 3 | 17 | 0.37773 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
9 | MV_524_0_line_9 |  | 4 | 5 | 0.004693 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
10 | MV_524_0_line_10 |  | 4 | 6 | 0.22363 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
11 | MV_524_0_line_11 |  | 5 | 53 | 0.003065 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
12 | MV_524_0_line_12 |  | 6 | 98 | 0.060987 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
13 | MV_524_0_line_13 |  | 7 | 44 | 0.051009 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_524_0_line_14 |  | 8 | 45 | 0.014308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_524_0_line_15 |  | 9 | 46 | 0.007905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_524_0_line_16 |  | 9 | 47 | 0.43717 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
17 | MV_524_0_line_17 |  | 10 | 43 | 0.027496 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_524_0_line_18 |  | 11 | 12 | 0.50532 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_524_0_line_19 |  | 11 | 13 | 0.011614 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_524_0_line_20 |  | 11 | 14 | 0.52425 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_524_0_line_21 |  | 12 | 15 | 0.057686 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_524_0_line_22 |  | 14 | 47 | 0.037018 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_524_0_line_23 |  | 16 | 17 | 0.10277 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
24 | MV_524_0_line_24 |  | 16 | 18 | 0.031261 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
25 | MV_524_0_line_25 |  | 17 | 19 | 0.37068 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
26 | MV_524_0_line_26 |  | 17 | 20 | 0.6627 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
27 | MV_524_0_line_27 |  | 17 | 21 | 0.045706 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
28 | MV_524_0_line_28 |  | 19 | 23 | 0.82708 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_524_0_line_29 |  | 19 | 24 | 0.057053 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_524_0_line_30 |  | 20 | 37 | 0.032596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_524_0_line_31 |  | 20 | 30 | 0.1315 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
32 | MV_524_0_line_32 |  | 20 | 33 | 0.41886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_524_0_line_33 |  | 20 | 35 | 0.17678 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
34 | MV_524_0_line_34 |  | 23 | 25 | 0.61498 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
35 | MV_524_0_line_35 |  | 23 | 26 | 0.010713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_524_0_line_36 |  | 25 | 27 | 0.60418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_524_0_line_37 |  | 25 | 28 | 0.92248 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
38 | MV_524_0_line_38 |  | 25 | 29 | 0.043352 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_524_0_line_39 |  | 27 | 51 | 0.11243 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_524_0_line_40 |  | 28 | 52 | 0.055915 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
41 | MV_524_0_line_41 |  | 29 | 54 | 0.054907 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_524_0_line_42 |  | 30 | 31 | 0.021594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_524_0_line_43 |  | 30 | 32 | 0.10154 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
44 | MV_524_0_line_44 |  | 32 | 58 | 0.028539 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
45 | MV_524_0_line_45 |  | 33 | 34 | 0.00476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_524_0_line_46 |  | 34 | 61 | 0.051231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_524_0_line_47 |  | 35 | 36 | 0.03783 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_524_0_line_48 |  | 38 | 39 | 0.089077 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_524_0_line_49 |  | 38 | 40 | 0.12305 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_524_0_line_50 |  | 39 | 62 | 0.21545 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_524_0_line_51 |  | 39 | 63 | 0.1237 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_524_0_line_52 |  | 39 | 64 | 0.21969 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_524_0_line_53 |  | 40 | 65 | 0.0092856 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_524_0_line_54 |  | 41 | 42 | 0.007355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_524_0_line_55 |  | 42 | 43 | 0.059594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_524_0_line_56 |  | 46 | 48 | 0.050334 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_524_0_line_57 |  | 48 | 49 | 0.55068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_524_0_line_58 |  | 49 | 50 | 0.029772 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_524_0_line_59 |  | 52 | 79 | 0.097378 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
60 | MV_524_0_line_60 |  | 53 | 101 | 0.2554 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
61 | MV_524_0_line_61 |  | 54 | 96 | 0.060735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_524_0_line_62 |  | 55 | 56 | 1.0516 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
63 | MV_524_0_line_63 |  | 55 | 57 | 0.005533 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
64 | MV_524_0_line_64 |  | 56 | 95 | 0.048871 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
65 | MV_524_0_line_65 |  | 57 | 108 | 0.57039 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
66 | MV_524_0_line_66 |  | 58 | 73 | 0.15717 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
67 | MV_524_0_line_67 |  | 59 | 60 | 0.10461 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_524_0_line_68 |  | 60 | 75 | 0.040967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_524_0_line_69 |  | 61 | 78 | 0.12205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_524_0_line_70 |  | 62 | 72 | 0.063033 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_524_0_line_71 |  | 62 | 74 | 0.039572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_524_0_line_72 |  | 62 | 76 | 0.34143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_524_0_line_73 |  | 63 | 123 | 0.021582 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_524_0_line_74 |  | 66 | 67 | 0.051808 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_524_0_line_75 |  | 67 | 131 | 0.11276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_524_0_line_76 |  | 68 | 69 | 0.069974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_524_0_line_77 |  | 68 | 70 | 1.232 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
78 | MV_524_0_line_78 |  | 69 | 71 | 0.14597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_524_0_line_79 |  | 71 | 72 | 0.003936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_524_0_line_80 |  | 73 | 74 | 0.037342 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
81 | MV_524_0_line_81 |  | 75 | 76 | 0.010516 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_524_0_line_82 |  | 77 | 78 | 0.1005 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_524_0_line_83 |  | 79 | 94 | 0.043755 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
84 | MV_524_0_line_84 |  | 80 | 81 | 0.02861 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_524_0_line_85 |  | 81 | 82 | 0.60423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_524_0_line_86 |  | 82 | 83 | 0.057428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_524_0_line_87 |  | 83 | 88 | 0.11119 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_524_0_line_88 |  | 84 | 85 | 0.11071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_524_0_line_89 |  | 84 | 86 | 0.21466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_524_0_line_90 |  | 84 | 87 | 0.01788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_524_0_line_91 |  | 85 | 89 | 0.015447 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_524_0_line_92 |  | 86 | 90 | 0.039138 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_524_0_line_93 |  | 86 | 91 | 0.024265 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_524_0_line_94 |  | 86 | 92 | 0.019769 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_524_0_line_95 |  | 88 | 104 | 0.064534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_524_0_line_96 |  | 88 | 105 | 0.057902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_524_0_line_97 |  | 89 | 144 | 0.004713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_524_0_line_98 |  | 91 | 146 | 0.048583 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_524_0_line_99 |  | 92 | 147 | 0.029737 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_524_0_line_100 |  | 93 | 94 | 0.077722 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
101 | MV_524_0_line_101 |  | 93 | 95 | 0.53574 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
102 | MV_524_0_line_102 |  | 96 | 97 | 0.050226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_524_0_line_103 |  | 98 | 99 | 0.15021 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
104 | MV_524_0_line_104 |  | 99 | 100 | 0.017165 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
105 | MV_524_0_line_105 |  | 100 | 126 | 0.086067 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
106 | MV_524_0_line_106 |  | 101 | 102 | 0.047781 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_524_0_line_107 |  | 101 | 103 | 0.34322 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
108 | MV_524_0_line_108 |  | 102 | 129 | 0.002697 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_524_0_line_109 |  | 103 | 124 | 0.060317 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
110 | MV_524_0_line_110 |  | 104 | 106 | 0.040979 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_524_0_line_111 |  | 105 | 107 | 0.0018878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_524_0_line_112 |  | 106 | 111 | 0.086511 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
113 | MV_524_0_line_113 |  | 108 | 109 | 0.0119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_524_0_line_114 |  | 108 | 110 | 0.34269 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
115 | MV_524_0_line_115 |  | 110 | 111 | 0.064272 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
116 | MV_524_0_line_116 |  | 111 | 112 | 0.22639 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_524_0_line_117 |  | 111 | 113 | 0.14788 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
118 | MV_524_0_line_118 |  | 113 | 124 | 0.025144 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
119 | MV_524_0_line_119 |  | 114 | 115 | 0.007082 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_524_0_line_120 |  | 115 | 116 | 0.035229 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_524_0_line_121 |  | 116 | 117 | 0.036413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_524_0_line_122 |  | 116 | 118 | 0.010784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_524_0_line_123 |  | 116 | 119 | 0.016001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_524_0_line_124 |  | 117 | 121 | 0.020101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_524_0_line_125 |  | 118 | 120 | 0.027286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_524_0_line_126 |  | 119 | 122 | 0.024292 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_524_0_line_127 |  | 121 | 136 | 0.021656 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_524_0_line_128 |  | 122 | 141 | 0.01559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_524_0_line_129 |  | 125 | 126 | 0.17155 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
130 | MV_524_0_line_130 |  | 125 | 127 | 0.060292 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
131 | MV_524_0_line_131 |  | 126 | 128 | 0.0052552 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
132 | MV_524_0_line_132 |  | 127 | 130 | 0.018463 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
133 | MV_524_0_line_133 |  | 130 | 143 | 0.009192 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
134 | MV_524_0_line_134 |  | 131 | 132 | 0.057237 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_524_0_line_135 |  | 131 | 133 | 0.26891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_524_0_line_136 |  | 131 | 134 | 0.040801 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_524_0_line_137 |  | 133 | 138 | 0.045513 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_524_0_line_138 |  | 133 | 135 | 0.066965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_524_0_line_139 |  | 135 | 136 | 0.019431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_524_0_line_140 |  | 135 | 137 | 0.028127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_524_0_line_141 |  | 137 | 140 | 0.025333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_524_0_line_142 |  | 137 | 139 | 0.043872 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_524_0_line_143 |  | 141 | 142 | 0.0053366 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_524_0_line_144 |  | 141 | 143 | 0.17074 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
145 | MV_524_0_line_145 |  | 141 | 144 | 0.21897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_524_0_line_146 |  | 143 | 145 | 0.023946 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_524_0_line_147 |  | 146 | 155 | 0.020847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_524_0_line_148 |  | 148 | 149 | 0.035998 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_524_0_line_149 |  | 148 | 150 | 0.048744 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_524_0_line_150 |  | 149 | 151 | 0.15961 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_524_0_line_151 |  | 149 | 152 | 0.3185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_524_0_line_152 |  | 150 | 153 | 0.070889 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_524_0_line_153 |  | 151 | 154 | 0.007795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_524_0_line_154 |  | 152 | 155 | 0.095363 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_524_0_line_155 |  | 152 | 156 | 0.057598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_524_0_line_156 |  | 153 | 159 | 0.019983 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_524_0_line_157 |  | 155 | 157 | 0.10197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_524_0_line_158 |  | 157 | 158 | 0.013618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_524_0_line_159 |  | 159 | 160 | 0.013368 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_524_0_line_160 |  | 160 | 163 | 0.036399 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_524_0_line_161 |  | 161 | 162 | 0.035038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_524_0_line_162 |  | 162 | 163 | 0.067795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_524_0_line_163 |  | 162 | 164 | 0.023712 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_524_0_trafo_58 | 25 MVA 110/20 kV | 165 | 56 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2680547.864 | 1252471.963
1 | 2680554.1433 | 1252473.6163
2 | 2680875.2716 | 1252358.1043
3 | 2680647.3044 | 1252660.3447
4 | 2682840.0739 | 1252613.7483
5 | 2682840.8015 | 1252618.3842
6 | 2682988.1526 | 1252534.6277
7 | 2680998.0437 | 1252513.597
8 | 2681166.8163 | 1252218.6087
9 | 2681392.6218 | 1252024.6391
10 | 2680897.2545 | 1252329.5387
11 | 2680775.0562 | 1252172.4437
12 | 2680651.7469 | 1252139.6732
13 | 2680767.5247 | 1252181.2365
14 | 2681200.1479 | 1251865.6248
15 | 2680654.7737 | 1252197.2795
16 | 2680452.4232 | 1252801.9344
17 | 2680522.6672 | 1252797.5074
18 | 2680424.8641 | 1252816.838
19 | 2680616.0075 | 1252917.5439
20 | 2680327.6666 | 1252930.6488
21 | 2680489.8231 | 1252792.2174
22 | 2680652.7438 | 1252664.911
23 | 2681005.0111 | 1252959.7585
24 | 2680569.5163 | 1252950.614
25 | 2681011.0124 | 1253196.2283
26 | 2681007.8766 | 1252949.4344
27 | 2680739.2382 | 1253233.2463
28 | 2681270.9543 | 1253621.2174
29 | 2681043.5437 | 1253167.574
30 | 2680234.6804 | 1252926.6415
31 | 2680240.7006 | 1252947.3829
32 | 2680141.4929 | 1252966.4879
33 | 2680426.042 | 1252647.3389
34 | 2680421.6544 | 1252649.2141
35 | 2680310.2177 | 1253040.9167
36 | 2680326.2719 | 1253075.1709
37 | 2680357.4112 | 1252917.3174
38 | 2680138.4904 | 1253228.4536
39 | 2680107.2767 | 1253145.0248
40 | 2680015.9494 | 1253239.628
41 | 2680956.9287 | 1252277.248
42 | 2680961.0415 | 1252283.3532
43 | 2680922.9654 | 1252319.7936
44 | 2680954.6429 | 1252540.3911
45 | 2681161.299 | 1252205.4011
46 | 2681400.129 | 1252022.0959
47 | 2681220.7751 | 1251834.8846
48 | 2681447.9176 | 1252005.8737
49 | 2681704.9423 | 1252061.4643
50 | 2681730.9274 | 1252046.8006
51 | 2680711.3497 | 1253342.1588
52 | 2681327.0307 | 1253621.9652
53 | 2682843.8485 | 1252617.9821
54 | 2681093.2237 | 1253144.1918
55 | 2682831.6064 | 1253401.8108
56 | 2681800.4188 | 1253195.6294
57 | 2682837.0683 | 1253400.8308
58 | 2680133.2127 | 1252939.856
59 | 2680117.5214 | 1252706.8927
60 | 2680029.7456 | 1252763.8044
61 | 2680401.0928 | 1252602.2668
62 | 2679922.0621 | 1253034.9528
63 | 2679984.2233 | 1253157.6941
64 | 2679896.2516 | 1253206.1225
65 | 2680012.5963 | 1253230.9689
66 | 2682917.2887 | 1252266.3169
67 | 2682968.9738 | 1252262.7442
68 | 2679681.8546 | 1253079.2728
69 | 2679750.2278 | 1253085.1415
70 | 2678570.8996 | 1253611.7879
71 | 2679875.6614 | 1253078.4595
72 | 2679873.4262 | 1253075.2158
73 | 2679984.2113 | 1252989.8801
74 | 2679953.3585 | 1253010.8234
75 | 2679995.6191 | 1252780.0335
76 | 2679994.8662 | 1252790.52
77 | 2680306.6741 | 1252433.6165
78 | 2680362.6351 | 1252517.0928
79 | 2681385.4633 | 1253699.8634
80 | 2683586.8642 | 1252629.7144
81 | 2683558.7333 | 1252624.069
82 | 2683566.0867 | 1252893.3752
83 | 2683523.5239 | 1252931.8707
84 | 2683575.9919 | 1252446.112
85 | 2683497.8865 | 1252495.3034
86 | 2683507.0715 | 1252310.1271
87 | 2683566.2972 | 1252431.088
88 | 2683434.8124 | 1252998.9046
89 | 2683485.9086 | 1252501.228
90 | 2683546.1663 | 1252311.9743
91 | 2683487.5444 | 1252303.8472
92 | 2683505.7446 | 1252290.4435
93 | 2681429.4625 | 1253623.073
94 | 2681429.2084 | 1253700.7945
95 | 2681756.6069 | 1253198.8159
96 | 2681137.3333 | 1253113.7729
97 | 2681185.3301 | 1253098.7303
98 | 2682989.5375 | 1252474.0461
99 | 2683125.1339 | 1252409.4238
100 | 2683119.2126 | 1252393.4143
101 | 2683063.1225 | 1252748.939
102 | 2683019.6829 | 1252729.0375
103 | 2683220.4007 | 1252815.8628
104 | 2683384.5882 | 1253021.0365
105 | 2683394.7486 | 1252979.5816
106 | 2683358.9015 | 1252989.1122
107 | 2683393.5342 | 1252978.1361
108 | 2682880.0198 | 1253047.2212
109 | 2682870.7164 | 1253054.6745
110 | 2683213.0403 | 1252966.3836
111 | 2683274.7725 | 1252968.9529
112 | 2683239.4426 | 1253192.5691
113 | 2683302.7144 | 1252831.3088
114 | 2683432.9909 | 1252296.9515
115 | 2683437.4164 | 1252302.1177
116 | 2683413.9831 | 1252308.4481
117 | 2683377.6179 | 1252306.5901
118 | 2683417.4439 | 1252301.1914
119 | 2683414.039 | 1252324.4489
120 | 2683390.203 | 1252299.6257
121 | 2683357.5456 | 1252305.5234
122 | 2683413.6562 | 1252348.7074
123 | 2679964.0808 | 1253165.4449
124 | 2683280.2933 | 1252822.9964
125 | 2683262.3983 | 1252378.9914
126 | 2683197.5243 | 1252393.858
127 | 2683321.8136 | 1252388.2143
128 | 2683200.9464 | 1252389.8697
129 | 2683018.4643 | 1252731.4444
130 | 2683339.6309 | 1252393.0521
131 | 2683077.303 | 1252251.9094
132 | 2683070.8866 | 1252195.1049
133 | 2683258.76 | 1252292.0751
134 | 2683087.7309 | 1252291.3548
135 | 2683316.5315 | 1252303.0731
136 | 2683335.9281 | 1252304.2319
137 | 2683314.4538 | 1252331.1205
138 | 2683304.1983 | 1252294.6847
139 | 2683291.4019 | 1252352.2122
140 | 2683289.0843 | 1252329.7183
141 | 2683411.975 | 1252364.2061
142 | 2683410.0783 | 1252369.1943
143 | 2683348.5558 | 1252395.2482
144 | 2683481.798 | 1252498.9016
145 | 2683371.903 | 1252390.7414
146 | 2683492.7081 | 1252255.783
147 | 2683509.4334 | 1252260.9994
148 | 2683311.5773 | 1252094.08
149 | 2683309.0257 | 1252058.1728
150 | 2683317.9954 | 1252142.173
151 | 2683189.0193 | 1252059.6436
152 | 2683525.9683 | 1252149.206
153 | 2683280.7267 | 1252171.0597
154 | 2683186.8837 | 1252067.1415
155 | 2683498.9407 | 1252235.8901
156 | 2683524.7127 | 1252091.7514
157 | 2683428.5494 | 1252216.8622
158 | 2683414.9046 | 1252216.2474
159 | 2683261.0261 | 1252174.0147
160 | 2683247.6895 | 1252174.9317
161 | 2683169.1305 | 1252117.0369
162 | 2683171.4342 | 1252151.9993
163 | 2683232.1868 | 1252155.0657
164 | 2683149.4152 | 1252160.7969
165 | 2681800.4188 | 1253195.6294

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98893 | -0.24723 | 0.33656 | 0.163
1 | 0.98893 | -0.24725 | 0 | 0
2 | 0.98854 | -0.24929 | 0 | 0
3 | 0.98923 | -0.2456 | 0 | 0
4 | 0.98871 | -0.49752 | 0 | 0
5 | 0.98872 | -0.49748 | 0.20763 | 0.10056
6 | 0.98831 | -0.49929 | 0 | 0
7 | 0.98842 | -0.25011 | 0 | 0
8 | 0.98832 | -0.25072 | 0 | 0
9 | 0.98811 | -0.27531 | 0 | 0
10 | 0.98851 | -0.24949 | 0.16193 | 0.078426
11 | 0.9877 | -0.27807 | 0 | 0
12 | 0.98759 | -0.27727 | 0 | 0
13 | 0.98769 | -0.27805 | 0.13912 | 0.067381
14 | 0.988 | -0.27556 | 0.30127 | 0.14591
15 | 0.98758 | -0.27739 | 0.16054 | 0.077752
16 | 0.98957 | -0.24363 | 0 | 0
17 | 0.98958 | -0.24358 | 0 | 0
18 | 0.98957 | -0.24365 | 0.37063 | 0.17951
19 | 0.99038 | -0.23924 | 0 | 0
20 | 0.98889 | -0.24689 | 0 | 0
21 | 0.98958 | -0.24362 | 0.11612 | 0.05624
22 | 0.98922 | -0.24563 | 0.37281 | 0.18056
23 | 0.99222 | -0.22885 | 0 | 0
24 | 0.99035 | -0.23943 | 0.27449 | 0.13294
25 | 0.99365 | -0.22054 | 0 | 0
26 | 0.99222 | -0.22881 | 0.27173 | 0.1316
27 | 0.99338 | -0.21825 | 0 | 0
28 | 0.99601 | -0.2064 | 0 | 0
29 | 0.99361 | -0.22077 | 0.22825 | 0.11055
30 | 0.9888 | -0.24729 | 0 | 0
31 | 0.98879 | -0.24726 | 0.093244 | 0.04516
32 | 0.98873 | -0.24757 | 0 | 0
33 | 0.98855 | -0.24392 | 0 | 0
34 | 0.98854 | -0.24388 | 0.37577 | 0.182
35 | 0.98885 | -0.24726 | 0 | 0
36 | 0.98883 | -0.24743 | 0.35524 | 0.17205
37 | 0.98888 | -0.24684 | 0.13636 | 0.06604
38 | 0.98812 | -0.25771 | 0 | 0
39 | 0.98813 | -0.25761 | 0.27505 | 0.13321
40 | 0.98809 | -0.25784 | 0 | 0
41 | 0.98848 | -0.24937 | 0.26718 | 0.1294
42 | 0.98848 | -0.24939 | 0 | 0
43 | 0.9885 | -0.24958 | 0 | 0
44 | 0.98839 | -0.24991 | 0.32618 | 0.15798
45 | 0.98831 | -0.25066 | 0.35407 | 0.17148
46 | 0.98811 | -0.27527 | 0.25601 | 0.12399
47 | 0.98803 | -0.2758 | 0 | 0
48 | 0.98809 | -0.27518 | 0 | 0
49 | 0.98794 | -0.27398 | 0 | 0
50 | 0.98793 | -0.2739 | 0.21623 | 0.10473
51 | 0.9933 | -0.21874 | 0.35101 | 0.17
52 | 0.99615 | -0.20552 | 0.24394 | 0.11815
53 | 0.98872 | -0.49745 | 0 | 0
54 | 0.99359 | -0.22092 | 0 | 0
55 | 0.99419 | -0.32983 | 0.27653 | 0.13393
56 | 1 | 0 | -16.9439 | -7.6726
57 | 0.99417 | -0.3299 | 0 | 0
58 | 0.98871 | -0.24764 | 0.34772 | 0.16841
59 | 0.98816 | -0.25508 | 0.14845 | 0.071899
60 | 0.98819 | -0.25489 | 0 | 0
61 | 0.98853 | -0.24374 | 0 | 0
62 | 0.98834 | -0.25623 | 0 | 0
63 | 0.98811 | -0.25772 | 0 | 0
64 | 0.9881 | -0.25782 | 0.076179 | 0.036895
65 | 0.98809 | -0.25783 | 0.086285 | 0.04179
66 | 0.98621 | -0.53282 | 0.072988 | 0.03535
67 | 0.98621 | -0.53287 | 0 | 0
68 | 0.98818 | -0.25478 | 0.19094 | 0.092476
69 | 0.98822 | -0.25508 | 0 | 0
70 | 0.98775 | -0.25759 | 0.17943 | 0.0869
71 | 0.98828 | -0.2557 | 0 | 0
72 | 0.98829 | -0.25572 | 0.33607 | 0.16277
73 | 0.98845 | -0.25644 | 0 | 0
74 | 0.98842 | -0.25693 | 0.10877 | 0.052679
75 | 0.9882 | -0.25496 | 0.17498 | 0.084747
76 | 0.9882 | -0.255 | 0 | 0
77 | 0.98844 | -0.24369 | 0.25291 | 0.12249
78 | 0.98849 | -0.24337 | 0 | 0
79 | 0.99666 | -0.17457 | 0.10444 | 0.050584
80 | 0.99 | -0.43568 | 0.38745 | 0.18765
81 | 0.99002 | -0.43582 | 0 | 0
82 | 0.99032 | -0.43837 | 0 | 0
83 | 0.99034 | -0.43858 | 0.4019 | 0.19465
84 | 0.98581 | -0.52946 | 0 | 0
85 | 0.98605 | -0.5315 | 0 | 0
86 | 0.98537 | -0.52571 | 0 | 0
87 | 0.98581 | -0.52944 | 0.097045 | 0.047001
88 | 0.99051 | -0.43734 | 0 | 0
89 | 0.98608 | -0.53178 | 0.40874 | 0.19796
90 | 0.98536 | -0.52565 | 0.12028 | 0.058254
91 | 0.98533 | -0.52536 | 0 | 0
92 | 0.98537 | -0.52568 | 0.071072 | 0.034422
93 | 0.99699 | -0.17261 | 0 | 0
94 | 0.99678 | -0.17386 | 0 | 0
95 | 0.99986 | -0.000789 | 0.36643 | 0.17747
96 | 0.99358 | -0.22078 | 0 | 0
97 | 0.99356 | -0.22067 | 0.19216 | 0.093065
98 | 0.9882 | -0.49976 | 0.232 | 0.11236
99 | 0.98768 | -0.52973 | 0.1055 | 0.051095
100 | 0.98765 | -0.52986 | 0 | 0
101 | 0.98969 | -0.44221 | 0 | 0
102 | 0.98966 | -0.44235 | 0 | 0
103 | 0.99034 | -0.43924 | 0 | 0
104 | 0.99059 | -0.43796 | 0 | 0
105 | 0.99051 | -0.43728 | 0 | 0
106 | 0.99063 | -0.43835 | 0.098707 | 0.047806
107 | 0.99051 | -0.43728 | 0.09073 | 0.043943
108 | 0.99269 | -0.33663 | 0 | 0
109 | 0.99269 | -0.33657 | 0.3685 | 0.17847
110 | 0.99095 | -0.43644 | 0.29749 | 0.14408
111 | 0.9908 | -0.43715 | 0 | 0
112 | 0.99064 | -0.43812 | 0.34475 | 0.16697
113 | 0.99051 | -0.43849 | 0 | 0
114 | 0.98651 | -0.53542 | 0.29632 | 0.14351
115 | 0.98652 | -0.53544 | 0 | 0
116 | 0.98653 | -0.53557 | 0 | 0
117 | 0.98646 | -0.53499 | 0.10367 | 0.050211
118 | 0.98653 | -0.53553 | 0 | 0
119 | 0.98657 | -0.53594 | 0.15092 | 0.073093
120 | 0.98651 | -0.53543 | 0.30182 | 0.14618
121 | 0.98643 | -0.5347 | 0.11075 | 0.053641
122 | 0.98664 | -0.53654 | 0.10936 | 0.052966
123 | 0.98811 | -0.2577 | 0.068767 | 0.033306
124 | 0.99046 | -0.43871 | 0.083135 | 0.040264
125 | 0.98724 | -0.53169 | 0 | 0
126 | 0.98751 | -0.53049 | 0 | 0
127 | 0.98714 | -0.53211 | 0.1046 | 0.050659
128 | 0.98751 | -0.53051 | 0.22955 | 0.11118
129 | 0.98966 | -0.44235 | 0.25279 | 0.12243
130 | 0.98711 | -0.53223 | 0.11684 | 0.05659
131 | 0.98622 | -0.53295 | 0 | 0
132 | 0.98622 | -0.5329 | 0.071059 | 0.034415
133 | 0.9863 | -0.53357 | 0 | 0
134 | 0.98622 | -0.53291 | 0.092391 | 0.044747
135 | 0.98637 | -0.53418 | 0 | 0
136 | 0.9864 | -0.53441 | 0.12296 | 0.059551
137 | 0.98636 | -0.53411 | 0 | 0
138 | 0.98627 | -0.53325 | 0.58208 | 0.28191
139 | 0.98636 | -0.53404 | 0.12883 | 0.062394
140 | 0.98636 | -0.53407 | 0.10325 | 0.050006
141 | 0.98668 | -0.53695 | 0 | 0
142 | 0.98668 | -0.53694 | 0.12243 | 0.059295
143 | 0.9871 | -0.53229 | 0 | 0
144 | 0.98609 | -0.53189 | 0 | 0
145 | 0.9871 | -0.53226 | 0.11152 | 0.05401
146 | 0.98525 | -0.52465 | 0.071283 | 0.034524
147 | 0.98536 | -0.52565 | 0.076166 | 0.036889
148 | 0.9848 | -0.52083 | 0.093606 | 0.045335
149 | 0.98482 | -0.5211 | 0 | 0
150 | 0.98476 | -0.52053 | 0 | 0
151 | 0.98481 | -0.52097 | 0 | 0
152 | 0.98512 | -0.52356 | 0 | 0
153 | 0.98471 | -0.52008 | 0 | 0
154 | 0.98481 | -0.52096 | 0.077166 | 0.037373
155 | 0.98521 | -0.52437 | 0 | 0
156 | 0.98511 | -0.5235 | 0.08815 | 0.042693
157 | 0.98515 | -0.52381 | 0 | 0
158 | 0.98515 | -0.52373 | 0.45192 | 0.21887
159 | 0.9847 | -0.51995 | 0.069947 | 0.033877
160 | 0.98469 | -0.51988 | 0 | 0
161 | 0.98462 | -0.51926 | 0.074144 | 0.035909
162 | 0.98463 | -0.51929 | 0 | 0
163 | 0.98467 | -0.51967 | 0 | 0
164 | 0.98461 | -0.51941 | 0.39412 | 0.19088
165 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.33656 | -0.163 | 0.33656 | 0.16285 | 1.0299e-06 | -0.00015089 | 0.010916 | 0.010914 | 0.010916 | 0.98893 | -0.24723 | 0.98893 | -0.24725 | 4.9619
1 | 2.184 | 0.96507 | -2.1832 | -0.99805 | 0.0008221 | -0.032986 | 0.069698 | 0.070099 | 0.070099 | 0.98893 | -0.24725 | 0.98854 | -0.24929 | 10.9873
2 | -2.5205 | -1.1279 | 2.5213 | 1.106 | 0.0007254 | -0.021873 | 0.080607 | 0.080344 | 0.080607 | 0.98893 | -0.24725 | 0.98923 | -0.2456 | 12.6343
3 | 0.32623 | 0.15658 | -0.32619 | -0.15679 | 3.9426e-05 | -0.0002064 | 0.010567 | 0.01057 | 0.01057 | 0.98854 | -0.24929 | 0.98842 | -0.25011 | 5.0333
4 | 0.35415 | 0.17082 | -0.35407 | -0.17115 | 7.5949e-05 | -0.00032939 | 0.011482 | 0.011487 | 0.011487 | 0.98854 | -0.24929 | 0.98832 | -0.25072 | 5.4699
5 | 1.0737 | 0.46445 | -1.0734 | -0.46459 | 0.0002565 | -0.00014133 | 0.034161 | 0.03417 | 0.03417 | 0.98854 | -0.24929 | 0.98811 | -0.27531 | 5.2977
6 | 0.42913 | 0.2062 | -0.42911 | -0.20623 | 1.2414e-05 | -3.4273e-05 | 0.013903 | 0.013904 | 0.013904 | 0.98854 | -0.24929 | 0.98851 | -0.24949 | 6.6207
7 | 0.37281 | 0.18055 | -0.37281 | -0.18056 | 1.849e-06 | -7.1386e-06 | 0.012088 | 0.012088 | 0.012088 | 0.98923 | -0.2456 | 0.98922 | -0.24563 | 5.7563
8 | -2.8941 | -1.2866 | 2.8951 | 1.2639 | 0.00099409 | -0.022674 | 0.092424 | 0.092151 | 0.092424 | 0.98923 | -0.2456 | 0.98958 | -0.24358 | 14.4866
9 | -5.3751 | -2.4948 | 5.3751 | 2.4945 | 4.3409e-05 | -0.00026381 | 0.17302 | 0.17301 | 0.17302 | 0.98871 | -0.49752 | 0.98872 | -0.49748 | 27.1187
10 | 5.3751 | 2.4948 | -5.373 | -2.5074 | 0.0020706 | -0.012564 | 0.17302 | 0.17319 | 0.17319 | 0.98871 | -0.49752 | 0.98831 | -0.49929 | 27.1452
11 | -5.5827 | -2.5951 | 5.5828 | 2.5949 | 3.0599e-05 | -0.00017103 | 0.17975 | 0.17975 | 0.17975 | 0.98872 | -0.49748 | 0.98872 | -0.49745 | 28.1738
12 | 5.373 | 2.5074 | -5.3724 | -2.5108 | 0.00056538 | -0.0034241 | 0.17319 | 0.17323 | 0.17323 | 0.98831 | -0.49929 | 0.9882 | -0.49976 | 27.1525
13 | 0.32619 | 0.15679 | -0.32618 | -0.15798 | 7.6189e-06 | -0.0011876 | 0.01057 | 0.010585 | 0.010585 | 0.98842 | -0.25011 | 0.98839 | -0.24991 | 4.8114
14 | 0.35407 | 0.17115 | -0.35407 | -0.17148 | 2.5213e-06 | -0.00033293 | 0.011487 | 0.011491 | 0.011491 | 0.98832 | -0.25072 | 0.98831 | -0.25066 | 5.2232
15 | 0.47229 | 0.21385 | -0.47229 | -0.21403 | 2.4214e-06 | -0.00018356 | 0.015146 | 0.015149 | 0.015149 | 0.98811 | -0.27531 | 0.98811 | -0.27527 | 6.8857
16 | 0.60111 | 0.25074 | -0.60106 | -0.27753 | 4.9705e-05 | -0.026789 | 0.019028 | 0.019343 | 0.019343 | 0.98811 | -0.27531 | 0.98803 | -0.2758 | 3.0318
17 | 0.26719 | 0.12781 | -0.26718 | -0.12784 | 3.6651e-06 | -2.9779e-05 | 0.0086494 | 0.0086498 | 0.0086498 | 0.98851 | -0.24949 | 0.9885 | -0.24958 | 4.1189
18 | 0.16056 | 0.065923 | -0.16054 | -0.077686 | 1.7827e-05 | -0.011764 | 0.0050728 | 0.0052132 | 0.0052132 | 0.9877 | -0.27807 | 0.98759 | -0.27727 | 2.3696
19 | 0.13912 | 0.06711 | -0.13912 | -0.067381 | 3.1625e-07 | -0.00027042 | 0.0045146 | 0.004518 | 0.004518 | 0.9877 | -0.27807 | 0.98769 | -0.27805 | 2.0536
20 | -0.29968 | -0.13303 | 0.29977 | 0.13248 | 8.5715e-05 | -0.00055705 | 0.0095831 | 0.0095758 | 0.0095831 | 0.9877 | -0.27807 | 0.988 | -0.27556 | 4.5634
21 | 0.16054 | 0.077686 | -0.16054 | -0.077752 | 2.7937e-06 | -6.5416e-05 | 0.0052132 | 0.005214 | 0.005214 | 0.98759 | -0.27727 | 0.98758 | -0.27739 | 2.4829
22 | -0.60104 | -0.27839 | 0.60106 | 0.27753 | 1.85e-05 | -0.00085729 | 0.019354 | 0.019343 | 0.019354 | 0.988 | -0.27556 | 0.98803 | -0.2758 | 8.7971
23 | -0.37064 | -0.17758 | 0.37064 | 0.17126 | 4.5343e-06 | -0.0063205 | 0.011989 | 0.011911 | 0.011989 | 0.98957 | -0.24363 | 0.98958 | -0.24358 | 1.8792
24 | 0.37064 | 0.17758 | -0.37063 | -0.17951 | 1.3913e-06 | -0.0019226 | 0.011989 | 0.012013 | 0.012013 | 0.98957 | -0.24363 | 0.98957 | -0.24365 | 1.883
25 | -6.5916 | -2.9452 | 6.5967 | 2.9252 | 0.0050739 | -0.019969 | 0.21061 | 0.21034 | 0.21061 | 0.98958 | -0.24358 | 0.99038 | -0.23924 | 33.0106
26 | 3.2098 | 1.4555 | -3.2076 | -1.495 | 0.0021749 | -0.039523 | 0.10281 | 0.10331 | 0.10331 | 0.98958 | -0.24358 | 0.98889 | -0.24689 | 16.1923
27 | 0.11612 | 0.054531 | -0.11612 | -0.05624 | 2.3562e-07 | -0.0017096 | 0.0037423 | 0.0037638 | 0.0037638 | 0.98958 | -0.24358 | 0.98958 | -0.24362 | 0.89402
28 | -6.8712 | -3.0581 | 6.8834 | 3.0139 | 0.012248 | -0.04417 | 0.21922 | 0.21862 | 0.21922 | 0.99038 | -0.23924 | 0.99222 | -0.22885 | 34.3607
29 | 0.2745 | 0.13288 | -0.27449 | -0.13294 | 8.0334e-06 | -6.1772e-05 | 0.0088894 | 0.0088902 | 0.0088902 | 0.99038 | -0.23924 | 0.99035 | -0.23943 | 4.2334
30 | 0.13636 | 0.065279 | -0.13636 | -0.06604 | 8.4936e-07 | -0.00076081 | 0.0044132 | 0.0044228 | 0.0044228 | 0.98889 | -0.24689 | 0.98888 | -0.24684 | 2.0104
31 | 2.087 | 0.9731 | -2.0869 | -0.98108 | 0.00018389 | -0.0079756 | 0.067222 | 0.067322 | 0.067322 | 0.98889 | -0.24689 | 0.9888 | -0.24729 | 10.552
32 | 0.62895 | 0.29052 | -0.62872 | -0.30023 | 0.00023008 | -0.0097081 | 0.020224 | 0.020346 | 0.020346 | 0.98889 | -0.24689 | 0.98855 | -0.24392 | 9.248
33 | 0.35526 | 0.16609 | -0.35525 | -0.17201 | 1.1263e-05 | -0.0059221 | 0.011448 | 0.011522 | 0.011522 | 0.98889 | -0.24689 | 0.98885 | -0.24726 | 3.183
34 | -7.1552 | -3.1453 | 7.165 | 3.1127 | 0.009807 | -0.032574 | 0.2274 | 0.22695 | 0.2274 | 0.99222 | -0.22885 | 0.99365 | -0.22054 | 35.642
35 | 0.27173 | 0.13135 | -0.27173 | -0.1316 | 1.1031e-06 | -0.00025149 | 0.0087808 | 0.008784 | 0.008784 | 0.99222 | -0.22885 | 0.99222 | -0.22881 | 3.9927
36 | 0.35113 | 0.15567 | -0.35103 | -0.16988 | 0.00010198 | -0.014209 | 0.011159 | 0.011333 | 0.011333 | 0.99365 | -0.22054 | 0.99338 | -0.21825 | 5.1513
37 | -7.9365 | -3.4693 | 7.9545 | 3.4221 | 0.018002 | -0.047226 | 0.25164 | 0.25098 | 0.25164 | 0.99365 | -0.22054 | 0.99601 | -0.2064 | 39.442
38 | 0.42043 | 0.20089 | -0.42042 | -0.20094 | 1.4155e-05 | -4.223e-05 | 0.013537 | 0.013538 | 0.013538 | 0.99365 | -0.22054 | 0.99361 | -0.22077 | 6.4466
39 | 0.35103 | 0.16988 | -0.35101 | -0.17 | 2.573e-05 | -0.00011632 | 0.011333 | 0.011334 | 0.011334 | 0.99338 | -0.21825 | 0.9933 | -0.21874 | 5.3974
40 | -7.9545 | -3.4221 | 7.9556 | 3.4192 | 0.0010881 | -0.002873 | 0.25098 | 0.25094 | 0.25098 | 0.99601 | -0.2064 | 0.99615 | -0.20552 | 39.3382
41 | 0.19217 | 0.090389 | -0.19216 | -0.090452 | 3.7245e-06 | -6.238e-05 | 0.0061698 | 0.0061706 | 0.0061706 | 0.99361 | -0.22077 | 0.99359 | -0.22092 | 2.9384
42 | 0.093245 | 0.044656 | -0.093244 | -0.04516 | 2.6319e-07 | -0.00050401 | 0.0030183 | 0.0030247 | 0.0030247 | 0.9888 | -0.24729 | 0.98879 | -0.24726 | 1.3749
43 | 1.9936 | 0.93642 | -1.9935 | -0.94259 | 0.00012989 | -0.0061642 | 0.064304 | 0.064381 | 0.064381 | 0.9888 | -0.24729 | 0.98873 | -0.24757 | 10.0911
44 | 1.9935 | 0.94259 | -1.9934 | -0.94432 | 3.6565e-05 | -0.0017323 | 0.064381 | 0.064403 | 0.064403 | 0.98873 | -0.24757 | 0.98871 | -0.24764 | 10.0945
45 | 0.62872 | 0.30023 | -0.62872 | -0.30034 | 2.6307e-06 | -0.00011028 | 0.020346 | 0.020347 | 0.020347 | 0.98855 | -0.24392 | 0.98854 | -0.24388 | 9.2487
46 | 0.25294 | 0.11834 | -0.25294 | -0.11954 | 4.5566e-06 | -0.001194 | 0.0081549 | 0.0081697 | 0.0081697 | 0.98854 | -0.24388 | 0.98853 | -0.24374 | 3.7135
47 | 0.35525 | 0.17201 | -0.35524 | -0.17205 | 8.9491e-06 | -3.8553e-05 | 0.011522 | 0.011523 | 0.011523 | 0.98885 | -0.24726 | 0.98883 | -0.24743 | 5.4872
48 | -0.086287 | -0.041431 | 0.086289 | 0.041328 | 1.2405e-06 | -0.00010305 | 0.0027964 | 0.0027951 | 0.0027964 | 0.98812 | -0.25771 | 0.98813 | -0.25761 | 1.3316
49 | 0.086287 | 0.041431 | -0.086286 | -0.041574 | 1.7155e-06 | -0.00014235 | 0.0027964 | 0.0027982 | 0.0027982 | 0.98812 | -0.25771 | 0.98809 | -0.25784 | 1.3325
50 | -0.50628 | -0.24384 | 0.50639 | 0.24365 | 0.00010344 | -0.0001864 | 0.016417 | 0.016414 | 0.016417 | 0.98813 | -0.25761 | 0.98834 | -0.25623 | 7.8175
51 | 0.068769 | 0.032659 | -0.068768 | -0.032802 | 1.0911e-06 | -0.00014351 | 0.0022241 | 0.0022259 | 0.0022259 | 0.98813 | -0.25761 | 0.98811 | -0.25772 | 1.0599
52 | 0.076181 | 0.036641 | -0.076179 | -0.036895 | 2.3905e-06 | -0.00025457 | 0.0024696 | 0.0024729 | 0.0024729 | 0.98813 | -0.25761 | 0.9881 | -0.25782 | 1.1776
53 | 0.086286 | 0.041574 | -0.086285 | -0.04179 | 9.716e-08 | -0.00021643 | 0.0027982 | 0.002801 | 0.002801 | 0.98809 | -0.25784 | 0.98809 | -0.25783 | 1.2732
54 | -0.26718 | -0.1294 | 0.26718 | 0.12923 | 7.3782e-07 | -0.00017137 | 0.0086696 | 0.0086674 | 0.0086696 | 0.98848 | -0.24937 | 0.98848 | -0.24939 | 3.9407
55 | -0.26718 | -0.12923 | 0.26718 | 0.12784 | 5.9646e-06 | -0.0013885 | 0.0086674 | 0.0086498 | 0.0086674 | 0.98848 | -0.24939 | 0.9885 | -0.24958 | 3.9397
56 | 0.21628 | 0.090037 | -0.21627 | -0.09121 | 3.1537e-06 | -0.0011724 | 0.0068441 | 0.0068574 | 0.0068574 | 0.98811 | -0.27527 | 0.98809 | -0.27518 | 3.117
57 | 0.21627 | 0.09121 | -0.21624 | -0.10403 | 3.5331e-05 | -0.012824 | 0.0068574 | 0.0070116 | 0.0070116 | 0.98809 | -0.27518 | 0.98794 | -0.27398 | 3.1871
58 | 0.21624 | 0.10403 | -0.21623 | -0.10473 | 1.9565e-06 | -0.00069321 | 0.0070116 | 0.0070204 | 0.0070204 | 0.98794 | -0.27398 | 0.98793 | -0.2739 | 3.1911
59 | -8.1996 | -3.5373 | 8.2019 | 3.5435 | 0.0023281 | 0.0061268 | 0.25878 | 0.25878 | 0.25878 | 0.99615 | -0.20552 | 0.99666 | -0.17457 | 40.1216
60 | -5.5828 | -2.5949 | 5.5857 | 2.6025 | 0.0029458 | 0.007576 | 0.17975 | 0.17974 | 0.17975 | 0.98872 | -0.49745 | 0.98969 | -0.44221 | 27.8677
61 | 0.19216 | 0.090452 | -0.19216 | -0.091882 | 3.0962e-06 | -0.0014306 | 0.0061706 | 0.0061884 | 0.0061884 | 0.99359 | -0.22092 | 0.99358 | -0.22078 | 2.8129
62 | -8.2144 | -3.7964 | 8.2403 | 3.8646 | 0.025918 | 0.068249 | 0.26276 | 0.26274 | 0.26276 | 0.99419 | -0.32983 | 1 | 0 | 40.7373
63 | 7.9378 | 3.6624 | -7.9377 | -3.6627 | 0.00011016 | -0.00028158 | 0.25384 | 0.25384 | 0.25384 | 0.99419 | -0.32983 | 0.99417 | -0.3299 | 39.7868
64 | 8.6896 | 3.7975 | -8.6885 | -3.8 | 0.0011319 | -0.0024329 | 0.27376 | 0.27379 | 0.27379 | 1 | 0 | 0.99986 | -0.000789 | 42.914
65 | 7.9377 | 3.6627 | -7.9263 | -3.6917 | 0.011376 | -0.028964 | 0.25384 | 0.25427 | 0.25427 | 0.99417 | -0.3299 | 0.99269 | -0.33663 | 39.8546
66 | 1.6457 | 0.77591 | -1.6454 | -0.77565 | 0.00031618 | 0.00025896 | 0.053123 | 0.053126 | 0.053126 | 0.98871 | -0.24764 | 0.98845 | -0.25644 | 12.9575
67 | -0.14845 | -0.071899 | 0.14846 | 0.07178 | 4.3264e-06 | -0.00011924 | 0.0048187 | 0.0048171 | 0.0048187 | 0.98816 | -0.25508 | 0.98819 | -0.25489 | 2.2946
68 | -0.14846 | -0.07178 | 0.14846 | 0.070825 | 1.2659e-06 | -0.0009548 | 0.0048171 | 0.0048051 | 0.0048171 | 0.98819 | -0.25489 | 0.9882 | -0.25496 | 2.1896
69 | 0.25294 | 0.11954 | -0.25293 | -0.12238 | 1.0923e-05 | -0.0028442 | 0.0081697 | 0.0082056 | 0.0082056 | 0.98853 | -0.24374 | 0.98849 | -0.24337 | 3.7298
70 | 0.7066 | 0.33418 | -0.70656 | -0.33564 | 4.3895e-05 | -0.001457 | 0.02283 | 0.022849 | 0.022849 | 0.98834 | -0.25623 | 0.98829 | -0.25572 | 10.3857
71 | -1.5365 | -0.72522 | 1.5366 | 0.72433 | 0.00013007 | -0.00088442 | 0.049625 | 0.049614 | 0.049625 | 0.98834 | -0.25623 | 0.98842 | -0.25693 | 22.5569
72 | 0.32349 | 0.14738 | -0.32344 | -0.15533 | 4.96e-05 | -0.0079471 | 0.010383 | 0.010481 | 0.010481 | 0.98834 | -0.25623 | 0.9882 | -0.255 | 4.7643
73 | 0.068768 | 0.032802 | -0.068767 | -0.033306 | 1.4316e-07 | -0.00050308 | 0.0022259 | 0.0022323 | 0.0022323 | 0.98811 | -0.25772 | 0.98811 | -0.2577 | 1.0147
74 | -0.072988 | -0.03535 | 0.072989 | 0.034147 | 3.8725e-07 | -0.001203 | 0.0023738 | 0.0023587 | 0.0023738 | 0.98621 | -0.53282 | 0.98621 | -0.53287 | 1.079
75 | -0.072989 | -0.034147 | 0.07299 | 0.031529 | 8.2621e-07 | -0.0026184 | 0.0023587 | 0.0023273 | 0.0023587 | 0.98621 | -0.53287 | 0.98622 | -0.53295 | 1.0721
76 | -0.37044 | -0.17799 | 0.37045 | 0.17636 | 1.3442e-05 | -0.0016275 | 0.012006 | 0.011985 | 0.012006 | 0.98818 | -0.25478 | 0.98822 | -0.25508 | 5.4572
77 | 0.1795 | 0.085511 | -0.17943 | -0.0869 | 7.4284e-05 | -0.001389 | 0.0058083 | 0.0058265 | 0.0058265 | 0.98818 | -0.25478 | 0.98775 | -0.25759 | 2.7745
78 | -0.37045 | -0.17636 | 0.37048 | 0.17296 | 2.7893e-05 | -0.0033955 | 0.011985 | 0.011943 | 0.011985 | 0.98822 | -0.25508 | 0.98828 | -0.2557 | 5.4479
79 | -0.37048 | -0.17296 | 0.37048 | 0.17287 | 7.494e-07 | -9.1565e-05 | 0.011943 | 0.011942 | 0.011943 | 0.98828 | -0.2557 | 0.98829 | -0.25572 | 5.4286
80 | 1.6454 | 0.77565 | -1.6454 | -0.77701 | 3.8586e-05 | -0.0013583 | 0.053126 | 0.053143 | 0.053143 | 0.98845 | -0.25644 | 0.98842 | -0.25693 | 12.6231
81 | -0.32344 | -0.15557 | 0.32344 | 0.15533 | 1.5428e-06 | -0.00024473 | 0.010485 | 0.010481 | 0.010485 | 0.9882 | -0.25496 | 0.9882 | -0.255 | 4.7657
82 | -0.25291 | -0.12249 | 0.25293 | 0.12238 | 1.2059e-05 | -0.00010967 | 0.0082071 | 0.0082056 | 0.0082071 | 0.98844 | -0.24369 | 0.98849 | -0.24337 | 3.9081
83 | -8.3063 | -3.594 | 8.3073 | 3.5918 | 0.00092898 | -0.0022081 | 0.26214 | 0.26211 | 0.26214 | 0.99666 | -0.17457 | 0.99678 | -0.17386 | 41.088
84 | -0.38745 | -0.18765 | 0.38746 | 0.18699 | 6.0146e-06 | -0.00066773 | 0.012553 | 0.012545 | 0.012553 | 0.99 | -0.43568 | 0.99002 | -0.43582 | 5.706
85 | -0.38746 | -0.18699 | 0.38759 | 0.17288 | 0.00012516 | -0.014107 | 0.012545 | 0.012371 | 0.012545 | 0.99002 | -0.43582 | 0.99032 | -0.43837 | 5.7021
86 | -0.38759 | -0.17288 | 0.3876 | 0.17154 | 1.1718e-05 | -0.0013413 | 0.012371 | 0.012355 | 0.012371 | 0.99032 | -0.43837 | 0.99034 | -0.43858 | 5.6232
87 | -0.7895 | -0.36619 | 0.78963 | 0.36614 | 0.00012748 | -5.036e-05 | 0.025368 | 0.025366 | 0.025368 | 0.99034 | -0.43858 | 0.99051 | -0.43734 | 12.08
88 | -1.6863 | -0.78174 | 1.6868 | 0.7793 | 0.00043759 | -0.0024396 | 0.054429 | 0.054398 | 0.054429 | 0.98581 | -0.52946 | 0.98605 | -0.5315 | 24.7406
89 | 1.5893 | 0.73515 | -1.5885 | -0.73991 | 0.00075441 | -0.0047549 | 0.051277 | 0.051339 | 0.051339 | 0.98581 | -0.52946 | 0.98537 | -0.52571 | 23.3358
90 | 0.097045 | 0.046586 | -0.097045 | -0.047001 | 2.3758e-07 | -0.00041481 | 0.0031523 | 0.0031575 | 0.0031575 | 0.98581 | -0.52946 | 0.98581 | -0.52944 | 1.4352
91 | -1.6868 | -0.7793 | 1.6868 | 0.77896 | 6.1017e-05 | -0.00034051 | 0.054398 | 0.054393 | 0.054398 | 0.98605 | -0.5315 | 0.98608 | -0.53178 | 24.7262
92 | 0.12028 | 0.057347 | -0.12028 | -0.058254 | 7.9861e-07 | -0.00090709 | 0.0039038 | 0.0039153 | 0.0039153 | 0.98537 | -0.52571 | 0.98536 | -0.52565 | 1.7797
93 | 1.321 | 0.6124 | -1.321 | -0.61294 | 5.8954e-05 | -0.00054501 | 0.042657 | 0.042664 | 0.042664 | 0.98537 | -0.52571 | 0.98533 | -0.52536 | 19.3927
94 | 0.14724 | 0.070163 | -0.14724 | -0.070621 | 6.033e-07 | -0.00045811 | 0.0047782 | 0.004784 | 0.004784 | 0.98537 | -0.52571 | 0.98537 | -0.52568 | 2.1746
95 | -0.88036 | -0.40868 | 0.88043 | 0.40719 | 6.889e-05 | -0.0014914 | 0.028287 | 0.028268 | 0.028287 | 0.99051 | -0.43734 | 0.99059 | -0.43796 | 12.8577
96 | 0.090731 | 0.042542 | -0.09073 | -0.043899 | 6.6313e-07 | -0.0013562 | 0.0029205 | 0.0029375 | 0.0029375 | 0.99051 | -0.43734 | 0.99051 | -0.43728 | 1.3352
97 | -2.0956 | -0.97692 | 2.0956 | 0.97682 | 2.8826e-05 | -0.00010087 | 0.067687 | 0.067686 | 0.067687 | 0.98608 | -0.53178 | 0.98609 | -0.53189 | 30.7668
98 | 1.321 | 0.61294 | -1.3208 | -0.61403 | 0.0001181 | -0.0010911 | 0.042664 | 0.042678 | 0.042678 | 0.98533 | -0.52536 | 0.98525 | -0.52465 | 19.3991
99 | 0.076166 | 0.036199 | -0.076166 | -0.036889 | 2.4316e-07 | -0.00068929 | 0.0024706 | 0.0024793 | 0.0024793 | 0.98537 | -0.52568 | 0.98536 | -0.52565 | 1.127
100 | 8.3089 | 3.5879 | -8.3073 | -3.5918 | 0.0016496 | -0.0039241 | 0.26205 | 0.26211 | 0.26211 | 0.99699 | -0.17261 | 0.99678 | -0.17386 | 41.083
101 | -8.3089 | -3.5879 | 8.3221 | 3.6225 | 0.013134 | 0.03458 | 0.26205 | 0.26205 | 0.26205 | 0.99699 | -0.17261 | 0.99986 | -0.000789 | 40.6285
102 | 0.19216 | 0.091882 | -0.19216 | -0.093065 | 2.574e-06 | -0.0011831 | 0.0061884 | 0.0062033 | 0.0062033 | 0.99358 | -0.22078 | 0.99356 | -0.22067 | 2.8197
103 | 5.1404 | 2.3984 | -5.1389 | -2.3947 | 0.0014724 | 0.0037568 | 0.1657 | 0.16571 | 0.16571 | 0.9882 | -0.49976 | 0.98768 | -0.52973 | 25.6908
104 | 5.0334 | 2.3436 | -5.0333 | -2.3446 | 0.00013969 | -0.00097338 | 0.16228 | 0.16229 | 0.16229 | 0.98768 | -0.52973 | 0.98765 | -0.52986 | 25.4378
105 | 5.0333 | 2.3446 | -5.0326 | -2.3494 | 0.00070076 | -0.0048797 | 0.16229 | 0.16236 | 0.16236 | 0.98765 | -0.52986 | 0.98751 | -0.53049 | 25.448
106 | 0.25279 | 0.12231 | -0.25279 | -0.12237 | 5.7127e-06 | -5.2292e-05 | 0.0081913 | 0.008192 | 0.008192 | 0.98969 | -0.44221 | 0.98966 | -0.44235 | 3.901
107 | -5.8385 | -2.7248 | 5.8422 | 2.7058 | 0.0037405 | -0.01903 | 0.18793 | 0.18767 | 0.18793 | 0.98969 | -0.44221 | 0.99034 | -0.43924 | 29.4565
108 | 0.25279 | 0.12237 | -0.25279 | -0.12243 | 2.4167e-07 | -6.2998e-05 | 0.008192 | 0.0081928 | 0.0081928 | 0.98966 | -0.44235 | 0.98966 | -0.44235 | 3.724
109 | -5.8422 | -2.7058 | 5.8429 | 2.7024 | 0.00065629 | -0.0033479 | 0.18767 | 0.18763 | 0.18767 | 0.99034 | -0.43924 | 0.99046 | -0.43871 | 29.4158
110 | -0.88043 | -0.40719 | 0.88047 | 0.40624 | 4.3699e-05 | -0.00094718 | 0.028268 | 0.028257 | 0.028268 | 0.99059 | -0.43796 | 0.99063 | -0.43835 | 12.8493
111 | 0.09073 | 0.043899 | -0.09073 | -0.043943 | 2.176e-08 | -4.4216e-05 | 0.0029375 | 0.0029381 | 0.0029381 | 0.99051 | -0.43728 | 0.99051 | -0.43728 | 1.3355
112 | -0.97918 | -0.45405 | 0.97933 | 0.45404 | 0.00015247 | -5.8644e-06 | 0.031452 | 0.031451 | 0.031452 | 0.99063 | -0.43835 | 0.9908 | -0.43715 | 14.9772
113 | 0.3685 | 0.17819 | -0.3685 | -0.17847 | 2.2515e-06 | -0.00027932 | 0.011903 | 0.011907 | 0.011907 | 0.99269 | -0.33663 | 0.99269 | -0.33657 | 5.4121
114 | 7.5578 | 3.5135 | -7.5507 | -3.4946 | 0.0071869 | 0.01886 | 0.24237 | 0.24238 | 0.24238 | 0.99269 | -0.33663 | 0.99095 | -0.43644 | 37.5777
115 | 7.2532 | 3.3505 | -7.2521 | -3.3539 | 0.0010761 | -0.003359 | 0.23275 | 0.2328 | 0.2328 | 0.99095 | -0.43644 | 0.9908 | -0.43715 | 36.4885
116 | 0.3448 | 0.16673 | -0.34475 | -0.16697 | 5.0241e-05 | -0.0002338 | 0.011159 | 0.011162 | 0.011162 | 0.9908 | -0.43715 | 0.99064 | -0.43812 | 5.3153
117 | 5.928 | 2.7331 | -5.9263 | -2.7413 | 0.0016538 | -0.0081873 | 0.19019 | 0.1903 | 0.1903 | 0.9908 | -0.43715 | 0.99051 | -0.43849 | 29.8276
118 | 5.9263 | 2.7413 | -5.926 | -2.7427 | 0.00028139 | -0.0013915 | 0.1903 | 0.19032 | 0.19032 | 0.99051 | -0.43849 | 0.99046 | -0.43871 | 29.8306
119 | -0.29632 | -0.14351 | 0.29632 | 0.14335 | 8.7739e-07 | -0.0001643 | 0.0096344 | 0.0096323 | 0.0096344 | 0.98651 | -0.53542 | 0.98652 | -0.53544 | 4.3793
120 | -0.29632 | -0.14335 | 0.29633 | 0.14253 | 4.3589e-06 | -0.00081732 | 0.0096323 | 0.0096219 | 0.0096323 | 0.98652 | -0.53544 | 0.98653 | -0.53557 | 4.3783
121 | 1.3883 | 0.65284 | -1.3882 | -0.65366 | 9.7986e-05 | -0.00081701 | 0.044891 | 0.044902 | 0.044902 | 0.98653 | -0.53557 | 0.98646 | -0.53499 | 20.41
122 | 0.30182 | 0.14529 | -0.30182 | -0.14554 | 1.3836e-06 | -0.00025018 | 0.0098019 | 0.0098051 | 0.0098051 | 0.98653 | -0.53557 | 0.98653 | -0.53553 | 4.4569
123 | -1.9865 | -0.94067 | 1.9865 | 0.94032 | 8.8352e-05 | -0.00034563 | 0.064315 | 0.06431 | 0.064315 | 0.98653 | -0.53557 | 0.98657 | -0.53594 | 29.234
124 | 1.2845 | 0.60345 | -1.2845 | -0.6039 | 4.6292e-05 | -0.00045328 | 0.041531 | 0.041537 | 0.041537 | 0.98646 | -0.53499 | 0.98643 | -0.5347 | 18.8805
125 | 0.30182 | 0.14554 | -0.30182 | -0.14618 | 3.5049e-06 | -0.000633 | 0.0098051 | 0.0098131 | 0.0098131 | 0.98653 | -0.53553 | 0.98651 | -0.53543 | 4.4605
126 | -2.1375 | -1.0134 | 2.1376 | 1.0129 | 0.00015535 | -0.00051847 | 0.069217 | 0.069209 | 0.069217 | 0.98657 | -0.53594 | 0.98664 | -0.53654 | 31.462
127 | 1.1737 | 0.55026 | -1.1737 | -0.55075 | 4.1614e-05 | -0.00049077 | 0.037936 | 0.037942 | 0.037942 | 0.98643 | -0.5347 | 0.9864 | -0.53441 | 17.2465
128 | -2.247 | -1.0659 | 2.2471 | 1.0655 | 0.00011019 | -0.00032967 | 0.072765 | 0.07276 | 0.072765 | 0.98664 | -0.53654 | 0.98668 | -0.53695 | 33.0748
129 | -4.8018 | -2.2481 | 4.8031 | 2.2383 | 0.001273 | -0.0097916 | 0.15503 | 0.1549 | 0.15503 | 0.98724 | -0.53169 | 0.98751 | -0.53049 | 24.2999
130 | 4.8018 | 2.2481 | -4.8013 | -2.2515 | 0.00044791 | -0.0034396 | 0.15503 | 0.15508 | 0.15508 | 0.98724 | -0.53169 | 0.98714 | -0.53211 | 24.307
131 | 0.22955 | 0.11117 | -0.22955 | -0.11118 | 5.2052e-07 | -5.7919e-06 | 0.0074559 | 0.007456 | 0.007456 | 0.98751 | -0.53049 | 0.98751 | -0.53051 | 3.5505
132 | 4.6967 | 2.2008 | -4.6966 | -2.2019 | 0.00013127 | -0.0010565 | 0.15168 | 0.15169 | 0.15169 | 0.98714 | -0.53211 | 0.98711 | -0.53223 | 23.7766
133 | 4.5798 | 2.1453 | -4.5797 | -2.1458 | 6.2132e-05 | -0.00052777 | 0.1479 | 0.14791 | 0.14791 | 0.98711 | -0.53223 | 0.9871 | -0.53229 | 23.1826
134 | 0.071059 | 0.033086 | -0.071059 | -0.034415 | 4.0515e-07 | -0.0013291 | 0.0022944 | 0.0023111 | 0.0023111 | 0.98622 | -0.53295 | 0.98622 | -0.5329 | 1.0505
135 | -0.23644 | -0.10841 | 0.23646 | 0.10218 | 2.0605e-05 | -0.0062392 | 0.0076137 | 0.0075393 | 0.0076137 | 0.98622 | -0.53295 | 0.9863 | -0.53357 | 3.4608
136 | 0.092391 | 0.0438 | -0.092391 | -0.044747 | 4.8984e-07 | -0.00094735 | 0.0029929 | 0.0030049 | 0.0030049 | 0.98622 | -0.53295 | 0.98622 | -0.53291 | 1.3658
137 | 0.5821 | 0.28086 | -0.58208 | -0.28191 | 2.1758e-05 | -0.0010506 | 0.018917 | 0.01893 | 0.01893 | 0.9863 | -0.53357 | 0.98627 | -0.53325 | 8.6046
138 | -0.81856 | -0.38304 | 0.81862 | 0.3815 | 6.2503e-05 | -0.0015369 | 0.026451 | 0.026432 | 0.026451 | 0.9863 | -0.53357 | 0.98637 | -0.53418 | 12.0233
139 | -1.0507 | -0.49164 | 1.0507 | 0.4912 | 2.9894e-05 | -0.00044253 | 0.03395 | 0.033944 | 0.03395 | 0.98637 | -0.53418 | 0.9864 | -0.53441 | 15.4318
140 | 0.23208 | 0.11014 | -0.23208 | -0.11079 | 2.1247e-06 | -0.00065275 | 0.0075182 | 0.0075264 | 0.0075264 | 0.98637 | -0.53418 | 0.98636 | -0.53411 | 3.4211
141 | 0.10325 | 0.049418 | -0.10325 | -0.050006 | 3.804e-07 | -0.00058836 | 0.0033501 | 0.0033575 | 0.0033575 | 0.98636 | -0.53411 | 0.98636 | -0.53407 | 1.5262
142 | 0.12883 | 0.061375 | -0.12883 | -0.062394 | 1.0247e-06 | -0.0010188 | 0.0041764 | 0.0041893 | 0.0041893 | 0.98636 | -0.53411 | 0.98636 | -0.53404 | 1.9042
143 | 0.12243 | 0.059171 | -0.12243 | -0.059295 | 1.128e-07 | -0.00012401 | 0.0039783 | 0.0039799 | 0.0039799 | 0.98668 | -0.53695 | 0.98668 | -0.53694 | 1.809
144 | -4.4665 | -2.0968 | 4.4682 | 2.0924 | 0.0017178 | -0.0044567 | 0.14436 | 0.14429 | 0.14436 | 0.98668 | -0.53695 | 0.9871 | -0.53229 | 39.8783
145 | 2.0969 | 0.97213 | -2.0956 | -0.97682 | 0.001338 | -0.00469 | 0.067623 | 0.067686 | 0.067686 | 0.98668 | -0.53695 | 0.98609 | -0.53189 | 30.7661
146 | 0.11152 | 0.053453 | -0.11152 | -0.05401 | 4.1894e-07 | -0.00055695 | 0.0036166 | 0.0036236 | 0.0036236 | 0.9871 | -0.53229 | 0.9871 | -0.53226 | 1.6471
147 | 1.2496 | 0.57951 | -1.2495 | -0.57998 | 4.5335e-05 | -0.00046969 | 0.040358 | 0.040364 | 0.040364 | 0.98525 | -0.52465 | 0.98521 | -0.52437 | 18.3471
148 | -0.63192 | -0.29924 | 0.63194 | 0.29842 | 2.0177e-05 | -0.00082759 | 0.020496 | 0.020485 | 0.020496 | 0.9848 | -0.52083 | 0.98482 | -0.5211 | 9.3162
149 | 0.53831 | 0.25391 | -0.5383 | -0.25503 | 1.9824e-05 | -0.0011228 | 0.017447 | 0.017461 | 0.017461 | 0.9848 | -0.52083 | 0.98476 | -0.52053 | 7.9369
150 | 0.077167 | 0.033497 | -0.077166 | -0.037193 | 1.3189e-06 | -0.0036956 | 0.0024659 | 0.002511 | 0.002511 | 0.98482 | -0.5211 | 0.98481 | -0.52097 | 1.1414
151 | -0.70911 | -0.33191 | 0.70933 | 0.3246 | 0.00022306 | -0.0073115 | 0.02295 | 0.022859 | 0.02295 | 0.98482 | -0.5211 | 0.98512 | -0.52356 | 10.4318
152 | 0.5383 | 0.25503 | -0.53827 | -0.25666 | 2.8888e-05 | -0.0016327 | 0.017461 | 0.017482 | 0.017482 | 0.98476 | -0.52053 | 0.98471 | -0.52008 | 7.9463
153 | 0.077166 | 0.037193 | -0.077166 | -0.037373 | 6.5689e-08 | -0.00018048 | 0.002511 | 0.0025133 | 0.0025133 | 0.98481 | -0.52097 | 0.98481 | -0.52096 | 1.1424
154 | -0.79748 | -0.36596 | 0.79757 | 0.36378 | 8.4079e-05 | -0.0021849 | 0.025712 | 0.025685 | 0.025712 | 0.98512 | -0.52356 | 0.98521 | -0.52437 | 11.6874
155 | 0.08815 | 0.041359 | -0.08815 | -0.042693 | 6.2969e-07 | -0.0013344 | 0.0028533 | 0.0028701 | 0.0028701 | 0.98512 | -0.52356 | 0.98511 | -0.5235 | 1.3046
156 | 0.53827 | 0.25666 | -0.53826 | -0.25712 | 8.1555e-06 | -0.00046021 | 0.017482 | 0.017488 | 0.017488 | 0.98471 | -0.52008 | 0.9847 | -0.51995 | 7.9489
157 | 0.45195 | 0.2162 | -0.45192 | -0.21856 | 2.9394e-05 | -0.0023542 | 0.01468 | 0.01471 | 0.01471 | 0.98521 | -0.52437 | 0.98515 | -0.52381 | 6.6863
158 | 0.45192 | 0.21856 | -0.45192 | -0.21887 | 3.9348e-06 | -0.00031439 | 0.01471 | 0.014714 | 0.014714 | 0.98515 | -0.52381 | 0.98515 | -0.52373 | 6.6881
159 | 0.46831 | 0.22325 | -0.46831 | -0.22356 | 4.1293e-06 | -0.00030826 | 0.015209 | 0.015213 | 0.015213 | 0.9847 | -0.51995 | 0.98469 | -0.51988 | 6.9151
160 | 0.46831 | 0.22356 | -0.4683 | -0.2244 | 1.1254e-05 | -0.0008393 | 0.015213 | 0.015224 | 0.015224 | 0.98469 | -0.51988 | 0.98467 | -0.51967 | 6.9199
161 | -0.074144 | -0.035909 | 0.074144 | 0.035098 | 2.7172e-07 | -0.00081097 | 0.0024153 | 0.002405 | 0.0024153 | 0.98462 | -0.51926 | 0.98463 | -0.51929 | 1.0979
162 | -0.46828 | -0.22596 | 0.4683 | 0.2244 | 2.1004e-05 | -0.0015631 | 0.015244 | 0.015224 | 0.015244 | 0.98463 | -0.51929 | 0.98467 | -0.51967 | 6.929
163 | 0.39413 | 0.19086 | -0.39412 | -0.19088 | 6.9639e-06 | -2.3081e-05 | 0.012839 | 0.012839 | 0.012839 | 0.98463 | -0.51929 | 0.98461 | -0.51941 | 6.1139

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 16.9439 | 7.6726

## res_load
| p_mw | q_mvar
0 | 0.33656 | 0.163
1 | 0.20763 | 0.10056
2 | 0.16193 | 0.078426
3 | 0.13912 | 0.067381
4 | 0.30127 | 0.14591
5 | 0.16054 | 0.077752
6 | 0.37063 | 0.17951
7 | 0.11612 | 0.05624
8 | 0.37281 | 0.18056
9 | 0.27449 | 0.13294
10 | 0.27173 | 0.1316
11 | 0.22825 | 0.11055
12 | 0.093244 | 0.04516
13 | 0.37577 | 0.182
14 | 0.35524 | 0.17205
15 | 0.13636 | 0.06604
16 | 0.27505 | 0.13321
17 | 0.26718 | 0.1294
18 | 0.32618 | 0.15798
19 | 0.35407 | 0.17148
20 | 0.25601 | 0.12399
21 | 0.21623 | 0.10473
22 | 0.35101 | 0.17
23 | 0.24394 | 0.11815
24 | 0.27653 | 0.13393
25 | 0.34772 | 0.16841
26 | 0.14845 | 0.071899
27 | 0.076179 | 0.036895
28 | 0.086285 | 0.04179
29 | 0.072988 | 0.03535
30 | 0.19094 | 0.092476
31 | 0.17943 | 0.0869
32 | 0.33607 | 0.16277
33 | 0.10877 | 0.052679
34 | 0.17498 | 0.084747
35 | 0.25291 | 0.12249
36 | 0.10444 | 0.050584
37 | 0.38745 | 0.18765
38 | 0.4019 | 0.19465
39 | 0.097045 | 0.047001
40 | 0.40874 | 0.19796
41 | 0.12028 | 0.058254
42 | 0.071072 | 0.034422
43 | 0.36643 | 0.17747
44 | 0.19216 | 0.093065
45 | 0.232 | 0.11236
46 | 0.1055 | 0.051095
47 | 0.098707 | 0.047806
48 | 0.09073 | 0.043943
49 | 0.3685 | 0.17847
50 | 0.29749 | 0.14408
51 | 0.34475 | 0.16697
52 | 0.29632 | 0.14351
53 | 0.10367 | 0.050211
54 | 0.15092 | 0.073093
55 | 0.30182 | 0.14618
56 | 0.11075 | 0.053641
57 | 0.10936 | 0.052966
58 | 0.068767 | 0.033306
59 | 0.083135 | 0.040264
60 | 0.1046 | 0.050659
61 | 0.22955 | 0.11118
62 | 0.25279 | 0.12243
63 | 0.11684 | 0.05659
64 | 0.071059 | 0.034415
65 | 0.092391 | 0.044747
66 | 0.12296 | 0.059551
67 | 0.58208 | 0.28191
68 | 0.12883 | 0.062394
69 | 0.10325 | 0.050006
70 | 0.12243 | 0.059295
71 | 0.11152 | 0.05401
72 | 0.071283 | 0.034524
73 | 0.076166 | 0.036889
74 | 0.093606 | 0.045335
75 | 0.077166 | 0.037373
76 | 0.08815 | 0.042693
77 | 0.45192 | 0.21887
78 | 0.069947 | 0.033877
79 | 0.074144 | 0.035909
80 | 0.39412 | 0.19088

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1