## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_526_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_526_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_526_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_526_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_526_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_526_0_node_5 | 20 | n |  | TRUE
6 | bus_MV_526_0_node_80 | 20 | n |  | TRUE
7 | bus_MV_526_0_node_78 | 20 | n |  | TRUE
8 | bus_MV_526_0_node_18 | 20 | n |  | TRUE
9 | bus_MV_526_0_node_79 | 20 | n |  | TRUE
10 | bus_MV_526_0_node_6 | 20 | n |  | TRUE
11 | bus_MV_526_0_node_7 | 20 | n |  | TRUE
12 | bus_MV_526_0_node_8 | 20 | n |  | TRUE
13 | bus_MV_526_0_node_35 | 20 | n |  | TRUE
14 | bus_MV_526_0_node_44 | 20 | n |  | TRUE
15 | bus_MV_526_0_node_36 | 20 | n |  | TRUE
16 | bus_MV_526_0_node_73 | 20 | n |  | TRUE
17 | bus_MV_526_0_node_45 | 20 | n |  | TRUE
18 | bus_MV_526_0_node_9 | 20 | n |  | TRUE
19 | bus_MV_526_0_node_10 | 20 | n |  | TRUE
20 | bus_MV_526_0_node_11 | 20 | n |  | TRUE
21 | bus_MV_526_0_node_12 | 20 | n |  | TRUE
22 | bus_MV_526_0_node_59 | 20 | n |  | TRUE
23 | bus_MV_526_0_node_58 | 20 | n |  | TRUE
24 | bus_MV_526_0_node_57 | 20 | n |  | TRUE
25 | bus_MV_526_0_node_60 | 20 | n |  | TRUE
26 | bus_MV_526_0_node_61 | 20 | n |  | TRUE
27 | bus_MV_526_0_node_13 | 20 | n |  | TRUE
28 | bus_MV_526_0_node_14 | 20 | n |  | TRUE
29 | bus_MV_526_0_node_15 | 20 | n |  | TRUE
30 | bus_MV_526_0_node_16 | 20 | n |  | TRUE
31 | bus_MV_526_0_node_17 | 20 | n |  | TRUE
32 | bus_MV_526_0_node_19 | 20 | n |  | TRUE
33 | bus_MV_526_0_node_21 | 20 | n |  | TRUE
34 | bus_MV_526_0_node_23 | 20 | n |  | TRUE
35 | bus_MV_526_0_node_106 | 20 | n |  | TRUE
36 | bus_MV_526_0_node_20 | 20 | n |  | TRUE
37 | bus_MV_526_0_node_26 | 20 | n |  | TRUE
38 | bus_MV_526_0_node_25 | 20 | n |  | TRUE
39 | bus_MV_526_0_node_31 | 20 | n |  | TRUE
40 | bus_MV_526_0_node_22 | 20 | n |  | TRUE
41 | bus_MV_526_0_node_76 | 20 | n |  | TRUE
42 | bus_MV_526_0_node_24 | 20 | n |  | TRUE
43 | bus_MV_526_0_node_56 | 20 | n |  | TRUE
44 | bus_MV_526_0_node_50 | 20 | n |  | TRUE
45 | bus_MV_526_0_node_27 | 20 | n |  | TRUE
46 | bus_MV_526_0_node_28 | 20 | n |  | TRUE
47 | bus_MV_526_0_node_30 | 20 | n |  | TRUE
48 | bus_MV_526_0_node_29 | 20 | n |  | TRUE
49 | bus_MV_526_0_node_102 | 20 | n |  | TRUE
50 | bus_MV_526_0_node_82 | 20 | n |  | TRUE
51 | bus_MV_526_0_node_100 | 20 | n |  | TRUE
52 | bus_MV_526_0_node_83 | 20 | n |  | TRUE
53 | bus_MV_526_0_node_32 | 20 | n |  | TRUE
54 | bus_MV_526_0_node_33 | 20 | n |  | TRUE
55 | bus_MV_526_0_node_34 | 20 | n |  | TRUE
56 | bus_MV_526_0_node_37 | 20 | n |  | TRUE
57 | bus_MV_526_0_node_54 | 20 | n |  | TRUE
58 | bus_MV_526_0_node_85 | 20 | n |  | TRUE
59 | bus_MV_526_0_node_38 | 20 | n |  | TRUE
60 | bus_MV_526_0_node_72 | 20 | n |  | TRUE
61 | bus_MV_526_0_node_95 | 20 | n |  | TRUE
62 | bus_MV_526_0_node_39 | 20 | n |  | TRUE
63 | bus_MV_526_0_node_107 | 20 | n |  | TRUE
64 | bus_MV_526_0_node_93 | 20 | n |  | TRUE
65 | bus_MV_526_0_node_55 | 20 | n |  | TRUE
66 | bus_MV_526_0_node_49 | 20 | n |  | TRUE
67 | bus_MV_526_0_node_86 | 20 | n |  | TRUE
68 | bus_MV_526_0_node_74 | 20 | n |  | TRUE
69 | bus_MV_526_0_node_108 | 20 | n |  | TRUE
70 | bus_MV_526_0_node_62 | 20 | n |  | TRUE
71 | bus_MV_526_0_node_84 | 20 | n |  | TRUE
72 | bus_MV_526_0_node_40 | 20 | n |  | TRUE
73 | bus_MV_526_0_node_41 | 20 | n |  | TRUE
74 | bus_MV_526_0_node_42 | 20 | n |  | TRUE
75 | bus_MV_526_0_node_43 | 20 | n |  | TRUE
76 | bus_MV_526_0_node_65 | 20 | n |  | TRUE
77 | bus_MV_526_0_node_67 | 20 | n |  | TRUE
78 | bus_MV_526_0_node_64 | 20 | n |  | TRUE
79 | bus_MV_526_0_node_46 | 20 | n |  | TRUE
80 | bus_MV_526_0_node_75 | 20 | n |  | TRUE
81 | bus_MV_526_0_node_47 | 20 | n |  | TRUE
82 | bus_MV_526_0_node_48 | 20 | n |  | TRUE
83 | bus_MV_526_0_node_51 | 20 | n |  | TRUE
84 | bus_MV_526_0_node_53 | 20 | n |  | TRUE
85 | bus_MV_526_0_node_91 | 20 | n |  | TRUE
86 | bus_MV_526_0_node_52 | 20 | n |  | TRUE
87 | bus_MV_526_0_node_89 | 20 | n |  | TRUE
88 | bus_MV_526_0_node_70 | 20 | n |  | TRUE
89 | bus_MV_526_0_node_77 | 20 | n |  | TRUE
90 | bus_MV_526_0_node_90 | 20 | n |  | TRUE
91 | bus_MV_526_0_node_88 | 20 | n |  | TRUE
92 | bus_MV_526_0_node_69 | 20 | n |  | TRUE
93 | bus_MV_526_0_node_68 | 20 | n |  | TRUE
94 | bus_MV_526_0_node_63 | 20 | n |  | TRUE
95 | bus_MV_526_0_node_66 | 20 | n |  | TRUE
96 | bus_MV_526_0_node_71 | 20 | n |  | TRUE
97 | bus_MV_526_0_node_99 | 20 | n |  | TRUE
98 | bus_MV_526_0_node_94 | 20 | n |  | TRUE
99 | bus_MV_526_0_node_101 | 20 | n |  | TRUE
100 | bus_MV_526_0_node_81 | 20 | n |  | TRUE
101 | bus_MV_526_0_node_103 | 20 | n |  | TRUE
102 | bus_MV_526_0_node_98 | 20 | n |  | TRUE
103 | bus_MV_526_0_node_96 | 20 | n |  | TRUE
104 | bus_MV_526_0_node_104 | 20 | n |  | TRUE
105 | bus_MV_526_0_node_97 | 20 | n |  | TRUE
106 | bus_MV_526_0_node_87 | 20 | n |  | TRUE
107 | bus_MV_526_0_node_105 | 20 | n |  | TRUE
108 | bus_MV_526_0_node_92 | 20 | n |  | TRUE
109 | bus_HV_526_0_node_56 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_526_0_load_0 | 0 | 0.37415 | 0.18121 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_526_0_load_3 | 3 | 0.075071 | 0.036359 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_526_0_load_4 | 4 | 0.35484 | 0.17186 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_526_0_load_80 | 6 | 0.15781 | 0.076433 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_526_0_load_78 | 7 | 0.4343 | 0.21034 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_526_0_load_6 | 10 | 0.29844 | 0.14454 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_526_0_load_44 | 14 | 0.56719 | 0.2747 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_526_0_load_73 | 16 | 0.25376 | 0.1229 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_526_0_load_9 | 18 | 0.25299 | 0.12253 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_526_0_load_59 | 22 | 0.28401 | 0.13755 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_526_0_load_57 | 24 | 0.31714 | 0.1536 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_526_0_load_61 | 26 | 0.19365 | 0.09379 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_526_0_load_13 | 27 | 2.172 | 1.052 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_526_0_load_23 | 34 | 1.0795 | 0.52284 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_526_0_load_106 | 35 | 0.32807 | 0.15889 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_526_0_load_25 | 38 | 0.080886 | 0.039175 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_526_0_load_31 | 39 | 0.46877 | 0.22703 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_526_0_load_76 | 41 | 1.3106 | 0.63476 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_526_0_load_24 | 42 | 0.084898 | 0.041118 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_526_0_load_56 | 43 | 0.071747 | 0.034749 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_526_0_load_27 | 45 | 1.9623 | 0.95038 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_526_0_load_102 | 49 | 0.24215 | 0.11728 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_526_0_load_82 | 50 | 0.21572 | 0.10448 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_526_0_load_83 | 52 | 0.20828 | 0.10087 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_526_0_load_33 | 54 | 0.078742 | 0.038137 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_526_0_load_85 | 58 | 0.58014 | 0.28097 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_526_0_load_72 | 60 | 0.36375 | 0.17617 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_526_0_load_95 | 61 | 0.38085 | 0.18445 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_526_0_load_107 | 63 | 0.21188 | 0.10262 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_526_0_load_93 | 64 | 0.53201 | 0.25767 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_526_0_load_55 | 65 | 0.23958 | 0.11603 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_526_0_load_74 | 68 | 0.19913 | 0.096442 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_526_0_load_108 | 69 | 0.10674 | 0.051698 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_526_0_load_84 | 71 | 0.40508 | 0.19619 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_526_0_load_40 | 72 | 0.16813 | 0.08143 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_526_0_load_42 | 74 | 0.16301 | 0.07895 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_526_0_load_43 | 75 | 0.25891 | 0.1254 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_526_0_load_75 | 80 | 0.56691 | 0.27457 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_526_0_load_47 | 81 | 0.53762 | 0.26038 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_526_0_load_91 | 85 | 0.13033 | 0.063123 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_526_0_load_70 | 88 | 0.21351 | 0.10341 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_526_0_load_77 | 89 | 0.12917 | 0.062562 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_526_0_load_88 | 91 | 2.8157 | 1.3637 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_526_0_load_63 | 94 | 0.14867 | 0.072005 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_526_0_load_71 | 96 | 0.19803 | 0.09591 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_526_0_load_99 | 97 | 0.21061 | 0.102 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_526_0_load_94 | 98 | 0.079938 | 0.038716 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_526_0_load_103 | 101 | 0.10375 | 0.050246 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_526_0_load_104 | 104 | 0.11977 | 0.058008 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_526_0_load_97 | 105 | 0.40363 | 0.19549 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_526_0_load_105 | 107 | 0.1907 | 0.092359 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_526_0_load_92 | 108 | 0.33727 | 0.16335 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 43 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_526_0_line_0 |  | 0 | 1 | 0.013031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_526_0_line_1 |  | 0 | 2 | 0.037059 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_526_0_line_2 |  | 1 | 3 | 0.029043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_526_0_line_3 |  | 2 | 4 | 0.061155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_526_0_line_4 |  | 2 | 5 | 0.19852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_526_0_line_5 |  | 5 | 6 | 0.037899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_526_0_line_6 |  | 5 | 7 | 0.019178 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_526_0_line_7 |  | 6 | 8 | 0.013714 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_526_0_line_8 |  | 7 | 9 | 0.02218 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_526_0_line_9 |  | 8 | 31 | 0.10205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_526_0_line_10 |  | 9 | 100 | 0.61076 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_526_0_line_11 |  | 10 | 11 | 0.066605 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_526_0_line_12 |  | 11 | 12 | 0.086418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_526_0_line_13 |  | 12 | 13 | 0.05785 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_526_0_line_14 |  | 12 | 14 | 0.034274 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_526_0_line_15 |  | 13 | 15 | 0.065932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_526_0_line_16 |  | 13 | 16 | 0.035672 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_526_0_line_17 |  | 14 | 17 | 0.0547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_526_0_line_18 |  | 15 | 56 | 0.26045 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
19 | MV_526_0_line_19 |  | 15 | 59 | 0.23103 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
20 | MV_526_0_line_20 |  | 15 | 60 | 0.016783 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_526_0_line_21 |  | 15 | 53 | 0.38174 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_526_0_line_22 |  | 16 | 68 | 0.019662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_526_0_line_23 |  | 17 | 79 | 0.093339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_526_0_line_24 |  | 18 | 19 | 0.065879 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_526_0_line_25 |  | 19 | 20 | 0.14851 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_526_0_line_26 |  | 19 | 21 | 0.21747 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
27 | MV_526_0_line_27 |  | 20 | 22 | 0.032233 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
28 | MV_526_0_line_28 |  | 21 | 23 | 0.046643 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
29 | MV_526_0_line_29 |  | 21 | 24 | 0.059466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_526_0_line_30 |  | 22 | 25 | 0.014943 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
31 | MV_526_0_line_31 |  | 23 | 26 | 0.040058 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
32 | MV_526_0_line_32 |  | 25 | 70 | 0.43531 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_526_0_line_33 |  | 25 | 62 | 0.090548 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
34 | MV_526_0_line_34 |  | 26 | 92 | 0.038592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_526_0_line_35 |  | 27 | 28 | 0.055841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_526_0_line_36 |  | 27 | 29 | 0.063887 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
37 | MV_526_0_line_37 |  | 28 | 30 | 0.013027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_526_0_line_38 |  | 28 | 31 | 0.32349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_526_0_line_39 |  | 29 | 32 | 0.18696 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
40 | MV_526_0_line_40 |  | 29 | 33 | 0.15231 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
41 | MV_526_0_line_41 |  | 30 | 34 | 0.027352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_526_0_line_42 |  | 31 | 35 | 0.004342 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_526_0_line_43 |  | 32 | 36 | 0.17796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_526_0_line_44 |  | 32 | 37 | 0.013551 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
45 | MV_526_0_line_45 |  | 32 | 38 | 0.07422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_526_0_line_46 |  | 33 | 40 | 0.15657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_526_0_line_47 |  | 33 | 41 | 0.023432 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
48 | MV_526_0_line_48 |  | 36 | 39 | 0.0038621 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_526_0_line_49 |  | 37 | 43 | 0.027218 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
50 | MV_526_0_line_50 |  | 40 | 42 | 0.020956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_526_0_line_51 |  | 41 | 44 | 0.040427 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
52 | MV_526_0_line_52 |  | 44 | 82 | 0.12037 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
53 | MV_526_0_line_53 |  | 45 | 46 | 0.020875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_526_0_line_54 |  | 46 | 47 | 0.10936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_526_0_line_55 |  | 47 | 50 | 0.022578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_526_0_line_56 |  | 47 | 48 | 0.20705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_526_0_line_57 |  | 48 | 49 | 0.027365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_526_0_line_58 |  | 49 | 51 | 0.023599 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_526_0_line_59 |  | 50 | 52 | 0.017458 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_526_0_line_60 |  | 51 | 99 | 0.11273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_526_0_line_61 |  | 53 | 54 | 0.039864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_526_0_line_62 |  | 55 | 56 | 0.29157 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_526_0_line_63 |  | 55 | 57 | 0.13058 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
64 | MV_526_0_line_64 |  | 55 | 58 | 0.0035526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_526_0_line_65 |  | 56 | 61 | 0.040009 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_526_0_line_66 |  | 57 | 65 | 0.062301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_526_0_line_67 |  | 57 | 66 | 0.061394 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
68 | MV_526_0_line_68 |  | 58 | 67 | 0.020106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_526_0_line_69 |  | 59 | 62 | 0.13033 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
70 | MV_526_0_line_70 |  | 59 | 63 | 0.0068209 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_526_0_line_71 |  | 62 | 64 | 0.051021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_526_0_line_72 |  | 63 | 69 | 0.049357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_526_0_line_73 |  | 66 | 84 | 0.05096 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_526_0_line_74 |  | 66 | 81 | 0.027764 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
75 | MV_526_0_line_75 |  | 67 | 106 | 0.17088 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_526_0_line_76 |  | 70 | 71 | 0.06459 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_526_0_line_77 |  | 72 | 73 | 0.033523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_526_0_line_78 |  | 73 | 74 | 0.040952 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_526_0_line_79 |  | 74 | 75 | 0.040739 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_526_0_line_80 |  | 75 | 76 | 0.017497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_526_0_line_81 |  | 76 | 77 | 0.067116 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_526_0_line_82 |  | 76 | 78 | 0.076594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_526_0_line_83 |  | 77 | 97 | 0.029056 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_526_0_line_84 |  | 77 | 95 | 0.045754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_526_0_line_85 |  | 78 | 92 | 0.33895 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_526_0_line_86 |  | 78 | 94 | 0.021837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_526_0_line_87 |  | 79 | 80 | 0.0030177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_526_0_line_88 |  | 81 | 82 | 0.011333 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
89 | MV_526_0_line_89 |  | 82 | 83 | 0.70974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_526_0_line_90 |  | 83 | 85 | 0.022217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_526_0_line_91 |  | 83 | 86 | 1.0277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_526_0_line_92 |  | 83 | 87 | 0.050503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_526_0_line_93 |  | 84 | 89 | 0.020684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_526_0_line_94 |  | 86 | 88 | 0.16299 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_526_0_line_95 |  | 87 | 90 | 0.034118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_526_0_line_96 |  | 87 | 91 | 0.04941 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_526_0_line_97 |  | 90 | 108 | 0.054063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_526_0_line_98 |  | 92 | 93 | 0.71415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_526_0_line_99 |  | 93 | 98 | 0.011474 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_526_0_line_100 |  | 95 | 96 | 0.018795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_526_0_line_101 |  | 97 | 99 | 0.011358 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_526_0_line_102 |  | 100 | 101 | 0.033425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_526_0_line_103 |  | 100 | 102 | 0.025729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_526_0_line_104 |  | 100 | 103 | 0.077793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_526_0_line_105 |  | 102 | 104 | 0.001204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_526_0_line_106 |  | 103 | 105 | 0.003431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_526_0_line_107 |  | 106 | 107 | 0.02717 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_526_0_trafo_56 | 25 MVA 110/20 kV | 109 | 43 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2681454.9289 | 1249491.7172
1 | 2681449.6865 | 1249479.7808
2 | 2681488.7859 | 1249476.4378
3 | 2681437.1779 | 1249453.57
4 | 2681480.7955 | 1249426.8403
5 | 2681558.6954 | 1249562.3292
6 | 2681523.687 | 1249576.8463
7 | 2681566.1022 | 1249580.0186
8 | 2681511.0193 | 1249582.0992
9 | 2681574.6686 | 1249600.4772
10 | 2681544.9428 | 1248836.6717
11 | 2681555.766 | 1248902.3912
12 | 2681484.6459 | 1248937.9841
13 | 2681439.2899 | 1248972.1194
14 | 2681466.1777 | 1248909.1116
15 | 2681485.9652 | 1248976.0302
16 | 2681405.9992 | 1248959.4692
17 | 2681433.9428 | 1248865.0226
18 | 2681774.5768 | 1248818.5765
19 | 2681821.4074 | 1248864.9123
20 | 2681778.3741 | 1248928.6433
21 | 2681882.9599 | 1249003.264
22 | 2681754.441 | 1248948.9247
23 | 2681843.9925 | 1249029.0672
24 | 2681835.0267 | 1248969.3683
25 | 2681741.7231 | 1248956.7698
26 | 2681867.0073 | 1249061.8481
27 | 2681318.2292 | 1249348.2557
28 | 2681268.3318 | 1249373.3136
29 | 2681375.6579 | 1249320.3133
30 | 2681256.5504 | 1249378.9452
31 | 2681431.5531 | 1249563.5491
32 | 2681462.7725 | 1249255.1616
33 | 2681302.4243 | 1249210.4721
34 | 2681245.9635 | 1249353.7254
35 | 2681427.4627 | 1249565.0384
36 | 2681578.8642 | 1249300.7137
37 | 2681464.6325 | 1249245.6468
38 | 2681529.7246 | 1249223.13
39 | 2681582.3699 | 1249299.0932
40 | 2681357.3591 | 1249227.5605
41 | 2681281.3288 | 1249220.6725
42 | 2681374.9736 | 1249216.2073
43 | 2681450.519 | 1249222.4671
44 | 2681244.9329 | 1249238.2712
45 | 2681754.762 | 1249452.2039
46 | 2681774.9613 | 1249447.7904
47 | 2681791.4228 | 1249470.1895
48 | 2681866.7566 | 1249371.9679
49 | 2681853.6327 | 1249347.9356
50 | 2681770.3916 | 1249478.3329
51 | 2681832.9486 | 1249336.575
52 | 2681753.7795 | 1249483.7027
53 | 2681689.332 | 1249249.6415
54 | 2681710.9387 | 1249283.1423
55 | 2681331.7111 | 1249029.2737
56 | 2681488.9441 | 1249134.9882
57 | 2681304.0674 | 1249117.7041
58 | 2681330.9321 | 1249025.8075
59 | 2681660.2163 | 1249015.0229
60 | 2681483.9854 | 1248963.787
61 | 2681510.7739 | 1249168.5575
62 | 2681670.3146 | 1248988.587
63 | 2681663.7912 | 1249020.832
64 | 2681648.7919 | 1248942.695
65 | 2681355.6581 | 1249152.6303
66 | 2681257.2584 | 1249152.2434
67 | 2681319.7733 | 1249010.485
68 | 2681387.5027 | 1248952.7999
69 | 2681693.285 | 1249060.4074
70 | 2681472.3498 | 1248871.1325
71 | 2681519.5405 | 1248913.6465
72 | 2681769.5958 | 1249134.399
73 | 2681741.8595 | 1249153.2276
74 | 2681764.1323 | 1249187.5932
75 | 2681786.2892 | 1249221.7798
76 | 2681795.5153 | 1249236.6625
77 | 2681777.1427 | 1249282.0981
78 | 2681850.9438 | 1249231.5681
79 | 2681374.4249 | 1248888.3338
80 | 2681371.8729 | 1248889.9444
81 | 2681233.9451 | 1249167.3212
82 | 2681224.4287 | 1249173.4759
83 | 2680869.0255 | 1249271.5009
84 | 2681241.2485 | 1249103.8662
85 | 2680881.4583 | 1249255.1109
86 | 2680662.4969 | 1248854.7146
87 | 2680914.5127 | 1249249.4608
88 | 2680512.2827 | 1248917.9833
89 | 2681221.1477 | 1249108.7423
90 | 2680945.5821 | 1249235.3635
91 | 2680934.8014 | 1249293.7222
92 | 2681888.9078 | 1249093.6128
93 | 2681930.3574 | 1248815.1134
94 | 2681839.4522 | 1249213.0274
95 | 2681757.2212 | 1249244.996
96 | 2681746.9359 | 1249229.2651
97 | 2681753.1603 | 1249298.5017
98 | 2681924.3607 | 1248805.3233
99 | 2681758.6334 | 1249308.4623
100 | 2681878.597 | 1249639.6514
101 | 2681858.123 | 1249621.9111
102 | 2681859.6196 | 1249655.679
103 | 2681839.6396 | 1249673.2272
104 | 2681859.0985 | 1249654.5932
105 | 2681836.4797 | 1249674.5846
106 | 2681198.5686 | 1249001.3394
107 | 2681207.5508 | 1249026.9813
108 | 2680997.0182 | 1249249.9322
109 | 2681450.519 | 1249222.4671

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9972 | 0.010342 | 0.37415 | 0.18121
1 | 0.9972 | 0.010353 | 0 | 0
2 | 0.99722 | 0.010145 | 0 | 0
3 | 0.9972 | 0.010379 | 0.075071 | 0.036359
4 | 0.99719 | 0.010404 | 0.35484 | 0.17186
5 | 0.99742 | 0.0082978 | 0 | 0
6 | 0.99751 | 0.007514 | 0.15781 | 0.076433
7 | 0.9974 | 0.0085197 | 0.4343 | 0.21034
8 | 0.99755 | 0.007205 | 0 | 0
9 | 0.99738 | 0.0086613 | 0 | 0
10 | 0.99692 | -0.010554 | 0.29844 | 0.14454
11 | 0.99696 | -0.010312 | 0 | 0
12 | 0.997 | -0.010616 | 0 | 0
13 | 0.9971 | -0.011587 | 0 | 0
14 | 0.99695 | -0.010157 | 0.56719 | 0.2747
15 | 0.99726 | -0.01304 | 0 | 0
16 | 0.99708 | -0.011394 | 0.25376 | 0.1229
17 | 0.99691 | -0.0097941 | 0 | 0
18 | 0.99664 | -0.015988 | 0.25299 | 0.12253
19 | 0.99668 | -0.015785 | 0 | 0
20 | 0.99679 | -0.015278 | 0 | 0
21 | 0.99652 | -0.016458 | 0 | 0
22 | 0.99681 | -0.015165 | 0.28401 | 0.13755
23 | 0.99649 | -0.016588 | 0 | 0
24 | 0.9965 | -0.016234 | 0.31714 | 0.1536
25 | 0.99683 | -0.01511 | 0 | 0
26 | 0.9964 | -0.017551 | 0.19365 | 0.09379
27 | 0.99902 | -0.0056577 | 2.172 | 1.052
28 | 0.99878 | -0.0035031 | 0 | 0
29 | 0.99922 | -0.0035886 | 0 | 0
30 | 0.99876 | -0.0033351 | 0 | 0
31 | 0.99781 | 0.0049147 | 0 | 0
32 | 0.99986 | -0.00065778 | 0 | 0
33 | 0.99883 | -0.0054084 | 0 | 0
34 | 0.99872 | -0.0029816 | 1.0795 | 0.52284
35 | 0.99781 | 0.0049318 | 0.32807 | 0.15889
36 | 0.99975 | 0.00031552 | 0 | 0
37 | 0.9999 | -0.00043929 | 0 | 0
38 | 0.99985 | -0.00059012 | 0.080886 | 0.039175
39 | 0.99975 | 0.00033718 | 0.46877 | 0.22703
40 | 0.99882 | -0.0052726 | 0 | 0
41 | 0.99877 | -0.0056846 | 1.3106 | 0.63476
42 | 0.99881 | -0.0052516 | 0.084898 | 0.041118
43 | 1 | 0 | -21.6803 | -10.0216
44 | 0.99868 | -0.0061293 | 0 | 0
45 | 0.99221 | 0.016528 | 1.9623 | 0.95038
46 | 0.99227 | 0.01603 | 0 | 0
47 | 0.99254 | 0.013436 | 0 | 0
48 | 0.99318 | 0.0075258 | 0 | 0
49 | 0.99326 | 0.0067501 | 0.24215 | 0.11728
50 | 0.99253 | 0.013551 | 0.21572 | 0.10448
51 | 0.99338 | 0.0075309 | 0 | 0
52 | 0.99253 | 0.013595 | 0.20828 | 0.10087
53 | 0.99722 | -0.012813 | 0 | 0
54 | 0.99722 | -0.012776 | 0.078742 | 0.038137
55 | 0.99804 | -0.0092657 | 0 | 0
56 | 0.99762 | -0.011325 | 0 | 0
57 | 0.99824 | -0.0082551 | 0 | 0
58 | 0.99804 | -0.0092339 | 0.58014 | 0.28097
59 | 0.99703 | -0.014159 | 0 | 0
60 | 0.99725 | -0.012967 | 0.36375 | 0.17617
61 | 0.9976 | -0.011143 | 0.38085 | 0.18445
62 | 0.9969 | -0.014743 | 0 | 0
63 | 0.99702 | -0.014186 | 0.21188 | 0.10262
64 | 0.99687 | -0.014418 | 0.53201 | 0.25767
65 | 0.99823 | -0.0080789 | 0.23958 | 0.11603
66 | 0.99834 | -0.0077654 | 0 | 0
67 | 0.99803 | -0.0091934 | 0 | 0
68 | 0.99708 | -0.011348 | 0.19913 | 0.096442
69 | 0.99702 | -0.014124 | 0.10674 | 0.051698
70 | 0.9966 | -0.013173 | 0 | 0
71 | 0.99657 | -0.012861 | 0.40508 | 0.19619
72 | 0.99417 | 0.002731 | 0.16813 | 0.08143
73 | 0.99418 | 0.0026636 | 0 | 0
74 | 0.99419 | 0.0025837 | 0.16301 | 0.07895
75 | 0.99421 | 0.0024263 | 0.25891 | 0.1254
76 | 0.99422 | 0.0023046 | 0 | 0
77 | 0.99396 | 0.0047093 | 0 | 0
78 | 0.99457 | -0.00096088 | 0 | 0
79 | 0.99684 | -0.0091641 | 0 | 0
80 | 0.99684 | -0.0091435 | 0.56691 | 0.27457
81 | 0.99839 | -0.0075403 | 0.53762 | 0.26038
82 | 0.99841 | -0.0074447 | 0 | 0
83 | 0.99524 | 0.020547 | 0 | 0
84 | 0.99833 | -0.0076899 | 0 | 0
85 | 0.99524 | 0.020582 | 0.13033 | 0.063123
86 | 0.99497 | 0.02214 | 0 | 0
87 | 0.99504 | 0.022459 | 0 | 0
88 | 0.99492 | 0.022541 | 0.21351 | 0.10341
89 | 0.99833 | -0.0076582 | 0.12917 | 0.062562
90 | 0.99502 | 0.022594 | 0 | 0
91 | 0.99486 | 0.024138 | 2.8157 | 1.3637
92 | 0.99621 | -0.015873 | 0 | 0
93 | 0.99614 | -0.015585 | 0 | 0
94 | 0.99457 | -0.00092198 | 0.14867 | 0.072005
95 | 0.99395 | 0.0048161 | 0 | 0
96 | 0.99394 | 0.0048609 | 0.19803 | 0.09591
97 | 0.9938 | 0.0036658 | 0.21061 | 0.102
98 | 0.99614 | -0.015574 | 0.079938 | 0.038716
99 | 0.99376 | 0.0040185 | 0 | 0
100 | 0.99689 | 0.012855 | 0 | 0
101 | 0.99689 | 0.012896 | 0.10375 | 0.050246
102 | 0.99689 | 0.012892 | 0 | 0
103 | 0.99685 | 0.013228 | 0 | 0
104 | 0.99689 | 0.012893 | 0.11977 | 0.058008
105 | 0.99685 | 0.013245 | 0.40363 | 0.19549
106 | 0.99799 | -0.0088245 | 0 | 0
107 | 0.99798 | -0.0088874 | 0.1907 | 0.092359
108 | 0.995 | 0.022812 | 0.33727 | 0.16335
109 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.075071 | 0.03536 | -0.075071 | -0.035669 | 1.0055e-07 | -0.00030936 | 0.0024022 | 0.002406 | 0.002406 | 0.9972 | 0.010342 | 0.9972 | 0.010353 | 1.0937
1 | -0.44922 | -0.21657 | 0.44923 | 0.21569 | 1.0303e-05 | -0.00087684 | 0.014437 | 0.014425 | 0.014437 | 0.9972 | 0.010342 | 0.99722 | 0.010145 | 6.5621
2 | 0.075071 | 0.035669 | -0.075071 | -0.036359 | 2.2526e-07 | -0.00068947 | 0.002406 | 0.0024147 | 0.0024147 | 0.9972 | 0.010353 | 0.9972 | 0.010379 | 1.0976
3 | 0.35485 | 0.17041 | -0.35484 | -0.17186 | 1.0618e-05 | -0.0014488 | 0.011395 | 0.011413 | 0.011413 | 0.99722 | 0.010145 | 0.99719 | 0.010404 | 5.188
4 | -0.80408 | -0.3861 | 0.80425 | 0.38144 | 0.00017629 | -0.0046622 | 0.025821 | 0.025762 | 0.025821 | 0.99722 | 0.010145 | 0.99742 | 0.0082978 | 11.7367
5 | -1.8661 | -0.87679 | 1.8663 | 0.87594 | 0.00018013 | -0.00084687 | 0.059673 | 0.059662 | 0.059673 | 0.99742 | 0.0082978 | 0.99751 | 0.007514 | 27.124
6 | 1.0618 | 0.49535 | -1.0618 | -0.4958 | 2.9446e-05 | -0.00044678 | 0.033911 | 0.033917 | 0.033917 | 0.99742 | 0.0082978 | 0.9974 | 0.0085197 | 15.4167
7 | -2.0241 | -0.95238 | 2.0242 | 0.95207 | 7.6718e-05 | -0.00030306 | 0.064736 | 0.064732 | 0.064736 | 0.99751 | 0.007514 | 0.99755 | 0.007205 | 29.4254
8 | 0.62751 | 0.28546 | -0.62749 | -0.28599 | 1.1792e-05 | -0.0005233 | 0.019953 | 0.019959 | 0.019959 | 0.9974 | 0.0085197 | 0.99738 | 0.0086613 | 9.0723
9 | -2.0242 | -0.95207 | 2.0247 | 0.94982 | 0.00057063 | -0.0022561 | 0.064732 | 0.064702 | 0.064732 | 0.99755 | 0.007205 | 0.99781 | 0.0049147 | 29.4236
10 | 0.62749 | 0.28599 | -0.62717 | -0.30039 | 0.00032768 | -0.014402 | 0.019959 | 0.020137 | 0.020137 | 0.99738 | 0.0086613 | 0.99689 | 0.012855 | 9.1531
11 | -0.29844 | -0.14454 | 0.29845 | 0.14447 | 1.094e-05 | -7.2175e-05 | 0.0096019 | 0.0096009 | 0.0096019 | 0.99692 | -0.010554 | 0.99696 | -0.010312 | 4.5723
12 | -0.29845 | -0.14447 | 0.29846 | 0.14242 | 1.0606e-05 | -0.0020477 | 0.0096009 | 0.0095752 | 0.0096009 | 0.99696 | -0.010312 | 0.997 | -0.010616 | 4.3641
13 | -1.4327 | -0.68733 | 1.4329 | 0.68601 | 0.00016343 | -0.0013246 | 0.04601 | 0.045993 | 0.04601 | 0.997 | -0.010616 | 0.9971 | -0.011587 | 20.9135
14 | 1.1342 | 0.54491 | -1.1342 | -0.54571 | 6.0756e-05 | -0.00079535 | 0.036435 | 0.036445 | 0.036445 | 0.997 | -0.010616 | 0.99695 | -0.010157 | 16.5658
15 | -1.8858 | -0.90404 | 1.8861 | 0.90257 | 0.00032255 | -0.0014697 | 0.060545 | 0.060525 | 0.060545 | 0.9971 | -0.011587 | 0.99726 | -0.01304 | 27.5204
16 | 0.4529 | 0.21803 | -0.45289 | -0.21888 | 1.0092e-05 | -0.00084376 | 0.014552 | 0.014563 | 0.014563 | 0.9971 | -0.011587 | 0.99708 | -0.011394 | 6.6196
17 | 0.56698 | 0.271 | -0.56695 | -0.27229 | 2.4201e-05 | -0.0012908 | 0.018196 | 0.018213 | 0.018213 | 0.99695 | -0.010157 | 0.99691 | -0.0097941 | 8.2785
18 | -8.5065 | -3.9184 | 8.5095 | 3.8875 | 0.0029532 | -0.030898 | 0.2711 | 0.27071 | 0.2711 | 0.99726 | -0.01304 | 0.99762 | -0.011325 | 21.2464
19 | 6.1779 | 2.8119 | -6.1766 | -2.84 | 0.0013804 | -0.028089 | 0.19648 | 0.19683 | 0.19683 | 0.99726 | -0.01304 | 0.99703 | -0.014159 | 15.4257
20 | 0.36375 | 0.17577 | -0.36375 | -0.17617 | 3.0654e-06 | -0.00039761 | 0.011694 | 0.011699 | 0.011699 | 0.99726 | -0.01304 | 0.99725 | -0.012967 | 5.3179
21 | 0.078746 | 0.028127 | -0.078743 | -0.03719 | 3.1034e-06 | -0.0090633 | 0.0024205 | 0.0025209 | 0.0025209 | 0.99726 | -0.01304 | 0.99722 | -0.012813 | 1.1459
22 | 0.19913 | 0.095975 | -0.19913 | -0.096442 | 1.0761e-06 | -0.0004664 | 0.0063999 | 0.0064057 | 0.0064057 | 0.99708 | -0.011394 | 0.99708 | -0.011348 | 2.9117
23 | 0.56695 | 0.27229 | -0.56691 | -0.2745 | 4.1396e-05 | -0.0022024 | 0.018213 | 0.018241 | 0.018241 | 0.99691 | -0.0097941 | 0.99684 | -0.0091641 | 8.2911
24 | -0.25299 | -0.12253 | 0.253 | 0.12246 | 7.7803e-06 | -7.325e-05 | 0.008142 | 0.008141 | 0.008142 | 0.99664 | -0.015988 | 0.99668 | -0.015785 | 3.8772
25 | -4.6349 | -2.1595 | 4.6354 | 2.1412 | 0.00050249 | -0.018258 | 0.1481 | 0.14787 | 0.1481 | 0.99668 | -0.015785 | 0.99679 | -0.015278 | 11.6066
26 | 4.3819 | 2.037 | -4.3813 | -2.0638 | 0.00065975 | -0.026772 | 0.13996 | 0.14029 | 0.14029 | 0.99668 | -0.015785 | 0.99652 | -0.016458 | 10.9948
27 | -4.6354 | -2.1412 | 4.6355 | 2.1373 | 0.00010886 | -0.0039633 | 0.14787 | 0.14783 | 0.14787 | 0.99679 | -0.015278 | 0.99681 | -0.015165 | 11.5889
28 | 4.0641 | 1.9116 | -4.064 | -1.9174 | 0.00012205 | -0.0057517 | 0.1301 | 0.13018 | 0.13018 | 0.99652 | -0.016458 | 0.99649 | -0.016588 | 10.2018
29 | 0.31714 | 0.15219 | -0.31714 | -0.1536 | 8.2578e-06 | -0.0014075 | 0.01019 | 0.010208 | 0.010208 | 0.99652 | -0.016458 | 0.9965 | -0.016234 | 4.6399
30 | -4.9195 | -2.2748 | 4.9196 | 2.273 | 5.6871e-05 | -0.0018338 | 0.15696 | 0.15694 | 0.15696 | 0.99681 | -0.015165 | 0.99683 | -0.01511 | 12.3011
31 | 4.064 | 1.9174 | -4.0637 | -1.9185 | 0.00032791 | -0.0011262 | 0.13018 | 0.13019 | 0.13019 | 0.99649 | -0.016588 | 0.9964 | -0.017551 | 35.9647
32 | 0.4052 | 0.18437 | -0.4051 | -0.19466 | 9.7527e-05 | -0.010296 | 0.012892 | 0.013019 | 0.013019 | 0.99683 | -0.01511 | 0.9966 | -0.013173 | 5.9175
33 | -5.3248 | -2.4573 | 5.3252 | 2.4463 | 0.00040317 | -0.01108 | 0.16983 | 0.16969 | 0.16983 | 0.99683 | -0.01511 | 0.9969 | -0.014743 | 13.3097
34 | 3.87 | 1.8247 | -3.8692 | -1.8254 | 0.00079172 | -0.00067979 | 0.12396 | 0.12397 | 0.12397 | 0.9964 | -0.017551 | 0.99621 | -0.015873 | 56.35
35 | 3.4357 | 1.6225 | -3.4348 | -1.6235 | 0.00089873 | -0.0010637 | 0.10979 | 0.10981 | 0.10981 | 0.99902 | -0.0056577 | 0.99878 | -0.0035031 | 49.9125
36 | -5.6077 | -2.6744 | 5.6087 | 2.673 | 0.00099435 | -0.0014652 | 0.17952 | 0.1795 | 0.17952 | 0.99902 | -0.0056577 | 0.99922 | -0.0035886 | 49.5924
37 | 1.0796 | 0.5219 | -1.0796 | -0.5222 | 2.0892e-05 | -0.00030407 | 0.034658 | 0.034662 | 0.034662 | 0.99878 | -0.0035031 | 0.99876 | -0.0033351 | 15.7554
38 | 2.3552 | 1.1016 | -2.3528 | -1.1086 | 0.0024421 | -0.0069729 | 0.075152 | 0.075246 | 0.075246 | 0.99878 | -0.0035031 | 0.99781 | 0.0049147 | 34.2028
39 | -21.1005 | -9.7705 | 21.1136 | 9.7544 | 0.01303 | -0.016135 | 0.67178 | 0.67149 | 0.67178 | 0.99922 | -0.0035886 | 0.99986 | -0.00065778 | 52.6473
40 | 15.4918 | 7.0976 | -15.4861 | -7.1134 | 0.0057058 | -0.01589 | 0.4923 | 0.49253 | 0.49253 | 0.99922 | -0.0035886 | 0.99883 | -0.0054084 | 38.5993
41 | 1.0796 | 0.5222 | -1.0795 | -0.52284 | 4.3881e-05 | -0.0006384 | 0.034662 | 0.03467 | 0.03467 | 0.99876 | -0.0033351 | 0.99872 | -0.0029816 | 15.7591
42 | 0.32807 | 0.15879 | -0.32807 | -0.15889 | 6.4459e-07 | -0.00010303 | 0.010545 | 0.010546 | 0.010546 | 0.99781 | 0.0049147 | 0.99781 | 0.0049318 | 4.7936
43 | 0.46882 | 0.22271 | -0.46877 | -0.22694 | 5.3539e-05 | -0.0042315 | 0.014985 | 0.015038 | 0.015038 | 0.99986 | -0.00065778 | 0.99975 | 0.00031552 | 6.8356
44 | -21.6633 | -10.0145 | 21.6643 | 10.0133 | 0.00099401 | -0.0011427 | 0.68905 | 0.68903 | 0.68905 | 0.99986 | -0.00065778 | 0.9999 | -0.00043929 | 54.0009
45 | 0.080887 | 0.037404 | -0.080886 | -0.039175 | 6.6148e-07 | -0.0017714 | 0.0025729 | 0.0025948 | 0.0025948 | 0.99986 | -0.00065778 | 0.99985 | -0.00059012 | 1.1795
46 | 0.0849 | 0.03689 | -0.084898 | -0.040619 | 1.5207e-06 | -0.0037291 | 0.0026753 | 0.0027201 | 0.0027201 | 0.99883 | -0.0054084 | 0.99882 | -0.0052726 | 1.2364
47 | 15.4012 | 7.0766 | -15.4003 | -7.079 | 0.00086877 | -0.0024483 | 0.48985 | 0.48989 | 0.48989 | 0.99883 | -0.0054084 | 0.99877 | -0.0056846 | 38.3924
48 | 0.46877 | 0.22694 | -0.46877 | -0.22703 | 1.1661e-06 | -9.1819e-05 | 0.015038 | 0.015039 | 0.015039 | 0.99975 | 0.00031552 | 0.99975 | 0.00033718 | 6.8361
49 | -21.6643 | -10.0133 | 21.6663 | 10.0111 | 0.0019964 | -0.0022959 | 0.68903 | 0.68899 | 0.68903 | 0.9999 | -0.00043929 | 1 | 0 | 53.9993
50 | 0.084898 | 0.040619 | -0.084898 | -0.041118 | 2.0747e-07 | -0.00049911 | 0.0027201 | 0.0027263 | 0.0027263 | 0.99882 | -0.0052726 | 0.99881 | -0.0052516 | 1.2392
51 | 14.0897 | 6.4443 | -14.0885 | -6.4486 | 0.0012527 | -0.0043619 | 0.44781 | 0.44787 | 0.44787 | 0.99877 | -0.0056846 | 0.99868 | -0.0061293 | 35.0994
52 | 14.0885 | 6.4486 | -14.0847 | -6.4616 | 0.0037318 | -0.01298 | 0.44787 | 0.44805 | 0.44805 | 0.99868 | -0.0061293 | 0.99841 | -0.0074447 | 35.1137
53 | -1.9623 | -0.95038 | 1.9624 | 0.94992 | 0.00011213 | -0.00045746 | 0.063434 | 0.063428 | 0.063434 | 0.99221 | 0.016528 | 0.99227 | 0.01603 | 28.8338
54 | -1.9624 | -0.94992 | 1.963 | 0.94753 | 0.00058708 | -0.0023975 | 0.063428 | 0.063396 | 0.063428 | 0.99227 | 0.01603 | 0.99254 | 0.013436 | 28.831
55 | 0.424 | 0.20441 | -0.424 | -0.20494 | 5.6519e-06 | -0.00052938 | 0.01369 | 0.013697 | 0.013697 | 0.99254 | 0.013436 | 0.99253 | 0.013551 | 6.2258
56 | -2.387 | -1.1519 | 2.3886 | 1.1476 | 0.0016412 | -0.0043864 | 0.077086 | 0.077024 | 0.077086 | 0.99254 | 0.013436 | 0.99318 | 0.0075258 | 35.039
57 | -2.3886 | -1.1476 | 2.3889 | 1.147 | 0.00021671 | -0.00058025 | 0.077024 | 0.077016 | 0.077024 | 0.99318 | 0.0075258 | 0.99326 | 0.0067501 | 35.0111
58 | -2.631 | -1.2642 | 2.6313 | 1.2644 | 0.00030261 | 0.00016175 | 0.084836 | 0.084835 | 0.084836 | 0.99326 | 0.0067501 | 0.99338 | 0.0075309 | 40.398
59 | 0.20828 | 0.10046 | -0.20828 | -0.10087 | 1.0551e-06 | -0.00041032 | 0.0067257 | 0.0067309 | 0.0067309 | 0.99253 | 0.013551 | 0.99253 | 0.013595 | 3.0595
60 | -2.6313 | -1.2644 | 2.6324 | 1.2621 | 0.0010827 | -0.0023358 | 0.084835 | 0.084802 | 0.084835 | 0.99338 | 0.0075309 | 0.99376 | 0.0040185 | 38.5615
61 | 0.078743 | 0.03719 | -0.078742 | -0.038137 | 3.3978e-07 | -0.00094642 | 0.0025209 | 0.0025327 | 0.0025327 | 0.99722 | -0.012813 | 0.99722 | -0.012776 | 1.1512
62 | 8.8939 | 4.0365 | -8.8903 | -4.071 | 0.0036007 | -0.034453 | 0.2825 | 0.28294 | 0.28294 | 0.99804 | -0.0092657 | 0.99762 | -0.011325 | 22.1741
63 | -9.6648 | -4.4052 | 9.6667 | 4.3899 | 0.0019028 | -0.015276 | 0.30721 | 0.30702 | 0.30721 | 0.99804 | -0.0092657 | 0.99824 | -0.0082551 | 24.0764
64 | 0.77085 | 0.36868 | -0.77084 | -0.36876 | 2.8972e-06 | -8.3632e-05 | 0.024715 | 0.024716 | 0.024716 | 0.99804 | -0.0092657 | 0.99804 | -0.0092339 | 11.2346
65 | 0.38086 | 0.18351 | -0.38085 | -0.18445 | 8.001e-06 | -0.00094832 | 0.012233 | 0.012245 | 0.012245 | 0.99762 | -0.011325 | 0.9976 | -0.011143 | 5.566
66 | 0.23958 | 0.11455 | -0.23958 | -0.11603 | 4.917e-06 | -0.0014808 | 0.0076796 | 0.0076981 | 0.0076981 | 0.99824 | -0.0082551 | 0.99823 | -0.0080789 | 3.4992
67 | -9.9063 | -4.5045 | 9.9072 | 4.4973 | 0.00093911 | -0.0071599 | 0.3147 | 0.31461 | 0.3147 | 0.99824 | -0.0082551 | 0.99834 | -0.0077654 | 24.6628
68 | 0.19071 | 0.087789 | -0.19071 | -0.088267 | 9.9072e-07 | -0.00047786 | 0.0060725 | 0.0060783 | 0.0060783 | 0.99804 | -0.0092339 | 0.99803 | -0.0091934 | 2.7629
69 | 5.8579 | 2.6868 | -5.8572 | -2.7027 | 0.00070187 | -0.015884 | 0.1866 | 0.18679 | 0.18679 | 0.99703 | -0.014159 | 0.9969 | -0.014743 | 14.6391
70 | 0.31863 | 0.15314 | -0.31862 | -0.15315 | 1.2732e-06 | -7.297e-06 | 0.010236 | 0.010236 | 0.010236 | 0.99703 | -0.014159 | 0.99702 | -0.014186 | 4.8741
71 | 0.53203 | 0.25646 | -0.53201 | -0.25767 | 1.9941e-05 | -0.0012047 | 0.017103 | 0.017118 | 0.017118 | 0.9969 | -0.014743 | 0.99687 | -0.014418 | 7.7809
72 | 0.10674 | 0.050527 | -0.10674 | -0.051698 | 7.737e-07 | -0.0011712 | 0.0034194 | 0.003434 | 0.003434 | 0.99702 | -0.014186 | 0.99702 | -0.014124 | 1.5609
73 | 0.12918 | 0.060858 | -0.12917 | -0.06207 | 1.164e-06 | -0.0012123 | 0.0041289 | 0.004144 | 0.004144 | 0.99834 | -0.0077654 | 0.99833 | -0.0076899 | 1.8836
74 | -10.0364 | -4.5582 | 10.0368 | 4.5549 | 0.00043573 | -0.0032322 | 0.31873 | 0.31869 | 0.31873 | 0.99834 | -0.0077654 | 0.99839 | -0.0075403 | 24.9791
75 | 0.19071 | 0.088267 | -0.1907 | -0.092328 | 8.4974e-06 | -0.0040612 | 0.0060783 | 0.0061286 | 0.0061286 | 0.99803 | -0.0091934 | 0.99799 | -0.0088245 | 2.7857
76 | 0.4051 | 0.19466 | -0.40508 | -0.19619 | 1.4636e-05 | -0.0015273 | 0.013019 | 0.013038 | 0.013038 | 0.9966 | -0.013173 | 0.99657 | -0.012861 | 5.9263
77 | -0.16813 | -0.08143 | 0.16813 | 0.080639 | 1.3144e-06 | -0.00079072 | 0.0054244 | 0.0054145 | 0.0054244 | 0.99417 | 0.002731 | 0.99418 | 0.0026636 | 2.4657
78 | -0.16813 | -0.080639 | 0.16813 | 0.079673 | 1.5992e-06 | -0.00096596 | 0.0054145 | 0.0054024 | 0.0054145 | 0.99418 | 0.0026636 | 0.99419 | 0.0025837 | 2.4611
79 | -0.33115 | -0.15862 | 0.33115 | 0.15766 | 6.1749e-06 | -0.0009596 | 0.010661 | 0.010649 | 0.010661 | 0.99419 | 0.0025837 | 0.99421 | 0.0024263 | 4.8461
80 | -0.59007 | -0.28306 | 0.59007 | 0.28265 | 8.4322e-06 | -0.00041044 | 0.019002 | 0.018997 | 0.019002 | 0.99421 | 0.0024263 | 0.99422 | 0.0023046 | 8.6374
81 | 3.0424 | 1.4571 | -3.0416 | -1.4585 | 0.00085977 | -0.0013286 | 0.097947 | 0.097967 | 0.097967 | 0.99422 | 0.0023046 | 0.99396 | 0.0047093 | 44.5304
82 | -3.6325 | -1.7398 | 3.6339 | 1.7384 | 0.0013981 | -0.0013936 | 0.11694 | 0.11692 | 0.11694 | 0.99422 | 0.0023046 | 0.99457 | -0.00096088 | 53.1565
83 | 2.8435 | 1.3641 | -2.8431 | -1.3638 | 0.00043433 | 0.00023779 | 0.091596 | 0.091596 | 0.091596 | 0.99396 | 0.0047093 | 0.9938 | 0.0036658 | 43.6172
84 | 0.19803 | 0.094388 | -0.19803 | -0.095467 | 2.4848e-06 | -0.0010785 | 0.0063713 | 0.0063849 | 0.0063849 | 0.99396 | 0.0047093 | 0.99395 | 0.0048161 | 2.9022
85 | -3.7826 | -1.8099 | 3.7893 | 1.8039 | 0.0066974 | -0.0060317 | 0.12171 | 0.12161 | 0.12171 | 0.99457 | -0.00096088 | 0.99621 | -0.015873 | 55.3226
86 | 0.14867 | 0.071489 | -0.14867 | -0.072005 | 6.6927e-07 | -0.00051555 | 0.0047881 | 0.0047946 | 0.0047946 | 0.99457 | -0.00096088 | 0.99457 | -0.00092198 | 2.1794
87 | 0.56691 | 0.2745 | -0.56691 | -0.27457 | 1.3405e-06 | -7.1198e-05 | 0.018241 | 0.018241 | 0.018241 | 0.99684 | -0.0091641 | 0.99684 | -0.0091435 | 8.2915
88 | -10.5744 | -4.8153 | 10.5746 | 4.814 | 0.00019762 | -0.0013083 | 0.33596 | 0.33594 | 0.33596 | 0.99839 | -0.0075403 | 0.99841 | -0.0074447 | 26.3291
89 | 3.5101 | 1.6476 | -3.4982 | -1.6609 | 0.011932 | -0.013299 | 0.11211 | 0.11232 | 0.11232 | 0.99841 | -0.0074447 | 0.99524 | 0.020547 | 51.0554
90 | 0.13033 | 0.062598 | -0.13033 | -0.063123 | 5.2247e-07 | -0.00052526 | 0.0041938 | 0.0042004 | 0.0042004 | 0.99524 | 0.020547 | 0.99524 | 0.020582 | 1.9093
91 | 0.21358 | 0.075279 | -0.21352 | -0.099559 | 6.1482e-05 | -0.024281 | 0.0065686 | 0.0068354 | 0.0068354 | 0.99524 | 0.020547 | 0.99497 | 0.02214 | 3.107
92 | 3.1543 | 1.523 | -3.1536 | -1.524 | 0.00069603 | -0.00098766 | 0.1016 | 0.10161 | 0.10161 | 0.99524 | 0.020547 | 0.99504 | 0.022459 | 46.1875
93 | 0.12917 | 0.06207 | -0.12917 | -0.062562 | 4.749e-07 | -0.00049206 | 0.004144 | 0.0041502 | 0.0041502 | 0.99833 | -0.0076899 | 0.99833 | -0.0076582 | 1.8865
94 | 0.21352 | 0.099559 | -0.21351 | -0.10341 | 1.0238e-05 | -0.0038494 | 0.0068354 | 0.0068834 | 0.0068834 | 0.99497 | 0.02214 | 0.99492 | 0.022541 | 3.1288
95 | 0.33729 | 0.16127 | -0.33728 | -0.16207 | 5.3632e-06 | -0.00080495 | 0.010846 | 0.010856 | 0.010856 | 0.99504 | 0.022459 | 0.99502 | 0.022594 | 4.9347
96 | 2.8163 | 1.3627 | -2.8157 | -1.3637 | 0.00054352 | -0.0010066 | 0.090767 | 0.090781 | 0.090781 | 0.99504 | 0.022459 | 0.99486 | 0.024138 | 41.2642
97 | 0.33728 | 0.16207 | -0.33727 | -0.16335 | 8.5189e-06 | -0.0012754 | 0.010856 | 0.010872 | 0.010872 | 0.99502 | 0.022594 | 0.995 | 0.022812 | 4.942
98 | 0.079944 | 0.021525 | -0.079938 | -0.038444 | 5.8361e-06 | -0.016919 | 0.0023991 | 0.0025705 | 0.0025705 | 0.99621 | -0.015873 | 0.99614 | -0.015585 | 1.1684
99 | 0.079938 | 0.038444 | -0.079938 | -0.038716 | 1.0134e-07 | -0.00027181 | 0.0025705 | 0.0025739 | 0.0025739 | 0.99614 | -0.015585 | 0.99614 | -0.015574 | 1.17
100 | 0.19803 | 0.095467 | -0.19803 | -0.09591 | 1.0238e-06 | -0.00044303 | 0.0063849 | 0.0063905 | 0.0063905 | 0.99395 | 0.0048161 | 0.99394 | 0.0048609 | 2.9048
101 | 2.6325 | 1.2618 | -2.6324 | -1.2621 | 0.00010904 | -0.00023548 | 0.084799 | 0.084802 | 0.084802 | 0.9938 | 0.0036658 | 0.99376 | 0.0040185 | 38.5463
102 | 0.10375 | 0.049453 | -0.10375 | -0.050246 | 4.9571e-07 | -0.00079296 | 0.0033281 | 0.003338 | 0.003338 | 0.99689 | 0.012855 | 0.99689 | 0.012896 | 1.5173
103 | 0.11977 | 0.05737 | -0.11977 | -0.05798 | 5.09e-07 | -0.00061035 | 0.0038457 | 0.0038533 | 0.0038533 | 0.99689 | 0.012855 | 0.99689 | 0.012892 | 1.7515
104 | 0.40365 | 0.19356 | -0.40363 | -0.19541 | 1.7483e-05 | -0.0018406 | 0.012963 | 0.012986 | 0.012986 | 0.99689 | 0.012855 | 0.99685 | 0.013228 | 5.9028
105 | 0.11977 | 0.05798 | -0.11977 | -0.058008 | 2.3798e-08 | -2.8561e-05 | 0.0038533 | 0.0038537 | 0.0038537 | 0.99689 | 0.012892 | 0.99689 | 0.012893 | 1.7517
106 | 0.40363 | 0.19541 | -0.40363 | -0.19549 | 7.7252e-07 | -8.1175e-05 | 0.012986 | 0.012987 | 0.012987 | 0.99685 | 0.013228 | 0.99685 | 0.013245 | 5.9033
107 | 0.1907 | 0.092328 | -0.1907 | -0.092359 | 1.8183e-06 | -3.1166e-05 | 0.0061286 | 0.006129 | 0.006129 | 0.99799 | -0.0088245 | 0.99798 | -0.0088874 | 2.9186

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.752 | 10.0563

## res_load
| p_mw | q_mvar
0 | 0.37415 | 0.18121
1 | 0.075071 | 0.036359
2 | 0.35484 | 0.17186
3 | 0.15781 | 0.076433
4 | 0.4343 | 0.21034
5 | 0.29844 | 0.14454
6 | 0.56719 | 0.2747
7 | 0.25376 | 0.1229
8 | 0.25299 | 0.12253
9 | 0.28401 | 0.13755
10 | 0.31714 | 0.1536
11 | 0.19365 | 0.09379
12 | 2.172 | 1.052
13 | 1.0795 | 0.52284
14 | 0.32807 | 0.15889
15 | 0.080886 | 0.039175
16 | 0.46877 | 0.22703
17 | 1.3106 | 0.63476
18 | 0.084898 | 0.041118
19 | 0.071747 | 0.034749
20 | 1.9623 | 0.95038
21 | 0.24215 | 0.11728
22 | 0.21572 | 0.10448
23 | 0.20828 | 0.10087
24 | 0.078742 | 0.038137
25 | 0.58014 | 0.28097
26 | 0.36375 | 0.17617
27 | 0.38085 | 0.18445
28 | 0.21188 | 0.10262
29 | 0.53201 | 0.25767
30 | 0.23958 | 0.11603
31 | 0.19913 | 0.096442
32 | 0.10674 | 0.051698
33 | 0.40508 | 0.19619
34 | 0.16813 | 0.08143
35 | 0.16301 | 0.07895
36 | 0.25891 | 0.1254
37 | 0.56691 | 0.27457
38 | 0.53762 | 0.26038
39 | 0.13033 | 0.063123
40 | 0.21351 | 0.10341
41 | 0.12917 | 0.062562
42 | 2.8157 | 1.3637
43 | 0.14867 | 0.072005
44 | 0.19803 | 0.09591
45 | 0.21061 | 0.102
46 | 0.079938 | 0.038716
47 | 0.10375 | 0.050246
48 | 0.11977 | 0.058008
49 | 0.40363 | 0.19549
50 | 0.1907 | 0.092359
51 | 0.33727 | 0.16335

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1