## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_529_1_node_4 | 20 | n |  | TRUE
1 | bus_MV_529_1_node_5 | 20 | n |  | TRUE
2 | bus_MV_529_1_node_132 | 20 | n |  | TRUE
3 | bus_MV_529_1_node_7 | 20 | n |  | TRUE
4 | bus_MV_529_1_node_151 | 20 | n |  | TRUE
5 | bus_MV_529_1_node_40 | 20 | n |  | TRUE
6 | bus_MV_529_1_node_86 | 20 | n |  | TRUE
7 | bus_MV_529_1_node_41 | 20 | n |  | TRUE
8 | bus_MV_529_1_node_131 | 20 | n |  | TRUE
9 | bus_MV_529_1_node_45 | 20 | n |  | TRUE
10 | bus_MV_529_1_node_39 | 20 | n |  | TRUE
11 | bus_MV_529_1_node_42 | 20 | n |  | TRUE
12 | bus_MV_529_1_node_122 | 20 | n |  | TRUE
13 | bus_MV_529_1_node_23 | 20 | n |  | TRUE
14 | bus_MV_529_1_node_38 | 20 | n |  | TRUE
15 | bus_MV_529_1_node_85 | 20 | n |  | TRUE
16 | bus_MV_529_1_node_47 | 20 | n |  | TRUE
17 | bus_MV_529_1_node_8 | 20 | n |  | TRUE
18 | bus_MV_529_1_node_9 | 20 | n |  | TRUE
19 | bus_MV_529_1_node_11 | 20 | n |  | TRUE
20 | bus_MV_529_1_node_13 | 20 | n |  | TRUE
21 | bus_MV_529_1_node_14 | 20 | n |  | TRUE
22 | bus_MV_529_1_node_102 | 20 | n |  | TRUE
23 | bus_MV_529_1_node_24 | 20 | n |  | TRUE
24 | bus_MV_529_1_node_22 | 20 | n |  | TRUE
25 | bus_MV_529_1_node_36 | 20 | n |  | TRUE
26 | bus_MV_529_1_node_130 | 20 | n |  | TRUE
27 | bus_MV_529_1_node_21 | 20 | n |  | TRUE
28 | bus_MV_529_1_node_44 | 20 | n |  | TRUE
29 | bus_MV_529_1_node_46 | 20 | n |  | TRUE
30 | bus_MV_529_1_node_37 | 20 | n |  | TRUE
31 | bus_MV_529_1_node_101 | 20 | n |  | TRUE
32 | bus_MV_529_1_node_43 | 20 | n |  | TRUE
33 | bus_MV_529_1_node_144 | 20 | n |  | TRUE
34 | bus_MV_529_1_node_67 | 20 | n |  | TRUE
35 | bus_MV_529_1_node_66 | 20 | n |  | TRUE
36 | bus_MV_529_1_node_123 | 20 | n |  | TRUE
37 | bus_MV_529_1_node_79 | 20 | n |  | TRUE
38 | bus_MV_529_1_node_68 | 20 | n |  | TRUE
39 | bus_MV_529_1_node_112 | 20 | n |  | TRUE
40 | bus_MV_529_1_node_70 | 20 | n |  | TRUE
41 | bus_MV_529_1_node_71 | 20 | n |  | TRUE
42 | bus_MV_529_1_node_106 | 20 | n |  | TRUE
43 | bus_MV_529_1_node_143 | 20 | n |  | TRUE
44 | bus_MV_529_1_node_142 | 20 | n |  | TRUE
45 | bus_MV_529_1_node_126 | 20 | n |  | TRUE
46 | bus_MV_529_1_node_60 | 20 | n |  | TRUE
47 | bus_MV_529_1_node_61 | 20 | n |  | TRUE
48 | bus_MV_529_1_node_62 | 20 | n |  | TRUE
49 | bus_MV_529_1_node_63 | 20 | n |  | TRUE
50 | bus_MV_529_1_node_64 | 20 | n |  | TRUE
51 | bus_MV_529_1_node_65 | 20 | n |  | TRUE
52 | bus_MV_529_1_node_99 | 20 | n |  | TRUE
53 | bus_MV_529_1_node_105 | 20 | n |  | TRUE
54 | bus_MV_529_1_node_103 | 20 | n |  | TRUE
55 | bus_MV_529_1_node_147 | 20 | n |  | TRUE
56 | bus_MV_529_1_node_121 | 20 | n |  | TRUE
57 | bus_MV_529_1_node_98 | 20 | n |  | TRUE
58 | bus_MV_529_1_node_104 | 20 | n |  | TRUE
59 | bus_MV_529_1_node_107 | 20 | n |  | TRUE
60 | bus_MV_529_1_node_72 | 20 | n |  | TRUE
61 | bus_MV_529_1_node_74 | 20 | n |  | TRUE
62 | bus_MV_529_1_node_73 | 20 | n |  | TRUE
63 | bus_MV_529_1_node_75 | 20 | n |  | TRUE
64 | bus_MV_529_1_node_76 | 20 | n |  | TRUE
65 | bus_MV_529_1_node_100 | 20 | n |  | TRUE
66 | bus_MV_529_1_node_77 | 20 | n |  | TRUE
67 | bus_MV_529_1_node_84 | 20 | n |  | TRUE
68 | bus_MV_529_1_node_80 | 20 | n |  | TRUE
69 | bus_MV_529_1_node_129 | 20 | n |  | TRUE
70 | bus_MV_529_1_node_110 | 20 | n |  | TRUE
71 | bus_MV_529_1_node_125 | 20 | n |  | TRUE
72 | bus_MV_529_1_node_83 | 20 | n |  | TRUE
73 | bus_MV_529_1_node_109 | 20 | n |  | TRUE
74 | bus_MV_529_1_node_108 | 20 | n |  | TRUE
75 | bus_MV_529_1_node_124 | 20 | n |  | TRUE
76 | bus_MV_529_1_node_133 | 20 | n |  | TRUE
77 | bus_HV_529_1_node_38 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_529_1_load_132 | 2 | 0.24483 | 0.11858 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_529_1_load_151 | 4 | 0.25186 | 0.12198 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_529_1_load_86 | 6 | 0.20162 | 0.097647 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_529_1_load_131 | 8 | 0.27743 | 0.13436 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_529_1_load_122 | 12 | 0.075301 | 0.03647 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_529_1_load_38 | 14 | 0.2863 | 0.13866 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_529_1_load_85 | 15 | 0.2663 | 0.12898 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_529_1_load_47 | 16 | 0.33204 | 0.16081 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_529_1_load_8 | 17 | 0.29157 | 0.14122 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_529_1_load_102 | 22 | 0.39309 | 0.19038 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_529_1_load_36 | 25 | 0.36933 | 0.17888 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_529_1_load_130 | 26 | 0.31248 | 0.15134 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_529_1_load_21 | 27 | 0.3815 | 0.18477 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_529_1_load_46 | 29 | 0.28944 | 0.14018 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_529_1_load_37 | 30 | 0.23529 | 0.11395 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_529_1_load_101 | 31 | 0.073859 | 0.035772 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_529_1_load_144 | 33 | 0.23362 | 0.11315 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_529_1_load_66 | 35 | 0.30933 | 0.14982 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_529_1_load_112 | 39 | 0.086576 | 0.041931 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_529_1_load_106 | 42 | 0.084271 | 0.040814 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_529_1_load_143 | 43 | 0.36826 | 0.17835 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_529_1_load_142 | 44 | 0.35846 | 0.17361 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_529_1_load_126 | 45 | 0.27324 | 0.13234 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_529_1_load_60 | 46 | 0.34824 | 0.16866 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_529_1_load_105 | 53 | 0.089674 | 0.043431 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_529_1_load_103 | 54 | 0.27944 | 0.13534 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_529_1_load_147 | 55 | 0.3374 | 0.16341 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_529_1_load_121 | 56 | 0.11318 | 0.054817 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_529_1_load_98 | 57 | 0.35352 | 0.17122 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_529_1_load_104 | 58 | 0.20413 | 0.098863 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_529_1_load_72 | 60 | 0.23965 | 0.11607 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_529_1_load_100 | 65 | 0.070444 | 0.034117 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_529_1_load_84 | 67 | 0.28563 | 0.13834 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_529_1_load_80 | 68 | 0.22564 | 0.10928 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_529_1_load_129 | 69 | 0.16472 | 0.079775 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_529_1_load_125 | 71 | 0.29042 | 0.14066 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_529_1_load_83 | 72 | 0.24836 | 0.12028 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_529_1_load_109 | 73 | 0.10922 | 0.052897 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_529_1_load_133 | 76 | 0.30731 | 0.14884 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_529_1_line_0 |  | 0 | 1 | 0.40219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_529_1_line_1 |  | 0 | 2 | 0.091503 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_529_1_line_2 |  | 1 | 3 | 1.1256 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_529_1_line_3 |  | 1 | 4 | 0.042874 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_529_1_line_4 |  | 3 | 5 | 0.14693 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_529_1_line_5 |  | 3 | 6 | 0.021443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_529_1_line_6 |  | 5 | 15 | 0.005551 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_529_1_line_7 |  | 5 | 7 | 0.34432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_529_1_line_8 |  | 7 | 8 | 0.017233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_529_1_line_9 |  | 7 | 9 | 0.73888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_529_1_line_10 |  | 7 | 10 | 0.79543 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_529_1_line_11 |  | 9 | 16 | 0.023917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_529_1_line_12 |  | 10 | 13 | 0.70488 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
13 | MV_529_1_line_13 |  | 10 | 14 | 0.02781 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
14 | MV_529_1_line_14 |  | 10 | 11 | 0.24618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_529_1_line_15 |  | 11 | 12 | 0.027165 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_529_1_line_16 |  | 12 | 36 | 0.026042 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_529_1_line_17 |  | 13 | 28 | 0.58281 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
18 | MV_529_1_line_18 |  | 13 | 29 | 0.048831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_529_1_line_19 |  | 13 | 24 | 0.3424 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_529_1_line_20 |  | 17 | 18 | 0.003148 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_529_1_line_21 |  | 18 | 19 | 0.26576 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_529_1_line_22 |  | 18 | 20 | 1.238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_529_1_line_23 |  | 19 | 21 | 0.19317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_529_1_line_24 |  | 19 | 22 | 0.049625 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_529_1_line_25 |  | 20 | 23 | 0.45253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_529_1_line_26 |  | 20 | 24 | 0.52415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_529_1_line_27 |  | 20 | 25 | 0.065876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_529_1_line_28 |  | 21 | 26 | 0.007984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_529_1_line_29 |  | 22 | 31 | 0.022688 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_529_1_line_30 |  | 23 | 30 | 0.089309 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_529_1_line_31 |  | 24 | 27 | 0.010012 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_529_1_line_32 |  | 28 | 34 | 0.058683 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_529_1_line_33 |  | 28 | 35 | 0.004359 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_529_1_line_34 |  | 28 | 32 | 0.22761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_529_1_line_35 |  | 32 | 33 | 0.023878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_529_1_line_36 |  | 33 | 37 | 0.14736 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_529_1_line_37 |  | 34 | 38 | 0.20978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_529_1_line_38 |  | 34 | 39 | 0.0059087 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_529_1_line_39 |  | 36 | 75 | 0.0091833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_529_1_line_40 |  | 37 | 69 | 0.08321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_529_1_line_41 |  | 37 | 70 | 0.10478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_529_1_line_42 |  | 37 | 61 | 0.14741 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_529_1_line_43 |  | 38 | 40 | 0.31965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_529_1_line_44 |  | 38 | 41 | 0.2948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_529_1_line_45 |  | 38 | 42 | 0.013142 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_529_1_line_46 |  | 38 | 43 | 0.063628 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_529_1_line_47 |  | 40 | 44 | 0.012797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_529_1_line_48 |  | 41 | 45 | 0.040272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_529_1_line_49 |  | 42 | 59 | 0.044276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_529_1_line_50 |  | 46 | 47 | 0.003323 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_529_1_line_51 |  | 47 | 48 | 0.15577 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_529_1_line_52 |  | 47 | 49 | 0.12722 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_529_1_line_53 |  | 48 | 50 | 0.18289 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_529_1_line_54 |  | 48 | 51 | 0.84263 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_529_1_line_55 |  | 48 | 52 | 0.17988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_529_1_line_56 |  | 48 | 53 | 0.049094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_529_1_line_57 |  | 49 | 54 | 0.013834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_529_1_line_58 |  | 50 | 55 | 0.035268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_529_1_line_59 |  | 51 | 56 | 0.021855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_529_1_line_60 |  | 52 | 57 | 0.038786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_529_1_line_61 |  | 54 | 58 | 0.008146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_529_1_line_62 |  | 57 | 63 | 0.036639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_529_1_line_63 |  | 59 | 74 | 0.068364 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_529_1_line_64 |  | 60 | 61 | 0.031588 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_529_1_line_65 |  | 60 | 62 | 0.077352 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
66 | MV_529_1_line_66 |  | 62 | 63 | 0.041966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_529_1_line_67 |  | 62 | 64 | 0.012113 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_529_1_line_68 |  | 64 | 65 | 0.020844 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_529_1_line_69 |  | 66 | 67 | 0.076172 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_529_1_line_70 |  | 66 | 68 | 0.28678 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_529_1_line_71 |  | 67 | 71 | 0.25617 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_529_1_line_72 |  | 68 | 72 | 0.40248 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_529_1_line_73 |  | 70 | 73 | 0.024662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_529_1_line_74 |  | 71 | 74 | 0.056869 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_529_1_line_75 |  | 75 | 76 | 0.005414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_529_1_trafo_38 | 25 MVA 110/20 kV | 77 | 14 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2679433.0173 | 1247108.0207
1 | 2679364.4364 | 1246912.216
2 | 2679368.656 | 1247173.0619
3 | 2679750.4169 | 1247187.1153
4 | 2679403.3838 | 1246894.291
5 | 2679638.3784 | 1247232.7097
6 | 2679768.7793 | 1247175.9542
7 | 2679476.161 | 1247424.8847
8 | 2679491.5265 | 1247421.944
9 | 2679080.1617 | 1247278.9408
10 | 2679512.6507 | 1247604.5601
11 | 2679697.9689 | 1247496.2131
12 | 2679722.86 | 1247485.3412
13 | 2679611.874 | 1247906.7559
14 | 2679485.4921 | 1247610.5448
15 | 2679643.1012 | 1247229.771
16 | 2679081.3546 | 1247302.7629
17 | 2680131.9421 | 1247758.719
18 | 2680134.1851 | 1247756.5032
19 | 2680140.8646 | 1247944.5308
20 | 2679980.1331 | 1247570.1099
21 | 2680087.8021 | 1248015.7882
22 | 2680189.5446 | 1247934.8929
23 | 2679740.5729 | 1247630.1611
24 | 2679761.9302 | 1247706.1593
25 | 2679937.7013 | 1247546.3983
26 | 2680081.3412 | 1248020.5044
27 | 2679771.1083 | 1247702.1576
28 | 2679274.7963 | 1247731.8241
29 | 2679576.9908 | 1247872.7127
30 | 2679684.7702 | 1247567.2097
31 | 2680210.4342 | 1247943.7465
32 | 2679315.8387 | 1247894.9917
33 | 2679296.1705 | 1247908.016
34 | 2679230.3509 | 1247747.8752
35 | 2679273.5076 | 1247727.6594
36 | 2679747.0691 | 1247475.7693
37 | 2679282.8023 | 1248054.7664
38 | 2679063.9926 | 1247705.0349
39 | 2679228.3055 | 1247753.4186
40 | 2679141.6935 | 1247587.2301
41 | 2678914.0551 | 1247558.7649
42 | 2679050.8635 | 1247704.6085
43 | 2679065.1681 | 1247768.6525
44 | 2679151.0866 | 1247595.9507
45 | 2678878.5173 | 1247546.2498
46 | 2679655.053 | 1248030.9819
47 | 2679657.0749 | 1248028.3405
48 | 2679682.8124 | 1248130.7276
49 | 2679585.3126 | 1248035.3932
50 | 2679811.3586 | 1248001.6509
51 | 2679908.1028 | 1248038.5362
52 | 2679576.879 | 1248152.1652
53 | 2679648.5123 | 1248095.6079
54 | 2679595.2239 | 1248045.0439
55 | 2679838.7286 | 1247979.3142
56 | 2679924.6498 | 1248024.2694
57 | 2679548.6794 | 1248125.5352
58 | 2679601.0602 | 1248050.7267
59 | 2679006.5896 | 1247704.9921
60 | 2679428.8121 | 1248073.2337
61 | 2679402.5773 | 1248055.525
62 | 2679492.3189 | 1248117.3946
63 | 2679522.0401 | 1248100.3807
64 | 2679497.4959 | 1248125.5811
65 | 2679512.4768 | 1248140.0734
66 | 2678894.8509 | 1248109.3544
67 | 2678952.1042 | 1248059.1131
68 | 2678688.8528 | 1247909.8389
69 | 2679220.8934 | 1248108.9785
70 | 2679204.453 | 1248029.1897
71 | 2678942.9998 | 1247803.1056
72 | 2678763.3878 | 1248305.3592
73 | 2679190.5695 | 1248018.0072
74 | 2678965.7117 | 1247750.9478
75 | 2679749.2685 | 1247470.0503
76 | 2679754.4638 | 1247468.4746
77 | 2679485.4921 | 1247610.5448

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99687 | 0.011119 | 0 | 0
1 | 0.997 | 0.010059 | 0 | 0
2 | 0.99683 | 0.010846 | 0.24483 | 0.11858
3 | 0.9977 | 0.0049978 | 0 | 0
4 | 0.99698 | 0.0099276 | 0.25186 | 0.12198
5 | 0.99783 | 0.0041288 | 0 | 0
6 | 0.9977 | 0.0050495 | 0.20162 | 0.097647
7 | 0.99825 | 0.0011235 | 0 | 0
8 | 0.99824 | 0.0011807 | 0.27743 | 0.13436
9 | 0.99794 | 0.0036277 | 0 | 0
10 | 0.99983 | -0.009985 | 0 | 0
11 | 0.99971 | -0.0089291 | 0 | 0
12 | 0.99969 | -0.0088069 | 0.075301 | 0.03647
13 | 0.99755 | -0.052263 | 0 | 0
14 | 1 | 0 | -9.4323 | -4.2769
15 | 0.99783 | 0.0041465 | 0.2663 | 0.12898
16 | 0.99793 | 0.0037227 | 0.33204 | 0.16081
17 | 0.99385 | -0.022831 | 0.29157 | 0.14122
18 | 0.99386 | -0.022842 | 0 | 0
19 | 0.99359 | -0.020469 | 0 | 0
20 | 0.99554 | -0.03682 | 0 | 0
21 | 0.99351 | -0.019768 | 0 | 0
22 | 0.99355 | -0.020753 | 0.39309 | 0.19038
23 | 0.99541 | -0.035752 | 0 | 0
24 | 0.99666 | -0.045357 | 0 | 0
25 | 0.99551 | -0.03653 | 0.36933 | 0.17888
26 | 0.99351 | -0.019738 | 0.31248 | 0.15134
27 | 0.99665 | -0.045311 | 0.3815 | 0.18477
28 | 0.99595 | -0.070226 | 0 | 0
29 | 0.99753 | -0.052095 | 0.28944 | 0.14018
30 | 0.99538 | -0.035504 | 0.23529 | 0.11395
31 | 0.99354 | -0.020774 | 0.073859 | 0.035772
32 | 0.99521 | -0.064027 | 0 | 0
33 | 0.99513 | -0.063372 | 0.23362 | 0.11315
34 | 0.99578 | -0.068756 | 0 | 0
35 | 0.99594 | -0.07021 | 0.30933 | 0.14982
36 | 0.99968 | -0.0087122 | 0 | 0
37 | 0.99448 | -0.068184 | 0 | 0
38 | 0.99521 | -0.06367 | 0 | 0
39 | 0.99578 | -0.06875 | 0.086576 | 0.041931
40 | 0.99506 | -0.06237 | 0 | 0
41 | 0.99511 | -0.062781 | 0 | 0
42 | 0.99519 | -0.063495 | 0.084271 | 0.040814
43 | 0.99516 | -0.063957 | 0.36826 | 0.17835
44 | 0.99506 | -0.062315 | 0.35846 | 0.17361
45 | 0.99509 | -0.06265 | 0.27324 | 0.13234
46 | 0.99302 | -0.060165 | 0.34824 | 0.16866
47 | 0.99302 | -0.060179 | 0 | 0
48 | 0.99319 | -0.061696 | 0 | 0
49 | 0.99295 | -0.059449 | 0 | 0
50 | 0.99311 | -0.060983 | 0 | 0
51 | 0.99307 | -0.061107 | 0 | 0
52 | 0.9935 | -0.06427 | 0 | 0
53 | 0.99318 | -0.061644 | 0.089674 | 0.043431
54 | 0.99294 | -0.059368 | 0.27944 | 0.13534
55 | 0.9931 | -0.060839 | 0.3374 | 0.16341
56 | 0.99307 | -0.061078 | 0.11318 | 0.054817
57 | 0.99357 | -0.064818 | 0.35352 | 0.17122
58 | 0.99293 | -0.059348 | 0.20413 | 0.098863
59 | 0.99513 | -0.062946 | 0 | 0
60 | 0.99401 | -0.064279 | 0.23965 | 0.11607
61 | 0.99409 | -0.064972 | 0 | 0
62 | 0.99374 | -0.066259 | 0 | 0
63 | 0.99365 | -0.065491 | 0 | 0
64 | 0.99374 | -0.066249 | 0 | 0
65 | 0.99374 | -0.066231 | 0.070444 | 0.034117
66 | 0.99451 | -0.064224 | 0 | 0
67 | 0.99458 | -0.063777 | 0.28563 | 0.13834
68 | 0.99425 | -0.065901 | 0.22564 | 0.10928
69 | 0.99446 | -0.068023 | 0.16472 | 0.079775
70 | 0.99446 | -0.068058 | 0 | 0
71 | 0.99496 | -0.061377 | 0.29042 | 0.14066
72 | 0.99406 | -0.067131 | 0.24836 | 0.12028
73 | 0.99446 | -0.068025 | 0.10922 | 0.052897
74 | 0.99504 | -0.062093 | 0 | 0
75 | 0.99968 | -0.0086786 | 0 | 0
76 | 0.99968 | -0.0086587 | 0.30731 | 0.14884
77 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.24484 | -0.11848 | 0.24487 | 0.10894 | 3.2812e-05 | -0.0095343 | 0.0078766 | 0.0077602 | 0.0078766 | 0.99687 | 0.011119 | 0.997 | 0.010059 | 3.5803
1 | 0.24484 | 0.11848 | -0.24483 | -0.11858 | 1.0116e-05 | -0.00010221 | 0.0078766 | 0.0078779 | 0.0078779 | 0.99687 | 0.011119 | 0.99683 | 0.010846 | 3.7514
2 | -0.49674 | -0.23087 | 0.49711 | 0.20425 | 0.00037044 | -0.026622 | 0.01586 | 0.01555 | 0.01586 | 0.997 | 0.010059 | 0.9977 | 0.0049978 | 7.2092
3 | 0.25186 | 0.12193 | -0.25186 | -0.12198 | 5.015e-06 | -4.7734e-05 | 0.0081022 | 0.0081029 | 0.0081029 | 0.997 | 0.010059 | 0.99698 | 0.0099276 | 3.8585
4 | -0.69872 | -0.30139 | 0.69882 | 0.29792 | 9.4918e-05 | -0.0034644 | 0.022017 | 0.021978 | 0.022017 | 0.9977 | 0.0049978 | 0.99783 | 0.0041288 | 10.0079
5 | 0.20162 | 0.097137 | -0.20162 | -0.097647 | 1.2015e-06 | -0.00050927 | 0.0064753 | 0.0064817 | 0.0064817 | 0.9977 | 0.0049978 | 0.9977 | 0.0050495 | 2.9462
6 | 0.2663 | 0.12884 | -0.2663 | -0.12898 | 5.4292e-07 | -0.0001318 | 0.0085585 | 0.0085602 | 0.0085602 | 0.99783 | 0.0041288 | 0.99783 | 0.0041465 | 3.891
7 | -0.96512 | -0.42677 | 0.96555 | 0.41871 | 0.00042708 | -0.0080621 | 0.030529 | 0.030434 | 0.030529 | 0.99783 | 0.0041288 | 0.99825 | 0.0011235 | 13.8769
8 | 0.27743 | 0.13396 | -0.27743 | -0.13436 | 1.8271e-06 | -0.00040947 | 0.008909 | 0.0089142 | 0.0089142 | 0.99825 | 0.0011235 | 0.99824 | 0.0011807 | 4.0519
9 | 0.33215 | 0.1427 | -0.33204 | -0.16025 | 0.00010994 | -0.017542 | 0.010454 | 0.010665 | 0.010665 | 0.99825 | 0.0011235 | 0.99794 | 0.0036277 | 4.8477
10 | -1.5751 | -0.69536 | 1.5777 | 0.67719 | 0.002621 | -0.018178 | 0.049791 | 0.049572 | 0.049791 | 0.99825 | 0.0011235 | 0.99983 | -0.009985 | 22.6322
11 | 0.33204 | 0.16025 | -0.33204 | -0.16081 | 3.6342e-06 | -0.00056761 | 0.010665 | 0.010672 | 0.010672 | 0.99794 | 0.0036277 | 0.99793 | 0.0037227 | 4.851
12 | 7.4569 | 3.409 | -7.4425 | -3.4226 | 0.014478 | -0.013566 | 0.23673 | 0.23706 | 0.23706 | 0.99983 | -0.009985 | 0.99755 | -0.052263 | 56.3078
13 | -9.4174 | -4.264 | 9.4183 | 4.2664 | 0.00088449 | 0.00234 | 0.29848 | 0.29848 | 0.29848 | 0.99983 | -0.009985 | 1 | 0 | 46.2754
14 | 0.38267 | 0.17783 | -0.38263 | -0.18369 | 4.9072e-05 | -0.0058604 | 0.012184 | 0.012256 | 0.012256 | 0.99983 | -0.009985 | 0.99971 | -0.0089291 | 5.5709
15 | 0.38263 | 0.18369 | -0.38262 | -0.18434 | 5.451e-06 | -0.00064659 | 0.012256 | 0.012264 | 0.012264 | 0.99971 | -0.0089291 | 0.99969 | -0.0088069 | 5.5746
16 | 0.30732 | 0.14787 | -0.30732 | -0.14849 | 3.3744e-06 | -0.00062038 | 0.0098481 | 0.0098559 | 0.0098559 | 0.99969 | -0.0088069 | 0.99968 | -0.0087122 | 4.4799
17 | 5.0897 | 2.361 | -5.0823 | -2.3754 | 0.0074319 | -0.014463 | 0.16236 | 0.16261 | 0.16261 | 0.99755 | -0.052263 | 0.99595 | -0.070226 | 44.9188
18 | 0.28944 | 0.13902 | -0.28944 | -0.14018 | 5.6374e-06 | -0.0011585 | 0.009292 | 0.0093066 | 0.0093066 | 0.99755 | -0.052263 | 0.99753 | -0.052095 | 4.2303
19 | 2.0633 | 0.92259 | -2.0614 | -0.93013 | 0.0019584 | -0.007547 | 0.065407 | 0.065503 | 0.065503 | 0.99755 | -0.052263 | 0.99666 | -0.045357 | 29.7742
20 | -0.29157 | -0.14122 | 0.29157 | 0.14114 | 3.7207e-07 | -7.4131e-05 | 0.0094101 | 0.0094091 | 0.0094101 | 0.99385 | -0.022831 | 0.99386 | -0.022842 | 4.2773
21 | 0.7797 | 0.36649 | -0.77948 | -0.37269 | 0.00022287 | -0.0061998 | 0.025024 | 0.025102 | 0.025102 | 0.99386 | -0.022842 | 0.99359 | -0.020469 | 11.4101
22 | -1.0713 | -0.50763 | 1.0732 | 0.47896 | 0.0019391 | -0.02867 | 0.034433 | 0.034078 | 0.034433 | 0.99386 | -0.022842 | 0.99554 | -0.03682 | 15.6513
23 | 0.3125 | 0.14661 | -0.31248 | -0.15115 | 2.6084e-05 | -0.0045451 | 0.010029 | 0.010086 | 0.010086 | 0.99359 | -0.020469 | 0.99351 | -0.019768 | 4.5844
24 | 0.46697 | 0.22608 | -0.46695 | -0.22613 | 2.0091e-05 | -4.5899e-05 | 0.015074 | 0.015075 | 0.015075 | 0.99359 | -0.020469 | 0.99355 | -0.020753 | 7.1783
25 | 0.23533 | 0.10115 | -0.23529 | -0.11184 | 3.3891e-05 | -0.010697 | 0.0074273 | 0.0075553 | 0.0075553 | 0.99554 | -0.03682 | 0.99541 | -0.035752 | 3.4342
26 | -1.6779 | -0.75743 | 1.6799 | 0.7456 | 0.0019884 | -0.011827 | 0.053381 | 0.053234 | 0.053381 | 0.99554 | -0.03682 | 0.99666 | -0.045357 | 24.264
27 | 0.36935 | 0.17732 | -0.36933 | -0.17888 | 1.2433e-05 | -0.0015551 | 0.01188 | 0.0119 | 0.0119 | 0.99554 | -0.03682 | 0.99551 | -0.03653 | 5.409
28 | 0.31248 | 0.15115 | -0.31248 | -0.15134 | 1.0845e-06 | -0.00018784 | 0.010086 | 0.010088 | 0.010088 | 0.99351 | -0.019768 | 0.99351 | -0.019738 | 4.5855
29 | 0.07386 | 0.035745 | -0.073859 | -0.035772 | 2.298e-07 | -2.6593e-05 | 0.0023841 | 0.0023844 | 0.0023844 | 0.99355 | -0.020753 | 0.99354 | -0.020774 | 1.1354
30 | 0.23529 | 0.11184 | -0.23529 | -0.11395 | 6.8296e-06 | -0.0021107 | 0.0075553 | 0.0075818 | 0.0075818 | 0.99541 | -0.035752 | 0.99538 | -0.035504 | 3.4463
31 | 0.3815 | 0.18453 | -0.3815 | -0.18477 | 2.0143e-06 | -0.00023685 | 0.012275 | 0.012278 | 0.012278 | 0.99666 | -0.045357 | 0.99665 | -0.045311 | 5.5808
32 | 2.2234 | 1.0487 | -2.223 | -1.0499 | 0.00039785 | -0.0012715 | 0.071254 | 0.071272 | 0.071272 | 0.99595 | -0.070226 | 0.99578 | -0.068756 | 32.3962
33 | 0.30933 | 0.14971 | -0.30933 | -0.14982 | 5.7744e-07 | -0.00010306 | 0.0099609 | 0.0099622 | 0.0099622 | 0.99595 | -0.070226 | 0.99594 | -0.07021 | 4.5283
34 | 2.5495 | 1.1771 | -2.5475 | -1.1819 | 0.0020146 | -0.0047888 | 0.081393 | 0.081459 | 0.081459 | 0.99595 | -0.070226 | 0.99521 | -0.064027 | 37.0266
35 | 2.5475 | 1.1819 | -2.5473 | -1.1824 | 0.00021154 | -0.00050187 | 0.081459 | 0.081465 | 0.081465 | 0.99521 | -0.064027 | 0.99513 | -0.063372 | 37.0297
36 | 2.3137 | 1.0692 | -2.3122 | -1.0685 | 0.0014353 | 0.00072493 | 0.073937 | 0.073939 | 0.073939 | 0.99513 | -0.063372 | 0.99448 | -0.068184 | 35.2089
37 | 2.1365 | 1.0081 | -2.1351 | -1.0127 | 0.0013147 | -0.0045737 | 0.068485 | 0.068546 | 0.068546 | 0.99578 | -0.068756 | 0.99521 | -0.06367 | 31.1574
38 | 0.086576 | 0.041791 | -0.086576 | -0.041931 | 6.1331e-08 | -0.00013987 | 0.0027869 | 0.0027887 | 0.0027887 | 0.99578 | -0.068756 | 0.99578 | -0.06875 | 1.2676
39 | 0.30732 | 0.14849 | -0.30731 | -0.14871 | 1.1912e-06 | -0.00021877 | 0.0098559 | 0.0098586 | 0.0098586 | 0.99968 | -0.0087122 | 0.99968 | -0.0086786 | 4.4812
40 | 0.16472 | 0.077811 | -0.16472 | -0.079775 | 3.1208e-06 | -0.0019639 | 0.0052881 | 0.0053127 | 0.0053127 | 0.99448 | -0.068184 | 0.99446 | -0.068023 | 2.4149
41 | 0.10922 | 0.049841 | -0.10922 | -0.052315 | 1.7136e-06 | -0.0024737 | 0.003485 | 0.0035154 | 0.0035154 | 0.99448 | -0.068184 | 0.99446 | -0.068058 | 1.5979
42 | 2.0383 | 0.94084 | -2.0374 | -0.94407 | 0.00083622 | -0.0032313 | 0.065166 | 0.065208 | 0.065208 | 0.99448 | -0.068184 | 0.99409 | -0.064972 | 29.6401
43 | 0.35852 | 0.16577 | -0.35846 | -0.17331 | 5.647e-05 | -0.0075412 | 0.011457 | 0.011551 | 0.011551 | 0.99521 | -0.06367 | 0.99506 | -0.06237 | 5.2504
44 | 0.27328 | 0.12443 | -0.27325 | -0.13139 | 3.0147e-05 | -0.0069618 | 0.0087098 | 0.0087955 | 0.0087955 | 0.99521 | -0.06367 | 0.99511 | -0.062781 | 3.998
45 | 1.1351 | 0.54423 | -1.1351 | -0.54454 | 2.3394e-05 | -0.00030384 | 0.036513 | 0.036517 | 0.036517 | 0.99521 | -0.06367 | 0.99519 | -0.063495 | 16.5988
46 | 0.36827 | 0.17829 | -0.36826 | -0.17835 | 1.597e-05 | -6.5228e-05 | 0.011868 | 0.011869 | 0.011869 | 0.99521 | -0.06367 | 0.99516 | -0.063957 | 5.652
47 | 0.35846 | 0.17331 | -0.35846 | -0.17361 | 2.2801e-06 | -0.00030186 | 0.011551 | 0.011555 | 0.011555 | 0.99506 | -0.06237 | 0.99506 | -0.062315 | 5.2521
48 | 0.27325 | 0.13139 | -0.27324 | -0.13234 | 4.1649e-06 | -0.0009509 | 0.0087955 | 0.0088075 | 0.0088075 | 0.99511 | -0.062781 | 0.99509 | -0.06265 | 4.0034
49 | 1.0508 | 0.50372 | -1.0507 | -0.50475 | 6.756e-05 | -0.0010269 | 0.033801 | 0.033814 | 0.033814 | 0.99519 | -0.063495 | 0.99513 | -0.062946 | 15.3702
50 | -0.34824 | -0.16866 | 0.34824 | 0.16858 | 5.6122e-07 | -7.8071e-05 | 0.011248 | 0.011247 | 0.011248 | 0.99302 | -0.060165 | 0.99302 | -0.060179 | 5.1129
51 | -0.83186 | -0.39929 | 0.83201 | 0.39566 | 0.00014937 | -0.0036238 | 0.026824 | 0.026778 | 0.026824 | 0.99302 | -0.060179 | 0.99319 | -0.061696 | 12.1927
52 | 0.48361 | 0.2307 | -0.48357 | -0.23369 | 4.1309e-05 | -0.0029829 | 0.015577 | 0.015614 | 0.015614 | 0.99302 | -0.060179 | 0.99295 | -0.059449 | 7.0974
53 | 0.33743 | 0.15828 | -0.3374 | -0.16258 | 2.8795e-05 | -0.0042986 | 0.010833 | 0.010887 | 0.010887 | 0.99319 | -0.061696 | 0.99311 | -0.060983 | 4.9485
54 | 0.1132 | 0.034464 | -0.11318 | -0.054303 | 1.405e-05 | -0.019839 | 0.0034393 | 0.0036492 | 0.0036492 | 0.99319 | -0.061696 | 0.99307 | -0.061107 | 1.6587
55 | -1.3723 | -0.63068 | 1.3728 | 0.62658 | 0.00046222 | -0.0041009 | 0.043898 | 0.043846 | 0.043898 | 0.99319 | -0.061696 | 0.9935 | -0.06427 | 19.9534
56 | 0.089674 | 0.042275 | -0.089674 | -0.043431 | 5.4693e-07 | -0.0011561 | 0.0028815 | 0.002896 | 0.002896 | 0.99319 | -0.061696 | 0.99318 | -0.061644 | 1.3164
57 | 0.48357 | 0.23369 | -0.48357 | -0.23401 | 4.5037e-06 | -0.00032431 | 0.015614 | 0.015618 | 0.015618 | 0.99295 | -0.059449 | 0.99294 | -0.059368 | 7.0992
58 | 0.3374 | 0.16258 | -0.3374 | -0.16341 | 5.5857e-06 | -0.00082883 | 0.010887 | 0.010897 | 0.010897 | 0.99311 | -0.060983 | 0.9931 | -0.060839 | 4.9533
59 | 0.11318 | 0.054303 | -0.11318 | -0.054817 | 3.8921e-07 | -0.00051448 | 0.0036492 | 0.0036557 | 0.0036557 | 0.99307 | -0.061107 | 0.99307 | -0.061078 | 1.6617
60 | -1.3728 | -0.62658 | 1.3729 | 0.6257 | 9.9521e-05 | -0.00088461 | 0.043846 | 0.043835 | 0.043846 | 0.9935 | -0.06427 | 0.99357 | -0.064818 | 19.9301
61 | 0.20413 | 0.098672 | -0.20413 | -0.098863 | 4.7267e-07 | -0.00019162 | 0.0065915 | 0.006594 | 0.006594 | 0.99294 | -0.059368 | 0.99293 | -0.059348 | 2.9973
62 | -1.7264 | -0.79692 | 1.7265 | 0.7961 | 0.00014926 | -0.00081938 | 0.055245 | 0.055235 | 0.055245 | 0.99357 | -0.064818 | 0.99365 | -0.065491 | 25.1115
63 | 1.0507 | 0.50475 | -1.0506 | -0.50633 | 0.00010442 | -0.0015853 | 0.033814 | 0.033835 | 0.033835 | 0.99513 | -0.062946 | 0.99504 | -0.062093 | 15.3794
64 | -2.0373 | -0.94476 | 2.0374 | 0.94407 | 0.00017934 | -0.00069206 | 0.065217 | 0.065208 | 0.065217 | 0.99401 | -0.064279 | 0.99409 | -0.064972 | 29.6443
65 | 1.7976 | 0.82869 | -1.7972 | -0.8285 | 0.00045544 | 0.00019406 | 0.057486 | 0.057487 | 0.057487 | 0.99401 | -0.064279 | 0.99374 | -0.066259 | 27.3746
66 | 1.7267 | 0.79516 | -1.7265 | -0.7961 | 0.00017089 | -0.00093872 | 0.055223 | 0.055235 | 0.055235 | 0.99374 | -0.066259 | 0.99365 | -0.065491 | 25.1067
67 | 0.070444 | 0.03334 | -0.070444 | -0.033626 | 8.3012e-08 | -0.00028558 | 0.002264 | 0.0022675 | 0.0022675 | 0.99374 | -0.066259 | 0.99374 | -0.066249 | 1.0307
68 | 0.070444 | 0.033626 | -0.070444 | -0.034117 | 1.4346e-07 | -0.00049141 | 0.0022675 | 0.0022737 | 0.0022737 | 0.99374 | -0.066249 | 0.99374 | -0.066231 | 1.0335
69 | -0.47416 | -0.22886 | 0.47419 | 0.22879 | 3.1695e-05 | -7.0093e-05 | 0.015283 | 0.015282 | 0.015283 | 0.99451 | -0.064224 | 0.99458 | -0.063777 | 7.2774
70 | 0.47416 | 0.22886 | -0.47404 | -0.22912 | 0.00011937 | -0.00026375 | 0.015283 | 0.015287 | 0.015287 | 0.99451 | -0.064224 | 0.99425 | -0.065901 | 7.2795
71 | -0.75982 | -0.36712 | 0.7601 | 0.36699 | 0.00027377 | -0.00013115 | 0.024493 | 0.024489 | 0.024493 | 0.99458 | -0.063777 | 0.99496 | -0.061377 | 11.6633
72 | 0.2484 | 0.11984 | -0.24836 | -0.12028 | 4.6017e-05 | -0.00044606 | 0.0080077 | 0.0080137 | 0.0080137 | 0.99425 | -0.065901 | 0.99406 | -0.067131 | 3.816
73 | 0.10922 | 0.052315 | -0.10922 | -0.052897 | 4.0773e-07 | -0.00058222 | 0.0035154 | 0.0035227 | 0.0035227 | 0.99446 | -0.068058 | 0.99446 | -0.068025 | 1.6012
74 | -1.0505 | -0.50765 | 1.0506 | 0.50633 | 8.6956e-05 | -0.0013185 | 0.033852 | 0.033835 | 0.033852 | 0.99496 | -0.061377 | 0.99504 | -0.062093 | 15.3871
75 | 0.30731 | 0.14871 | -0.30731 | -0.14884 | 7.026e-07 | -0.00012897 | 0.0098586 | 0.0098603 | 0.0098603 | 0.99968 | -0.0086786 | 0.99968 | -0.0086587 | 4.4819

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 9.7186 | 4.4155

## res_load
| p_mw | q_mvar
0 | 0.24483 | 0.11858
1 | 0.25186 | 0.12198
2 | 0.20162 | 0.097647
3 | 0.27743 | 0.13436
4 | 0.075301 | 0.03647
5 | 0.2863 | 0.13866
6 | 0.2663 | 0.12898
7 | 0.33204 | 0.16081
8 | 0.29157 | 0.14122
9 | 0.39309 | 0.19038
10 | 0.36933 | 0.17888
11 | 0.31248 | 0.15134
12 | 0.3815 | 0.18477
13 | 0.28944 | 0.14018
14 | 0.23529 | 0.11395
15 | 0.073859 | 0.035772
16 | 0.23362 | 0.11315
17 | 0.30933 | 0.14982
18 | 0.086576 | 0.041931
19 | 0.084271 | 0.040814
20 | 0.36826 | 0.17835
21 | 0.35846 | 0.17361
22 | 0.27324 | 0.13234
23 | 0.34824 | 0.16866
24 | 0.089674 | 0.043431
25 | 0.27944 | 0.13534
26 | 0.3374 | 0.16341
27 | 0.11318 | 0.054817
28 | 0.35352 | 0.17122
29 | 0.20413 | 0.098863
30 | 0.23965 | 0.11607
31 | 0.070444 | 0.034117
32 | 0.28563 | 0.13834
33 | 0.22564 | 0.10928
34 | 0.16472 | 0.079775
35 | 0.29042 | 0.14066
36 | 0.24836 | 0.12028
37 | 0.10922 | 0.052897
38 | 0.30731 | 0.14884

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1