## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_52_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_52_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_52_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_52_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_52_0_node_5 | 20 | n |  | TRUE
5 | bus_MV_52_0_node_8 | 20 | n |  | TRUE
6 | bus_MV_52_0_node_63 | 20 | n |  | TRUE
7 | bus_MV_52_0_node_58 | 20 | n |  | TRUE
8 | bus_MV_52_0_node_3 | 20 | n |  | TRUE
9 | bus_MV_52_0_node_78 | 20 | n |  | TRUE
10 | bus_MV_52_0_node_77 | 20 | n |  | TRUE
11 | bus_MV_52_0_node_76 | 20 | n |  | TRUE
12 | bus_MV_52_0_node_6 | 20 | n |  | TRUE
13 | bus_MV_52_0_node_7 | 20 | n |  | TRUE
14 | bus_MV_52_0_node_15 | 20 | n |  | TRUE
15 | bus_MV_52_0_node_16 | 20 | n |  | TRUE
16 | bus_MV_52_0_node_112 | 20 | n |  | TRUE
17 | bus_MV_52_0_node_17 | 20 | n |  | TRUE
18 | bus_MV_52_0_node_9 | 20 | n |  | TRUE
19 | bus_MV_52_0_node_13 | 20 | n |  | TRUE
20 | bus_MV_52_0_node_14 | 20 | n |  | TRUE
21 | bus_MV_52_0_node_18 | 20 | n |  | TRUE
22 | bus_MV_52_0_node_10 | 20 | n |  | TRUE
23 | bus_MV_52_0_node_19 | 20 | n |  | TRUE
24 | bus_MV_52_0_node_83 | 20 | n |  | TRUE
25 | bus_MV_52_0_node_80 | 20 | n |  | TRUE
26 | bus_MV_52_0_node_68 | 20 | n |  | TRUE
27 | bus_MV_52_0_node_70 | 20 | n |  | TRUE
28 | bus_MV_52_0_node_31 | 20 | n |  | TRUE
29 | bus_MV_52_0_node_66 | 20 | n |  | TRUE
30 | bus_MV_52_0_node_20 | 20 | n |  | TRUE
31 | bus_MV_52_0_node_22 | 20 | n |  | TRUE
32 | bus_MV_52_0_node_113 | 20 | n |  | TRUE
33 | bus_MV_52_0_node_23 | 20 | n |  | TRUE
34 | bus_MV_52_0_node_24 | 20 | n |  | TRUE
35 | bus_MV_52_0_node_26 | 20 | n |  | TRUE
36 | bus_MV_52_0_node_27 | 20 | n |  | TRUE
37 | bus_MV_52_0_node_30 | 20 | n |  | TRUE
38 | bus_MV_52_0_node_25 | 20 | n |  | TRUE
39 | bus_MV_52_0_node_28 | 20 | n |  | TRUE
40 | bus_MV_52_0_node_29 | 20 | n |  | TRUE
41 | bus_MV_52_0_node_116 | 20 | n |  | TRUE
42 | bus_MV_52_0_node_82 | 20 | n |  | TRUE
43 | bus_MV_52_0_node_79 | 20 | n |  | TRUE
44 | bus_MV_52_0_node_81 | 20 | n |  | TRUE
45 | bus_MV_52_0_node_33 | 20 | n |  | TRUE
46 | bus_MV_52_0_node_32 | 20 | n |  | TRUE
47 | bus_MV_52_0_node_86 | 20 | n |  | TRUE
48 | bus_MV_52_0_node_85 | 20 | n |  | TRUE
49 | bus_MV_52_0_node_35 | 20 | n |  | TRUE
50 | bus_MV_52_0_node_37 | 20 | n |  | TRUE
51 | bus_MV_52_0_node_39 | 20 | n |  | TRUE
52 | bus_MV_52_0_node_88 | 20 | n |  | TRUE
53 | bus_MV_52_0_node_90 | 20 | n |  | TRUE
54 | bus_MV_52_0_node_91 | 20 | n |  | TRUE
55 | bus_MV_52_0_node_89 | 20 | n |  | TRUE
56 | bus_MV_52_0_node_40 | 20 | n |  | TRUE
57 | bus_MV_52_0_node_41 | 20 | n |  | TRUE
58 | bus_MV_52_0_node_43 | 20 | n |  | TRUE
59 | bus_MV_52_0_node_44 | 20 | n |  | TRUE
60 | bus_MV_52_0_node_42 | 20 | n |  | TRUE
61 | bus_MV_52_0_node_49 | 20 | n |  | TRUE
62 | bus_MV_52_0_node_52 | 20 | n |  | TRUE
63 | bus_MV_52_0_node_75 | 20 | n |  | TRUE
64 | bus_MV_52_0_node_45 | 20 | n |  | TRUE
65 | bus_MV_52_0_node_115 | 20 | n |  | TRUE
66 | bus_MV_52_0_node_72 | 20 | n |  | TRUE
67 | bus_MV_52_0_node_50 | 20 | n |  | TRUE
68 | bus_MV_52_0_node_64 | 20 | n |  | TRUE
69 | bus_MV_52_0_node_48 | 20 | n |  | TRUE
70 | bus_MV_52_0_node_71 | 20 | n |  | TRUE
71 | bus_MV_52_0_node_47 | 20 | n |  | TRUE
72 | bus_MV_52_0_node_46 | 20 | n |  | TRUE
73 | bus_MV_52_0_node_51 | 20 | n |  | TRUE
74 | bus_MV_52_0_node_53 | 20 | n |  | TRUE
75 | bus_MV_52_0_node_61 | 20 | n |  | TRUE
76 | bus_MV_52_0_node_54 | 20 | n |  | TRUE
77 | bus_MV_52_0_node_117 | 20 | n |  | TRUE
78 | bus_MV_52_0_node_73 | 20 | n |  | TRUE
79 | bus_MV_52_0_node_74 | 20 | n |  | TRUE
80 | bus_MV_52_0_node_62 | 20 | n |  | TRUE
81 | bus_MV_52_0_node_55 | 20 | n |  | TRUE
82 | bus_MV_52_0_node_56 | 20 | n |  | TRUE
83 | bus_MV_52_0_node_57 | 20 | n |  | TRUE
84 | bus_MV_52_0_node_59 | 20 | n |  | TRUE
85 | bus_MV_52_0_node_97 | 20 | n |  | TRUE
86 | bus_MV_52_0_node_107 | 20 | n |  | TRUE
87 | bus_MV_52_0_node_95 | 20 | n |  | TRUE
88 | bus_MV_52_0_node_96 | 20 | n |  | TRUE
89 | bus_MV_52_0_node_65 | 20 | n |  | TRUE
90 | bus_MV_52_0_node_60 | 20 | n |  | TRUE
91 | bus_MV_52_0_node_102 | 20 | n |  | TRUE
92 | bus_MV_52_0_node_111 | 20 | n |  | TRUE
93 | bus_MV_52_0_node_101 | 20 | n |  | TRUE
94 | bus_MV_52_0_node_104 | 20 | n |  | TRUE
95 | bus_MV_52_0_node_105 | 20 | n |  | TRUE
96 | bus_MV_52_0_node_98 | 20 | n |  | TRUE
97 | bus_MV_52_0_node_67 | 20 | n |  | TRUE
98 | bus_MV_52_0_node_69 | 20 | n |  | TRUE
99 | bus_MV_52_0_node_92 | 20 | n |  | TRUE
100 | bus_MV_52_0_node_93 | 20 | n |  | TRUE
101 | bus_MV_52_0_node_87 | 20 | n |  | TRUE
102 | bus_MV_52_0_node_84 | 20 | n |  | TRUE
103 | bus_MV_52_0_node_94 | 20 | n |  | TRUE
104 | bus_MV_52_0_node_99 | 20 | n |  | TRUE
105 | bus_MV_52_0_node_100 | 20 | n |  | TRUE
106 | bus_MV_52_0_node_103 | 20 | n |  | TRUE
107 | bus_MV_52_0_node_110 | 20 | n |  | TRUE
108 | bus_MV_52_0_node_106 | 20 | n |  | TRUE
109 | bus_MV_52_0_node_108 | 20 | n |  | TRUE
110 | bus_MV_52_0_node_109 | 20 | n |  | TRUE
111 | bus_HV_52_0_node_106 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_52_0_load_0 | 0 | 0.37914 | 0.18363 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_52_0_load_63 | 6 | 0.25448 | 0.12325 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_52_0_load_78 | 9 | 0.14242 | 0.068976 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_52_0_load_77 | 10 | 0.073898 | 0.035791 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_52_0_load_76 | 11 | 0.11378 | 0.055107 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_52_0_load_112 | 16 | 0.14912 | 0.072224 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_52_0_load_17 | 17 | 0.18988 | 0.091965 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_52_0_load_9 | 18 | 0.40114 | 0.19428 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_52_0_load_13 | 19 | 0.1839 | 0.089065 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_52_0_load_14 | 20 | 0.38232 | 0.18517 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_52_0_load_18 | 21 | 0.21545 | 0.10435 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_52_0_load_10 | 22 | 0.39899 | 0.19324 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_52_0_load_19 | 23 | 0.15354 | 0.074364 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_52_0_load_83 | 24 | 0.34675 | 0.16794 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_52_0_load_80 | 25 | 0.19546 | 0.094667 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_52_0_load_31 | 28 | 0.11345 | 0.054947 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_52_0_load_66 | 29 | 0.15416 | 0.074664 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_52_0_load_113 | 32 | 0.11076 | 0.053644 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_52_0_load_23 | 33 | 0.22664 | 0.10977 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_52_0_load_24 | 34 | 0.40302 | 0.19519 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_52_0_load_30 | 37 | 0.085907 | 0.041607 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_52_0_load_29 | 40 | 0.084633 | 0.040989 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_52_0_load_116 | 41 | 0.13234 | 0.064097 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_52_0_load_82 | 42 | 0.24216 | 0.11729 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_52_0_load_32 | 46 | 0.077966 | 0.03776 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_52_0_load_35 | 49 | 0.18156 | 0.087935 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_52_0_load_37 | 50 | 0.11984 | 0.058043 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_52_0_load_39 | 51 | 0.31376 | 0.15196 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_52_0_load_88 | 52 | 0.099688 | 0.048281 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_52_0_load_90 | 53 | 0.37331 | 0.1808 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_52_0_load_91 | 54 | 0.11157 | 0.054035 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_52_0_load_40 | 56 | 0.33572 | 0.1626 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_52_0_load_52 | 62 | 0.3771 | 0.18264 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_52_0_load_75 | 63 | 0.18512 | 0.089657 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_52_0_load_115 | 65 | 0.34182 | 0.16555 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_52_0_load_72 | 66 | 0.25696 | 0.12445 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_52_0_load_64 | 68 | 0.33823 | 0.16381 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_52_0_load_71 | 70 | 0.25846 | 0.12518 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_52_0_load_46 | 72 | 0.19727 | 0.09554 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_52_0_load_51 | 73 | 0.33799 | 0.16369 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_52_0_load_117 | 77 | 0.11033 | 0.053437 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_52_0_load_73 | 78 | 0.32599 | 0.15789 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_52_0_load_55 | 81 | 0.38145 | 0.18474 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_52_0_load_107 | 86 | 0.17514 | 0.084824 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_52_0_load_95 | 87 | 0.16478 | 0.079804 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_52_0_load_96 | 88 | 0.084041 | 0.040703 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_52_0_load_65 | 89 | 0.25183 | 0.12197 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_52_0_load_60 | 90 | 0.39711 | 0.19233 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_52_0_load_111 | 92 | 0.27053 | 0.13103 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_52_0_load_101 | 93 | 0.15704 | 0.076058 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_52_0_load_104 | 94 | 0.18033 | 0.087337 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_52_0_load_105 | 95 | 2.052 | 0.99385 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_52_0_load_98 | 96 | 0.28437 | 0.13773 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_52_0_load_92 | 99 | 0.19187 | 0.092927 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_52_0_load_93 | 100 | 0.070171 | 0.033985 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_52_0_load_87 | 101 | 0.10218 | 0.049488 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_52_0_load_84 | 102 | 0.69423 | 0.33623 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_52_0_load_94 | 103 | 0.086163 | 0.041731 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_52_0_load_100 | 105 | 0.2066 | 0.10006 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_52_0_load_103 | 106 | 0.12996 | 0.062943 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_52_0_load_110 | 107 | 0.098071 | 0.047498 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_52_0_load_108 | 109 | 0.086794 | 0.042036 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_52_0_load_109 | 110 | 0.08688 | 0.042078 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 108 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_52_0_line_0 |  | 0 | 1 | 0.040214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_52_0_line_1 |  | 0 | 2 | 0.079875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_52_0_line_2 |  | 1 | 3 | 0.13687 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_52_0_line_3 |  | 1 | 4 | 0.29912 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_52_0_line_4 |  | 2 | 5 | 0.55709 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_52_0_line_5 |  | 3 | 10 | 0.047887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_52_0_line_6 |  | 4 | 11 | 0.055071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_52_0_line_7 |  | 4 | 6 | 0.90662 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_52_0_line_8 |  | 4 | 8 | 0.34414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_52_0_line_9 |  | 5 | 19 | 0.050137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_52_0_line_10 |  | 5 | 13 | 0.32176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_52_0_line_11 |  | 6 | 7 | 0.091789 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_52_0_line_12 |  | 7 | 64 | 0.60524 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_52_0_line_13 |  | 8 | 9 | 0.037409 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_52_0_line_14 |  | 12 | 13 | 0.10668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_52_0_line_15 |  | 12 | 14 | 0.47574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_52_0_line_16 |  | 12 | 15 | 1.1864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_52_0_line_17 |  | 12 | 16 | 0.008129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_52_0_line_18 |  | 12 | 17 | 0.77183 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_52_0_line_19 |  | 13 | 18 | 0.094351 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_52_0_line_20 |  | 14 | 20 | 0.085215 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_52_0_line_21 |  | 15 | 21 | 0.092097 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_52_0_line_22 |  | 19 | 22 | 0.51389 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_52_0_line_23 |  | 23 | 24 | 0.16939 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_52_0_line_24 |  | 24 | 25 | 0.12014 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_52_0_line_25 |  | 25 | 43 | 0.10261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_52_0_line_26 |  | 26 | 27 | 0.011712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_52_0_line_27 |  | 26 | 28 | 2.1531 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_52_0_line_28 |  | 26 | 29 | 0.19122 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
29 | MV_52_0_line_29 |  | 27 | 99 | 0.12191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_52_0_line_30 |  | 27 | 100 | 0.02734 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_52_0_line_31 |  | 28 | 45 | 0.034847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_52_0_line_32 |  | 28 | 46 | 0.16792 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_52_0_line_33 |  | 29 | 97 | 0.17903 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
34 | MV_52_0_line_34 |  | 30 | 31 | 0.04667 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_52_0_line_35 |  | 30 | 32 | 0.29751 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_52_0_line_36 |  | 31 | 33 | 0.044854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_52_0_line_37 |  | 31 | 34 | 0.020418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_52_0_line_38 |  | 32 | 36 | 0.005893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_52_0_line_39 |  | 33 | 42 | 0.00022785 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_52_0_line_40 |  | 34 | 43 | 0.0414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_52_0_line_41 |  | 35 | 36 | 0.24717 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_52_0_line_42 |  | 35 | 37 | 0.005232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_52_0_line_43 |  | 35 | 38 | 0.38993 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_52_0_line_44 |  | 36 | 39 | 0.1863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_52_0_line_45 |  | 38 | 41 | 0.006536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_52_0_line_46 |  | 39 | 40 | 0.044154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_52_0_line_47 |  | 43 | 44 | 0.12765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_52_0_line_48 |  | 44 | 101 | 0.012268 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_52_0_line_49 |  | 45 | 47 | 0.23125 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_52_0_line_50 |  | 47 | 48 | 0.023021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_52_0_line_51 |  | 48 | 102 | 0.004302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_52_0_line_52 |  | 49 | 50 | 0.03485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_52_0_line_53 |  | 50 | 51 | 0.098955 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_52_0_line_54 |  | 51 | 52 | 0.04617 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_52_0_line_55 |  | 52 | 55 | 0.075397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_52_0_line_56 |  | 53 | 54 | 0.014668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_52_0_line_57 |  | 53 | 55 | 0.052155 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_52_0_line_58 |  | 54 | 99 | 0.036303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_52_0_line_59 |  | 56 | 57 | 0.082121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_52_0_line_60 |  | 57 | 58 | 0.81824 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_52_0_line_61 |  | 57 | 59 | 0.45456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_52_0_line_62 |  | 58 | 63 | 0.010997 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_52_0_line_63 |  | 59 | 64 | 0.19023 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_52_0_line_64 |  | 59 | 65 | 0.067474 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_52_0_line_65 |  | 60 | 61 | 0.20958 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_52_0_line_66 |  | 60 | 62 | 0.1404 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
67 | MV_52_0_line_67 |  | 61 | 73 | 0.044998 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_52_0_line_68 |  | 61 | 67 | 0.24294 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_52_0_line_69 |  | 61 | 69 | 0.77993 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_52_0_line_70 |  | 62 | 74 | 0.013964 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
71 | MV_52_0_line_71 |  | 62 | 75 | 0.40661 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
72 | MV_52_0_line_72 |  | 63 | 77 | 0.93579 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_52_0_line_73 |  | 64 | 66 | 0.05656 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
74 | MV_52_0_line_74 |  | 66 | 83 | 0.03257 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
75 | MV_52_0_line_75 |  | 67 | 68 | 0.055504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_52_0_line_76 |  | 68 | 89 | 0.030274 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_52_0_line_77 |  | 69 | 70 | 0.084556 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
78 | MV_52_0_line_78 |  | 69 | 71 | 0.62215 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_52_0_line_79 |  | 71 | 72 | 0.070691 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
80 | MV_52_0_line_80 |  | 74 | 76 | 0.46302 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_52_0_line_81 |  | 75 | 80 | 0.28581 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
82 | MV_52_0_line_82 |  | 75 | 90 | 0.007954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_52_0_line_83 |  | 76 | 91 | 0.05694 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
84 | MV_52_0_line_84 |  | 76 | 92 | 0.06712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_52_0_line_85 |  | 78 | 79 | 0.024058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_52_0_line_86 |  | 79 | 80 | 0.099353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_52_0_line_87 |  | 80 | 87 | 0.035602 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
88 | MV_52_0_line_88 |  | 81 | 82 | 0.004851 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_52_0_line_89 |  | 82 | 83 | 0.12553 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
90 | MV_52_0_line_90 |  | 82 | 84 | 0.06346 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
91 | MV_52_0_line_91 |  | 84 | 85 | 0.021635 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
92 | MV_52_0_line_92 |  | 84 | 86 | 0.024308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_52_0_line_93 |  | 85 | 88 | 0.03972 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
94 | MV_52_0_line_94 |  | 87 | 88 | 0.020814 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
95 | MV_52_0_line_95 |  | 91 | 93 | 0.1305 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
96 | MV_52_0_line_96 |  | 93 | 94 | 0.061002 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
97 | MV_52_0_line_97 |  | 93 | 95 | 0.056152 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
98 | MV_52_0_line_98 |  | 93 | 96 | 0.065518 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
99 | MV_52_0_line_99 |  | 94 | 98 | 0.10002 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_52_0_line_100 |  | 95 | 107 | 0.13138 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
101 | MV_52_0_line_101 |  | 96 | 104 | 0.054046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_52_0_line_102 |  | 97 | 98 | 1.0861 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
103 | MV_52_0_line_103 |  | 100 | 103 | 0.011432 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_52_0_line_104 |  | 101 | 102 | 0.075647 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_52_0_line_105 |  | 104 | 105 | 0.064632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_52_0_line_106 |  | 105 | 106 | 0.0077974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_52_0_line_107 |  | 107 | 108 | 0.10174 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
108 | MV_52_0_line_108 |  | 107 | 109 | 0.0073832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_52_0_line_109 |  | 109 | 110 | 0.00016539 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_52_0_trafo_106 | 25 MVA 110/20 kV | 111 | 108 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2751721.4274 | 1229579.434
1 | 2751718.7148 | 1229539.3169
2 | 2751728.6742 | 1229658.9695
3 | 2751658.8604 | 1229435.5176
4 | 2751665.758 | 1229308.4105
5 | 2751961.8254 | 1230017.3286
6 | 2751874.8107 | 1228426.2265
7 | 2751861.0115 | 1228335.4802
8 | 2751833.9045 | 1229526.9228
9 | 2751845.3396 | 1229491.3043
10 | 2751684.5361 | 1229395.0957
11 | 2751635.8404 | 1229354.6465
12 | 2751722.8812 | 1230045.8319
13 | 2751787.1966 | 1230091.8931
14 | 2751681.5448 | 1230467.3754
15 | 2752261.276 | 1230867.8259
16 | 2751725.8936 | 1230038.2796
17 | 2750951.0586 | 1230042.9557
18 | 2751830.7451 | 1230175.5926
19 | 2751989.6677 | 1230058.9672
20 | 2751739.7122 | 1230529.6498
21 | 2752169.2976 | 1230863.156
22 | 2752493.7617 | 1230158.8299
23 | 2755658.6294 | 1230746.9513
24 | 2755689.4586 | 1230580.3914
25 | 2755704.0646 | 1230512.0529
26 | 2754324.6784 | 1228305.6757
27 | 2754329.3472 | 1228294.9313
28 | 2755310.4709 | 1230219.8115
29 | 2754143.107 | 1228326.7099
30 | 2755544.7492 | 1230521.038
31 | 2755586.2766 | 1230499.5153
32 | 2755413.8084 | 1230788.1864
33 | 2755606.5688 | 1230539.5171
34 | 2755604.4843 | 1230490.2763
35 | 2755397.8828 | 1230950.8445
36 | 2755413.8824 | 1230794.0494
37 | 2755393.0477 | 1230952.8756
38 | 2755578.7983 | 1231131.4776
39 | 2755304.1806 | 1230735.5954
40 | 2755286.1441 | 1230695.2756
41 | 2755577.8861 | 1231137.9487
42 | 2755606.6719 | 1230539.7203
43 | 2755641.4032 | 1230471.5428
44 | 2755617.6561 | 1230364.2766
45 | 2755341.9419 | 1230204.6637
46 | 2755159.1467 | 1230292.6029
47 | 2755555.961 | 1230292.2508
48 | 2755576.5027 | 1230281.745
49 | 2754378.7914 | 1227982.7146
50 | 2754375.5398 | 1228017.4123
51 | 2754470.1824 | 1228046.3054
52 | 2754461.0796 | 1228091.566
53 | 2754395.7379 | 1228174.684
54 | 2754393.6564 | 1228189.2038
55 | 2754447.1056 | 1228165.6568
56 | 2751846.8301 | 1227320.5922
57 | 2751927.6655 | 1227305.0193
58 | 2751356.0528 | 1227294.2079
59 | 2751726.3019 | 1227588.8952
60 | 2752601.0584 | 1227609.575
61 | 2752666.0299 | 1227466.1661
62 | 2752592.8881 | 1227749.7381
63 | 2751351.6109 | 1227304.2708
64 | 2751717.1713 | 1227747.5848
65 | 2751683.0312 | 1227537.1225
66 | 2751766.3882 | 1227775.4544
67 | 2752609.5874 | 1227285.6196
68 | 2752559.2157 | 1227262.3099
69 | 2752187.787 | 1227234.6917
70 | 2752177.9406 | 1227318.672
71 | 2752237.4402 | 1226954.5397
72 | 2752189.941 | 1227006.8946
73 | 2752710.9987 | 1227467.7771
74 | 2752606.8732 | 1227750.4864
75 | 2752196.4243 | 1227839.9987
76 | 2753069.7759 | 1227758.7077
77 | 2750704.5773 | 1227980.327
78 | 2752023.6453 | 1227607.2354
79 | 2752036.2737 | 1227627.5433
80 | 2752012.4091 | 1227695.262
81 | 2751909.1693 | 1227768.5475
82 | 2751907.9047 | 1227773.2306
83 | 2751797.9968 | 1227783.2234
84 | 2751928.0413 | 1227732.6522
85 | 2751943.2489 | 1227723.5434
86 | 2751909.6859 | 1227716.7153
87 | 2751991.772 | 1227724.273
88 | 2751979.3848 | 1227740.0325
89 | 2752571.9298 | 1227234.8348
90 | 2752195.4564 | 1227847.8923
91 | 2753126.8324 | 1227756.6407
92 | 2753073.0258 | 1227691.6669
93 | 2753256.2183 | 1227739.6284
94 | 2753316.3812 | 1227729.546
95 | 2753265.4992 | 1227795.008
96 | 2753253.4077 | 1227674.1706
97 | 2754094.6716 | 1228154.3405
98 | 2753415.0296 | 1227713.014
99 | 2754388.505 | 1228225.1394
100 | 2754333.0072 | 1228267.8372
101 | 2755612.1837 | 1230353.2898
102 | 2755578.4227 | 1230285.5948
103 | 2754334.5375 | 1228256.5083
104 | 2753255.8669 | 1227620.1823
105 | 2753319.9287 | 1227611.6847
106 | 2753327.6691 | 1227610.7439
107 | 2753282.5608 | 1227925.2728
108 | 2753181.7451 | 1227938.9661
109 | 2753289.8768 | 1227924.2791
110 | 2753290.0407 | 1227924.2569
111 | 2753181.7451 | 1227938.9661

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9869 | -0.17633 | 0.37914 | 0.18363
1 | 0.98702 | -0.17729 | 0 | 0
2 | 0.98671 | -0.17479 | 0 | 0
3 | 0.98701 | -0.17719 | 0 | 0
4 | 0.98793 | -0.18454 | 0 | 0
5 | 0.98534 | -0.16373 | 0 | 0
6 | 0.99254 | -0.14795 | 0.25448 | 0.12325
7 | 0.99305 | -0.14398 | 0 | 0
8 | 0.98787 | -0.18405 | 0 | 0
9 | 0.98786 | -0.18398 | 0.14242 | 0.068976
10 | 0.98701 | -0.17715 | 0.073898 | 0.035791
11 | 0.98792 | -0.18446 | 0.11378 | 0.055107
12 | 0.98466 | -0.15845 | 0 | 0
13 | 0.98478 | -0.1594 | 0 | 0
14 | 0.98442 | -0.15638 | 0 | 0
15 | 0.98433 | -0.15638 | 0 | 0
16 | 0.98466 | -0.15844 | 0.14912 | 0.072224
17 | 0.98437 | -0.16031 | 0.18988 | 0.091965
18 | 0.98471 | -0.15987 | 0.40114 | 0.19428
19 | 0.9853 | -0.16338 | 0.1839 | 0.089065
20 | 0.98436 | -0.15679 | 0.38232 | 0.18517
21 | 0.98429 | -0.15663 | 0.21545 | 0.10435
22 | 0.9849 | -0.16594 | 0.39899 | 0.19324
23 | 0.98251 | -0.14123 | 0.15354 | 0.074364
24 | 0.98256 | -0.1409 | 0.34675 | 0.16794
25 | 0.98264 | -0.14164 | 0.19546 | 0.094667
26 | 0.99739 | -0.051266 | 0 | 0
27 | 0.99737 | -0.051054 | 0 | 0
28 | 0.98487 | -0.13674 | 0.11345 | 0.054947
29 | 0.99786 | -0.046172 | 0.15416 | 0.074664
30 | 0.98261 | -0.14153 | 0 | 0
31 | 0.98264 | -0.14171 | 0 | 0
32 | 0.98238 | -0.14361 | 0.11076 | 0.053644
33 | 0.98261 | -0.14145 | 0.22664 | 0.10977
34 | 0.98266 | -0.1419 | 0.40302 | 0.19519
35 | 0.9823 | -0.14313 | 0 | 0
36 | 0.98237 | -0.1436 | 0 | 0
37 | 0.9823 | -0.14312 | 0.085907 | 0.041607
38 | 0.98224 | -0.14261 | 0 | 0
39 | 0.98235 | -0.14344 | 0 | 0
40 | 0.98235 | -0.1434 | 0.084633 | 0.040989
41 | 0.98224 | -0.1426 | 0.13234 | 0.064097
42 | 0.98261 | -0.14145 | 0.24216 | 0.11729
43 | 0.98273 | -0.14249 | 0 | 0
44 | 0.98306 | -0.14536 | 0 | 0
45 | 0.98475 | -0.13562 | 0 | 0
46 | 0.98485 | -0.1369 | 0.077966 | 0.03776
47 | 0.98349 | -0.14433 | 0 | 0
48 | 0.98341 | -0.14358 | 0 | 0
49 | 0.99683 | -0.048156 | 0.18156 | 0.087935
50 | 0.99684 | -0.048232 | 0.11984 | 0.058043
51 | 0.9969 | -0.047861 | 0.31376 | 0.15196
52 | 0.99693 | -0.048199 | 0.099688 | 0.048281
53 | 0.99707 | -0.048363 | 0.37331 | 0.1808
54 | 0.99709 | -0.048551 | 0.11157 | 0.054035
55 | 0.997 | -0.048834 | 0 | 0
56 | 0.99579 | -0.11308 | 0.33572 | 0.1626
57 | 0.99583 | -0.11341 | 0 | 0
58 | 0.99552 | -0.11107 | 0 | 0
59 | 0.99619 | -0.11605 | 0 | 0
60 | 0.99761 | -0.066477 | 0 | 0
61 | 0.99724 | -0.063578 | 0 | 0
62 | 0.99798 | -0.063559 | 0.3771 | 0.18264
63 | 0.99552 | -0.11103 | 0.18512 | 0.089657
64 | 0.99643 | -0.11784 | 0 | 0
65 | 0.99615 | -0.11633 | 0.34182 | 0.16555
66 | 0.99668 | -0.11113 | 0.25696 | 0.12445
67 | 0.99706 | -0.06193 | 0 | 0
68 | 0.99702 | -0.06154 | 0.33823 | 0.16381
69 | 0.99679 | -0.06051 | 0 | 0
70 | 0.99675 | -0.060776 | 0.25846 | 0.12518
71 | 0.99664 | -0.059329 | 0 | 0
72 | 0.99661 | -0.059499 | 0.19727 | 0.09554
73 | 0.99721 | -0.063763 | 0.33799 | 0.16369
74 | 0.998 | -0.063473 | 0 | 0
75 | 0.99722 | -0.10785 | 0 | 0
76 | 0.99855 | -0.06051 | 0 | 0
77 | 0.99532 | -0.11234 | 0.11033 | 0.053437
78 | 0.99693 | -0.10866 | 0.32599 | 0.15789
79 | 0.99694 | -0.10875 | 0 | 0
80 | 0.99698 | -0.10913 | 0 | 0
81 | 0.99684 | -0.10982 | 0.38145 | 0.18474
82 | 0.99684 | -0.10984 | 0 | 0
83 | 0.99675 | -0.11027 | 0 | 0
84 | 0.99689 | -0.1096 | 0 | 0
85 | 0.9969 | -0.10952 | 0 | 0
86 | 0.99688 | -0.10955 | 0.17514 | 0.084824
87 | 0.99695 | -0.10928 | 0.16478 | 0.079804
88 | 0.99693 | -0.10936 | 0.084041 | 0.040703
89 | 0.99701 | -0.061449 | 0.25183 | 0.12197
90 | 0.99722 | -0.10782 | 0.39711 | 0.19233
91 | 0.99862 | -0.060122 | 0 | 0
92 | 0.99853 | -0.060295 | 0.27053 | 0.13103
93 | 0.99895 | -0.040803 | 0.15704 | 0.076058
94 | 0.99891 | -0.041077 | 0.18033 | 0.087337
95 | 0.99907 | -0.040138 | 2.052 | 0.99385
96 | 0.99887 | -0.041312 | 0.28437 | 0.13773
97 | 0.998 | -0.045601 | 0 | 0
98 | 0.99883 | -0.041508 | 0 | 0
99 | 0.99715 | -0.049065 | 0.19187 | 0.092927
100 | 0.99736 | -0.051004 | 0.070171 | 0.033985
101 | 0.98309 | -0.14564 | 0.10218 | 0.049488
102 | 0.98339 | -0.14345 | 0.69423 | 0.33623
103 | 0.99736 | -0.050992 | 0.086163 | 0.041731
104 | 0.99885 | -0.041103 | 0 | 0
105 | 0.99882 | -0.040846 | 0.2066 | 0.10006
106 | 0.99882 | -0.040834 | 0.12996 | 0.062943
107 | 0.99974 | -0.001338 | 0.098071 | 0.047498
108 | 1 | 0 | -15.745 | -7.0801
109 | 0.99974 | -0.0013227 | 0.086794 | 0.042036
110 | 0.99974 | -0.0013225 | 0.08688 | 0.042078
111 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -2.3046 | -1.049 | 2.3049 | 1.0482 | 0.00029446 | -0.00084794 | 0.074066 | 0.074054 | 0.074066 | 0.9869 | -0.17633 | 0.98702 | -0.17729 | 33.6662
1 | 1.9254 | 0.86542 | -1.925 | -0.86716 | 0.00040671 | -0.0017365 | 0.061748 | 0.06177 | 0.06177 | 0.9869 | -0.17633 | 0.98671 | -0.17479 | 28.0772
2 | 0.0739 | 0.031493 | -0.073899 | -0.034677 | 1.0247e-06 | -0.0031833 | 0.0023494 | 0.0023875 | 0.0023875 | 0.98702 | -0.17729 | 0.98701 | -0.17719 | 1.0852
3 | -2.3788 | -1.0797 | 2.3811 | 1.0734 | 0.0023284 | -0.0062733 | 0.076403 | 0.076319 | 0.076403 | 0.98702 | -0.17729 | 0.98793 | -0.18454 | 34.7287
4 | 1.925 | 0.86716 | -1.9222 | -0.87924 | 0.0028448 | -0.012088 | 0.06177 | 0.061926 | 0.061926 | 0.98671 | -0.17479 | 0.98534 | -0.16373 | 28.1483
5 | 0.073899 | 0.034677 | -0.073898 | -0.035791 | 3.6653e-07 | -0.0011137 | 0.0023875 | 0.0024015 | 0.0024015 | 0.98701 | -0.17719 | 0.98701 | -0.17715 | 1.0916
6 | 0.11378 | 0.053824 | -0.11378 | -0.055107 | 9.9891e-07 | -0.001283 | 0.003678 | 0.0036942 | 0.0036942 | 0.98793 | -0.18454 | 0.98792 | -0.18446 | 1.6792
7 | -2.6373 | -1.1873 | 2.6488 | 1.1935 | 0.011535 | 0.0061641 | 0.084512 | 0.0845 | 0.084512 | 0.98793 | -0.18454 | 0.99254 | -0.14795 | 40.2439
8 | 0.14243 | 0.060088 | -0.14242 | -0.068105 | 9.569e-06 | -0.0080162 | 0.004517 | 0.0046131 | 0.0046131 | 0.98793 | -0.18454 | 0.98787 | -0.18405 | 2.0969
9 | 0.58307 | 0.28065 | -0.58304 | -0.28181 | 2.4075e-05 | -0.001155 | 0.018958 | 0.018973 | 0.018973 | 0.98534 | -0.16373 | 0.9853 | -0.16338 | 8.624
10 | 1.3391 | 0.59859 | -1.3383 | -0.60581 | 0.00079491 | -0.0072187 | 0.042974 | 0.043063 | 0.043063 | 0.98534 | -0.16373 | 0.98478 | -0.1594 | 19.5742
11 | -2.9033 | -1.3167 | 2.9047 | 1.3175 | 0.001406 | 0.00077264 | 0.092721 | 0.092719 | 0.092721 | 0.99254 | -0.14795 | 0.99305 | -0.14398 | 44.1527
12 | -2.9047 | -1.3175 | 2.914 | 1.3226 | 0.0092696 | 0.0050912 | 0.092719 | 0.092711 | 0.092719 | 0.99305 | -0.14398 | 0.99643 | -0.11784 | 44.152
13 | 0.14242 | 0.068105 | -0.14242 | -0.068976 | 1.0653e-06 | -0.00087132 | 0.0046131 | 0.0046242 | 0.0046242 | 0.98787 | -0.18405 | 0.98786 | -0.18398 | 2.1019
14 | -0.93703 | -0.41405 | 0.93716 | 0.41162 | 0.00012834 | -0.0024319 | 0.030034 | 0.030005 | 0.030034 | 0.98466 | -0.15845 | 0.98478 | -0.1594 | 13.6517
15 | 0.38244 | 0.1741 | -0.38234 | -0.18508 | 9.7451e-05 | -0.010981 | 0.012319 | 0.012457 | 0.012457 | 0.98466 | -0.15845 | 0.98442 | -0.15638 | 5.6621
16 | 0.21553 | 0.076812 | -0.21545 | -0.10424 | 7.4395e-05 | -0.027432 | 0.006708 | 0.0070194 | 0.0070194 | 0.98466 | -0.15845 | 0.98433 | -0.15638 | 3.1906
17 | 0.14913 | 0.072036 | -0.14912 | -0.072224 | 2.5595e-07 | -0.0001881 | 0.0048553 | 0.0048577 | 0.0048577 | 0.98466 | -0.15845 | 0.98466 | -0.15844 | 2.2081
18 | 0.18994 | 0.091105 | -0.18988 | -0.091965 | 5.2547e-05 | -0.00086018 | 0.0061759 | 0.0061872 | 0.0061872 | 0.98466 | -0.15845 | 0.98437 | -0.16031 | 2.9463
19 | 0.40117 | 0.19419 | -0.40114 | -0.19428 | 2.8697e-05 | -9.1252e-05 | 0.013065 | 0.013066 | 0.013066 | 0.98478 | -0.1594 | 0.98471 | -0.15987 | 6.2221
20 | 0.38234 | 0.18508 | -0.38232 | -0.18517 | 2.3561e-05 | -8.3821e-05 | 0.012457 | 0.012458 | 0.012458 | 0.98442 | -0.15638 | 0.98436 | -0.15679 | 5.9323
21 | 0.21545 | 0.10424 | -0.21545 | -0.10435 | 8.0865e-06 | -0.00010146 | 0.0070194 | 0.0070207 | 0.0070207 | 0.98433 | -0.15638 | 0.98429 | -0.15663 | 3.3432
22 | 0.39915 | 0.19274 | -0.39899 | -0.19324 | 0.0001545 | -0.00049856 | 0.012986 | 0.012994 | 0.012994 | 0.9853 | -0.16338 | 0.9849 | -0.16594 | 6.1876
23 | -0.15354 | -0.074364 | 0.15355 | 0.074174 | 7.5792e-06 | -0.00019047 | 0.0050126 | 0.0050101 | 0.0050126 | 0.98251 | -0.14123 | 0.98256 | -0.1409 | 2.3869
24 | -0.5003 | -0.24211 | 0.50034 | 0.23936 | 4.2675e-05 | -0.0027568 | 0.01633 | 0.016294 | 0.01633 | 0.98256 | -0.1409 | 0.98264 | -0.14164 | 7.4225
25 | -0.69581 | -0.33402 | 0.69588 | 0.33168 | 7.0334e-05 | -0.0023449 | 0.022674 | 0.022644 | 0.022674 | 0.98264 | -0.14164 | 0.98273 | -0.14249 | 10.3066
26 | 1.5485 | 0.74071 | -1.5485 | -0.74097 | 3.8597e-05 | -0.00026672 | 0.049683 | 0.049686 | 0.049686 | 0.99739 | -0.051266 | 0.99737 | -0.051054 | 22.5847
27 | 3.0105 | 1.426 | -2.9749 | -1.4062 | 0.035672 | 0.019819 | 0.096415 | 0.096447 | 0.096447 | 0.99739 | -0.051266 | 0.98487 | -0.13674 | 45.9269
28 | -4.5591 | -2.1667 | 4.561 | 2.1616 | 0.0019703 | -0.0050971 | 0.1461 | 0.14602 | 0.1461 | 0.99739 | -0.051266 | 0.99786 | -0.046172 | 40.3585
29 | 1.3922 | 0.66618 | -1.3918 | -0.66898 | 0.00032501 | -0.0027983 | 0.04467 | 0.044707 | 0.044707 | 0.99737 | -0.051054 | 0.99715 | -0.049065 | 20.3212
30 | 0.15633 | 0.074795 | -0.15633 | -0.075445 | 9.1987e-07 | -0.00064907 | 0.0050161 | 0.0050243 | 0.0050243 | 0.99737 | -0.051054 | 0.99736 | -0.051004 | 2.2838
31 | 2.7834 | 1.3137 | -2.7831 | -1.3144 | 0.00037866 | -0.00069461 | 0.090215 | 0.090225 | 0.090225 | 0.98487 | -0.13674 | 0.98475 | -0.13562 | 41.0115
32 | 0.077968 | 0.037567 | -0.077966 | -0.03776 | 1.9272e-06 | -0.00019324 | 0.0025367 | 0.0025392 | 0.0025392 | 0.98487 | -0.13674 | 0.98485 | -0.1369 | 1.2092
33 | -4.7152 | -2.2363 | 4.7158 | 2.2143 | 0.00062929 | -0.02205 | 0.15097 | 0.1507 | 0.15097 | 0.99786 | -0.046172 | 0.998 | -0.045601 | 11.8317
34 | -0.41377 | -0.17967 | 0.41378 | 0.17859 | 1.0932e-05 | -0.0010727 | 0.013252 | 0.01324 | 0.013252 | 0.98261 | -0.14153 | 0.98264 | -0.14171 | 6.0238
35 | 0.41377 | 0.17967 | -0.41367 | -0.17995 | 9.3122e-05 | -0.00028452 | 0.013252 | 0.013256 | 0.013256 | 0.98261 | -0.14153 | 0.98238 | -0.14361 | 6.3125
36 | 0.46882 | 0.22602 | -0.4688 | -0.22705 | 1.4011e-05 | -0.0010299 | 0.01529 | 0.015303 | 0.015303 | 0.98264 | -0.14171 | 0.98261 | -0.14145 | 6.9559
37 | -0.88259 | -0.40461 | 0.88262 | 0.40415 | 2.2172e-05 | -0.00046415 | 0.028523 | 0.028517 | 0.028523 | 0.98264 | -0.14171 | 0.98266 | -0.1419 | 12.9651
38 | 0.30291 | 0.12631 | -0.30291 | -0.12644 | 7.3183e-07 | -0.00013557 | 0.009644 | 0.0096456 | 0.0096456 | 0.98238 | -0.14361 | 0.98237 | -0.1436 | 4.3843
39 | 0.24216 | 0.11728 | -0.24216 | -0.11729 | 1.931e-08 | -5.247e-06 | 0.0079048 | 0.0079049 | 0.0079049 | 0.98261 | -0.14145 | 0.98261 | -0.14145 | 3.5931
40 | -1.2856 | -0.59934 | 1.2857 | 0.59841 | 9.5942e-05 | -0.00092609 | 0.04167 | 0.041658 | 0.04167 | 0.98266 | -0.1419 | 0.98273 | -0.14249 | 18.941
41 | -0.21826 | -0.096452 | 0.21828 | 0.090762 | 1.6072e-05 | -0.00569 | 0.0070125 | 0.0069466 | 0.0070125 | 0.9823 | -0.14313 | 0.98237 | -0.1436 | 3.1875
42 | 0.085907 | 0.041486 | -0.085907 | -0.041607 | 5.4956e-08 | -0.00012052 | 0.0028036 | 0.0028051 | 0.0028051 | 0.9823 | -0.14313 | 0.9823 | -0.14312 | 1.275
43 | 0.13235 | 0.054966 | -0.13234 | -0.063947 | 9.4647e-06 | -0.0089801 | 0.0042116 | 0.0043198 | 0.0043198 | 0.9823 | -0.14313 | 0.98224 | -0.14261 | 1.9635
44 | 0.084635 | 0.03568 | -0.084633 | -0.039972 | 1.8457e-06 | -0.0042922 | 0.002699 | 0.0027505 | 0.0027505 | 0.98237 | -0.1436 | 0.98235 | -0.14344 | 1.2502
45 | 0.13234 | 0.063947 | -0.13234 | -0.064097 | 1.6289e-07 | -0.00015051 | 0.0043198 | 0.0043217 | 0.0043217 | 0.98224 | -0.14261 | 0.98224 | -0.1426 | 1.9644
46 | 0.084633 | 0.039972 | -0.084633 | -0.040989 | 4.4801e-07 | -0.0010172 | 0.0027505 | 0.0027634 | 0.0027634 | 0.98235 | -0.14344 | 0.98235 | -0.1434 | 1.2561
47 | -1.9816 | -0.93009 | 1.9823 | 0.92735 | 0.00070424 | -0.0027356 | 0.064302 | 0.064266 | 0.064302 | 0.98273 | -0.14249 | 0.98306 | -0.14536 | 29.2283
48 | -1.9823 | -0.92735 | 1.9824 | 0.92709 | 6.7638e-05 | -0.00026302 | 0.064266 | 0.064262 | 0.064266 | 0.98306 | -0.14536 | 0.98309 | -0.14564 | 29.2116
49 | 2.7831 | 1.3144 | -2.7797 | -1.3126 | 0.0033542 | 0.0018336 | 0.090225 | 0.090229 | 0.090229 | 0.98475 | -0.13562 | 0.98349 | -0.14433 | 42.966
50 | 2.7797 | 1.3126 | -2.7795 | -1.313 | 0.00025022 | -0.00045739 | 0.090229 | 0.090235 | 0.090235 | 0.98349 | -0.14433 | 0.98341 | -0.14358 | 41.016
51 | 2.7795 | 1.313 | -2.7794 | -1.3131 | 4.6764e-05 | -8.5463e-05 | 0.090235 | 0.090237 | 0.090237 | 0.98341 | -0.14358 | 0.98339 | -0.14345 | 41.0166
52 | -0.18156 | -0.087935 | 0.18157 | 0.087109 | 1.5851e-06 | -0.00082634 | 0.0058422 | 0.0058318 | 0.0058422 | 0.99683 | -0.048156 | 0.99684 | -0.048232 | 2.6555
53 | -0.30141 | -0.14515 | 0.30143 | 0.14504 | 1.6545e-05 | -0.00010703 | 0.0096879 | 0.0096865 | 0.0096879 | 0.99684 | -0.048232 | 0.9969 | -0.047861 | 4.6133
54 | -0.61518 | -0.297 | 0.61521 | 0.29592 | 2.4102e-05 | -0.0010884 | 0.019782 | 0.019768 | 0.019782 | 0.9969 | -0.047861 | 0.99693 | -0.048199 | 8.9916
55 | -0.71489 | -0.3442 | 0.71495 | 0.34242 | 5.3079e-05 | -0.0017735 | 0.022975 | 0.022953 | 0.022975 | 0.99693 | -0.048199 | 0.997 | -0.048834 | 10.4432
56 | -1.0883 | -0.5232 | 1.0883 | 0.52285 | 2.3932e-05 | -0.00034108 | 0.034961 | 0.034957 | 0.034961 | 0.99707 | -0.048363 | 0.99709 | -0.048551 | 15.8913
57 | 0.715 | 0.34239 | -0.71495 | -0.34242 | 4.8953e-05 | -3.1232e-05 | 0.022952 | 0.022953 | 0.022953 | 0.99707 | -0.048363 | 0.997 | -0.048834 | 10.9298
58 | -1.1999 | -0.57689 | 1.2 | 0.57605 | 7.1986e-05 | -0.00084044 | 0.038546 | 0.038535 | 0.038546 | 0.99709 | -0.048551 | 0.99715 | -0.049065 | 17.5207
59 | -0.33572 | -0.1626 | 0.33573 | 0.16065 | 1.2791e-05 | -0.0019405 | 0.010814 | 0.010789 | 0.010814 | 0.99579 | -0.11308 | 0.99583 | -0.11341 | 4.9153
60 | 0.29557 | 0.1224 | -0.29547 | -0.14174 | 9.6208e-05 | -0.019339 | 0.0092738 | 0.0095028 | 0.0095028 | 0.99583 | -0.11341 | 0.99552 | -0.11107 | 4.3194
61 | -0.6313 | -0.28306 | 0.63154 | 0.27236 | 0.00024255 | -0.010695 | 0.020056 | 0.01993 | 0.020056 | 0.99583 | -0.11341 | 0.99619 | -0.11605 | 9.1162
62 | 0.29547 | 0.14174 | -0.29547 | -0.142 | 1.3262e-06 | -0.00025983 | 0.0095028 | 0.0095061 | 0.0095061 | 0.99552 | -0.11107 | 0.99552 | -0.11103 | 4.3209
63 | -0.97337 | -0.43784 | 0.97362 | 0.4334 | 0.00024251 | -0.0044366 | 0.030929 | 0.030875 | 0.030929 | 0.99619 | -0.11605 | 0.99643 | -0.11784 | 14.0584
64 | 0.34183 | 0.16548 | -0.34182 | -0.16555 | 1.4561e-05 | -7.0814e-05 | 0.011005 | 0.011006 | 0.011006 | 0.99619 | -0.11605 | 0.99615 | -0.11633 | 5.241
65 | 1.3847 | 0.6242 | -1.3842 | -0.62902 | 0.00054124 | -0.0048178 | 0.043953 | 0.044012 | 0.044012 | 0.99761 | -0.066477 | 0.99724 | -0.063578 | 20.0054
66 | -1.3847 | -0.6242 | 1.3852 | 0.62434 | 0.00048323 | 0.00013581 | 0.043953 | 0.043951 | 0.043953 | 0.99761 | -0.066477 | 0.99798 | -0.063559 | 20.9298
67 | 0.338 | 0.16365 | -0.33799 | -0.16369 | 9.4745e-06 | -4.7486e-05 | 0.010871 | 0.010871 | 0.010871 | 0.99724 | -0.063578 | 0.99721 | -0.063763 | 5.1768
68 | 0.59021 | 0.27802 | -0.59009 | -0.28375 | 0.00011611 | -0.005733 | 0.018886 | 0.018957 | 0.018957 | 0.99724 | -0.063578 | 0.99706 | -0.06193 | 8.6169
69 | 0.45599 | 0.18735 | -0.45578 | -0.2058 | 0.00021514 | -0.018447 | 0.01427 | 0.014483 | 0.014483 | 0.99724 | -0.063578 | 0.99679 | -0.06051 | 6.583
70 | -7.4411 | -3.3563 | 7.4412 | 3.3546 | 0.00012027 | -0.00168 | 0.23612 | 0.2361 | 0.23612 | 0.99798 | -0.063559 | 0.998 | -0.063473 | 18.5048
71 | 5.6787 | 2.5493 | -5.6764 | -2.5441 | 0.0023532 | 0.0052092 | 0.18006 | 0.18007 | 0.18007 | 0.99798 | -0.063559 | 0.99722 | -0.10785 | 13.9588
72 | 0.11035 | 0.052343 | -0.11033 | -0.053437 | 2.0996e-05 | -0.0010938 | 0.0035417 | 0.0035556 | 0.0035556 | 0.99552 | -0.11103 | 0.99532 | -0.11234 | 1.6931
73 | -3.8876 | -1.756 | 3.8884 | 1.7568 | 0.00079301 | 0.00083646 | 0.12359 | 0.12358 | 0.12359 | 0.99643 | -0.11784 | 0.99668 | -0.11113 | 35.3101
74 | -4.1454 | -1.8813 | 4.1457 | 1.8804 | 0.00027346 | -0.00091131 | 0.13185 | 0.13184 | 0.13185 | 0.99668 | -0.11113 | 0.99675 | -0.11027 | 36.423
75 | 0.59009 | 0.28375 | -0.59006 | -0.28506 | 2.6652e-05 | -0.0013095 | 0.018957 | 0.018974 | 0.018974 | 0.99706 | -0.06193 | 0.99702 | -0.06154 | 8.6245
76 | 0.25184 | 0.12125 | -0.25183 | -0.12197 | 2.6499e-06 | -0.00071773 | 0.0080927 | 0.0081018 | 0.0081018 | 0.99702 | -0.06154 | 0.99701 | -0.061449 | 3.6826
77 | 0.25847 | 0.12509 | -0.25846 | -0.12518 | 1.042e-05 | -9.3766e-05 | 0.008316 | 0.0083172 | 0.0083172 | 0.99679 | -0.06051 | 0.99675 | -0.060776 | 3.9606
78 | 0.1973 | 0.080712 | -0.19727 | -0.095459 | 3.2523e-05 | -0.014748 | 0.0061736 | 0.0063477 | 0.0063477 | 0.99679 | -0.06051 | 0.99664 | -0.059329 | 2.8853
79 | 0.19727 | 0.095459 | -0.19727 | -0.09554 | 5.0758e-06 | -8.0643e-05 | 0.0063477 | 0.0063488 | 0.0063488 | 0.99664 | -0.059329 | 0.99661 | -0.059499 | 3.0232
80 | -7.4412 | -3.3546 | 7.4452 | 3.2989 | 0.0039761 | -0.055746 | 0.2361 | 0.23542 | 0.2361 | 0.998 | -0.063473 | 0.99855 | -0.06051 | 18.5032
81 | 5.2793 | 2.352 | -5.278 | -2.387 | 0.0012391 | -0.03501 | 0.1673 | 0.16773 | 0.16773 | 0.99722 | -0.10785 | 0.99698 | -0.10913 | 13.1448
82 | 0.39711 | 0.19214 | -0.39711 | -0.19233 | 1.7321e-06 | -0.00018834 | 0.012771 | 0.012773 | 0.012773 | 0.99722 | -0.10785 | 0.99722 | -0.10782 | 5.8059
83 | -7.7157 | -3.4283 | 7.7162 | 3.4214 | 0.00052393 | -0.0068401 | 0.24408 | 0.244 | 0.24408 | 0.99855 | -0.06051 | 0.99862 | -0.060122 | 19.1287
84 | 0.27054 | 0.12943 | -0.27053 | -0.13103 | 6.7511e-06 | -0.0015959 | 0.0086701 | 0.0086901 | 0.0086901 | 0.99855 | -0.06051 | 0.99853 | -0.060295 | 3.9501
85 | -0.32599 | -0.15789 | 0.326 | 0.15732 | 3.5308e-06 | -0.00056984 | 0.010488 | 0.010481 | 0.010488 | 0.99693 | -0.10866 | 0.99694 | -0.10875 | 4.7675
86 | -0.326 | -0.15732 | 0.32601 | 0.15496 | 1.453e-05 | -0.0023534 | 0.010481 | 0.010452 | 0.010481 | 0.99694 | -0.10875 | 0.99698 | -0.10913 | 4.7642
87 | 4.952 | 2.232 | -4.9519 | -2.2364 | 0.00013611 | -0.0043701 | 0.15728 | 0.15733 | 0.15733 | 0.99698 | -0.10913 | 0.99695 | -0.10928 | 12.33
88 | -0.38145 | -0.18474 | 0.38145 | 0.18463 | 9.7549e-07 | -0.0001148 | 0.012274 | 0.012272 | 0.012274 | 0.99684 | -0.10982 | 0.99684 | -0.10984 | 5.579
89 | 4.146 | 1.8649 | -4.1457 | -1.8804 | 0.00033662 | -0.015484 | 0.13165 | 0.13184 | 0.13184 | 0.99684 | -0.10984 | 0.99675 | -0.11027 | 10.3321
90 | -4.5274 | -2.0495 | 4.5276 | 2.0417 | 0.00020295 | -0.0078104 | 0.14392 | 0.14382 | 0.14392 | 0.99684 | -0.10984 | 0.99689 | -0.1096 | 11.2789
91 | -4.7028 | -2.126 | 4.7029 | 2.1233 | 7.4644e-05 | -0.0026599 | 0.14945 | 0.14942 | 0.14945 | 0.99689 | -0.1096 | 0.9969 | -0.10952 | 11.7124
92 | 0.17514 | 0.084248 | -0.17514 | -0.084824 | 1.0292e-06 | -0.00057647 | 0.0056279 | 0.0056352 | 0.0056352 | 0.99689 | -0.1096 | 0.99688 | -0.10955 | 2.5615
93 | -4.7029 | -2.1233 | 4.703 | 2.1184 | 0.00013695 | -0.0048835 | 0.14942 | 0.14936 | 0.14942 | 0.9969 | -0.10952 | 0.99693 | -0.10936 | 11.7099
94 | 4.7871 | 2.1566 | -4.787 | -2.1591 | 7.4342e-05 | -0.0025577 | 0.15203 | 0.15206 | 0.15206 | 0.99695 | -0.10928 | 0.99693 | -0.10936 | 11.9171
95 | -7.7162 | -3.4214 | 7.7176 | 3.4248 | 0.0013868 | 0.0033693 | 0.244 | 0.24399 | 0.244 | 0.99862 | -0.060122 | 0.99895 | -0.040803 | 18.9147
96 | 4.9005 | 2.1478 | -4.9003 | -2.1553 | 0.00022544 | -0.0075224 | 0.15462 | 0.15471 | 0.15471 | 0.99895 | -0.040803 | 0.99891 | -0.041077 | 12.1243
97 | -13.3961 | -5.9463 | 13.3977 | 5.9402 | 0.001556 | -0.0061662 | 0.42354 | 0.42346 | 0.42354 | 0.99895 | -0.040803 | 0.99907 | -0.040138 | 33.193
98 | 0.62099 | 0.29767 | -0.62095 | -0.29772 | 4.6232e-05 | -4.9088e-05 | 0.0199 | 0.019901 | 0.019901 | 0.99895 | -0.040803 | 0.99887 | -0.041312 | 9.4769
99 | 4.7199 | 2.068 | -4.7196 | -2.0803 | 0.00034306 | -0.012348 | 0.14892 | 0.14907 | 0.14907 | 0.99891 | -0.041077 | 0.99883 | -0.041508 | 11.6823
100 | -15.4497 | -6.934 | 15.4553 | 6.9488 | 0.0056146 | 0.014735 | 0.48931 | 0.4893 | 0.48931 | 0.99907 | -0.040138 | 0.99974 | -0.001338 | 37.9308
101 | 0.33658 | 0.16 | -0.33657 | -0.16128 | 8.3818e-06 | -0.001285 | 0.01077 | 0.010786 | 0.010786 | 0.99887 | -0.041312 | 0.99885 | -0.041103 | 4.9028
102 | -4.7158 | -2.2143 | 4.7196 | 2.0803 | 0.0037691 | -0.13393 | 0.1507 | 0.14907 | 0.1507 | 0.998 | -0.045601 | 0.99883 | -0.041508 | 11.81
103 | 0.086163 | 0.041459 | -0.086163 | -0.041731 | 1.1704e-07 | -0.00027147 | 0.0027676 | 0.002771 | 0.002771 | 0.99736 | -0.051004 | 0.99736 | -0.050992 | 1.2595
104 | -2.0846 | -0.97658 | 2.0852 | 0.97688 | 0.00061582 | 0.00029842 | 0.067596 | 0.067594 | 0.067596 | 0.98309 | -0.14564 | 0.98339 | -0.14345 | 32.1884
105 | 0.33657 | 0.16128 | -0.33656 | -0.16282 | 1.0056e-05 | -0.0015366 | 0.010786 | 0.010806 | 0.010806 | 0.99885 | -0.041103 | 0.99882 | -0.040846 | 4.9116
106 | 0.12996 | 0.062757 | -0.12996 | -0.062943 | 1.8118e-07 | -0.00018568 | 0.0041711 | 0.0041734 | 0.0041734 | 0.99882 | -0.040846 | 0.99882 | -0.040834 | 1.897
107 | -15.7271 | -7.0802 | 15.731 | 7.0696 | 0.0038975 | -0.010587 | 0.49802 | 0.49787 | 0.49802 | 0.99974 | -0.001338 | 1 | 0 | 39.0295
108 | 0.17367 | 0.083934 | -0.17367 | -0.08411 | 3.059e-07 | -0.0001761 | 0.0055698 | 0.005572 | 0.005572 | 0.99974 | -0.001338 | 0.99974 | -0.0013227 | 2.5327
109 | 0.08688 | 0.042074 | -0.08688 | -0.042078 | 1.6244e-09 | -3.9463e-06 | 0.0027873 | 0.0027874 | 0.0027874 | 0.99974 | -0.0013227 | 0.99974 | -0.0013225 | 1.267

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 15.745 | 7.0801

## res_load
| p_mw | q_mvar
0 | 0.37914 | 0.18363
1 | 0.25448 | 0.12325
2 | 0.14242 | 0.068976
3 | 0.073898 | 0.035791
4 | 0.11378 | 0.055107
5 | 0.14912 | 0.072224
6 | 0.18988 | 0.091965
7 | 0.40114 | 0.19428
8 | 0.1839 | 0.089065
9 | 0.38232 | 0.18517
10 | 0.21545 | 0.10435
11 | 0.39899 | 0.19324
12 | 0.15354 | 0.074364
13 | 0.34675 | 0.16794
14 | 0.19546 | 0.094667
15 | 0.11345 | 0.054947
16 | 0.15416 | 0.074664
17 | 0.11076 | 0.053644
18 | 0.22664 | 0.10977
19 | 0.40302 | 0.19519
20 | 0.085907 | 0.041607
21 | 0.084633 | 0.040989
22 | 0.13234 | 0.064097
23 | 0.24216 | 0.11729
24 | 0.077966 | 0.03776
25 | 0.18156 | 0.087935
26 | 0.11984 | 0.058043
27 | 0.31376 | 0.15196
28 | 0.099688 | 0.048281
29 | 0.37331 | 0.1808
30 | 0.11157 | 0.054035
31 | 0.33572 | 0.1626
32 | 0.3771 | 0.18264
33 | 0.18512 | 0.089657
34 | 0.34182 | 0.16555
35 | 0.25696 | 0.12445
36 | 0.33823 | 0.16381
37 | 0.25846 | 0.12518
38 | 0.19727 | 0.09554
39 | 0.33799 | 0.16369
40 | 0.11033 | 0.053437
41 | 0.32599 | 0.15789
42 | 0.38145 | 0.18474
43 | 0.17514 | 0.084824
44 | 0.16478 | 0.079804
45 | 0.084041 | 0.040703
46 | 0.25183 | 0.12197
47 | 0.39711 | 0.19233
48 | 0.27053 | 0.13103
49 | 0.15704 | 0.076058
50 | 0.18033 | 0.087337
51 | 2.052 | 0.99385
52 | 0.28437 | 0.13773
53 | 0.19187 | 0.092927
54 | 0.070171 | 0.033985
55 | 0.10218 | 0.049488
56 | 0.69423 | 0.33623
57 | 0.086163 | 0.041731
58 | 0.2066 | 0.10006
59 | 0.12996 | 0.062943
60 | 0.098071 | 0.047498
61 | 0.086794 | 0.042036
62 | 0.08688 | 0.042078

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1