## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_531_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_531_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_531_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_531_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_531_0_node_4 | 20 | n |  | TRUE
5 | bus_MV_531_0_node_30 | 20 | n |  | TRUE
6 | bus_MV_531_0_node_5 | 20 | n |  | TRUE
7 | bus_MV_531_0_node_35 | 20 | n |  | TRUE
8 | bus_MV_531_0_node_87 | 20 | n |  | TRUE
9 | bus_MV_531_0_node_86 | 20 | n |  | TRUE
10 | bus_MV_531_0_node_33 | 20 | n |  | TRUE
11 | bus_MV_531_0_node_6 | 20 | n |  | TRUE
12 | bus_MV_531_0_node_76 | 20 | n |  | TRUE
13 | bus_MV_531_0_node_7 | 20 | n |  | TRUE
14 | bus_MV_531_0_node_92 | 20 | n |  | TRUE
15 | bus_MV_531_0_node_75 | 20 | n |  | TRUE
16 | bus_MV_531_0_node_8 | 20 | n |  | TRUE
17 | bus_MV_531_0_node_9 | 20 | n |  | TRUE
18 | bus_MV_531_0_node_91 | 20 | n |  | TRUE
19 | bus_MV_531_0_node_89 | 20 | n |  | TRUE
20 | bus_MV_531_0_node_10 | 20 | n |  | TRUE
21 | bus_MV_531_0_node_12 | 20 | n |  | TRUE
22 | bus_MV_531_0_node_14 | 20 | n |  | TRUE
23 | bus_MV_531_0_node_48 | 20 | n |  | TRUE
24 | bus_MV_531_0_node_20 | 20 | n |  | TRUE
25 | bus_MV_531_0_node_22 | 20 | n |  | TRUE
26 | bus_MV_531_0_node_49 | 20 | n |  | TRUE
27 | bus_MV_531_0_node_99 | 20 | n |  | TRUE
28 | bus_MV_531_0_node_66 | 20 | n |  | TRUE
29 | bus_MV_531_0_node_15 | 20 | n |  | TRUE
30 | bus_MV_531_0_node_17 | 20 | n |  | TRUE
31 | bus_MV_531_0_node_18 | 20 | n |  | TRUE
32 | bus_MV_531_0_node_16 | 20 | n |  | TRUE
33 | bus_MV_531_0_node_24 | 20 | n |  | TRUE
34 | bus_MV_531_0_node_25 | 20 | n |  | TRUE
35 | bus_MV_531_0_node_19 | 20 | n |  | TRUE
36 | bus_MV_531_0_node_83 | 20 | n |  | TRUE
37 | bus_MV_531_0_node_129 | 20 | n |  | TRUE
38 | bus_MV_531_0_node_21 | 20 | n |  | TRUE
39 | bus_MV_531_0_node_101 | 20 | n |  | TRUE
40 | bus_MV_531_0_node_100 | 20 | n |  | TRUE
41 | bus_MV_531_0_node_47 | 20 | n |  | TRUE
42 | bus_MV_531_0_node_123 | 20 | n |  | TRUE
43 | bus_MV_531_0_node_122 | 20 | n |  | TRUE
44 | bus_MV_531_0_node_81 | 20 | n |  | TRUE
45 | bus_MV_531_0_node_127 | 20 | n |  | TRUE
46 | bus_MV_531_0_node_26 | 20 | n |  | TRUE
47 | bus_MV_531_0_node_27 | 20 | n |  | TRUE
48 | bus_MV_531_0_node_28 | 20 | n |  | TRUE
49 | bus_MV_531_0_node_56 | 20 | n |  | TRUE
50 | bus_MV_531_0_node_57 | 20 | n |  | TRUE
51 | bus_MV_531_0_node_29 | 20 | n |  | TRUE
52 | bus_MV_531_0_node_77 | 20 | n |  | TRUE
53 | bus_MV_531_0_node_88 | 20 | n |  | TRUE
54 | bus_MV_531_0_node_78 | 20 | n |  | TRUE
55 | bus_MV_531_0_node_31 | 20 | n |  | TRUE
56 | bus_MV_531_0_node_32 | 20 | n |  | TRUE
57 | bus_MV_531_0_node_34 | 20 | n |  | TRUE
58 | bus_MV_531_0_node_110 | 20 | n |  | TRUE
59 | bus_MV_531_0_node_45 | 20 | n |  | TRUE
60 | bus_MV_531_0_node_44 | 20 | n |  | TRUE
61 | bus_MV_531_0_node_36 | 20 | n |  | TRUE
62 | bus_MV_531_0_node_37 | 20 | n |  | TRUE
63 | bus_MV_531_0_node_38 | 20 | n |  | TRUE
64 | bus_MV_531_0_node_39 | 20 | n |  | TRUE
65 | bus_MV_531_0_node_105 | 20 | n |  | TRUE
66 | bus_MV_531_0_node_120 | 20 | n |  | TRUE
67 | bus_MV_531_0_node_119 | 20 | n |  | TRUE
68 | bus_MV_531_0_node_40 | 20 | n |  | TRUE
69 | bus_MV_531_0_node_41 | 20 | n |  | TRUE
70 | bus_MV_531_0_node_42 | 20 | n |  | TRUE
71 | bus_MV_531_0_node_43 | 20 | n |  | TRUE
72 | bus_MV_531_0_node_55 | 20 | n |  | TRUE
73 | bus_MV_531_0_node_46 | 20 | n |  | TRUE
74 | bus_MV_531_0_node_109 | 20 | n |  | TRUE
75 | bus_MV_531_0_node_107 | 20 | n |  | TRUE
76 | bus_MV_531_0_node_50 | 20 | n |  | TRUE
77 | bus_MV_531_0_node_51 | 20 | n |  | TRUE
78 | bus_MV_531_0_node_52 | 20 | n |  | TRUE
79 | bus_MV_531_0_node_54 | 20 | n |  | TRUE
80 | bus_MV_531_0_node_126 | 20 | n |  | TRUE
81 | bus_MV_531_0_node_117 | 20 | n |  | TRUE
82 | bus_MV_531_0_node_98 | 20 | n |  | TRUE
83 | bus_MV_531_0_node_116 | 20 | n |  | TRUE
84 | bus_MV_531_0_node_58 | 20 | n |  | TRUE
85 | bus_MV_531_0_node_59 | 20 | n |  | TRUE
86 | bus_MV_531_0_node_60 | 20 | n |  | TRUE
87 | bus_MV_531_0_node_113 | 20 | n |  | TRUE
88 | bus_MV_531_0_node_114 | 20 | n |  | TRUE
89 | bus_MV_531_0_node_111 | 20 | n |  | TRUE
90 | bus_MV_531_0_node_118 | 20 | n |  | TRUE
91 | bus_MV_531_0_node_121 | 20 | n |  | TRUE
92 | bus_MV_531_0_node_104 | 20 | n |  | TRUE
93 | bus_MV_531_0_node_61 | 20 | n |  | TRUE
94 | bus_MV_531_0_node_62 | 20 | n |  | TRUE
95 | bus_MV_531_0_node_63 | 20 | n |  | TRUE
96 | bus_MV_531_0_node_65 | 20 | n |  | TRUE
97 | bus_MV_531_0_node_125 | 20 | n |  | TRUE
98 | bus_MV_531_0_node_64 | 20 | n |  | TRUE
99 | bus_MV_531_0_node_124 | 20 | n |  | TRUE
100 | bus_MV_531_0_node_108 | 20 | n |  | TRUE
101 | bus_MV_531_0_node_106 | 20 | n |  | TRUE
102 | bus_MV_531_0_node_95 | 20 | n |  | TRUE
103 | bus_MV_531_0_node_67 | 20 | n |  | TRUE
104 | bus_MV_531_0_node_68 | 20 | n |  | TRUE
105 | bus_MV_531_0_node_69 | 20 | n |  | TRUE
106 | bus_MV_531_0_node_70 | 20 | n |  | TRUE
107 | bus_MV_531_0_node_71 | 20 | n |  | TRUE
108 | bus_MV_531_0_node_72 | 20 | n |  | TRUE
109 | bus_MV_531_0_node_73 | 20 | n |  | TRUE
110 | bus_MV_531_0_node_74 | 20 | n |  | TRUE
111 | bus_MV_531_0_node_128 | 20 | n |  | TRUE
112 | bus_MV_531_0_node_80 | 20 | n |  | TRUE
113 | bus_MV_531_0_node_82 | 20 | n |  | TRUE
114 | bus_MV_531_0_node_84 | 20 | n |  | TRUE
115 | bus_MV_531_0_node_85 | 20 | n |  | TRUE
116 | bus_MV_531_0_node_93 | 20 | n |  | TRUE
117 | bus_MV_531_0_node_94 | 20 | n |  | TRUE
118 | bus_MV_531_0_node_96 | 20 | n |  | TRUE
119 | bus_MV_531_0_node_97 | 20 | n |  | TRUE
120 | bus_MV_531_0_node_102 | 20 | n |  | TRUE
121 | bus_MV_531_0_node_103 | 20 | n |  | TRUE
122 | bus_MV_531_0_node_112 | 20 | n |  | TRUE
123 | bus_MV_531_0_node_115 | 20 | n |  | TRUE
124 | bus_HV_531_0_node_73 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_531_0_load_0 | 0 | 0.39189 | 0.1898 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_531_0_load_30 | 5 | 0.25479 | 0.1234 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_531_0_load_35 | 7 | 0.075809 | 0.036716 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_531_0_load_87 | 8 | 0.12153 | 0.058861 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_531_0_load_86 | 9 | 0.078556 | 0.038046 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_531_0_load_33 | 10 | 0.071382 | 0.034572 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_531_0_load_6 | 11 | 0.35335 | 0.17114 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_531_0_load_76 | 12 | 0.071928 | 0.034837 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_531_0_load_7 | 13 | 0.15515 | 0.075142 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_531_0_load_92 | 14 | 0.19487 | 0.094378 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_531_0_load_8 | 16 | 0.32632 | 0.15804 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_531_0_load_9 | 17 | 0.068179 | 0.033021 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_531_0_load_10 | 20 | 0.32114 | 0.15554 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_531_0_load_48 | 23 | 0.081616 | 0.039528 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_531_0_load_99 | 27 | 0.27535 | 0.13336 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_531_0_load_66 | 28 | 0.73547 | 0.3562 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_531_0_load_15 | 29 | 0.2573 | 0.12462 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_531_0_load_16 | 32 | 0.078686 | 0.038109 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_531_0_load_24 | 33 | 0.06858 | 0.033215 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_531_0_load_129 | 37 | 0.080616 | 0.039044 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_531_0_load_100 | 40 | 0.2653 | 0.12849 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_531_0_load_47 | 41 | 2.1492 | 1.0409 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_531_0_load_123 | 42 | 0.23855 | 0.11553 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_531_0_load_122 | 43 | 0.11589 | 0.056128 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_531_0_load_81 | 44 | 0.12325 | 0.059693 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_531_0_load_127 | 45 | 0.14534 | 0.070391 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_531_0_load_26 | 46 | 0.21318 | 0.10325 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_531_0_load_56 | 49 | 0.37235 | 0.18034 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_531_0_load_77 | 52 | 0.10836 | 0.052479 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_531_0_load_88 | 53 | 0.14464 | 0.070051 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_531_0_load_31 | 55 | 0.41041 | 0.19877 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_531_0_load_110 | 58 | 0.19693 | 0.095375 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_531_0_load_45 | 59 | 0.19059 | 0.092306 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_531_0_load_36 | 61 | 0.39641 | 0.19199 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_531_0_load_105 | 65 | 0.069617 | 0.033717 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_531_0_load_120 | 66 | 0.27038 | 0.13095 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_531_0_load_40 | 68 | 0.19978 | 0.096759 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_531_0_load_42 | 70 | 0.39089 | 0.18932 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_531_0_load_55 | 72 | 0.073622 | 0.035657 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_531_0_load_46 | 73 | 0.19046 | 0.092243 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_531_0_load_107 | 75 | 0.088049 | 0.042644 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_531_0_load_50 | 76 | 0.12573 | 0.060896 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_531_0_load_126 | 80 | 0.41306 | 0.20006 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_531_0_load_117 | 81 | 0.27756 | 0.13443 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_531_0_load_60 | 86 | 0.11741 | 0.056866 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_531_0_load_113 | 87 | 0.14017 | 0.067888 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_531_0_load_121 | 91 | 0.65698 | 0.31819 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_531_0_load_61 | 93 | 0.075511 | 0.036571 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_531_0_load_125 | 97 | 0.27293 | 0.13218 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_531_0_load_124 | 99 | 0.21232 | 0.10283 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_531_0_load_108 | 100 | 0.078631 | 0.038083 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_531_0_load_106 | 101 | 0.077436 | 0.037504 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_531_0_load_67 | 103 | 0.083232 | 0.040311 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_531_0_load_68 | 104 | 0.20684 | 0.10018 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_531_0_load_69 | 105 | 0.078314 | 0.037929 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_531_0_load_70 | 106 | 0.088262 | 0.042747 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_531_0_load_72 | 108 | 0.077168 | 0.037374 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_531_0_load_128 | 111 | 0.13805 | 0.066861 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_531_0_load_80 | 112 | 0.34332 | 0.16628 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_531_0_load_85 | 115 | 0.081187 | 0.03932 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_531_0_load_93 | 116 | 0.15309 | 0.074143 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_531_0_load_97 | 119 | 0.13659 | 0.066152 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_531_0_load_102 | 120 | 0.35666 | 0.17274 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_531_0_load_112 | 122 | 0.084483 | 0.040917 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 109 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_531_0_line_0 |  | 0 | 1 | 0.003116 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_531_0_line_1 |  | 0 | 2 | 0.045909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_531_0_line_2 |  | 1 | 3 | 0.061482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_531_0_line_3 |  | 2 | 4 | 0.011098 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_531_0_line_4 |  | 3 | 5 | 0.006453 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_531_0_line_5 |  | 4 | 6 | 0.014434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_531_0_line_6 |  | 4 | 7 | 0.053865 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_531_0_line_7 |  | 6 | 8 | 0.015206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_531_0_line_8 |  | 6 | 9 | 0.053659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_531_0_line_9 |  | 7 | 10 | 0.019457 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_531_0_line_10 |  | 10 | 55 | 0.011891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_531_0_line_11 |  | 11 | 12 | 0.020283 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
12 | MV_531_0_line_12 |  | 11 | 13 | 0.024598 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_531_0_line_13 |  | 11 | 14 | 0.046949 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
14 | MV_531_0_line_14 |  | 12 | 15 | 0.03092 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
15 | MV_531_0_line_15 |  | 13 | 16 | 0.010472 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_531_0_line_16 |  | 14 | 18 | 0.04209 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
17 | MV_531_0_line_17 |  | 15 | 108 | 0.013031 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
18 | MV_531_0_line_18 |  | 16 | 17 | 0.0054276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_531_0_line_19 |  | 18 | 19 | 0.063199 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
20 | MV_531_0_line_20 |  | 19 | 53 | 0.027776 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
21 | MV_531_0_line_21 |  | 20 | 21 | 0.030855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_531_0_line_22 |  | 21 | 22 | 0.17756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_531_0_line_23 |  | 22 | 23 | 0.049566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_531_0_line_24 |  | 22 | 24 | 0.10504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_531_0_line_25 |  | 24 | 25 | 0.018206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_531_0_line_26 |  | 24 | 26 | 0.285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_531_0_line_27 |  | 24 | 27 | 0.065425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_531_0_line_28 |  | 25 | 41 | 0.020893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_531_0_line_29 |  | 25 | 35 | 0.024768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_531_0_line_30 |  | 26 | 28 | 0.059041 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_531_0_line_31 |  | 29 | 30 | 0.003355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_531_0_line_32 |  | 29 | 31 | 0.004165 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
33 | MV_531_0_line_33 |  | 29 | 32 | 0.054836 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_531_0_line_34 |  | 30 | 33 | 0.013679 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_531_0_line_35 |  | 31 | 34 | 0.004278 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
36 | MV_531_0_line_36 |  | 32 | 35 | 0.031355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_531_0_line_37 |  | 33 | 36 | 0.04014 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_531_0_line_38 |  | 34 | 37 | 0.10013 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
39 | MV_531_0_line_39 |  | 36 | 44 | 0.029673 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_531_0_line_40 |  | 36 | 43 | 0.059364 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_531_0_line_41 |  | 37 | 45 | 0.086138 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
42 | MV_531_0_line_42 |  | 38 | 39 | 0.081883 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_531_0_line_43 |  | 38 | 40 | 0.007968 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_531_0_line_44 |  | 39 | 42 | 0.027287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_531_0_line_45 |  | 42 | 115 | 0.033283 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_531_0_line_46 |  | 44 | 113 | 0.028199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_531_0_line_47 |  | 45 | 109 | 0.032847 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
48 | MV_531_0_line_48 |  | 46 | 47 | 0.00745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_531_0_line_49 |  | 47 | 48 | 0.0521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_531_0_line_50 |  | 48 | 52 | 0.023358 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_531_0_line_51 |  | 48 | 49 | 0.038585 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_531_0_line_52 |  | 49 | 50 | 0.0072749 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
53 | MV_531_0_line_53 |  | 49 | 51 | 0.066159 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
54 | MV_531_0_line_54 |  | 50 | 84 | 0.031519 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
55 | MV_531_0_line_55 |  | 51 | 53 | 0.00025509 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
56 | MV_531_0_line_56 |  | 52 | 54 | 0.027652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_531_0_line_57 |  | 54 | 112 | 0.014608 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_531_0_line_58 |  | 55 | 56 | 0.004727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_531_0_line_59 |  | 56 | 57 | 0.020378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_531_0_line_60 |  | 57 | 58 | 0.025185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_531_0_line_61 |  | 57 | 59 | 0.019943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_531_0_line_62 |  | 59 | 60 | 0.017373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_531_0_line_63 |  | 60 | 73 | 0.025902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_531_0_line_64 |  | 60 | 70 | 0.043231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_531_0_line_65 |  | 61 | 62 | 0.071846 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_531_0_line_66 |  | 62 | 63 | 0.21057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_531_0_line_67 |  | 63 | 64 | 0.23888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_531_0_line_68 |  | 63 | 65 | 0.028687 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_531_0_line_69 |  | 64 | 66 | 0.024997 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_531_0_line_70 |  | 66 | 67 | 0.021716 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_531_0_line_71 |  | 67 | 90 | 0.026576 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_531_0_line_72 |  | 68 | 69 | 0.020869 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_531_0_line_73 |  | 68 | 70 | 0.056089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_531_0_line_74 |  | 69 | 71 | 0.02286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_531_0_line_75 |  | 71 | 72 | 0.044978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_531_0_line_76 |  | 73 | 74 | 0.015086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_531_0_line_77 |  | 74 | 75 | 0.015921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_531_0_line_78 |  | 75 | 101 | 0.030929 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_531_0_line_79 |  | 76 | 77 | 0.036893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_531_0_line_80 |  | 77 | 78 | 0.026873 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_531_0_line_81 |  | 78 | 79 | 0.13754 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
82 | MV_531_0_line_82 |  | 78 | 80 | 0.005992 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
83 | MV_531_0_line_83 |  | 79 | 81 | 0.001994 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
84 | MV_531_0_line_84 |  | 80 | 82 | 0.005593 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_531_0_line_85 |  | 81 | 83 | 0.006775 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
86 | MV_531_0_line_86 |  | 82 | 118 | 0.11264 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_531_0_line_87 |  | 83 | 123 | 0.004186 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_531_0_line_88 |  | 84 | 85 | 0.016471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_531_0_line_89 |  | 84 | 86 | 0.045889 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
90 | MV_531_0_line_90 |  | 85 | 87 | 0.017286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_531_0_line_91 |  | 85 | 88 | 0.034852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_531_0_line_92 |  | 86 | 89 | 0.0071221 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
93 | MV_531_0_line_93 |  | 87 | 90 | 0.024737 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_531_0_line_94 |  | 88 | 91 | 0.03266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_531_0_line_95 |  | 89 | 92 | 0.01261 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
96 | MV_531_0_line_96 |  | 92 | 122 | 0.022119 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
97 | MV_531_0_line_97 |  | 92 | 121 | 0.025104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_531_0_line_98 |  | 93 | 94 | 0.026027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_531_0_line_99 |  | 94 | 95 | 0.022645 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_531_0_line_100 |  | 94 | 96 | 0.01464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_531_0_line_101 |  | 95 | 97 | 0.02901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_531_0_line_102 |  | 96 | 100 | 0.040174 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_531_0_line_103 |  | 96 | 101 | 0.015318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_531_0_line_104 |  | 96 | 98 | 0.030897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_531_0_line_105 |  | 98 | 99 | 0.028237 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_531_0_line_106 |  | 99 | 102 | 0.039513 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_531_0_line_107 |  | 102 | 118 | 0.16589 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_531_0_line_108 |  | 102 | 117 | 0.16152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_531_0_line_109 |  | 103 | 104 | 0.004958 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_531_0_line_110 |  | 103 | 105 | 0.043276 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_531_0_line_111 |  | 105 | 106 | 0.017648 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_531_0_line_112 |  | 106 | 107 | 0.032032 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_531_0_line_113 |  | 107 | 108 | 0.011621 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
114 | MV_531_0_line_114 |  | 107 | 109 | 0.066851 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
115 | MV_531_0_line_115 |  | 109 | 110 | 0.080866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_531_0_line_116 |  | 110 | 111 | 0.011417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_531_0_line_117 |  | 113 | 114 | 0.049238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_531_0_line_118 |  | 114 | 115 | 0.016743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_531_0_line_119 |  | 116 | 117 | 0.024471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_531_0_line_120 |  | 118 | 119 | 0.027677 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_531_0_line_121 |  | 120 | 121 | 0.037421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_531_0_line_122 |  | 122 | 123 | 0.018329 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_531_0_trafo_73 | 25 MVA 110/20 kV | 124 | 109 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2682960.0564 | 1247711.7169
1 | 2682961.8445 | 1247709.1623
2 | 2682915.6103 | 1247720.5685
3 | 2683007.9458 | 1247681.3869
4 | 2682909.5924 | 1247711.2442
5 | 2683014.3829 | 1247680.721
6 | 2682904.6354 | 1247720.5706
7 | 2682880.3315 | 1247666.02
8 | 2682891.5793 | 1247728.4272
9 | 2682934.8262 | 1247764.9278
10 | 2682869.7618 | 1247649.684
11 | 2682562.2789 | 1247619.7203
12 | 2682576.3729 | 1247605.1338
13 | 2682543.2351 | 1247635.2898
14 | 2682518.9756 | 1247601.5816
15 | 2682589.1914 | 1247633.2717
16 | 2682534.3425 | 1247640.8205
17 | 2682529.5535 | 1247643.3658
18 | 2682485.8785 | 1247627.2071
19 | 2682434.5761 | 1247590.3
20 | 2682899.9276 | 1247815.7527
21 | 2682874.9711 | 1247831.4932
22 | 2682762.2731 | 1247874.6622
23 | 2682726.6717 | 1247840.1758
24 | 2682723.4346 | 1247946.6845
25 | 2682710.9566 | 1247934.8239
26 | 2682864.3224 | 1248002.0923
27 | 2682760.9508 | 1248000.2415
28 | 2682828.7909 | 1247954.9398
29 | 2682643.423 | 1247879.7863
30 | 2682641.0633 | 1247882.1774
31 | 2682640.5344 | 1247876.7772
32 | 2682681.3757 | 1247919.3657
33 | 2682631.4539 | 1247891.9122
34 | 2682638.3424 | 1247873.0995
35 | 2682703.0769 | 1247941.9971
36 | 2682603.2554 | 1247920.4788
37 | 2682584.5831 | 1247799.1739
38 | 2682671.0879 | 1248069.3893
39 | 2682616.4158 | 1248044.3089
40 | 2682675.8615 | 1248075.7665
41 | 2682726.3567 | 1247920.7042
42 | 2682636.7532 | 1248026.1166
43 | 2682644.0427 | 1247963.6118
44 | 2682582.2295 | 1247941.4172
45 | 2682593.5342 | 1247713.5023
46 | 2682396.9256 | 1247571.0738
47 | 2682398.4922 | 1247563.7902
48 | 2682414.1638 | 1247536.7547
49 | 2682434.1186 | 1247503.73
50 | 2682433.4867 | 1247496.4826
51 | 2682451.1156 | 1247567.6688
52 | 2682391.7202 | 1247530.2848
53 | 2682450.9651 | 1247567.8748
54 | 2682365.1654 | 1247522.5747
55 | 2682863.302 | 1247639.7001
56 | 2682859.4862 | 1247642.5044
57 | 2682856.796 | 1247656.6327
58 | 2682870.5336 | 1247677.7412
59 | 2682850.0509 | 1247639.6237
60 | 2682840.8339 | 1247624.8975
61 | 2682612.6777 | 1247293.5574
62 | 2682581.842 | 1247229.973
63 | 2682464.8633 | 1247319.5555
64 | 2682402.2966 | 1247380.8976
65 | 2682475.225 | 1247346.3063
66 | 2682395.9054 | 1247405.0549
67 | 2682390.7901 | 1247426.1599
68 | 2682776.4338 | 1247672.5481
69 | 2682758.371 | 1247683
70 | 2682804.5793 | 1247648.5864
71 | 2682749.7436 | 1247697.179
72 | 2682774.6351 | 1247734.6417
73 | 2682827.9899 | 1247607.4979
74 | 2682819.7875 | 1247594.837
75 | 2682811.3018 | 1247581.366
76 | 2682658.6255 | 1247536.8389
77 | 2682647.0021 | 1247501.8248
78 | 2682640.5207 | 1247481.8198
79 | 2682532.3004 | 1247525.3003
80 | 2682646.1618 | 1247479.7525
81 | 2682530.4033 | 1247525.9299
82 | 2682648.227 | 1247484.9517
83 | 2682528.3101 | 1247519.4849
84 | 2682443.2022 | 1247466.4956
85 | 2682427.4544 | 1247461.5175
86 | 2682486.9562 | 1247480.3298
87 | 2682410.704 | 1247457.2458
88 | 2682419.566 | 1247437.8016
89 | 2682493.747 | 1247482.4769
90 | 2682386.7342 | 1247451.133
91 | 2682450.8704 | 1247447.069
92 | 2682505.6839 | 1247486.646
93 | 2682756.2422 | 1247544.6155
94 | 2682778.056 | 1247530.4181
95 | 2682766.4155 | 1247510.9969
96 | 2682786.653 | 1247542.2357
97 | 2682738.4411 | 1247518.6795
98 | 2682788.3673 | 1247520.0878
99 | 2682776.8663 | 1247494.3287
100 | 2682752.7622 | 1247563.8088
101 | 2682794.817 | 1247555.1962
102 | 2682783.5145 | 1247459.7757
103 | 2682525.9962 | 1247714.1375
104 | 2682522.3682 | 1247717.5168
105 | 2682558.1692 | 1247685.2566
106 | 2682572.4623 | 1247674.9052
107 | 2682598.4052 | 1247656.1168
108 | 2682594.4269 | 1247645.198
109 | 2682620.5275 | 1247694.6755
110 | 2682669.1287 | 1247746.3909
111 | 2682659.636 | 1247752.7743
112 | 2682363.7662 | 1247508.0335
113 | 2682562.2479 | 1247961.3156
114 | 2682598.3277 | 1247994.3979
115 | 2682609.7967 | 1248006.5949
116 | 2682737.3655 | 1247381.3375
117 | 2682732.8182 | 1247357.2929
118 | 2682712.9728 | 1247452.1414
119 | 2682712.8849 | 1247424.6699
120 | 2682509.0855 | 1247434.5285
121 | 2682520.2659 | 1247470.1034
122 | 2682517.4117 | 1247503.9493
123 | 2682524.3624 | 1247520.9088
124 | 2682620.5275 | 1247694.6755

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99572 | -0.023811 | 0.39189 | 0.1898
1 | 0.99572 | -0.023801 | 0 | 0
2 | 0.99576 | -0.024162 | 0 | 0
3 | 0.9957 | -0.023616 | 0 | 0
4 | 0.99577 | -0.024247 | 0 | 0
5 | 0.9957 | -0.023596 | 0.25479 | 0.1234
6 | 0.99576 | -0.024214 | 0 | 0
7 | 0.99583 | -0.024778 | 0.075809 | 0.036716
8 | 0.99576 | -0.024192 | 0.12153 | 0.058861
9 | 0.99576 | -0.024165 | 0.078556 | 0.038046
10 | 0.99585 | -0.024986 | 0.071382 | 0.034572
11 | 0.9995 | -0.0083301 | 0.35335 | 0.17114
12 | 0.99963 | -0.0014778 | 0.071928 | 0.034837
13 | 0.99948 | -0.0084945 | 0.15515 | 0.075142
14 | 0.99925 | -0.022601 | 0.19487 | 0.094378
15 | 0.99972 | -0.0011171 | 0 | 0
16 | 0.99947 | -0.0084452 | 0.32632 | 0.15804
17 | 0.99947 | -0.0084408 | 0.068179 | 0.033021
18 | 0.99914 | -0.023036 | 0 | 0
19 | 0.99898 | -0.023686 | 0 | 0
20 | 0.99867 | -0.01547 | 0.32114 | 0.15554
21 | 0.99869 | -0.015588 | 0 | 0
22 | 0.99876 | -0.01624 | 0 | 0
23 | 0.99875 | -0.016193 | 0.081616 | 0.039528
24 | 0.99881 | -0.016698 | 0 | 0
25 | 0.99885 | -0.016985 | 0 | 0
26 | 0.99855 | -0.014271 | 0 | 0
27 | 0.99879 | -0.016485 | 0.27535 | 0.13336
28 | 0.99849 | -0.013752 | 0.73547 | 0.3562
29 | 0.99949 | -0.016795 | 0.2573 | 0.12462
30 | 0.99948 | -0.016761 | 0 | 0
31 | 0.9995 | -0.01668 | 0 | 0
32 | 0.9991 | -0.01931 | 0.078686 | 0.038109
33 | 0.99947 | -0.01662 | 0.06858 | 0.033215
34 | 0.9995 | -0.016655 | 0 | 0
35 | 0.99896 | -0.018012 | 0 | 0
36 | 0.99942 | -0.01624 | 0 | 0
37 | 0.99966 | -0.01605 | 0.080616 | 0.039044
38 | 0.99926 | -0.015237 | 0 | 0
39 | 0.99929 | -0.015491 | 0 | 0
40 | 0.99926 | -0.015212 | 0.2653 | 0.12849
41 | 0.99879 | -0.016447 | 2.1492 | 1.0409
42 | 0.9993 | -0.015574 | 0.23855 | 0.11553
43 | 0.99941 | -0.016324 | 0.11589 | 0.056128
44 | 0.9994 | -0.015999 | 0.12325 | 0.059693
45 | 0.99995 | -0.00020832 | 0.14534 | 0.070391
46 | 0.9985 | -0.043418 | 0.21318 | 0.10325
47 | 0.9985 | -0.043437 | 0 | 0
48 | 0.99851 | -0.043567 | 0 | 0
49 | 0.99856 | -0.043247 | 0.37235 | 0.18034
50 | 0.99855 | -0.043312 | 0 | 0
51 | 0.99891 | -0.023973 | 0 | 0
52 | 0.9985 | -0.043442 | 0.10836 | 0.052479
53 | 0.99891 | -0.02397 | 0.14464 | 0.070051
54 | 0.99849 | -0.043329 | 0 | 0
55 | 0.99586 | -0.025123 | 0.41041 | 0.19877
56 | 0.99587 | -0.025201 | 0 | 0
57 | 0.99591 | -0.025537 | 0 | 0
58 | 0.9959 | -0.025478 | 0.19693 | 0.095375
59 | 0.99595 | -0.025911 | 0.19059 | 0.092306
60 | 0.99599 | -0.026277 | 0 | 0
61 | 0.99806 | -0.039982 | 0.39641 | 0.19199
62 | 0.9981 | -0.04032 | 0 | 0
63 | 0.9982 | -0.041266 | 0 | 0
64 | 0.99834 | -0.042445 | 0 | 0
65 | 0.9982 | -0.041242 | 0.069617 | 0.033717
66 | 0.99836 | -0.042564 | 0.27038 | 0.13095
67 | 0.99838 | -0.042737 | 0 | 0
68 | 0.99593 | -0.025766 | 0.19978 | 0.096759
69 | 0.99593 | -0.02575 | 0 | 0
70 | 0.99595 | -0.025941 | 0.39089 | 0.18932
71 | 0.99593 | -0.025732 | 0 | 0
72 | 0.99592 | -0.025694 | 0.073622 | 0.035657
73 | 0.99607 | -0.027021 | 0.19046 | 0.092243
74 | 0.99612 | -0.027488 | 0 | 0
75 | 0.99617 | -0.027981 | 0.088049 | 0.042644
76 | 0.99809 | -0.045031 | 0.12573 | 0.060896
77 | 0.99809 | -0.045086 | 0 | 0
78 | 0.9981 | -0.045125 | 0 | 0
79 | 0.99829 | -0.044353 | 0 | 0
80 | 0.99808 | -0.045269 | 0.41306 | 0.20006
81 | 0.99829 | -0.044342 | 0.27756 | 0.13443
82 | 0.99806 | -0.04503 | 0 | 0
83 | 0.9983 | -0.044302 | 0 | 0
84 | 0.99848 | -0.043591 | 0 | 0
85 | 0.99845 | -0.043306 | 0 | 0
86 | 0.9984 | -0.043901 | 0.11741 | 0.056866
87 | 0.99843 | -0.043141 | 0.14017 | 0.067888
88 | 0.99842 | -0.043034 | 0 | 0
89 | 0.99839 | -0.043948 | 0 | 0
90 | 0.9984 | -0.042947 | 0 | 0
91 | 0.99839 | -0.042777 | 0.65698 | 0.31819
92 | 0.99837 | -0.044031 | 0 | 0
93 | 0.99633 | -0.029392 | 0.075511 | 0.036571
94 | 0.99633 | -0.029415 | 0 | 0
95 | 0.99632 | -0.029342 | 0 | 0
96 | 0.99634 | -0.029474 | 0 | 0
97 | 0.99631 | -0.029247 | 0.27293 | 0.13218
98 | 0.99647 | -0.030642 | 0 | 0
99 | 0.99658 | -0.031707 | 0.21232 | 0.10283
100 | 0.99633 | -0.029437 | 0.078631 | 0.038083
101 | 0.99628 | -0.028971 | 0.077436 | 0.037504
102 | 0.99676 | -0.033296 | 0 | 0
103 | 0.99975 | -0.000432 | 0.083232 | 0.040311
104 | 0.99975 | -0.00041975 | 0.20684 | 0.10018
105 | 0.99976 | -0.00058051 | 0.078314 | 0.037929
106 | 0.99977 | -0.0006568 | 0.088262 | 0.042747
107 | 0.99979 | -0.00082788 | 0 | 0
108 | 0.99976 | -0.00096483 | 0.077168 | 0.037374
109 | 1 | 0 | -14.7293 | -7.0115
110 | 0.99999 | 0.00012718 | 0 | 0
111 | 0.99998 | 0.00014594 | 0.13805 | 0.066861
112 | 0.99848 | -0.04339 | 0.34332 | 0.16628
113 | 0.99938 | -0.01581 | 0 | 0
114 | 0.99934 | -0.015477 | 0 | 0
115 | 0.99933 | -0.015363 | 0.081187 | 0.03932
116 | 0.99672 | -0.03298 | 0.15309 | 0.074143
117 | 0.99672 | -0.033024 | 0 | 0
118 | 0.99752 | -0.040195 | 0 | 0
119 | 0.99751 | -0.04015 | 0.13659 | 0.066152
120 | 0.99834 | -0.043766 | 0.35666 | 0.17274
121 | 0.99836 | -0.043925 | 0 | 0
122 | 0.99833 | -0.044166 | 0.084483 | 0.040917
123 | 0.99831 | -0.044276 | 0 | 0
124 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.2548 | 0.12172 | -0.2548 | -0.1218 | 2.7879e-07 | -7.368e-05 | 0.0081867 | 0.0081877 | 0.0081877 | 0.99572 | -0.023811 | 0.99572 | -0.023801 | 3.7217
1 | -0.64669 | -0.31152 | 0.64672 | 0.31044 | 2.6525e-05 | -0.0010789 | 0.020811 | 0.020797 | 0.020811 | 0.99572 | -0.023811 | 0.99576 | -0.024162 | 9.4593
2 | 0.2548 | 0.1218 | -0.2548 | -0.12325 | 5.5146e-06 | -0.0014538 | 0.0081877 | 0.0082059 | 0.0082059 | 0.99572 | -0.023801 | 0.9957 | -0.023616 | 3.73
3 | -0.64672 | -0.31044 | 0.64672 | 0.31018 | 6.4068e-06 | -0.00026083 | 0.020797 | 0.020794 | 0.020797 | 0.99576 | -0.024162 | 0.99577 | -0.024247 | 9.4531
4 | 0.2548 | 0.12325 | -0.25479 | -0.1234 | 5.8024e-07 | -0.00015258 | 0.0082059 | 0.0082079 | 0.0082079 | 0.9957 | -0.023616 | 0.9957 | -0.023596 | 3.7308
5 | 0.20009 | 0.094936 | -0.20009 | -0.095277 | 7.9483e-07 | -0.00034147 | 0.0064205 | 0.0064247 | 0.0064247 | 0.99577 | -0.024247 | 0.99576 | -0.024214 | 2.9203
6 | -0.84681 | -0.40512 | 0.84687 | 0.40386 | 5.3225e-05 | -0.0012595 | 0.027214 | 0.027198 | 0.027214 | 0.99577 | -0.024247 | 0.99583 | -0.024778 | 12.37
7 | 0.12153 | 0.058501 | -0.12153 | -0.058861 | 3.1075e-07 | -0.0003599 | 0.0039102 | 0.0039148 | 0.0039148 | 0.99576 | -0.024214 | 0.99576 | -0.024192 | 1.7794
8 | 0.078557 | 0.036776 | -0.078556 | -0.038046 | 4.558e-07 | -0.0012702 | 0.0025146 | 0.0025304 | 0.0025304 | 0.99576 | -0.024214 | 0.99576 | -0.024165 | 1.1502
9 | -0.92268 | -0.44058 | 0.9227 | 0.44012 | 2.2815e-05 | -0.00045393 | 0.02964 | 0.029634 | 0.02964 | 0.99583 | -0.024778 | 0.99585 | -0.024986 | 13.4726
10 | -0.99408 | -0.47469 | 0.9941 | 0.47442 | 1.6186e-05 | -0.00027677 | 0.031933 | 0.03193 | 0.031933 | 0.99585 | -0.024986 | 0.99586 | -0.025123 | 14.5151
11 | -8.9453 | -4.2524 | 8.9459 | 4.254 | 0.00059256 | 0.0015654 | 0.28606 | 0.28606 | 0.28606 | 0.9995 | -0.0083301 | 0.99963 | -0.0014778 | 44.351
12 | 0.54967 | 0.26581 | -0.54965 | -0.26583 | 1.3629e-05 | -2.0799e-05 | 0.017634 | 0.017635 | 0.017635 | 0.9995 | -0.0083301 | 0.99948 | -0.0084945 | 8.3974
13 | 8.0423 | 3.8154 | -8.0412 | -3.8125 | 0.0011078 | 0.0029142 | 0.25709 | 0.25709 | 0.25709 | 0.9995 | -0.0083301 | 0.99925 | -0.022601 | 39.8592
14 | -9.0179 | -4.2888 | 9.0187 | 4.2873 | 0.00079445 | -0.0014941 | 0.28837 | 0.28835 | 0.28837 | 0.99963 | -0.0014778 | 0.99972 | -0.0011171 | 45.1993
15 | 0.3945 | 0.19069 | -0.3945 | -0.19094 | 2.2397e-06 | -0.00024911 | 0.012655 | 0.012659 | 0.012659 | 0.99948 | -0.0084945 | 0.99947 | -0.0084452 | 5.7539
16 | 7.8463 | 3.7182 | -7.8455 | -3.7203 | 0.00081842 | -0.0021795 | 0.25084 | 0.25087 | 0.25087 | 0.99925 | -0.022601 | 0.99914 | -0.023036 | 39.3213
17 | -9.0187 | -4.2873 | 9.019 | 4.2867 | 0.00033477 | -0.00062981 | 0.28835 | 0.28834 | 0.28835 | 0.99972 | -0.0011171 | 0.99976 | -0.00096483 | 45.1955
18 | 0.068179 | 0.032891 | -0.068179 | -0.033021 | 3.4669e-08 | -0.00012944 | 0.0021864 | 0.002188 | 0.002188 | 0.99947 | -0.0084452 | 0.99947 | -0.0084408 | 0.99455
19 | 7.8455 | 3.7203 | -7.8443 | -3.7236 | 0.0012293 | -0.0032712 | 0.25087 | 0.25092 | 0.25092 | 0.99914 | -0.023036 | 0.99898 | -0.023686 | 39.329
20 | 7.8443 | 3.7236 | -7.8438 | -3.725 | 0.00054042 | -0.0014372 | 0.25092 | 0.25094 | 0.25094 | 0.99898 | -0.023686 | 0.99891 | -0.02397 | 39.3324
21 | -0.32114 | -0.15554 | 0.32115 | 0.1548 | 4.3782e-06 | -0.00073346 | 0.010314 | 0.010305 | 0.010314 | 0.99867 | -0.01547 | 0.99869 | -0.015588 | 4.6883
22 | -0.32115 | -0.1548 | 0.32117 | 0.15058 | 2.5044e-05 | -0.0042213 | 0.010305 | 0.010253 | 0.010305 | 0.99869 | -0.015588 | 0.99876 | -0.01624 | 4.6841
23 | 0.081616 | 0.038348 | -0.081616 | -0.039528 | 4.5205e-07 | -0.0011804 | 0.0026064 | 0.0026211 | 0.0026211 | 0.99876 | -0.01624 | 0.99875 | -0.016193 | 1.1914
24 | -0.40279 | -0.18893 | 0.40281 | 0.18643 | 2.3132e-05 | -0.002495 | 0.012859 | 0.012828 | 0.012859 | 0.99876 | -0.01624 | 0.99881 | -0.016698 | 5.845
25 | -1.4139 | -0.66632 | 1.4139 | 0.66591 | 4.9595e-05 | -0.00041897 | 0.045175 | 0.045169 | 0.045175 | 0.99881 | -0.016698 | 0.99885 | -0.016985 | 20.5339
26 | 0.73572 | 0.34809 | -0.73551 | -0.35481 | 0.00021129 | -0.0067241 | 0.023524 | 0.023608 | 0.023608 | 0.99881 | -0.016698 | 0.99855 | -0.014271 | 10.731
27 | 0.27536 | 0.1318 | -0.27535 | -0.13336 | 6.8144e-06 | -0.0015563 | 0.0088231 | 0.0088426 | 0.0088426 | 0.99881 | -0.016698 | 0.99879 | -0.016485 | 4.0194
28 | 2.1493 | 1.0404 | -2.1492 | -1.0409 | 0.00013286 | -0.00045826 | 0.069013 | 0.069019 | 0.069019 | 0.99885 | -0.016985 | 0.99879 | -0.016447 | 31.3723
29 | -3.5633 | -1.7063 | 3.5637 | 1.7059 | 0.00043105 | -0.00046221 | 0.11418 | 0.11417 | 0.11418 | 0.99885 | -0.016985 | 0.99896 | -0.018012 | 51.9002
30 | 0.73551 | 0.35481 | -0.73547 | -0.3562 | 4.3963e-05 | -0.0013925 | 0.023608 | 0.023626 | 0.023626 | 0.99855 | -0.014271 | 0.99849 | -0.013752 | 10.739
31 | 0.8929 | 0.42521 | -0.8929 | -0.42529 | 3.6545e-06 | -7.8938e-05 | 0.028564 | 0.028565 | 0.028565 | 0.99949 | -0.016795 | 0.99948 | -0.016761 | 12.9841
32 | -4.7945 | -2.294 | 4.7945 | 2.2939 | 4.7406e-05 | -0.00010829 | 0.15351 | 0.15351 | 0.15351 | 0.99949 | -0.016795 | 0.9995 | -0.01668 | 42.4061
33 | 3.6443 | 1.7442 | -3.6429 | -1.7434 | 0.0013303 | 0.00076791 | 0.11669 | 0.11669 | 0.11669 | 0.99949 | -0.016795 | 0.9991 | -0.01931 | 55.5666
34 | 0.8929 | 0.42529 | -0.89289 | -0.42561 | 1.4903e-05 | -0.00032183 | 0.028565 | 0.028569 | 0.028569 | 0.99948 | -0.016761 | 0.99947 | -0.01662 | 12.986
35 | -4.7945 | -2.2939 | 4.7945 | 2.2936 | 3.115e-05 | -0.00025099 | 0.15351 | 0.15351 | 0.15351 | 0.9995 | -0.01668 | 0.9995 | -0.016655 | 24.0609
36 | 3.5642 | 1.7053 | -3.5637 | -1.7059 | 0.0005456 | -0.00058533 | 0.11416 | 0.11417 | 0.11417 | 0.9991 | -0.01931 | 0.99896 | -0.018012 | 51.8968
37 | 0.82431 | 0.3924 | -0.82427 | -0.39334 | 3.7275e-05 | -0.00094626 | 0.026368 | 0.02638 | 0.02638 | 0.99947 | -0.01662 | 0.99942 | -0.01624 | 11.991
38 | -4.7945 | -2.2936 | 4.7953 | 2.2878 | 0.00072867 | -0.0058756 | 0.15351 | 0.15343 | 0.15351 | 0.9995 | -0.016655 | 0.99966 | -0.01605 | 24.0604
39 | 0.70838 | 0.33728 | -0.70836 | -0.33799 | 2.0352e-05 | -0.00070161 | 0.022662 | 0.022671 | 0.022671 | 0.99942 | -0.01624 | 0.9994 | -0.015999 | 10.3048
40 | 0.11589 | 0.056059 | -0.11589 | -0.056128 | 1.4628e-06 | -6.987e-05 | 0.0037185 | 0.0037194 | 0.0037194 | 0.99942 | -0.01624 | 0.99941 | -0.016324 | 1.7711
41 | -4.8759 | -2.3268 | 4.8766 | 2.3287 | 0.00074848 | 0.0018937 | 0.15601 | 0.15601 | 0.15601 | 0.99966 | -0.01605 | 0.99995 | -0.00020832 | 24.1881
42 | -0.2653 | -0.1283 | 0.26531 | 0.12635 | 7.9001e-06 | -0.0019499 | 0.0085134 | 0.008489 | 0.0085134 | 0.99926 | -0.015237 | 0.99929 | -0.015491 | 3.8697
43 | 0.2653 | 0.1283 | -0.2653 | -0.12849 | 7.7118e-07 | -0.00018973 | 0.0085134 | 0.0085158 | 0.0085158 | 0.99926 | -0.015237 | 0.99926 | -0.015212 | 3.8708
44 | -0.26531 | -0.12635 | 0.26531 | 0.1257 | 2.6227e-06 | -0.00064981 | 0.008489 | 0.0084809 | 0.008489 | 0.99929 | -0.015491 | 0.9993 | -0.015574 | 3.8586
45 | -0.50386 | -0.24124 | 0.50387 | 0.24121 | 1.5443e-05 | -3.0006e-05 | 0.016138 | 0.016137 | 0.016138 | 0.9993 | -0.015574 | 0.99933 | -0.015363 | 7.6846
46 | 0.58511 | 0.27829 | -0.58509 | -0.27896 | 1.3192e-05 | -0.00066856 | 0.018715 | 0.018723 | 0.018723 | 0.9994 | -0.015999 | 0.99938 | -0.01581 | 8.5106
47 | -5.022 | -2.3991 | 5.0222 | 2.3972 | 0.00026198 | -0.0019162 | 0.16067 | 0.16065 | 0.16067 | 0.99995 | -0.00020832 | 1 | 0 | 25.184
48 | -0.21318 | -0.10325 | 0.21318 | 0.10307 | 4.6627e-07 | -0.0001772 | 0.0068481 | 0.0068458 | 0.0068481 | 0.9985 | -0.043418 | 0.9985 | -0.043437 | 3.1128
49 | -0.21318 | -0.10307 | 0.21318 | 0.10183 | 3.2522e-06 | -0.0012393 | 0.0068458 | 0.0068303 | 0.0068458 | 0.9985 | -0.043437 | 0.99851 | -0.043567 | 3.1117
50 | 0.45169 | 0.21753 | -0.45169 | -0.21809 | 6.554e-06 | -0.00055408 | 0.014494 | 0.014501 | 0.014501 | 0.99851 | -0.043567 | 0.9985 | -0.043442 | 6.5914
51 | -0.66488 | -0.31936 | 0.66491 | 0.31934 | 3.1261e-05 | -2.6348e-05 | 0.021324 | 0.021324 | 0.021324 | 0.99851 | -0.043567 | 0.99856 | -0.043247 | 10.1545
52 | 6.6604 | 3.1516 | -6.6603 | -3.152 | 0.000102 | -0.00039834 | 0.21301 | 0.21302 | 0.21302 | 0.99856 | -0.043247 | 0.99855 | -0.043312 | 33.3887
53 | -7.6977 | -3.6512 | 7.6991 | 3.655 | 0.0014328 | 0.0037616 | 0.2463 | 0.2463 | 0.2463 | 0.99856 | -0.043247 | 0.99891 | -0.023973 | 38.1857
54 | 6.6603 | 3.152 | -6.6599 | -3.1537 | 0.000442 | -0.0017256 | 0.21302 | 0.21304 | 0.21304 | 0.99855 | -0.043312 | 0.99848 | -0.043591 | 33.3925
55 | -7.6991 | -3.655 | 7.6991 | 3.655 | 4.7804e-06 | -1.3299e-05 | 0.2463 | 0.2463 | 0.2463 | 0.99891 | -0.023973 | 0.99891 | -0.02397 | 38.6045
56 | 0.34333 | 0.16561 | -0.34333 | -0.16626 | 4.4867e-06 | -0.00065689 | 0.01102 | 0.011029 | 0.011029 | 0.9985 | -0.043442 | 0.99849 | -0.043329 | 5.013
57 | 0.34333 | 0.16626 | -0.34332 | -0.16628 | 3.1659e-06 | -1.5404e-05 | 0.011029 | 0.011029 | 0.011029 | 0.99849 | -0.043329 | 0.99848 | -0.04339 | 5.2519
58 | -1.4045 | -0.67319 | 1.4045 | 0.67308 | 1.2863e-05 | -0.00010812 | 0.045148 | 0.045147 | 0.045148 | 0.99586 | -0.025123 | 0.99587 | -0.025201 | 20.5219
59 | -1.4045 | -0.67308 | 1.4046 | 0.67262 | 5.5441e-05 | -0.0004661 | 0.045147 | 0.045141 | 0.045147 | 0.99587 | -0.025201 | 0.99591 | -0.025537 | 20.5213
60 | 0.19693 | 0.094779 | -0.19693 | -0.095375 | 1.3509e-06 | -0.00059601 | 0.0063349 | 0.0063424 | 0.0063424 | 0.99591 | -0.025537 | 0.9959 | -0.025478 | 2.8829
61 | -1.6015 | -0.76739 | 1.6016 | 0.76694 | 7.0537e-05 | -0.00045136 | 0.051476 | 0.05147 | 0.051476 | 0.99591 | -0.025537 | 0.99595 | -0.025911 | 23.398
62 | -1.7922 | -0.85925 | 1.7922 | 0.85886 | 7.6961e-05 | -0.00038863 | 0.057608 | 0.057602 | 0.057608 | 0.99595 | -0.025911 | 0.99599 | -0.026277 | 26.1853
63 | -2.4566 | -1.1762 | 2.4568 | 1.1756 | 0.00021546 | -0.00054962 | 0.078941 | 0.078933 | 0.078941 | 0.99599 | -0.026277 | 0.99607 | -0.027021 | 35.8821
64 | 0.66433 | 0.31729 | -0.6643 | -0.31831 | 2.6294e-05 | -0.0010161 | 0.021338 | 0.021351 | 0.021351 | 0.99599 | -0.026277 | 0.99595 | -0.025941 | 9.705
65 | -0.39641 | -0.19199 | 0.39643 | 0.19029 | 1.5541e-05 | -0.0017042 | 0.01274 | 0.012718 | 0.01274 | 0.99806 | -0.039982 | 0.9981 | -0.04032 | 5.7908
66 | -0.39643 | -0.19029 | 0.39648 | 0.18529 | 4.5248e-05 | -0.0049956 | 0.012718 | 0.012656 | 0.012718 | 0.9981 | -0.04032 | 0.9982 | -0.041266 | 5.781
67 | -0.46609 | -0.21833 | 0.46616 | 0.21266 | 7.0325e-05 | -0.0056629 | 0.014885 | 0.014816 | 0.014885 | 0.9982 | -0.041266 | 0.99834 | -0.042445 | 6.7658
68 | 0.069617 | 0.033035 | -0.069617 | -0.033717 | 1.9091e-07 | -0.00068242 | 0.0022285 | 0.002237 | 0.002237 | 0.9982 | -0.041266 | 0.9982 | -0.041242 | 1.0168
69 | -0.46616 | -0.21266 | 0.46617 | 0.21207 | 7.3215e-06 | -0.00059269 | 0.014816 | 0.014809 | 0.014816 | 0.99834 | -0.042445 | 0.99836 | -0.042564 | 6.7344
70 | -0.73655 | -0.34302 | 0.73657 | 0.34251 | 1.5997e-05 | -0.00051206 | 0.023494 | 0.023487 | 0.023494 | 0.99836 | -0.042564 | 0.99838 | -0.042737 | 10.679
71 | -0.73657 | -0.34251 | 0.73659 | 0.34188 | 1.9566e-05 | -0.00062668 | 0.023487 | 0.02348 | 0.023487 | 0.99838 | -0.042737 | 0.9984 | -0.042947 | 10.6761
72 | 0.073622 | 0.033556 | -0.073622 | -0.03405 | 1.5362e-07 | -0.00049419 | 0.0023452 | 0.0023512 | 0.0023512 | 0.99593 | -0.025766 | 0.99593 | -0.02575 | 1.0687
73 | -0.2734 | -0.13031 | 0.27341 | 0.12899 | 5.7599e-06 | -0.0013266 | 0.0087789 | 0.0087624 | 0.0087789 | 0.99593 | -0.025766 | 0.99595 | -0.025941 | 3.9904
74 | 0.073622 | 0.03405 | -0.073622 | -0.034592 | 1.6918e-07 | -0.00054133 | 0.0023512 | 0.0023578 | 0.0023578 | 0.99593 | -0.02575 | 0.99593 | -0.025732 | 1.0717
75 | 0.073622 | 0.034592 | -0.073622 | -0.035657 | 3.3568e-07 | -0.0010651 | 0.0023578 | 0.0023711 | 0.0023711 | 0.99593 | -0.025732 | 0.99592 | -0.025694 | 1.0778
76 | -2.6472 | -1.2678 | 2.6474 | 1.2675 | 0.00014573 | -0.00031415 | 0.085066 | 0.085061 | 0.085066 | 0.99607 | -0.027021 | 0.99612 | -0.027488 | 38.6663
77 | -2.6474 | -1.2675 | 2.6475 | 1.2672 | 0.00015378 | -0.00033159 | 0.085061 | 0.085057 | 0.085061 | 0.99612 | -0.027488 | 0.99617 | -0.027981 | 38.6643
78 | -2.7356 | -1.3098 | 2.7359 | 1.3092 | 0.00031893 | -0.0006383 | 0.087892 | 0.087883 | 0.087892 | 0.99617 | -0.027981 | 0.99628 | -0.028971 | 39.9508
79 | -0.12573 | -0.060896 | 0.12574 | 0.060019 | 8.0195e-07 | -0.00087726 | 0.0040407 | 0.0040297 | 0.0040407 | 0.99809 | -0.045031 | 0.99809 | -0.045086 | 1.8367
80 | -0.12574 | -0.060019 | 0.12574 | 0.05938 | 5.8142e-07 | -0.00063901 | 0.0040297 | 0.0040218 | 0.0040297 | 0.99809 | -0.045086 | 0.9981 | -0.045125 | 1.8317
81 | -4.2882 | -2.0403 | 4.289 | 2.0322 | 0.0008011 | -0.0081593 | 0.13735 | 0.13724 | 0.13735 | 0.9981 | -0.045125 | 0.99829 | -0.044353 | 21.5281
82 | 4.1625 | 1.981 | -4.1624 | -1.9811 | 5.1448e-05 | -0.00016739 | 0.13333 | 0.13333 | 0.13333 | 0.9981 | -0.045125 | 0.99808 | -0.045269 | 36.8315
83 | -4.289 | -2.0322 | 4.289 | 2.0321 | 1.1605e-05 | -0.00011832 | 0.13724 | 0.13724 | 0.13724 | 0.99829 | -0.044353 | 0.99829 | -0.044342 | 21.5113
84 | 3.7493 | 1.7811 | -3.7492 | -1.7812 | 0.00010762 | -0.0001011 | 0.12006 | 0.12006 | 0.12006 | 0.99808 | -0.045269 | 0.99806 | -0.04503 | 54.5715
85 | -4.5666 | -2.1665 | 4.5666 | 2.1661 | 4.472e-05 | -0.00039905 | 0.14616 | 0.14615 | 0.14616 | 0.99829 | -0.044342 | 0.9983 | -0.044302 | 22.9088
86 | 3.7492 | 1.7812 | -3.7471 | -1.7832 | 0.0021681 | -0.0020344 | 0.12006 | 0.12009 | 0.12009 | 0.99806 | -0.04503 | 0.99752 | -0.040195 | 54.5867
87 | -4.5666 | -2.1661 | 4.5666 | 2.1658 | 2.7629e-05 | -0.00024656 | 0.14615 | 0.14615 | 0.14615 | 0.9983 | -0.044302 | 0.99831 | -0.044276 | 22.908
88 | 1.5339 | 0.725 | -1.5338 | -0.72538 | 5.2909e-05 | -0.00037636 | 0.049051 | 0.049055 | 0.049055 | 0.99848 | -0.043591 | 0.99845 | -0.043306 | 22.2979
89 | 5.126 | 2.4287 | -5.1256 | -2.4314 | 0.00038143 | -0.0026595 | 0.16399 | 0.16403 | 0.16403 | 0.99848 | -0.043591 | 0.9984 | -0.043901 | 25.7099
90 | 0.87679 | 0.40878 | -0.87678 | -0.40919 | 1.8057e-05 | -0.00040609 | 0.02797 | 0.027975 | 0.027975 | 0.99845 | -0.043306 | 0.99843 | -0.043141 | 12.7159
91 | 0.65702 | 0.31659 | -0.657 | -0.31742 | 2.0698e-05 | -0.00082339 | 0.021086 | 0.021097 | 0.021097 | 0.99845 | -0.043306 | 0.99842 | -0.043034 | 9.5895
92 | 5.0082 | 2.3745 | -5.0082 | -2.3749 | 5.6522e-05 | -0.00041423 | 0.16026 | 0.16026 | 0.16026 | 0.9984 | -0.043901 | 0.99839 | -0.043948 | 25.1196
93 | 0.7366 | 0.3413 | -0.73659 | -0.34188 | 1.82e-05 | -0.00058335 | 0.023473 | 0.02348 | 0.02348 | 0.99843 | -0.043141 | 0.9984 | -0.042947 | 10.6726
94 | 0.657 | 0.31742 | -0.65698 | -0.31819 | 1.9415e-05 | -0.00077155 | 0.021097 | 0.021107 | 0.021107 | 0.99842 | -0.043034 | 0.99839 | -0.042777 | 9.5939
95 | 5.0082 | 2.3749 | -5.0081 | -2.3756 | 0.00010008 | -0.00073338 | 0.16026 | 0.16027 | 0.16027 | 0.99839 | -0.043948 | 0.99837 | -0.044031 | 25.1211
96 | 4.6514 | 2.2044 | -4.6512 | -2.2057 | 0.00015142 | -0.0012999 | 0.14883 | 0.14885 | 0.14885 | 0.99837 | -0.044031 | 0.99833 | -0.044166 | 23.3307
97 | 0.35667 | 0.17125 | -0.35666 | -0.17185 | 4.389e-06 | -0.00059612 | 0.01144 | 0.011448 | 0.011448 | 0.99837 | -0.044031 | 0.99836 | -0.043925 | 5.2035
98 | -0.075511 | -0.036571 | 0.075511 | 0.035955 | 2.0467e-07 | -0.00061681 | 0.0024309 | 0.0024232 | 0.0024309 | 0.99633 | -0.029392 | 0.99633 | -0.029415 | 1.105
99 | 0.27293 | 0.13096 | -0.27293 | -0.1315 | 2.3275e-06 | -0.00053601 | 0.0087711 | 0.0087779 | 0.0087779 | 0.99633 | -0.029415 | 0.99632 | -0.029342 | 3.9899
100 | -0.34844 | -0.16692 | 0.34845 | 0.16657 | 2.4482e-06 | -0.00034626 | 0.011194 | 0.01119 | 0.011194 | 0.99633 | -0.029415 | 0.99634 | -0.029474 | 5.0883
101 | 0.27293 | 0.1315 | -0.27293 | -0.13218 | 2.987e-06 | -0.00068667 | 0.0087779 | 0.0087865 | 0.0087865 | 0.99632 | -0.029342 | 0.99631 | -0.029247 | 3.9939
102 | 0.078631 | 0.037131 | -0.078631 | -0.038083 | 3.4205e-07 | -0.00095209 | 0.0025195 | 0.0025314 | 0.0025314 | 0.99634 | -0.029474 | 0.99633 | -0.029437 | 1.1506
103 | 2.8135 | 1.3464 | -2.8133 | -1.3467 | 0.00016701 | -0.00031349 | 0.090371 | 0.090376 | 0.090376 | 0.99634 | -0.029474 | 0.99628 | -0.028971 | 41.0798
104 | -3.2406 | -1.5501 | 3.241 | 1.5495 | 0.00044678 | -0.00059986 | 0.10408 | 0.10407 | 0.10408 | 0.99634 | -0.029474 | 0.99647 | -0.030642 | 47.3093
105 | -3.241 | -1.5495 | 3.2414 | 1.5489 | 0.00040825 | -0.00054842 | 0.10407 | 0.10406 | 0.10407 | 0.99647 | -0.030642 | 0.99658 | -0.031707 | 47.3051
106 | -3.4538 | -1.6518 | 3.4544 | 1.651 | 0.00064865 | -0.00074473 | 0.1109 | 0.11088 | 0.1109 | 0.99658 | -0.031707 | 0.99676 | -0.033296 | 50.4075
107 | -3.6075 | -1.7208 | 3.6105 | 1.7177 | 0.0029663 | -0.0030584 | 0.11576 | 0.11571 | 0.11576 | 0.99676 | -0.033296 | 0.99752 | -0.040195 | 52.6164
108 | 0.15309 | 0.069733 | -0.15309 | -0.073563 | 5.1674e-06 | -0.0038298 | 0.0048721 | 0.0049191 | 0.0049191 | 0.99676 | -0.033296 | 0.99672 | -0.033024 | 2.236
109 | 0.20684 | 0.10006 | -0.20684 | -0.10018 | 2.9144e-07 | -0.00011823 | 0.0066347 | 0.0066361 | 0.0066361 | 0.99975 | -0.000432 | 0.99975 | -0.00041975 | 3.0164
110 | -0.29007 | -0.14037 | 0.29008 | 0.13934 | 4.9953e-06 | -0.0010313 | 0.009305 | 0.009292 | 0.009305 | 0.99975 | -0.000432 | 0.99976 | -0.00058051 | 4.2295
111 | -0.36839 | -0.17727 | 0.3684 | 0.17685 | 3.2815e-06 | -0.00042019 | 0.011805 | 0.011799 | 0.011805 | 0.99976 | -0.00058051 | 0.99977 | -0.0006568 | 5.3657
112 | -0.45666 | -0.2196 | 0.45667 | 0.21883 | 9.1479e-06 | -0.00076175 | 0.014631 | 0.014621 | 0.014631 | 0.99977 | -0.0006568 | 0.99979 | -0.00082788 | 6.6504
113 | 9.0965 | 4.3235 | -9.0962 | -4.324 | 0.00030368 | -0.00055883 | 0.2908 | 0.29081 | 0.29081 | 0.99979 | -0.00082788 | 0.99976 | -0.00096483 | 45.582
114 | -9.5531 | -4.5423 | 9.5551 | 4.5392 | 0.0019266 | -0.0031146 | 0.30543 | 0.30537 | 0.30543 | 0.99979 | -0.00082788 | 1 | 0 | 47.8723
115 | 0.13805 | 0.064659 | -0.13805 | -0.066589 | 2.102e-06 | -0.0019301 | 0.0044007 | 0.0044246 | 0.0044246 | 1 | 0 | 0.99999 | 0.00012718 | 2.0112
116 | 0.13805 | 0.066589 | -0.13805 | -0.066861 | 2.9863e-07 | -0.0002725 | 0.0044246 | 0.0044281 | 0.0044281 | 0.99999 | 0.00012718 | 0.99998 | 0.00014594 | 2.0128
117 | 0.58509 | 0.27896 | -0.58507 | -0.28013 | 2.3061e-05 | -0.0011673 | 0.018723 | 0.018738 | 0.018738 | 0.99938 | -0.01581 | 0.99934 | -0.015477 | 8.5173
118 | 0.58507 | 0.28013 | -0.58506 | -0.28053 | 7.8502e-06 | -0.0003969 | 0.018738 | 0.018743 | 0.018743 | 0.99934 | -0.015477 | 0.99933 | -0.015363 | 8.5195
119 | -0.15309 | -0.074143 | 0.15309 | 0.073563 | 7.9167e-07 | -0.00058021 | 0.0049264 | 0.0049191 | 0.0049264 | 0.99672 | -0.03298 | 0.99672 | -0.033024 | 2.2393
120 | 0.13659 | 0.065495 | -0.13659 | -0.066152 | 7.1137e-07 | -0.00065733 | 0.0043837 | 0.004392 | 0.004392 | 0.99752 | -0.040195 | 0.99751 | -0.04015 | 1.9963
121 | -0.35666 | -0.17274 | 0.35666 | 0.17185 | 6.5531e-06 | -0.00088857 | 0.011459 | 0.011448 | 0.011459 | 0.99834 | -0.043766 | 0.99836 | -0.043925 | 5.2085
122 | 4.5668 | 2.1648 | -4.5666 | -2.1658 | 0.00012096 | -0.0010796 | 0.14614 | 0.14615 | 0.14615 | 0.99833 | -0.044166 | 0.99831 | -0.044276 | 22.9075

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 14.7293 | 7.0115

## res_load
| p_mw | q_mvar
0 | 0.39189 | 0.1898
1 | 0.25479 | 0.1234
2 | 0.075809 | 0.036716
3 | 0.12153 | 0.058861
4 | 0.078556 | 0.038046
5 | 0.071382 | 0.034572
6 | 0.35335 | 0.17114
7 | 0.071928 | 0.034837
8 | 0.15515 | 0.075142
9 | 0.19487 | 0.094378
10 | 0.32632 | 0.15804
11 | 0.068179 | 0.033021
12 | 0.32114 | 0.15554
13 | 0.081616 | 0.039528
14 | 0.27535 | 0.13336
15 | 0.73547 | 0.3562
16 | 0.2573 | 0.12462
17 | 0.078686 | 0.038109
18 | 0.06858 | 0.033215
19 | 0.080616 | 0.039044
20 | 0.2653 | 0.12849
21 | 2.1492 | 1.0409
22 | 0.23855 | 0.11553
23 | 0.11589 | 0.056128
24 | 0.12325 | 0.059693
25 | 0.14534 | 0.070391
26 | 0.21318 | 0.10325
27 | 0.37235 | 0.18034
28 | 0.10836 | 0.052479
29 | 0.14464 | 0.070051
30 | 0.41041 | 0.19877
31 | 0.19693 | 0.095375
32 | 0.19059 | 0.092306
33 | 0.39641 | 0.19199
34 | 0.069617 | 0.033717
35 | 0.27038 | 0.13095
36 | 0.19978 | 0.096759
37 | 0.39089 | 0.18932
38 | 0.073622 | 0.035657
39 | 0.19046 | 0.092243
40 | 0.088049 | 0.042644
41 | 0.12573 | 0.060896
42 | 0.41306 | 0.20006
43 | 0.27756 | 0.13443
44 | 0.11741 | 0.056866
45 | 0.14017 | 0.067888
46 | 0.65698 | 0.31819
47 | 0.075511 | 0.036571
48 | 0.27293 | 0.13218
49 | 0.21232 | 0.10283
50 | 0.078631 | 0.038083
51 | 0.077436 | 0.037504
52 | 0.083232 | 0.040311
53 | 0.20684 | 0.10018
54 | 0.078314 | 0.037929
55 | 0.088262 | 0.042747
56 | 0.077168 | 0.037374
57 | 0.13805 | 0.066861
58 | 0.34332 | 0.16628
59 | 0.081187 | 0.03932
60 | 0.15309 | 0.074143
61 | 0.13659 | 0.066152
62 | 0.35666 | 0.17274
63 | 0.084483 | 0.040917

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1