## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_533_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_533_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_533_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_533_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_533_0_node_20 | 20 | n |  | TRUE
5 | bus_MV_533_0_node_21 | 20 | n |  | TRUE
6 | bus_MV_533_0_node_99 | 20 | n |  | TRUE
7 | bus_MV_533_0_node_5 | 20 | n |  | TRUE
8 | bus_MV_533_0_node_6 | 20 | n |  | TRUE
9 | bus_MV_533_0_node_10 | 20 | n |  | TRUE
10 | bus_MV_533_0_node_28 | 20 | n |  | TRUE
11 | bus_MV_533_0_node_33 | 20 | n |  | TRUE
12 | bus_MV_533_0_node_19 | 20 | n |  | TRUE
13 | bus_MV_533_0_node_32 | 20 | n |  | TRUE
14 | bus_MV_533_0_node_105 | 20 | n |  | TRUE
15 | bus_MV_533_0_node_27 | 20 | n |  | TRUE
16 | bus_MV_533_0_node_8 | 20 | n |  | TRUE
17 | bus_MV_533_0_node_7 | 20 | n |  | TRUE
18 | bus_MV_533_0_node_9 | 20 | n |  | TRUE
19 | bus_MV_533_0_node_25 | 20 | n |  | TRUE
20 | bus_MV_533_0_node_26 | 20 | n |  | TRUE
21 | bus_MV_533_0_node_65 | 20 | n |  | TRUE
22 | bus_MV_533_0_node_11 | 20 | n |  | TRUE
23 | bus_MV_533_0_node_12 | 20 | n |  | TRUE
24 | bus_MV_533_0_node_13 | 20 | n |  | TRUE
25 | bus_MV_533_0_node_17 | 20 | n |  | TRUE
26 | bus_MV_533_0_node_14 | 20 | n |  | TRUE
27 | bus_MV_533_0_node_16 | 20 | n |  | TRUE
28 | bus_MV_533_0_node_47 | 20 | n |  | TRUE
29 | bus_MV_533_0_node_98 | 20 | n |  | TRUE
30 | bus_MV_533_0_node_15 | 20 | n |  | TRUE
31 | bus_MV_533_0_node_34 | 20 | n |  | TRUE
32 | bus_MV_533_0_node_30 | 20 | n |  | TRUE
33 | bus_MV_533_0_node_29 | 20 | n |  | TRUE
34 | bus_MV_533_0_node_35 | 20 | n |  | TRUE
35 | bus_MV_533_0_node_31 | 20 | n |  | TRUE
36 | bus_MV_533_0_node_18 | 20 | n |  | TRUE
37 | bus_MV_533_0_node_22 | 20 | n |  | TRUE
38 | bus_MV_533_0_node_23 | 20 | n |  | TRUE
39 | bus_MV_533_0_node_24 | 20 | n |  | TRUE
40 | bus_MV_533_0_node_66 | 20 | n |  | TRUE
41 | bus_MV_533_0_node_67 | 20 | n |  | TRUE
42 | bus_MV_533_0_node_68 | 20 | n |  | TRUE
43 | bus_MV_533_0_node_108 | 20 | n |  | TRUE
44 | bus_MV_533_0_node_36 | 20 | n |  | TRUE
45 | bus_MV_533_0_node_90 | 20 | n |  | TRUE
46 | bus_MV_533_0_node_91 | 20 | n |  | TRUE
47 | bus_MV_533_0_node_100 | 20 | n |  | TRUE
48 | bus_MV_533_0_node_89 | 20 | n |  | TRUE
49 | bus_MV_533_0_node_88 | 20 | n |  | TRUE
50 | bus_MV_533_0_node_92 | 20 | n |  | TRUE
51 | bus_MV_533_0_node_37 | 20 | n |  | TRUE
52 | bus_MV_533_0_node_38 | 20 | n |  | TRUE
53 | bus_MV_533_0_node_39 | 20 | n |  | TRUE
54 | bus_MV_533_0_node_40 | 20 | n |  | TRUE
55 | bus_MV_533_0_node_41 | 20 | n |  | TRUE
56 | bus_MV_533_0_node_106 | 20 | n |  | TRUE
57 | bus_MV_533_0_node_50 | 20 | n |  | TRUE
58 | bus_MV_533_0_node_51 | 20 | n |  | TRUE
59 | bus_MV_533_0_node_82 | 20 | n |  | TRUE
60 | bus_MV_533_0_node_86 | 20 | n |  | TRUE
61 | bus_MV_533_0_node_81 | 20 | n |  | TRUE
62 | bus_MV_533_0_node_80 | 20 | n |  | TRUE
63 | bus_MV_533_0_node_96 | 20 | n |  | TRUE
64 | bus_MV_533_0_node_76 | 20 | n |  | TRUE
65 | bus_MV_533_0_node_78 | 20 | n |  | TRUE
66 | bus_MV_533_0_node_42 | 20 | n |  | TRUE
67 | bus_MV_533_0_node_43 | 20 | n |  | TRUE
68 | bus_MV_533_0_node_44 | 20 | n |  | TRUE
69 | bus_MV_533_0_node_45 | 20 | n |  | TRUE
70 | bus_MV_533_0_node_46 | 20 | n |  | TRUE
71 | bus_MV_533_0_node_87 | 20 | n |  | TRUE
72 | bus_MV_533_0_node_94 | 20 | n |  | TRUE
73 | bus_MV_533_0_node_93 | 20 | n |  | TRUE
74 | bus_MV_533_0_node_48 | 20 | n |  | TRUE
75 | bus_MV_533_0_node_49 | 20 | n |  | TRUE
76 | bus_MV_533_0_node_95 | 20 | n |  | TRUE
77 | bus_MV_533_0_node_52 | 20 | n |  | TRUE
78 | bus_MV_533_0_node_53 | 20 | n |  | TRUE
79 | bus_MV_533_0_node_58 | 20 | n |  | TRUE
80 | bus_MV_533_0_node_56 | 20 | n |  | TRUE
81 | bus_MV_533_0_node_54 | 20 | n |  | TRUE
82 | bus_MV_533_0_node_55 | 20 | n |  | TRUE
83 | bus_MV_533_0_node_57 | 20 | n |  | TRUE
84 | bus_MV_533_0_node_64 | 20 | n |  | TRUE
85 | bus_MV_533_0_node_72 | 20 | n |  | TRUE
86 | bus_MV_533_0_node_74 | 20 | n |  | TRUE
87 | bus_MV_533_0_node_97 | 20 | n |  | TRUE
88 | bus_MV_533_0_node_71 | 20 | n |  | TRUE
89 | bus_MV_533_0_node_101 | 20 | n |  | TRUE
90 | bus_MV_533_0_node_70 | 20 | n |  | TRUE
91 | bus_MV_533_0_node_102 | 20 | n |  | TRUE
92 | bus_MV_533_0_node_73 | 20 | n |  | TRUE
93 | bus_MV_533_0_node_104 | 20 | n |  | TRUE
94 | bus_MV_533_0_node_69 | 20 | n |  | TRUE
95 | bus_MV_533_0_node_75 | 20 | n |  | TRUE
96 | bus_MV_533_0_node_59 | 20 | n |  | TRUE
97 | bus_MV_533_0_node_60 | 20 | n |  | TRUE
98 | bus_MV_533_0_node_61 | 20 | n |  | TRUE
99 | bus_MV_533_0_node_63 | 20 | n |  | TRUE
100 | bus_MV_533_0_node_62 | 20 | n |  | TRUE
101 | bus_MV_533_0_node_103 | 20 | n |  | TRUE
102 | bus_MV_533_0_node_79 | 20 | n |  | TRUE
103 | bus_MV_533_0_node_107 | 20 | n |  | TRUE
104 | bus_MV_533_0_node_77 | 20 | n |  | TRUE
105 | bus_MV_533_0_node_84 | 20 | n |  | TRUE
106 | bus_MV_533_0_node_83 | 20 | n |  | TRUE
107 | bus_MV_533_0_node_85 | 20 | n |  | TRUE
108 | bus_HV_533_0_node_78 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_533_0_load_0 | 0 | 0.37794 | 0.18305 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_533_0_load_21 | 5 | 0.24637 | 0.11932 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_533_0_load_99 | 6 | 0.079497 | 0.038502 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_533_0_load_10 | 9 | 0.2887 | 0.13982 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_533_0_load_28 | 10 | 0.22051 | 0.1068 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_533_0_load_33 | 11 | 0.28452 | 0.1378 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_533_0_load_105 | 14 | 0.41554 | 0.20125 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_533_0_load_7 | 17 | 0.31388 | 0.15202 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_533_0_load_65 | 21 | 0.31523 | 0.15267 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_533_0_load_11 | 22 | 0.27781 | 0.13455 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_533_0_load_47 | 28 | 0.32407 | 0.15695 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_533_0_load_98 | 29 | 0.089798 | 0.043491 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_533_0_load_34 | 31 | 0.24896 | 0.12058 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_533_0_load_30 | 32 | 0.28792 | 0.13944 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_533_0_load_29 | 33 | 0.2479 | 0.12006 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_533_0_load_18 | 36 | 0.29161 | 0.14123 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_533_0_load_22 | 37 | 0.33818 | 0.16379 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_533_0_load_66 | 40 | 0.21441 | 0.10385 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_533_0_load_108 | 43 | 0.12376 | 0.059938 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_533_0_load_91 | 46 | 0.16392 | 0.07939 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_533_0_load_100 | 47 | 0.35324 | 0.17108 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_533_0_load_88 | 49 | 0.098573 | 0.047741 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_533_0_load_37 | 51 | 0.27234 | 0.1319 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_533_0_load_41 | 55 | 0.23266 | 0.11268 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_533_0_load_106 | 56 | 0.31621 | 0.15315 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_533_0_load_86 | 60 | 0.27822 | 0.13475 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_533_0_load_80 | 62 | 0.34505 | 0.16712 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_533_0_load_96 | 63 | 0.11783 | 0.057067 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_533_0_load_76 | 64 | 0.38663 | 0.18725 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_533_0_load_42 | 66 | 0.2547 | 0.12335 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_533_0_load_94 | 72 | 0.14128 | 0.068426 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_533_0_load_93 | 73 | 0.30876 | 0.14954 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_533_0_load_48 | 74 | 0.31309 | 0.15164 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_533_0_load_95 | 76 | 0.10377 | 0.050256 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_533_0_load_52 | 77 | 0.30073 | 0.14565 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_533_0_load_56 | 80 | 0.083342 | 0.040365 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_533_0_load_64 | 84 | 0.21705 | 0.10512 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_533_0_load_97 | 87 | 0.19417 | 0.094041 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_533_0_load_101 | 89 | 0.35233 | 0.17064 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_533_0_load_102 | 91 | 0.25693 | 0.12444 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_533_0_load_104 | 93 | 0.36979 | 0.1791 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_533_0_load_69 | 94 | 0.35374 | 0.17132 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_533_0_load_75 | 95 | 0.38278 | 0.18539 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_533_0_load_59 | 96 | 0.41132 | 0.19921 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_533_0_load_103 | 101 | 0.32538 | 0.15759 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_533_0_load_107 | 103 | 0.28966 | 0.14029 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_533_0_load_83 | 106 | 0.36398 | 0.17629 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 65 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_533_0_line_0 |  | 0 | 1 | 0.005897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_533_0_line_1 |  | 1 | 2 | 0.33482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_533_0_line_2 |  | 2 | 6 | 0.015456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_533_0_line_3 |  | 2 | 3 | 0.13825 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_533_0_line_4 |  | 3 | 4 | 0.13088 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_533_0_line_5 |  | 3 | 5 | 0.046672 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_533_0_line_6 |  | 4 | 11 | 0.002893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_533_0_line_7 |  | 4 | 12 | 0.14302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_533_0_line_8 |  | 6 | 13 | 0.05214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_533_0_line_9 |  | 7 | 8 | 0.89212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_533_0_line_10 |  | 7 | 9 | 0.005799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_533_0_line_11 |  | 8 | 10 | 0.008436 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_533_0_line_12 |  | 9 | 16 | 0.18931 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_533_0_line_13 |  | 12 | 36 | 0.037645 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_533_0_line_14 |  | 13 | 35 | 0.089955 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_533_0_line_15 |  | 14 | 15 | 0.0054 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_533_0_line_16 |  | 15 | 39 | 0.077168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_533_0_line_17 |  | 16 | 18 | 0.39893 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_533_0_line_18 |  | 16 | 17 | 0.029196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_533_0_line_19 |  | 18 | 19 | 0.059029 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_533_0_line_20 |  | 19 | 20 | 0.087732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_533_0_line_21 |  | 19 | 21 | 0.003726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_533_0_line_22 |  | 20 | 40 | 0.1051 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_533_0_line_23 |  | 20 | 38 | 0.24284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_533_0_line_24 |  | 22 | 23 | 0.043972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_533_0_line_25 |  | 23 | 24 | 0.10995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_533_0_line_26 |  | 23 | 25 | 0.37923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_533_0_line_27 |  | 24 | 26 | 0.044221 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_533_0_line_28 |  | 24 | 27 | 0.18565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_533_0_line_29 |  | 24 | 28 | 0.028967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_533_0_line_30 |  | 25 | 33 | 0.005495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_533_0_line_31 |  | 26 | 29 | 0.029631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_533_0_line_32 |  | 27 | 32 | 0.033933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_533_0_line_33 |  | 27 | 30 | 0.10524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_533_0_line_34 |  | 30 | 31 | 0.00487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_533_0_line_35 |  | 31 | 34 | 0.040127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_533_0_line_36 |  | 32 | 35 | 0.00598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_533_0_line_37 |  | 34 | 44 | 0.097899 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_533_0_line_38 |  | 37 | 38 | 0.002575 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_533_0_line_39 |  | 37 | 39 | 0.004769 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_533_0_line_40 |  | 40 | 41 | 0.004468 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_533_0_line_41 |  | 41 | 42 | 0.028169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_533_0_line_42 |  | 42 | 43 | 0.030618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_533_0_line_43 |  | 43 | 90 | 0.12828 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_533_0_line_44 |  | 44 | 45 | 0.073487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_533_0_line_45 |  | 44 | 46 | 0.042873 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_533_0_line_46 |  | 45 | 47 | 0.007149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_533_0_line_47 |  | 45 | 48 | 0.02216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_533_0_line_48 |  | 46 | 50 | 0.024623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_533_0_line_49 |  | 48 | 49 | 0.041444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_533_0_line_50 |  | 50 | 70 | 0.006343 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_533_0_line_51 |  | 51 | 52 | 0.003252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_533_0_line_52 |  | 52 | 53 | 0.058848 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_533_0_line_53 |  | 52 | 54 | 0.11841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_533_0_line_54 |  | 53 | 55 | 0.004285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_533_0_line_55 |  | 54 | 56 | 0.004514 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_533_0_line_56 |  | 56 | 64 | 0.084559 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
57 | MV_533_0_line_57 |  | 56 | 65 | 0.011922 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
58 | MV_533_0_line_58 |  | 57 | 58 | 0.042256 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_533_0_line_59 |  | 57 | 59 | 0.18872 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
60 | MV_533_0_line_60 |  | 57 | 60 | 0.005018 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
61 | MV_533_0_line_61 |  | 58 | 76 | 0.011523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_533_0_line_62 |  | 58 | 75 | 0.090691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_533_0_line_63 |  | 59 | 63 | 0.02585 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
64 | MV_533_0_line_64 |  | 59 | 61 | 0.037526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_533_0_line_65 |  | 60 | 71 | 0.00518 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
66 | MV_533_0_line_66 |  | 61 | 62 | 0.005275 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_533_0_line_67 |  | 63 | 98 | 0.020443 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
68 | MV_533_0_line_68 |  | 64 | 104 | 0.025291 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
69 | MV_533_0_line_69 |  | 66 | 67 | 0.005885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_533_0_line_70 |  | 66 | 68 | 0.006467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_533_0_line_71 |  | 67 | 69 | 0.006745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_533_0_line_72 |  | 68 | 70 | 0.047847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_533_0_line_73 |  | 69 | 71 | 0.072612 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
74 | MV_533_0_line_74 |  | 69 | 72 | 0.041662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_533_0_line_75 |  | 70 | 73 | 0.010198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_533_0_line_76 |  | 74 | 75 | 0.004504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_533_0_line_77 |  | 77 | 78 | 0.003143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_533_0_line_78 |  | 78 | 79 | 0.22585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_533_0_line_79 |  | 79 | 80 | 0.046814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_533_0_line_80 |  | 80 | 81 | 0.02481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_533_0_line_81 |  | 81 | 82 | 0.003917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_533_0_line_82 |  | 81 | 83 | 0.01662 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_533_0_line_83 |  | 82 | 84 | 0.005767 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_533_0_line_84 |  | 83 | 85 | 0.22248 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_533_0_line_85 |  | 83 | 86 | 0.26747 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_533_0_line_86 |  | 83 | 87 | 0.040172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_533_0_line_87 |  | 85 | 91 | 0.051186 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_533_0_line_88 |  | 86 | 95 | 0.004203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_533_0_line_89 |  | 86 | 92 | 0.2391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_533_0_line_90 |  | 88 | 89 | 0.004277 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_533_0_line_91 |  | 88 | 90 | 0.2123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_533_0_line_92 |  | 90 | 94 | 0.004358 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_533_0_line_93 |  | 91 | 107 | 0.004249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_533_0_line_94 |  | 92 | 93 | 0.0085752 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_533_0_line_95 |  | 94 | 105 | 0.094976 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_533_0_line_96 |  | 96 | 97 | 0.006091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_533_0_line_97 |  | 97 | 98 | 0.18345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_533_0_line_98 |  | 98 | 99 | 0.11879 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_533_0_line_99 |  | 98 | 100 | 0.10209 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
100 | MV_533_0_line_100 |  | 99 | 103 | 0.042347 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
101 | MV_533_0_line_101 |  | 100 | 101 | 0.01222 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_533_0_line_102 |  | 100 | 102 | 0.095814 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
103 | MV_533_0_line_103 |  | 102 | 104 | 0.12182 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
104 | MV_533_0_line_104 |  | 104 | 106 | 0.10654 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
105 | MV_533_0_line_105 |  | 105 | 107 | 0.071112 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_533_0_line_106 |  | 105 | 106 | 0.004881 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_533_0_trafo_78 | 25 MVA 110/20 kV | 108 | 65 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2681084.3024 | 1247488.2547
1 | 2681088.1554 | 1247483.7819
2 | 2681299.1255 | 1247501.7945
3 | 2681207.3339 | 1247515.7471
4 | 2681296.0686 | 1247593.5864
5 | 2681172.1547 | 1247485.0764
6 | 2681310.9047 | 1247511.8016
7 | 2680959.9759 | 1247353.6578
8 | 2681109.5493 | 1247649.1621
9 | 2680956.8856 | 1247348.7454
10 | 2681115.2691 | 1247642.9469
11 | 2681298.1806 | 1247591.6028
12 | 2681214.4968 | 1247686.9927
13 | 2681351.9821 | 1247541.0369
14 | 2681124.8162 | 1247213.1076
15 | 2681128.3329 | 1247217.2142
16 | 2680834.9512 | 1247203.932
17 | 2680811.107 | 1247220.875
18 | 2681101.2829 | 1247085.8261
19 | 2681142.6731 | 1247043.7392
20 | 2681200.854 | 1247094.4726
21 | 2681140.2875 | 1247040.8712
22 | 2681352.2325 | 1247772.7272
23 | 2681392.0276 | 1247754.0535
24 | 2681450.531 | 1247736.1436
25 | 2681246.0975 | 1247787.3991
26 | 2681441.5346 | 1247766.9648
27 | 2681434.1448 | 1247628.1061
28 | 2681468.3598 | 1247713.9166
29 | 2681469.691 | 1247757.7337
30 | 2681504.126 | 1247600.6473
31 | 2681500.4232 | 1247597.4718
32 | 2681408.3756 | 1247607.0257
33 | 2681250.209 | 1247791.0581
34 | 2681526.6664 | 1247567.0547
35 | 2681403.975 | 1247602.9623
36 | 2681186.9984 | 1247712.7017
37 | 2681185.3238 | 1247251.5859
38 | 2681187.8238 | 1247251.053
39 | 2681181.603 | 1247248.5883
40 | 2681271.2244 | 1247016.4127
41 | 2681274.6292 | 1247019.317
42 | 2681293.7703 | 1247003.4122
43 | 2681317.4884 | 1247017.8479
44 | 2681474.0776 | 1247502.3958
45 | 2681416.1327 | 1247480.584
46 | 2681482.2161 | 1247460.393
47 | 2681410.9213 | 1247485.4939
48 | 2681405.7404 | 1247467.2872
49 | 2681433.3222 | 1247436.3542
50 | 2681487.2759 | 1247436.2954
51 | 2681307.9309 | 1247394.0252
52 | 2681309.9525 | 1247391.4733
53 | 2681355.2464 | 1247416.0457
54 | 2681369.0037 | 1247318.4964
55 | 2681358.5167 | 1247418.826
56 | 2681371.9215 | 1247315.045
57 | 2681575.6178 | 1247388.308
58 | 2681589.6673 | 1247399.8431
59 | 2681599.3926 | 1247262.4096
60 | 2681575.9663 | 1247393.1719
61 | 2681570.1994 | 1247269.3909
62 | 2681566.611 | 1247273.2666
63 | 2681612.7397 | 1247240.2718
64 | 2681404.1648 | 1247236.8747
65 | 2681376.0483 | 1247303.8601
66 | 2681537.416 | 1247461.0137
67 | 2681541.2244 | 1247456.5183
68 | 2681531.4241 | 1247461.7096
69 | 2681545.5857 | 1247451.3634
70 | 2681492.4529 | 1247434.4429
71 | 2681580.0925 | 1247396.3199
72 | 2681578.7833 | 1247476.4645
73 | 2681498.2112 | 1247426.0159
74 | 2681645.3867 | 1247446.6886
75 | 2681641.4186 | 1247446.8675
76 | 2681598.4996 | 1247407.2442
77 | 2681743.1114 | 1246880.587
78 | 2681744.9146 | 1246878.01
79 | 2681751.5457 | 1246979.9871
80 | 2681704.8325 | 1246977.8458
81 | 2681680.8742 | 1246971.4183
82 | 2681680.0283 | 1246975.2428
83 | 2681673.593 | 1246960.9326
84 | 2681678.7874 | 1246980.8742
85 | 2681529.6177 | 1247043.9235
86 | 2681719.0124 | 1246771.6198
87 | 2681696.862 | 1246928.1865
88 | 2681392.9782 | 1246884.0189
89 | 2681388.9179 | 1246882.6399
90 | 2681445.4435 | 1247008.7191
91 | 2681481.6096 | 1247061.6768
92 | 2681662.8473 | 1246677.1883
93 | 2681669.1815 | 1246682.9687
94 | 2681445.8145 | 1247013.0607
95 | 2681721.6936 | 1246768.3766
96 | 2681699.3459 | 1247089.6481
97 | 2681703.0791 | 1247094.4697
98 | 2681623.2948 | 1247222.765
99 | 2681697.2305 | 1247268.3164
100 | 2681575.3122 | 1247173.4354
101 | 2681577.9164 | 1247161.4959
102 | 2681480.8567 | 1247189.5155
103 | 2681665.5853 | 1247296.4567
104 | 2681417.4562 | 1247215.4415
105 | 2681424.5999 | 1247105.6371
106 | 2681421.0115 | 1247108.9569
107 | 2681477.9684 | 1247063.8839
108 | 2681376.0483 | 1247303.8601

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99598 | -0.030604 | 0.37794 | 0.18305
1 | 0.99598 | -0.030631 | 0 | 0
2 | 0.99614 | -0.032068 | 0 | 0
3 | 0.996 | -0.030771 | 0 | 0
4 | 0.9959 | -0.029904 | 0 | 0
5 | 0.99598 | -0.030911 | 0.24637 | 0.11932
6 | 0.99617 | -0.032274 | 0.079497 | 0.038502
7 | 0.99621 | -0.042733 | 0 | 0
8 | 0.99596 | -0.040978 | 0 | 0
9 | 0.99621 | -0.042741 | 0.2887 | 0.13982
10 | 0.99596 | -0.040956 | 0.22051 | 0.1068
11 | 0.9959 | -0.029894 | 0.28452 | 0.1378
12 | 0.99585 | -0.029417 | 0 | 0
13 | 0.99625 | -0.033015 | 0 | 0
14 | 0.99675 | -0.042163 | 0.41554 | 0.20125
15 | 0.99675 | -0.04219 | 0 | 0
16 | 0.99639 | -0.041217 | 0 | 0
17 | 0.99638 | -0.041107 | 0.31388 | 0.15202
18 | 0.99681 | -0.044478 | 0 | 0
19 | 0.9969 | -0.043726 | 0 | 0
20 | 0.99703 | -0.044742 | 0 | 0
21 | 0.9969 | -0.043712 | 0.31523 | 0.15267
22 | 0.99616 | -0.032303 | 0.27781 | 0.13455
23 | 0.99618 | -0.032449 | 0 | 0
24 | 0.99625 | -0.033065 | 0 | 0
25 | 0.99606 | -0.031428 | 0 | 0
26 | 0.99625 | -0.033021 | 0 | 0
27 | 0.99648 | -0.03496 | 0 | 0
28 | 0.99624 | -0.032952 | 0.32407 | 0.15695
29 | 0.99625 | -0.032989 | 0.089798 | 0.043491
30 | 0.99681 | -0.037844 | 0 | 0
31 | 0.99683 | -0.037977 | 0.24896 | 0.12058
32 | 0.99641 | -0.034367 | 0.28792 | 0.13944
33 | 0.99606 | -0.031412 | 0.2479 | 0.12006
34 | 0.99697 | -0.039192 | 0 | 0
35 | 0.9964 | -0.034283 | 0 | 0
36 | 0.99583 | -0.029551 | 0.29161 | 0.14123
37 | 0.99679 | -0.042594 | 0.33818 | 0.16379
38 | 0.99679 | -0.042617 | 0 | 0
39 | 0.99679 | -0.042571 | 0 | 0
40 | 0.99741 | -0.041945 | 0.21441 | 0.10385
41 | 0.99742 | -0.042047 | 0 | 0
42 | 0.9975 | -0.042684 | 0 | 0
43 | 0.99758 | -0.043375 | 0.12376 | 0.059938
44 | 0.99731 | -0.042144 | 0 | 0
45 | 0.99727 | -0.041757 | 0 | 0
46 | 0.99749 | -0.043655 | 0.16392 | 0.07939
47 | 0.99726 | -0.041726 | 0.35324 | 0.17108
48 | 0.99727 | -0.041732 | 0 | 0
49 | 0.99726 | -0.041684 | 0.098573 | 0.047741
50 | 0.99759 | -0.04457 | 0 | 0
51 | 0.99984 | -0.0017693 | 0.27234 | 0.1319
52 | 0.99985 | -0.0017799 | 0 | 0
53 | 0.99983 | -0.0016191 | 0 | 0
54 | 0.99992 | -0.0024728 | 0 | 0
55 | 0.99983 | -0.0016072 | 0.23266 | 0.11268
56 | 0.99992 | -0.0024988 | 0.31621 | 0.15315
57 | 0.99811 | -0.045751 | 0 | 0
58 | 0.99809 | -0.045547 | 0 | 0
59 | 0.9984 | -0.044504 | 0 | 0
60 | 0.9981 | -0.045781 | 0.27822 | 0.13475
61 | 0.99839 | -0.04435 | 0 | 0
62 | 0.99839 | -0.044328 | 0.34505 | 0.16712
63 | 0.99845 | -0.04432 | 0.11783 | 0.057067
64 | 0.99943 | -0.019086 | 0.38663 | 0.18725
65 | 1 | 0 | -12.6154 | -5.9387
66 | 0.99787 | -0.047019 | 0.2547 | 0.12335
67 | 0.9979 | -0.047277 | 0 | 0
68 | 0.99784 | -0.046756 | 0 | 0
69 | 0.99794 | -0.047572 | 0 | 0
70 | 0.99762 | -0.044805 | 0 | 0
71 | 0.9981 | -0.04581 | 0 | 0
72 | 0.99793 | -0.047503 | 0.14128 | 0.068426
73 | 0.99761 | -0.044768 | 0.30876 | 0.14954
74 | 0.99805 | -0.045196 | 0.31309 | 0.15164
75 | 0.99805 | -0.045213 | 0 | 0
76 | 0.99809 | -0.045533 | 0.10377 | 0.050256
77 | 0.99779 | -0.03038 | 0.30073 | 0.14565
78 | 0.99779 | -0.030391 | 0 | 0
79 | 0.99788 | -0.031167 | 0 | 0
80 | 0.99789 | -0.031319 | 0.083342 | 0.040365
81 | 0.99791 | -0.031422 | 0 | 0
82 | 0.9979 | -0.031412 | 0 | 0
83 | 0.99792 | -0.031534 | 0 | 0
84 | 0.9979 | -0.031397 | 0.21705 | 0.10512
85 | 0.99836 | -0.035335 | 0 | 0
86 | 0.99766 | -0.029269 | 0 | 0
87 | 0.99791 | -0.031442 | 0.19417 | 0.094041
88 | 0.99803 | -0.038557 | 0 | 0
89 | 0.99803 | -0.038539 | 0.35233 | 0.17064
90 | 0.99813 | -0.03942 | 0 | 0
91 | 0.99851 | -0.034258 | 0.25693 | 0.12444
92 | 0.99755 | -0.02825 | 0 | 0
93 | 0.99754 | -0.028288 | 0.36979 | 0.1791
94 | 0.99814 | -0.039542 | 0.35374 | 0.17132
95 | 0.99766 | -0.02925 | 0.38278 | 0.18539
96 | 0.99838 | -0.043263 | 0.41132 | 0.19921
97 | 0.99839 | -0.043293 | 0 | 0
98 | 0.99848 | -0.044171 | 0 | 0
99 | 0.99844 | -0.043769 | 0 | 0
100 | 0.99868 | -0.043328 | 0 | 0
101 | 0.99867 | -0.043376 | 0.32538 | 0.15759
102 | 0.99909 | -0.020546 | 0 | 0
103 | 0.99841 | -0.043918 | 0.28966 | 0.14029
104 | 0.99933 | -0.019487 | 0 | 0
105 | 0.99868 | -0.03576 | 0 | 0
106 | 0.99869 | -0.035621 | 0.36398 | 0.17629
107 | 0.99852 | -0.034343 | 0 | 0
108 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.37794 | -0.18305 | 0.37794 | 0.18291 | 1.1661e-06 | -0.00013932 | 0.012171 | 0.01217 | 0.012171 | 0.99598 | -0.030604 | 0.99598 | -0.030631 | 5.5325
1 | -0.37794 | -0.18291 | 0.37801 | 0.17499 | 6.5659e-05 | -0.0079118 | 0.01217 | 0.012071 | 0.01217 | 0.99598 | -0.030631 | 0.99614 | -0.032068 | 5.5317
2 | -1.2007 | -0.56349 | 1.2008 | 0.56313 | 3.0481e-05 | -0.00035716 | 0.038437 | 0.038433 | 0.038437 | 0.99614 | -0.032068 | 0.99617 | -0.032274 | 17.4715
3 | 0.82272 | 0.38849 | -0.82259 | -0.39173 | 0.0001285 | -0.0032367 | 0.026366 | 0.026407 | 0.026407 | 0.99614 | -0.032068 | 0.996 | -0.030771 | 12.0032
4 | 0.57622 | 0.27246 | -0.57616 | -0.27554 | 5.9752e-05 | -0.0030818 | 0.018474 | 0.018512 | 0.018512 | 0.996 | -0.030771 | 0.9959 | -0.029904 | 8.4147
5 | 0.24638 | 0.11927 | -0.24637 | -0.11932 | 5.2344e-06 | -5.1992e-05 | 0.0079336 | 0.0079342 | 0.0079342 | 0.996 | -0.030771 | 0.99598 | -0.030911 | 3.7782
6 | 0.28452 | 0.13773 | -0.28452 | -0.1378 | 3.243e-07 | -6.8412e-05 | 0.0091627 | 0.0091636 | 0.0091636 | 0.9959 | -0.029904 | 0.9959 | -0.029894 | 4.1653
7 | 0.29163 | 0.13781 | -0.29162 | -0.14119 | 1.6766e-05 | -0.0033817 | 0.0093497 | 0.0093921 | 0.0093921 | 0.9959 | -0.029904 | 0.99585 | -0.029417 | 4.2691
8 | -1.2803 | -0.60163 | 1.2804 | 0.60043 | 0.00011692 | -0.0012008 | 0.040992 | 0.040977 | 0.040992 | 0.99617 | -0.032274 | 0.99625 | -0.033015 | 18.6329
9 | 0.22057 | 0.085483 | -0.22051 | -0.1066 | 5.7881e-05 | -0.021117 | 0.0068548 | 0.0070991 | 0.0070991 | 0.99621 | -0.042733 | 0.99596 | -0.040978 | 3.2269
10 | -0.22057 | -0.085483 | 0.22057 | 0.085346 | 3.6366e-07 | -0.0001373 | 0.0068548 | 0.0068534 | 0.0068548 | 0.99621 | -0.042733 | 0.99621 | -0.042741 | 3.1158
11 | 0.22051 | 0.1066 | -0.22051 | -0.1068 | 5.6779e-07 | -0.00019963 | 0.0070991 | 0.0071017 | 0.0071017 | 0.99596 | -0.040978 | 0.99596 | -0.040956 | 3.228
12 | -0.50927 | -0.22517 | 0.50936 | 0.225 | 8.7801e-05 | -0.00016934 | 0.016135 | 0.016133 | 0.016135 | 0.99621 | -0.042741 | 0.99639 | -0.041217 | 7.6835
13 | 0.29162 | 0.14119 | -0.29161 | -0.14123 | 5.9168e-06 | -4.0861e-05 | 0.0093921 | 0.0093926 | 0.0093926 | 0.99585 | -0.029417 | 0.99583 | -0.029551 | 4.4727
14 | -1.2804 | -0.60043 | 1.2806 | 0.59836 | 0.00020152 | -0.0020722 | 0.040977 | 0.040951 | 0.040977 | 0.99625 | -0.033015 | 0.9964 | -0.034283 | 18.626
15 | -0.41554 | -0.20125 | 0.41554 | 0.20113 | 1.2889e-06 | -0.00012771 | 0.013372 | 0.01337 | 0.013372 | 0.99675 | -0.042163 | 0.99675 | -0.04219 | 6.0782
16 | -0.41554 | -0.20113 | 0.41556 | 0.1993 | 1.8385e-05 | -0.0018251 | 0.01337 | 0.013347 | 0.01337 | 0.99675 | -0.04219 | 0.99679 | -0.042571 | 6.0774
17 | -0.82324 | -0.37633 | 0.8236 | 0.36697 | 0.00036469 | -0.0093521 | 0.026225 | 0.026112 | 0.026225 | 0.99639 | -0.041217 | 0.99681 | -0.044478 | 11.9204
18 | 0.31388 | 0.15133 | -0.31388 | -0.15202 | 3.9759e-06 | -0.00069088 | 0.010095 | 0.010104 | 0.010104 | 0.99639 | -0.041217 | 0.99638 | -0.041107 | 4.5928
19 | -0.8236 | -0.36697 | 0.82368 | 0.36695 | 7.1708e-05 | -2.5111e-05 | 0.026112 | 0.026111 | 0.026112 | 0.99681 | -0.044478 | 0.9969 | -0.043726 | 12.4343
20 | -1.1389 | -0.51953 | 1.1391 | 0.5175 | 0.00015379 | -0.0020364 | 0.036249 | 0.036224 | 0.036249 | 0.9969 | -0.043726 | 0.99703 | -0.044742 | 16.4768
21 | 0.31523 | 0.15258 | -0.31523 | -0.15267 | 5.1166e-07 | -8.826e-05 | 0.010141 | 0.010142 | 0.010142 | 0.9969 | -0.043726 | 0.9969 | -0.043712 | 4.6102
22 | -1.893 | -0.87471 | 1.8937 | 0.87501 | 0.00068259 | 0.00030279 | 0.060377 | 0.060376 | 0.060377 | 0.99703 | -0.044742 | 0.99741 | -0.041945 | 28.7511
23 | 0.75393 | 0.35721 | -0.75374 | -0.36292 | 0.00018972 | -0.0057061 | 0.024155 | 0.024227 | 0.024227 | 0.99703 | -0.044742 | 0.99679 | -0.042617 | 11.0124
24 | -0.27781 | -0.13455 | 0.27781 | 0.13351 | 4.69e-06 | -0.0010405 | 0.008945 | 0.0089319 | 0.008945 | 0.99616 | -0.032303 | 0.99618 | -0.032449 | 4.0659
25 | -0.52575 | -0.24447 | 0.52579 | 0.24187 | 4.1357e-05 | -0.002593 | 0.016802 | 0.01677 | 0.016802 | 0.99618 | -0.032449 | 0.99625 | -0.033065 | 7.6371
26 | 0.24793 | 0.11096 | -0.2479 | -0.11993 | 3.18e-05 | -0.0089749 | 0.0078714 | 0.0079813 | 0.0079813 | 0.99618 | -0.032449 | 0.99606 | -0.031428 | 3.6279
27 | 0.089798 | 0.041741 | -0.089798 | -0.042789 | 4.8823e-07 | -0.0010478 | 0.0028694 | 0.0028823 | 0.0028823 | 0.99625 | -0.033065 | 0.99625 | -0.033021 | 1.3101
28 | -0.93966 | -0.43988 | 0.93988 | 0.43555 | 0.00022361 | -0.0043342 | 0.030063 | 0.03001 | 0.030063 | 0.99625 | -0.033065 | 0.99648 | -0.03496 | 13.6652
29 | 0.32407 | 0.15627 | -0.32407 | -0.15695 | 4.2063e-06 | -0.00068519 | 0.010425 | 0.010434 | 0.010434 | 0.99625 | -0.033065 | 0.99624 | -0.032952 | 4.7426
30 | 0.2479 | 0.11993 | -0.2479 | -0.12006 | 4.6741e-07 | -0.00013003 | 0.0079813 | 0.0079829 | 0.0079829 | 0.99606 | -0.031428 | 0.99606 | -0.031412 | 3.6286
31 | 0.089798 | 0.042789 | -0.089798 | -0.043491 | 3.2963e-07 | -0.00070208 | 0.0028823 | 0.0028911 | 0.0028911 | 0.99625 | -0.033021 | 0.99625 | -0.032989 | 1.3141
32 | 1.5686 | 0.7369 | -1.5685 | -0.73767 | 0.00011421 | -0.00077055 | 0.050207 | 0.050217 | 0.050217 | 0.99648 | -0.03496 | 0.99641 | -0.034367 | 22.8258
33 | -2.5085 | -1.1724 | 2.5094 | 1.1702 | 0.00090368 | -0.0022278 | 0.080216 | 0.080185 | 0.080216 | 0.99648 | -0.03496 | 0.99681 | -0.037844 | 36.4618
34 | -2.5094 | -1.1702 | 2.5094 | 1.1701 | 4.1802e-05 | -0.00010314 | 0.080185 | 0.080184 | 0.080185 | 0.99681 | -0.037844 | 0.99683 | -0.037977 | 36.4479
35 | -2.7584 | -1.2907 | 2.7588 | 1.2899 | 0.00041662 | -0.00082856 | 0.088194 | 0.088182 | 0.088194 | 0.99683 | -0.037977 | 0.99697 | -0.039192 | 40.0882
36 | 1.2806 | 0.59822 | -1.2806 | -0.59836 | 1.3387e-05 | -0.00013778 | 0.040949 | 0.040951 | 0.040951 | 0.99641 | -0.034367 | 0.9964 | -0.034283 | 18.6141
37 | -2.7588 | -1.2899 | 2.7598 | 1.2878 | 0.001016 | -0.0020227 | 0.088182 | 0.088154 | 0.088182 | 0.99697 | -0.039192 | 0.99731 | -0.042144 | 40.0829
38 | -0.75374 | -0.36298 | 0.75374 | 0.36292 | 2.0177e-06 | -6.0489e-05 | 0.024228 | 0.024227 | 0.024228 | 0.99679 | -0.042594 | 0.99679 | -0.042617 | 11.0127
39 | 0.41556 | 0.19919 | -0.41556 | -0.1993 | 1.1341e-06 | -0.0001128 | 0.013346 | 0.013347 | 0.013347 | 0.99679 | -0.042594 | 0.99679 | -0.042571 | 6.067
40 | -2.1081 | -0.97886 | 2.1081 | 0.97876 | 2.6992e-05 | -9.8121e-05 | 0.06727 | 0.067269 | 0.06727 | 0.99741 | -0.041945 | 0.99742 | -0.042047 | 30.5773
41 | -2.1081 | -0.97876 | 2.1083 | 0.97814 | 0.00017015 | -0.00061868 | 0.067269 | 0.067261 | 0.067269 | 0.99742 | -0.042047 | 0.9975 | -0.042684 | 30.5767
42 | -2.1083 | -0.97814 | 2.1085 | 0.97747 | 0.00018489 | -0.0006726 | 0.067261 | 0.067252 | 0.067261 | 0.9975 | -0.042684 | 0.99758 | -0.043375 | 30.573
43 | -2.2322 | -1.0374 | 2.2334 | 1.038 | 0.0011596 | 0.00057386 | 0.07123 | 0.071228 | 0.07123 | 0.99758 | -0.043375 | 0.99813 | -0.03942 | 33.9192
44 | 0.45184 | 0.2154 | -0.45182 | -0.21714 | 2.0625e-05 | -0.001739 | 0.014489 | 0.014511 | 0.014511 | 0.99731 | -0.042144 | 0.99727 | -0.041757 | 6.5957
45 | -3.2117 | -1.5032 | 3.2123 | 1.5024 | 0.00060292 | -0.00083947 | 0.10264 | 0.10263 | 0.10264 | 0.99731 | -0.042144 | 0.99749 | -0.043655 | 46.6555
46 | 0.35324 | 0.17091 | -0.35324 | -0.17108 | 1.2317e-06 | -0.00016939 | 0.011359 | 0.011361 | 0.011361 | 0.99727 | -0.041757 | 0.99726 | -0.041726 | 5.1642
47 | 0.098574 | 0.046231 | -0.098574 | -0.046757 | 2.9445e-07 | -0.00052613 | 0.0031516 | 0.0031581 | 0.0031581 | 0.99727 | -0.041757 | 0.99727 | -0.041732 | 1.4355
48 | -3.3762 | -1.5818 | 3.3766 | 1.5813 | 0.00038268 | -0.0004715 | 0.1079 | 0.10789 | 0.1079 | 0.99749 | -0.043655 | 0.99759 | -0.04457 | 49.0455
49 | 0.098574 | 0.046757 | -0.098573 | -0.047741 | 5.5396e-07 | -0.00098395 | 0.0031581 | 0.0031704 | 0.0031704 | 0.99727 | -0.041732 | 0.99726 | -0.041684 | 1.4411
50 | -3.3766 | -1.5813 | 3.3767 | 1.5812 | 9.8572e-05 | -0.00012148 | 0.10789 | 0.10789 | 0.10789 | 0.99759 | -0.04457 | 0.99762 | -0.044805 | 49.0423
51 | -0.27234 | -0.1319 | 0.27234 | 0.13182 | 3.3134e-07 | -7.7523e-05 | 0.0087365 | 0.0087356 | 0.0087365 | 0.99984 | -0.0017693 | 0.99985 | -0.0017799 | 3.9712
52 | 0.23266 | 0.11118 | -0.23266 | -0.11258 | 4.3647e-06 | -0.0014033 | 0.0074449 | 0.0074625 | 0.0074625 | 0.99985 | -0.0017799 | 0.99983 | -0.0016191 | 3.3921
53 | -0.505 | -0.243 | 0.50504 | 0.24018 | 4.1295e-05 | -0.0028143 | 0.01618 | 0.016145 | 0.01618 | 0.99985 | -0.0017799 | 0.99992 | -0.0024728 | 7.3548
54 | 0.23266 | 0.11258 | -0.23266 | -0.11268 | 3.1863e-07 | -0.00010218 | 0.0074625 | 0.0074638 | 0.0074638 | 0.99983 | -0.0016191 | 0.99983 | -0.0016072 | 3.3926
55 | -0.50504 | -0.24018 | 0.50504 | 0.24008 | 1.5707e-06 | -0.00010729 | 0.016145 | 0.016144 | 0.016145 | 0.99992 | -0.0024728 | 0.99992 | -0.0024988 | 7.3388
56 | 11.7795 | 5.534 | -11.7752 | -5.5281 | 0.0042545 | 0.005941 | 0.37573 | 0.37573 | 0.37573 | 0.99992 | -0.0024988 | 0.99943 | -0.019086 | 45.821
57 | -12.6007 | -5.9272 | 12.6014 | 5.9282 | 0.0006867 | 0.00096336 | 0.40202 | 0.40202 | 0.40202 | 0.99992 | -0.0024988 | 1 | 0 | 49.0263
58 | 0.41688 | 0.19836 | -0.41687 | -0.19936 | 1.0067e-05 | -0.0010021 | 0.013352 | 0.013365 | 0.013365 | 0.99811 | -0.045751 | 0.99809 | -0.045547 | 6.075
59 | -4.7785 | -2.2505 | 4.7798 | 2.2395 | 0.0013596 | -0.011051 | 0.15276 | 0.15262 | 0.15276 | 0.99811 | -0.045751 | 0.9984 | -0.044504 | 23.9442
60 | 4.3616 | 2.0522 | -4.3615 | -2.0525 | 3.0137e-05 | -0.00029713 | 0.13941 | 0.13942 | 0.13942 | 0.99811 | -0.045751 | 0.9981 | -0.045781 | 21.852
61 | 0.10377 | 0.049982 | -0.10377 | -0.050256 | 1.709e-07 | -0.00027403 | 0.0033312 | 0.0033347 | 0.0033347 | 0.99809 | -0.045547 | 0.99809 | -0.045533 | 1.5158
62 | 0.31311 | 0.14938 | -0.31309 | -0.15153 | 1.2222e-05 | -0.0021534 | 0.010034 | 0.010061 | 0.010061 | 0.99809 | -0.045547 | 0.99805 | -0.045213 | 4.5731
63 | -5.1249 | -2.4056 | 5.1251 | 2.4041 | 0.000214 | -0.0014986 | 0.16369 | 0.16367 | 0.16369 | 0.9984 | -0.044504 | 0.99845 | -0.04432 | 25.6569
64 | 0.34506 | 0.1661 | -0.34505 | -0.16699 | 6.1481e-06 | -0.00089127 | 0.011073 | 0.011084 | 0.011084 | 0.9984 | -0.044504 | 0.99839 | -0.04435 | 5.0381
65 | 4.0833 | 1.9177 | -4.0833 | -1.918 | 2.7249e-05 | -0.00030889 | 0.13048 | 0.13048 | 0.13048 | 0.9981 | -0.045781 | 0.9981 | -0.04581 | 20.4513
66 | 0.34505 | 0.16699 | -0.34505 | -0.16712 | 8.6524e-07 | -0.00012528 | 0.011084 | 0.011085 | 0.011085 | 0.99839 | -0.04435 | 0.99839 | -0.044328 | 5.0388
67 | -5.2429 | -2.4611 | 5.2431 | 2.46 | 0.00017711 | -0.0011808 | 0.16746 | 0.16744 | 0.16746 | 0.99845 | -0.04432 | 0.99848 | -0.044171 | 26.247
68 | 11.3886 | 5.3408 | -11.3876 | -5.3418 | 0.0010317 | -0.0010062 | 0.36332 | 0.36334 | 0.36334 | 0.99943 | -0.019086 | 0.99933 | -0.019487 | 56.9505
69 | -3.9411 | -1.8529 | 3.9413 | 1.8528 | 0.0001247 | -0.00010293 | 0.12598 | 0.12598 | 0.12598 | 0.99787 | -0.047019 | 0.9979 | -0.047277 | 57.2659
70 | 3.6864 | 1.7295 | -3.6863 | -1.7296 | 0.0001198 | -0.00011821 | 0.1178 | 0.1178 | 0.1178 | 0.99787 | -0.047019 | 0.99784 | -0.046756 | 53.5458
71 | -3.9413 | -1.8528 | 3.9414 | 1.8526 | 0.00014292 | -0.00011798 | 0.12598 | 0.12598 | 0.12598 | 0.9979 | -0.047277 | 0.99794 | -0.047572 | 57.2651
72 | 3.6863 | 1.7296 | -3.6854 | -1.7305 | 0.00088651 | -0.00087425 | 0.1178 | 0.11781 | 0.11781 | 0.99784 | -0.046756 | 0.99762 | -0.044805 | 53.5521
73 | -4.0827 | -1.9201 | 4.0833 | 1.918 | 0.00059723 | -0.0020472 | 0.13051 | 0.13048 | 0.13051 | 0.99794 | -0.047572 | 0.9981 | -0.04581 | 36.0524
74 | 0.14128 | 0.067436 | -0.14128 | -0.068426 | 1.1438e-06 | -0.00099027 | 0.0045286 | 0.004541 | 0.004541 | 0.99794 | -0.047572 | 0.99793 | -0.047503 | 2.0641
75 | 0.30876 | 0.1493 | -0.30876 | -0.14954 | 1.3413e-06 | -0.00024193 | 0.0099242 | 0.0099273 | 0.0099273 | 0.99762 | -0.044805 | 0.99761 | -0.044768 | 4.5124
76 | -0.31309 | -0.15164 | 0.31309 | 0.15153 | 6.0871e-07 | -0.00010694 | 0.010062 | 0.010061 | 0.010062 | 0.99805 | -0.045196 | 0.99805 | -0.045213 | 4.5737
77 | -0.30073 | -0.14565 | 0.30073 | 0.14558 | 3.9208e-07 | -7.4595e-05 | 0.0096673 | 0.0096663 | 0.0096673 | 0.99779 | -0.03038 | 0.99779 | -0.030391 | 4.3942
78 | -0.30073 | -0.14558 | 0.30076 | 0.14021 | 2.7977e-05 | -0.0053608 | 0.0096663 | 0.0095997 | 0.0096663 | 0.99779 | -0.030391 | 0.99788 | -0.031167 | 4.3938
79 | -0.30076 | -0.14021 | 0.30076 | 0.1391 | 5.7512e-06 | -0.0011113 | 0.0095997 | 0.0095861 | 0.0095997 | 0.99788 | -0.031167 | 0.99789 | -0.031319 | 4.3635
80 | -0.38411 | -0.17947 | 0.38411 | 0.17888 | 4.9793e-06 | -0.00058841 | 0.012265 | 0.012257 | 0.012265 | 0.99789 | -0.031319 | 0.99791 | -0.031422 | 5.5748
81 | 0.21705 | 0.10489 | -0.21705 | -0.10498 | 2.5433e-07 | -9.3056e-05 | 0.0069735 | 0.0069747 | 0.0069747 | 0.99791 | -0.031422 | 0.9979 | -0.031412 | 3.1703
82 | -0.60116 | -0.28377 | 0.60117 | 0.28338 | 8.203e-06 | -0.00039272 | 0.01923 | 0.019226 | 0.01923 | 0.99791 | -0.031422 | 0.99792 | -0.031534 | 8.7411
83 | 0.21705 | 0.10498 | -0.21705 | -0.10512 | 3.7462e-07 | -0.00013701 | 0.0069747 | 0.0069764 | 0.0069764 | 0.9979 | -0.031412 | 0.9979 | -0.031397 | 3.1711
84 | -1.5482 | -0.72887 | 1.5489 | 0.7238 | 0.00072679 | -0.0050766 | 0.0495 | 0.049435 | 0.0495 | 0.99792 | -0.031534 | 0.99836 | -0.035335 | 22.4999
85 | 0.75282 | 0.35241 | -0.75261 | -0.35871 | 0.00020712 | -0.0062964 | 0.024045 | 0.024124 | 0.024124 | 0.99792 | -0.031534 | 0.99766 | -0.029269 | 10.9654
86 | 0.19417 | 0.093087 | -0.19417 | -0.094041 | 2.0849e-06 | -0.00095452 | 0.0062291 | 0.0062411 | 0.0062411 | 0.99792 | -0.031534 | 0.99791 | -0.031442 | 2.8369
87 | -1.5489 | -0.7238 | 1.5491 | 0.72387 | 0.00022286 | 7.8681e-05 | 0.049435 | 0.049434 | 0.049435 | 0.99836 | -0.035335 | 0.99851 | -0.034258 | 23.5404
88 | 0.38278 | 0.18529 | -0.38278 | -0.18539 | 8.4968e-07 | -9.963e-05 | 0.012305 | 0.012306 | 0.012306 | 0.99766 | -0.029269 | 0.99766 | -0.02925 | 5.5938
89 | 0.36983 | 0.17342 | -0.36979 | -0.17909 | 4.4856e-05 | -0.0056682 | 0.011819 | 0.01189 | 0.01189 | 0.99766 | -0.029269 | 0.99755 | -0.02825 | 5.4045
90 | 0.35233 | 0.17054 | -0.35233 | -0.17064 | 7.3202e-07 | -0.0001015 | 0.011322 | 0.011323 | 0.011323 | 0.99803 | -0.038557 | 0.99803 | -0.038539 | 5.147
91 | -0.35233 | -0.17054 | 0.35237 | 0.1655 | 3.6128e-05 | -0.0050387 | 0.011322 | 0.011259 | 0.011322 | 0.99803 | -0.038557 | 0.99813 | -0.03942 | 5.1464
92 | -2.5858 | -1.2035 | 2.5858 | 1.2034 | 3.9586e-05 | -9.1922e-05 | 0.082488 | 0.082486 | 0.082488 | 0.99813 | -0.03942 | 0.99814 | -0.039542 | 37.4943
93 | -1.806 | -0.84831 | 1.8061 | 0.84822 | 1.8876e-05 | -9.5549e-05 | 0.057687 | 0.057685 | 0.057687 | 0.99851 | -0.034258 | 0.99852 | -0.034343 | 26.2212
94 | 0.36979 | 0.17909 | -0.36979 | -0.1791 | 2.16e-06 | -8.834e-06 | 0.01189 | 0.01189 | 0.01189 | 0.99755 | -0.02825 | 0.99754 | -0.028288 | 5.662
95 | -2.9395 | -1.3747 | 2.941 | 1.3755 | 0.0014905 | 0.00082058 | 0.093852 | 0.093851 | 0.093852 | 0.99814 | -0.039542 | 0.99868 | -0.03576 | 44.6915
96 | -0.41132 | -0.19921 | 0.41132 | 0.19906 | 1.4197e-06 | -0.00014454 | 0.013214 | 0.013213 | 0.013214 | 0.99838 | -0.043263 | 0.99839 | -0.043293 | 6.0065
97 | -0.41132 | -0.19906 | 0.41136 | 0.19471 | 4.2576e-05 | -0.0043537 | 0.013213 | 0.013158 | 0.013213 | 0.99839 | -0.043293 | 0.99848 | -0.044171 | 6.0057
98 | 0.28968 | 0.13742 | -0.28967 | -0.14024 | 1.3678e-05 | -0.0028234 | 0.0092697 | 0.0093051 | 0.0093051 | 0.99848 | -0.044171 | 0.99844 | -0.043769 | 4.2296
99 | -5.9441 | -2.7921 | 5.9453 | 2.7863 | 0.0011368 | -0.0057563 | 0.18987 | 0.18979 | 0.18987 | 0.99848 | -0.044171 | 0.99868 | -0.043328 | 29.7598
100 | 0.28967 | 0.14024 | -0.28966 | -0.14029 | 6.5332e-06 | -4.6303e-05 | 0.0093051 | 0.0093057 | 0.0093057 | 0.99844 | -0.043769 | 0.99841 | -0.043918 | 4.4313
101 | 0.32538 | 0.15758 | -0.32538 | -0.15759 | 2.3778e-06 | -1.3061e-05 | 0.01045 | 0.01045 | 0.01045 | 0.99868 | -0.043328 | 0.99867 | -0.043376 | 4.9764
102 | -6.2707 | -2.9439 | 6.272 | 2.9475 | 0.0013715 | 0.0035559 | 0.20024 | 0.20024 | 0.20024 | 0.99868 | -0.043328 | 0.99909 | -0.020546 | 31.0448
103 | -6.272 | -2.9475 | 6.2735 | 2.9407 | 0.0015086 | -0.0067927 | 0.20024 | 0.20014 | 0.20024 | 0.99909 | -0.020546 | 0.99933 | -0.019487 | 31.3851
104 | 5.114 | 2.4012 | -5.1114 | -2.3983 | 0.0026051 | 0.002846 | 0.1632 | 0.1632 | 0.1632 | 0.99933 | -0.019487 | 0.99869 | -0.035621 | 46.6293
105 | 1.8064 | 0.84662 | -1.8061 | -0.84822 | 0.00031579 | -0.0015995 | 0.057665 | 0.057685 | 0.057685 | 0.99868 | -0.03576 | 0.99852 | -0.034343 | 26.2206
106 | -4.7474 | -2.2221 | 4.7474 | 2.222 | 5.4121e-05 | -0.00012768 | 0.15152 | 0.15151 | 0.15152 | 0.99868 | -0.03576 | 0.99869 | -0.035621 | 41.8551

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 12.6154 | 5.9387

## res_load
| p_mw | q_mvar
0 | 0.37794 | 0.18305
1 | 0.24637 | 0.11932
2 | 0.079497 | 0.038502
3 | 0.2887 | 0.13982
4 | 0.22051 | 0.1068
5 | 0.28452 | 0.1378
6 | 0.41554 | 0.20125
7 | 0.31388 | 0.15202
8 | 0.31523 | 0.15267
9 | 0.27781 | 0.13455
10 | 0.32407 | 0.15695
11 | 0.089798 | 0.043491
12 | 0.24896 | 0.12058
13 | 0.28792 | 0.13944
14 | 0.2479 | 0.12006
15 | 0.29161 | 0.14123
16 | 0.33818 | 0.16379
17 | 0.21441 | 0.10385
18 | 0.12376 | 0.059938
19 | 0.16392 | 0.07939
20 | 0.35324 | 0.17108
21 | 0.098573 | 0.047741
22 | 0.27234 | 0.1319
23 | 0.23266 | 0.11268
24 | 0.31621 | 0.15315
25 | 0.27822 | 0.13475
26 | 0.34505 | 0.16712
27 | 0.11783 | 0.057067
28 | 0.38663 | 0.18725
29 | 0.2547 | 0.12335
30 | 0.14128 | 0.068426
31 | 0.30876 | 0.14954
32 | 0.31309 | 0.15164
33 | 0.10377 | 0.050256
34 | 0.30073 | 0.14565
35 | 0.083342 | 0.040365
36 | 0.21705 | 0.10512
37 | 0.19417 | 0.094041
38 | 0.35233 | 0.17064
39 | 0.25693 | 0.12444
40 | 0.36979 | 0.1791
41 | 0.35374 | 0.17132
42 | 0.38278 | 0.18539
43 | 0.41132 | 0.19921
44 | 0.32538 | 0.15759
45 | 0.28966 | 0.14029
46 | 0.36398 | 0.17629

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1