## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_535_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_535_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_535_0_node_5 | 20 | n |  | TRUE
3 | bus_MV_535_0_node_6 | 20 | n |  | TRUE
4 | bus_MV_535_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_535_0_node_81 | 20 | n |  | TRUE
6 | bus_MV_535_0_node_4 | 20 | n |  | TRUE
7 | bus_MV_535_0_node_79 | 20 | n |  | TRUE
8 | bus_MV_535_0_node_128 | 20 | n |  | TRUE
9 | bus_MV_535_0_node_94 | 20 | n |  | TRUE
10 | bus_MV_535_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_535_0_node_134 | 20 | n |  | TRUE
12 | bus_MV_535_0_node_8 | 20 | n |  | TRUE
13 | bus_MV_535_0_node_46 | 20 | n |  | TRUE
14 | bus_MV_535_0_node_80 | 20 | n |  | TRUE
15 | bus_MV_535_0_node_165 | 20 | n |  | TRUE
16 | bus_MV_535_0_node_75 | 20 | n |  | TRUE
17 | bus_MV_535_0_node_96 | 20 | n |  | TRUE
18 | bus_MV_535_0_node_74 | 20 | n |  | TRUE
19 | bus_MV_535_0_node_9 | 20 | n |  | TRUE
20 | bus_MV_535_0_node_10 | 20 | n |  | TRUE
21 | bus_MV_535_0_node_11 | 20 | n |  | TRUE
22 | bus_MV_535_0_node_98 | 20 | n |  | TRUE
23 | bus_MV_535_0_node_90 | 20 | n |  | TRUE
24 | bus_MV_535_0_node_97 | 20 | n |  | TRUE
25 | bus_MV_535_0_node_12 | 20 | n |  | TRUE
26 | bus_MV_535_0_node_155 | 20 | n |  | TRUE
27 | bus_MV_535_0_node_13 | 20 | n |  | TRUE
28 | bus_MV_535_0_node_87 | 20 | n |  | TRUE
29 | bus_MV_535_0_node_14 | 20 | n |  | TRUE
30 | bus_MV_535_0_node_15 | 20 | n |  | TRUE
31 | bus_MV_535_0_node_57 | 20 | n |  | TRUE
32 | bus_MV_535_0_node_16 | 20 | n |  | TRUE
33 | bus_MV_535_0_node_18 | 20 | n |  | TRUE
34 | bus_MV_535_0_node_17 | 20 | n |  | TRUE
35 | bus_MV_535_0_node_143 | 20 | n |  | TRUE
36 | bus_MV_535_0_node_59 | 20 | n |  | TRUE
37 | bus_MV_535_0_node_58 | 20 | n |  | TRUE
38 | bus_MV_535_0_node_199 | 20 | n |  | TRUE
39 | bus_MV_535_0_node_56 | 20 | n |  | TRUE
40 | bus_MV_535_0_node_54 | 20 | n |  | TRUE
41 | bus_MV_535_0_node_55 | 20 | n |  | TRUE
42 | bus_MV_535_0_node_144 | 20 | n |  | TRUE
43 | bus_MV_535_0_node_92 | 20 | n |  | TRUE
44 | bus_MV_535_0_node_202 | 20 | n |  | TRUE
45 | bus_MV_535_0_node_19 | 20 | n |  | TRUE
46 | bus_MV_535_0_node_21 | 20 | n |  | TRUE
47 | bus_MV_535_0_node_22 | 20 | n |  | TRUE
48 | bus_MV_535_0_node_20 | 20 | n |  | TRUE
49 | bus_MV_535_0_node_24 | 20 | n |  | TRUE
50 | bus_MV_535_0_node_25 | 20 | n |  | TRUE
51 | bus_MV_535_0_node_23 | 20 | n |  | TRUE
52 | bus_MV_535_0_node_28 | 20 | n |  | TRUE
53 | bus_MV_535_0_node_33 | 20 | n |  | TRUE
54 | bus_MV_535_0_node_145 | 20 | n |  | TRUE
55 | bus_MV_535_0_node_26 | 20 | n |  | TRUE
56 | bus_MV_535_0_node_78 | 20 | n |  | TRUE
57 | bus_MV_535_0_node_172 | 20 | n |  | TRUE
58 | bus_MV_535_0_node_29 | 20 | n |  | TRUE
59 | bus_MV_535_0_node_30 | 20 | n |  | TRUE
60 | bus_MV_535_0_node_77 | 20 | n |  | TRUE
61 | bus_MV_535_0_node_76 | 20 | n |  | TRUE
62 | bus_MV_535_0_node_127 | 20 | n |  | TRUE
63 | bus_MV_535_0_node_171 | 20 | n |  | TRUE
64 | bus_MV_535_0_node_34 | 20 | n |  | TRUE
65 | bus_MV_535_0_node_27 | 20 | n |  | TRUE
66 | bus_MV_535_0_node_32 | 20 | n |  | TRUE
67 | bus_MV_535_0_node_35 | 20 | n |  | TRUE
68 | bus_MV_535_0_node_36 | 20 | n |  | TRUE
69 | bus_MV_535_0_node_51 | 20 | n |  | TRUE
70 | bus_MV_535_0_node_198 | 20 | n |  | TRUE
71 | bus_MV_535_0_node_139 | 20 | n |  | TRUE
72 | bus_MV_535_0_node_138 | 20 | n |  | TRUE
73 | bus_MV_535_0_node_37 | 20 | n |  | TRUE
74 | bus_MV_535_0_node_190 | 20 | n |  | TRUE
75 | bus_MV_535_0_node_135 | 20 | n |  | TRUE
76 | bus_MV_535_0_node_66 | 20 | n |  | TRUE
77 | bus_MV_535_0_node_95 | 20 | n |  | TRUE
78 | bus_MV_535_0_node_41 | 20 | n |  | TRUE
79 | bus_MV_535_0_node_42 | 20 | n |  | TRUE
80 | bus_MV_535_0_node_100 | 20 | n |  | TRUE
81 | bus_MV_535_0_node_160 | 20 | n |  | TRUE
82 | bus_MV_535_0_node_61 | 20 | n |  | TRUE
83 | bus_MV_535_0_node_60 | 20 | n |  | TRUE
84 | bus_MV_535_0_node_99 | 20 | n |  | TRUE
85 | bus_MV_535_0_node_161 | 20 | n |  | TRUE
86 | bus_MV_535_0_node_101 | 20 | n |  | TRUE
87 | bus_MV_535_0_node_43 | 20 | n |  | TRUE
88 | bus_MV_535_0_node_45 | 20 | n |  | TRUE
89 | bus_MV_535_0_node_44 | 20 | n |  | TRUE
90 | bus_MV_535_0_node_48 | 20 | n |  | TRUE
91 | bus_MV_535_0_node_47 | 20 | n |  | TRUE
92 | bus_MV_535_0_node_126 | 20 | n |  | TRUE
93 | bus_MV_535_0_node_177 | 20 | n |  | TRUE
94 | bus_MV_535_0_node_164 | 20 | n |  | TRUE
95 | bus_MV_535_0_node_64 | 20 | n |  | TRUE
96 | bus_MV_535_0_node_191 | 20 | n |  | TRUE
97 | bus_MV_535_0_node_162 | 20 | n |  | TRUE
98 | bus_MV_535_0_node_49 | 20 | n |  | TRUE
99 | bus_MV_535_0_node_50 | 20 | n |  | TRUE
100 | bus_MV_535_0_node_52 | 20 | n |  | TRUE
101 | bus_MV_535_0_node_53 | 20 | n |  | TRUE
102 | bus_MV_535_0_node_204 | 20 | n |  | TRUE
103 | bus_MV_535_0_node_85 | 20 | n |  | TRUE
104 | bus_MV_535_0_node_170 | 20 | n |  | TRUE
105 | bus_MV_535_0_node_137 | 20 | n |  | TRUE
106 | bus_MV_535_0_node_196 | 20 | n |  | TRUE
107 | bus_MV_535_0_node_205 | 20 | n |  | TRUE
108 | bus_MV_535_0_node_86 | 20 | n |  | TRUE
109 | bus_MV_535_0_node_84 | 20 | n |  | TRUE
110 | bus_MV_535_0_node_62 | 20 | n |  | TRUE
111 | bus_MV_535_0_node_63 | 20 | n |  | TRUE
112 | bus_MV_535_0_node_65 | 20 | n |  | TRUE
113 | bus_MV_535_0_node_178 | 20 | n |  | TRUE
114 | bus_MV_535_0_node_67 | 20 | n |  | TRUE
115 | bus_MV_535_0_node_68 | 20 | n |  | TRUE
116 | bus_MV_535_0_node_69 | 20 | n |  | TRUE
117 | bus_MV_535_0_node_70 | 20 | n |  | TRUE
118 | bus_MV_535_0_node_71 | 20 | n |  | TRUE
119 | bus_MV_535_0_node_140 | 20 | n |  | TRUE
120 | bus_MV_535_0_node_125 | 20 | n |  | TRUE
121 | bus_MV_535_0_node_182 | 20 | n |  | TRUE
122 | bus_MV_535_0_node_72 | 20 | n |  | TRUE
123 | bus_MV_535_0_node_181 | 20 | n |  | TRUE
124 | bus_MV_535_0_node_154 | 20 | n |  | TRUE
125 | bus_MV_535_0_node_180 | 20 | n |  | TRUE
126 | bus_MV_535_0_node_141 | 20 | n |  | TRUE
127 | bus_MV_535_0_node_185 | 20 | n |  | TRUE
128 | bus_MV_535_0_node_184 | 20 | n |  | TRUE
129 | bus_MV_535_0_node_153 | 20 | n |  | TRUE
130 | bus_MV_535_0_node_73 | 20 | n |  | TRUE
131 | bus_MV_535_0_node_129 | 20 | n |  | TRUE
132 | bus_MV_535_0_node_130 | 20 | n |  | TRUE
133 | bus_MV_535_0_node_82 | 20 | n |  | TRUE
134 | bus_MV_535_0_node_83 | 20 | n |  | TRUE
135 | bus_MV_535_0_node_115 | 20 | n |  | TRUE
136 | bus_MV_535_0_node_203 | 20 | n |  | TRUE
137 | bus_MV_535_0_node_173 | 20 | n |  | TRUE
138 | bus_MV_535_0_node_123 | 20 | n |  | TRUE
139 | bus_MV_535_0_node_89 | 20 | n |  | TRUE
140 | bus_MV_535_0_node_91 | 20 | n |  | TRUE
141 | bus_MV_535_0_node_93 | 20 | n |  | TRUE
142 | bus_MV_535_0_node_197 | 20 | n |  | TRUE
143 | bus_MV_535_0_node_158 | 20 | n |  | TRUE
144 | bus_MV_535_0_node_156 | 20 | n |  | TRUE
145 | bus_MV_535_0_node_159 | 20 | n |  | TRUE
146 | bus_MV_535_0_node_157 | 20 | n |  | TRUE
147 | bus_MV_535_0_node_103 | 20 | n |  | TRUE
148 | bus_MV_535_0_node_104 | 20 | n |  | TRUE
149 | bus_MV_535_0_node_175 | 20 | n |  | TRUE
150 | bus_MV_535_0_node_183 | 20 | n |  | TRUE
151 | bus_MV_535_0_node_105 | 20 | n |  | TRUE
152 | bus_MV_535_0_node_106 | 20 | n |  | TRUE
153 | bus_MV_535_0_node_107 | 20 | n |  | TRUE
154 | bus_MV_535_0_node_168 | 20 | n |  | TRUE
155 | bus_MV_535_0_node_167 | 20 | n |  | TRUE
156 | bus_MV_535_0_node_108 | 20 | n |  | TRUE
157 | bus_MV_535_0_node_109 | 20 | n |  | TRUE
158 | bus_MV_535_0_node_110 | 20 | n |  | TRUE
159 | bus_MV_535_0_node_114 | 20 | n |  | TRUE
160 | bus_MV_535_0_node_111 | 20 | n |  | TRUE
161 | bus_MV_535_0_node_113 | 20 | n |  | TRUE
162 | bus_MV_535_0_node_174 | 20 | n |  | TRUE
163 | bus_MV_535_0_node_193 | 20 | n |  | TRUE
164 | bus_MV_535_0_node_112 | 20 | n |  | TRUE
165 | bus_MV_535_0_node_133 | 20 | n |  | TRUE
166 | bus_MV_535_0_node_200 | 20 | n |  | TRUE
167 | bus_MV_535_0_node_189 | 20 | n |  | TRUE
168 | bus_MV_535_0_node_118 | 20 | n |  | TRUE
169 | bus_MV_535_0_node_166 | 20 | n |  | TRUE
170 | bus_MV_535_0_node_132 | 20 | n |  | TRUE
171 | bus_MV_535_0_node_119 | 20 | n |  | TRUE
172 | bus_MV_535_0_node_117 | 20 | n |  | TRUE
173 | bus_MV_535_0_node_120 | 20 | n |  | TRUE
174 | bus_MV_535_0_node_121 | 20 | n |  | TRUE
175 | bus_MV_535_0_node_122 | 20 | n |  | TRUE
176 | bus_MV_535_0_node_124 | 20 | n |  | TRUE
177 | bus_MV_535_0_node_131 | 20 | n |  | TRUE
178 | bus_MV_535_0_node_142 | 20 | n |  | TRUE
179 | bus_MV_535_0_node_146 | 20 | n |  | TRUE
180 | bus_MV_535_0_node_147 | 20 | n |  | TRUE
181 | bus_MV_535_0_node_148 | 20 | n |  | TRUE
182 | bus_MV_535_0_node_195 | 20 | n |  | TRUE
183 | bus_MV_535_0_node_194 | 20 | n |  | TRUE
184 | bus_MV_535_0_node_176 | 20 | n |  | TRUE
185 | bus_MV_535_0_node_152 | 20 | n |  | TRUE
186 | bus_MV_535_0_node_150 | 20 | n |  | TRUE
187 | bus_MV_535_0_node_151 | 20 | n |  | TRUE
188 | bus_MV_535_0_node_163 | 20 | n |  | TRUE
189 | bus_MV_535_0_node_201 | 20 | n |  | TRUE
190 | bus_MV_535_0_node_188 | 20 | n |  | TRUE
191 | bus_MV_535_0_node_169 | 20 | n |  | TRUE
192 | bus_MV_535_0_node_179 | 20 | n |  | TRUE
193 | bus_MV_535_0_node_187 | 20 | n |  | TRUE
194 | bus_MV_535_0_node_192 | 20 | n |  | TRUE
195 | bus_MV_535_0_node_186 | 20 | n |  | TRUE
196 | bus_HV_535_0_node_37 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_535_0_load_0 | 0 | 0.35067 | 0.16984 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_535_0_load_81 | 5 | 0.089672 | 0.04343 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_535_0_load_79 | 7 | 0.40235 | 0.19487 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_535_0_load_128 | 8 | 0.11062 | 0.053575 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_535_0_load_94 | 9 | 0.36714 | 0.17781 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_535_0_load_134 | 11 | 0.11314 | 0.054796 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_535_0_load_8 | 12 | 0.40112 | 0.19427 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_535_0_load_165 | 15 | 0.083363 | 0.040375 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_535_0_load_9 | 19 | 0.3739 | 0.18109 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_535_0_load_97 | 24 | 0.27861 | 0.13494 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_535_0_load_155 | 26 | 0.093071 | 0.045077 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_535_0_load_13 | 27 | 0.24581 | 0.11905 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_535_0_load_87 | 28 | 0.30123 | 0.14589 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_535_0_load_57 | 31 | 0.34857 | 0.16882 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_535_0_load_143 | 35 | 0.12313 | 0.059634 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_535_0_load_58 | 37 | 0.32343 | 0.15664 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_535_0_load_199 | 38 | 0.38939 | 0.18859 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_535_0_load_92 | 43 | 0.40279 | 0.19508 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_535_0_load_202 | 44 | 0.28277 | 0.13695 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_535_0_load_19 | 45 | 0.28531 | 0.13818 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_535_0_load_145 | 54 | 0.12798 | 0.061982 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_535_0_load_26 | 55 | 0.39738 | 0.19246 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_535_0_load_172 | 57 | 0.080894 | 0.039179 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_535_0_load_29 | 58 | 0.082026 | 0.039727 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_535_0_load_76 | 61 | 0.35438 | 0.17163 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_535_0_load_127 | 62 | 0.19895 | 0.096354 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_535_0_load_171 | 63 | 0.077895 | 0.037726 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_535_0_load_34 | 64 | 0.26595 | 0.1288 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_535_0_load_198 | 70 | 0.34594 | 0.16755 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_535_0_load_138 | 72 | 0.082618 | 0.040014 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_535_0_load_37 | 73 | 0.32896 | 0.15932 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_535_0_load_190 | 74 | 0.34088 | 0.1651 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_535_0_load_135 | 75 | 0.11515 | 0.055771 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_535_0_load_66 | 76 | 0.40497 | 0.19614 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_535_0_load_160 | 81 | 0.16027 | 0.077623 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_535_0_load_60 | 83 | 0.34814 | 0.16861 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_535_0_load_99 | 84 | 0.17682 | 0.085636 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_535_0_load_101 | 86 | 0.33413 | 0.16183 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_535_0_load_43 | 87 | 0.23525 | 0.11394 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_535_0_load_126 | 92 | 0.32993 | 0.15979 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_535_0_load_177 | 93 | 0.085085 | 0.041208 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_535_0_load_191 | 96 | 0.09392 | 0.045488 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_535_0_load_49 | 98 | 0.37313 | 0.18071 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_535_0_load_204 | 102 | 0.35384 | 0.17137 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_535_0_load_170 | 104 | 0.086892 | 0.042084 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_535_0_load_137 | 105 | 0.18869 | 0.091387 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_535_0_load_196 | 106 | 0.41141 | 0.19925 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_535_0_load_205 | 107 | 0.11413 | 0.055278 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_535_0_load_86 | 108 | 0.071449 | 0.034604 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_535_0_load_84 | 109 | 0.31457 | 0.15235 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_535_0_load_62 | 110 | 0.30994 | 0.15011 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_535_0_load_178 | 113 | 0.069649 | 0.033732 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_535_0_load_67 | 114 | 0.30219 | 0.14636 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_535_0_load_140 | 119 | 0.080994 | 0.039227 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_535_0_load_125 | 120 | 0.36263 | 0.17563 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_535_0_load_181 | 123 | 0.075798 | 0.036711 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_535_0_load_180 | 125 | 0.10973 | 0.053147 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_535_0_load_184 | 128 | 0.1415 | 0.068532 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_535_0_load_153 | 129 | 0.089953 | 0.043566 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_535_0_load_73 | 130 | 0.40123 | 0.19432 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_535_0_load_129 | 131 | 0.087901 | 0.042573 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_535_0_load_115 | 135 | 0.37129 | 0.17982 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_535_0_load_203 | 136 | 0.088465 | 0.042846 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_535_0_load_173 | 137 | 0.10111 | 0.04897 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_535_0_load_123 | 138 | 0.17523 | 0.084869 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_535_0_load_93 | 141 | 0.32897 | 0.15933 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_535_0_load_197 | 142 | 0.25821 | 0.12506 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_535_0_load_156 | 144 | 0.11908 | 0.057672 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_535_0_load_159 | 145 | 0.076082 | 0.036848 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_535_0_load_175 | 149 | 0.14781 | 0.071587 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_535_0_load_183 | 150 | 0.098945 | 0.047921 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_535_0_load_105 | 151 | 0.28454 | 0.13781 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_535_0_load_107 | 153 | 0.071642 | 0.034698 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_535_0_load_108 | 156 | 0.28416 | 0.13763 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_535_0_load_174 | 162 | 0.12496 | 0.060521 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_535_0_load_193 | 163 | 0.4434 | 0.21475 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_535_0_load_200 | 166 | 0.11348 | 0.05496 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_535_0_load_189 | 167 | 0.14725 | 0.071315 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_535_0_load_118 | 168 | 0.22508 | 0.10901 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_535_0_load_166 | 169 | 0.083635 | 0.040506 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_535_0_load_122 | 175 | 0.24602 | 0.11916 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_535_0_load_124 | 176 | 0.088025 | 0.042632 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_535_0_load_131 | 177 | 0.15178 | 0.073512 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_535_0_load_142 | 178 | 0.12174 | 0.05896 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_535_0_load_146 | 179 | 0.13772 | 0.066699 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_535_0_load_195 | 182 | 0.38711 | 0.18749 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_535_0_load_176 | 184 | 0.094497 | 0.045767 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_535_0_load_150 | 186 | 0.069869 | 0.033839 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_535_0_load_201 | 189 | 0.072418 | 0.035074 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_535_0_load_188 | 190 | 0.14832 | 0.071836 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_535_0_load_179 | 192 | 0.19287 | 0.09341 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_535_0_load_192 | 194 | 0.70754 | 0.34268 | 0 | 0 |  | 1 | TRUE | wye
92 | MV_535_0_load_186 | 195 | 0.42325 | 0.20499 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 73 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_535_0_line_0 |  | 0 | 1 | 0.004628 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_535_0_line_1 |  | 1 | 2 | 0.004898 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_535_0_line_2 |  | 1 | 3 | 0.068843 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_535_0_line_3 |  | 2 | 9 | 0.080198 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_535_0_line_4 |  | 3 | 10 | 0.071219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_535_0_line_5 |  | 3 | 11 | 0.022784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_535_0_line_6 |  | 4 | 5 | 0.026306 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
7 | MV_535_0_line_7 |  | 4 | 6 | 0.14496 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
8 | MV_535_0_line_8 |  | 4 | 7 | 0.024402 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_535_0_line_9 |  | 5 | 13 | 0.026793 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
10 | MV_535_0_line_10 |  | 6 | 8 | 0.027557 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
11 | MV_535_0_line_11 |  | 7 | 14 | 0.037661 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_535_0_line_12 |  | 8 | 15 | 0.043367 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
13 | MV_535_0_line_13 |  | 9 | 16 | 0.021127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_535_0_line_14 |  | 10 | 12 | 0.015098 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_535_0_line_15 |  | 13 | 89 | 0.028147 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
16 | MV_535_0_line_16 |  | 14 | 133 | 0.083035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_535_0_line_17 |  | 15 | 132 | 0.021375 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
18 | MV_535_0_line_18 |  | 16 | 17 | 0.092878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_535_0_line_19 |  | 16 | 18 | 0.042298 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_535_0_line_20 |  | 17 | 131 | 0.028133 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_535_0_line_21 |  | 17 | 132 | 0.054337 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
22 | MV_535_0_line_22 |  | 17 | 77 | 0.11876 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
23 | MV_535_0_line_23 |  | 18 | 130 | 0.023629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_535_0_line_24 |  | 19 | 20 | 0.004393 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_535_0_line_25 |  | 20 | 21 | 0.044189 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_535_0_line_26 |  | 21 | 25 | 0.094943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_535_0_line_27 |  | 21 | 26 | 0.058768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_535_0_line_28 |  | 21 | 22 | 0.13617 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_535_0_line_29 |  | 22 | 23 | 0.20102 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_535_0_line_30 |  | 22 | 24 | 0.063546 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_535_0_line_31 |  | 23 | 142 | 0.004889 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_535_0_line_32 |  | 25 | 27 | 0.11674 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_535_0_line_33 |  | 26 | 28 | 0.12476 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_535_0_line_34 |  | 27 | 29 | 0.006604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_535_0_line_35 |  | 29 | 30 | 0.036072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_535_0_line_36 |  | 30 | 31 | 0.06058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_535_0_line_37 |  | 31 | 40 | 0.15632 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_535_0_line_38 |  | 31 | 41 | 0.10978 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_535_0_line_39 |  | 32 | 33 | 0.16508 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_535_0_line_40 |  | 32 | 34 | 0.072977 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_535_0_line_41 |  | 32 | 35 | 0.032832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_535_0_line_42 |  | 33 | 38 | 0.046392 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_535_0_line_43 |  | 33 | 39 | 0.096486 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_535_0_line_44 |  | 34 | 36 | 0.072043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_535_0_line_45 |  | 34 | 37 | 0.005956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_535_0_line_46 |  | 35 | 42 | 0.029926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_535_0_line_47 |  | 36 | 43 | 0.007324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_535_0_line_48 |  | 39 | 44 | 0.019649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_535_0_line_49 |  | 39 | 40 | 0.16795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_535_0_line_50 |  | 40 | 105 | 0.029328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_535_0_line_51 |  | 40 | 69 | 0.15326 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
52 | MV_535_0_line_52 |  | 40 | 99 | 0.15777 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_535_0_line_53 |  | 40 | 100 | 0.24486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_535_0_line_54 |  | 41 | 106 | 0.006377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_535_0_line_55 |  | 42 | 147 | 0.041279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_535_0_line_56 |  | 44 | 76 | 0.068864 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_535_0_line_57 |  | 45 | 46 | 0.004287 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
58 | MV_535_0_line_58 |  | 45 | 47 | 0.026127 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
59 | MV_535_0_line_59 |  | 45 | 48 | 0.049151 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
60 | MV_535_0_line_60 |  | 46 | 49 | 0.003389 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
61 | MV_535_0_line_61 |  | 47 | 50 | 0.031539 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
62 | MV_535_0_line_62 |  | 48 | 51 | 0.015043 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_535_0_line_63 |  | 49 | 54 | 0.028908 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
64 | MV_535_0_line_64 |  | 50 | 58 | 0.028774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_535_0_line_65 |  | 50 | 59 | 0.052496 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
66 | MV_535_0_line_66 |  | 51 | 56 | 0.070274 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_535_0_line_67 |  | 51 | 57 | 0.017047 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
68 | MV_535_0_line_68 |  | 52 | 53 | 0.016733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_535_0_line_69 |  | 52 | 54 | 0.062658 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
70 | MV_535_0_line_70 |  | 52 | 55 | 0.05816 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
71 | MV_535_0_line_71 |  | 53 | 74 | 0.044302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_535_0_line_72 |  | 55 | 65 | 0.004704 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
73 | MV_535_0_line_73 |  | 56 | 62 | 0.036057 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_535_0_line_74 |  | 56 | 60 | 0.076282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_535_0_line_75 |  | 57 | 63 | 0.046922 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
76 | MV_535_0_line_76 |  | 59 | 64 | 0.004057 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_535_0_line_77 |  | 60 | 61 | 0.004327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_535_0_line_78 |  | 63 | 77 | 0.020802 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_535_0_line_79 |  | 64 | 67 | 0.007849 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_535_0_line_80 |  | 65 | 66 | 0.069879 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_535_0_line_81 |  | 66 | 73 | 0.004023 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
82 | MV_535_0_line_82 |  | 67 | 68 | 0.05399 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
83 | MV_535_0_line_83 |  | 68 | 75 | 0.020287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_535_0_line_84 |  | 68 | 70 | 0.080619 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
85 | MV_535_0_line_85 |  | 69 | 70 | 0.011684 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
86 | MV_535_0_line_86 |  | 69 | 71 | 0.028906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_535_0_line_87 |  | 71 | 72 | 0.0068383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_535_0_line_88 |  | 78 | 79 | 0.15388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_535_0_line_89 |  | 78 | 80 | 0.006285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_535_0_line_90 |  | 78 | 81 | 0.025434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_535_0_line_91 |  | 79 | 82 | 0.11666 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_535_0_line_92 |  | 79 | 83 | 0.023173 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
93 | MV_535_0_line_93 |  | 80 | 84 | 0.006292 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_535_0_line_94 |  | 81 | 85 | 0.030794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_535_0_line_95 |  | 82 | 86 | 0.007004 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_535_0_line_96 |  | 85 | 97 | 0.09079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_535_0_line_97 |  | 85 | 188 | 0.023751 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_535_0_line_98 |  | 87 | 88 | 0.007875 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
99 | MV_535_0_line_99 |  | 87 | 89 | 0.065469 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
100 | MV_535_0_line_100 |  | 88 | 90 | 0.015776 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_535_0_line_101 |  | 89 | 91 | 0.078226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_535_0_line_102 |  | 90 | 93 | 0.024358 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_535_0_line_103 |  | 90 | 94 | 0.062303 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
104 | MV_535_0_line_104 |  | 91 | 92 | 0.004838 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_535_0_line_105 |  | 92 | 95 | 0.051254 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
106 | MV_535_0_line_106 |  | 94 | 96 | 0.024327 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_535_0_line_107 |  | 94 | 97 | 0.15407 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
108 | MV_535_0_line_108 |  | 95 | 112 | 0.013651 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_535_0_line_109 |  | 97 | 189 | 0.006496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_535_0_line_110 |  | 97 | 183 | 0.18594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_535_0_line_111 |  | 98 | 99 | 0.008625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_535_0_line_112 |  | 100 | 101 | 0.085266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_535_0_line_113 |  | 100 | 102 | 0.024656 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_535_0_line_114 |  | 101 | 103 | 0.0122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_535_0_line_115 |  | 101 | 104 | 0.024181 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_535_0_line_116 |  | 102 | 107 | 0.058578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_535_0_line_117 |  | 103 | 108 | 0.052753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_535_0_line_118 |  | 103 | 109 | 0.036273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_535_0_line_119 |  | 110 | 111 | 0.005195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_535_0_line_120 |  | 111 | 112 | 0.016471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_535_0_line_121 |  | 112 | 113 | 0.017422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_535_0_line_122 |  | 114 | 115 | 0.008471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_535_0_line_123 |  | 115 | 116 | 0.092706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_535_0_line_124 |  | 115 | 117 | 0.085124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_535_0_line_125 |  | 116 | 118 | 0.073038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_535_0_line_126 |  | 116 | 119 | 0.022722 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_535_0_line_127 |  | 117 | 120 | 0.037398 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
128 | MV_535_0_line_128 |  | 118 | 121 | 0.035202 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_535_0_line_129 |  | 118 | 122 | 0.13118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_535_0_line_130 |  | 118 | 123 | 0.00897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_535_0_line_131 |  | 119 | 126 | 0.012637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_535_0_line_132 |  | 121 | 127 | 1.1439 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_535_0_line_133 |  | 121 | 128 | 0.011311 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_535_0_line_134 |  | 122 | 124 | 0.035455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_535_0_line_135 |  | 122 | 125 | 0.024137 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_535_0_line_136 |  | 124 | 129 | 0.038225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_535_0_line_137 |  | 126 | 178 | 0.012328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_535_0_line_138 |  | 127 | 193 | 0.012572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_535_0_line_139 |  | 127 | 194 | 0.038651 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_535_0_line_140 |  | 129 | 187 | 0.062444 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_535_0_line_141 |  | 133 | 134 | 0.16288 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_535_0_line_142 |  | 133 | 135 | 0.005336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_535_0_line_143 |  | 134 | 136 | 0.0415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_535_0_line_144 |  | 135 | 137 | 0.071693 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_535_0_line_145 |  | 136 | 138 | 0.044724 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
146 | MV_535_0_line_146 |  | 137 | 173 | 0.036545 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_535_0_line_147 |  | 139 | 140 | 0.073605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_535_0_line_148 |  | 139 | 141 | 0.011998 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_535_0_line_149 |  | 140 | 143 | 0.001586 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_535_0_line_150 |  | 140 | 144 | 0.044749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_535_0_line_151 |  | 143 | 145 | 0.047294 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_535_0_line_152 |  | 144 | 146 | 0.029149 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_535_0_line_153 |  | 146 | 148 | 0.019667 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_535_0_line_154 |  | 147 | 148 | 0.049262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_535_0_line_155 |  | 147 | 149 | 0.04458 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_535_0_line_156 |  | 148 | 150 | 0.015219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_535_0_line_157 |  | 151 | 152 | 0.028226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_535_0_line_158 |  | 152 | 153 | 0.021845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_535_0_line_159 |  | 153 | 154 | 0.031324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_535_0_line_160 |  | 154 | 155 | 0.007863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_535_0_line_161 |  | 155 | 191 | 0.036167 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_535_0_line_162 |  | 155 | 169 | 0.016132 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_535_0_line_163 |  | 156 | 157 | 0.00478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_535_0_line_164 |  | 157 | 158 | 0.073177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_535_0_line_165 |  | 157 | 159 | 0.19475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_535_0_line_166 |  | 158 | 160 | 0.23258 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_535_0_line_167 |  | 158 | 161 | 0.048841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_535_0_line_168 |  | 158 | 162 | 0.022202 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_535_0_line_169 |  | 159 | 168 | 0.00251 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_535_0_line_170 |  | 160 | 163 | 0.002986 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_535_0_line_171 |  | 160 | 164 | 0.21279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_535_0_line_172 |  | 160 | 165 | 0.065398 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_535_0_line_173 |  | 161 | 167 | 0.047504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_535_0_line_174 |  | 164 | 166 | 0.018779 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_535_0_line_175 |  | 165 | 169 | 0.023504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_535_0_line_176 |  | 165 | 170 | 0.049864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_535_0_line_177 |  | 168 | 171 | 0.004632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_535_0_line_178 |  | 168 | 172 | 0.048482 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
179 | MV_535_0_line_179 |  | 170 | 177 | 0.012003 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_535_0_line_180 |  | 171 | 174 | 0.009085 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_535_0_line_181 |  | 172 | 173 | 0.044774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
182 | MV_535_0_line_182 |  | 174 | 175 | 0.003953 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
183 | MV_535_0_line_183 |  | 175 | 176 | 0.014969 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
184 | MV_535_0_line_184 |  | 179 | 180 | 0.033672 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
185 | MV_535_0_line_185 |  | 180 | 181 | 0.0219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
186 | MV_535_0_line_186 |  | 181 | 184 | 0.057113 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
187 | MV_535_0_line_187 |  | 181 | 182 | 0.067948 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
188 | MV_535_0_line_188 |  | 182 | 183 | 0.007482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
189 | MV_535_0_line_189 |  | 184 | 185 | 0.030818 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
190 | MV_535_0_line_190 |  | 185 | 187 | 0.014329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
191 | MV_535_0_line_191 |  | 186 | 187 | 0.023632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
192 | MV_535_0_line_192 |  | 188 | 190 | 0.022542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
193 | MV_535_0_line_193 |  | 191 | 192 | 0.027708 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
194 | MV_535_0_line_194 |  | 193 | 195 | 0.057039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_535_0_trafo_37 | 25 MVA 110/20 kV | 196 | 73 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2682278.3109 | 1247859.1386
1 | 2682281.5734 | 1247862.4307
2 | 2682284.9983 | 1247858.9201
3 | 2682330.8137 | 1247899.2412
4 | 2682157.9344 | 1247831.6495
5 | 2682135.3595 | 1247845.1533
6 | 2682224.2652 | 1247791.9174
7 | 2682170.3623 | 1247852.6705
8 | 2682245.7426 | 1247774.6512
9 | 2682337.8988 | 1247798.6434
10 | 2682352.5703 | 1247945.6886
11 | 2682347.3105 | 1247883.5255
12 | 2682358.8509 | 1247958.4296
13 | 2682113.1432 | 1247860.1167
14 | 2682172.2426 | 1247890.2797
15 | 2682287.616 | 1247785.9348
16 | 2682351.1344 | 1247782.1484
17 | 2682293.8363 | 1247732.1273
18 | 2682378.6812 | 1247750.0518
19 | 2681924.2645 | 1247008.847
20 | 2681920.8738 | 1247006.0425
21 | 2681891.7761 | 1247033.3273
22 | 2681803.5487 | 1246929.6006
23 | 2681805.3077 | 1246842.6613
24 | 2681765.3118 | 1246980.3549
25 | 2681963.8081 | 1247077.8216
26 | 2681854.3995 | 1247078.6762
27 | 2682030.7651 | 1247173.4506
28 | 2681744.2802 | 1247137.3177
29 | 2682026.6148 | 1247178.597
30 | 2682036.2877 | 1247204.5053
31 | 2682071.2605 | 1247253.703
32 | 2681900.8346 | 1247272.661
33 | 2682032.1215 | 1247312.3045
34 | 2681894.3247 | 1247232.6529
35 | 2681877.5591 | 1247295.817
36 | 2681835.3761 | 1247214.5148
37 | 2681897.0043 | 1247227.3305
38 | 2682004.2712 | 1247349.4132
39 | 2682105.5757 | 1247374.8668
40 | 2682216.0499 | 1247312.6183
41 | 2682176.6036 | 1247222.7946
42 | 2681856.3436 | 1247316.9237
43 | 2681828.9127 | 1247211.0342
44 | 2682095.6942 | 1247391.8647
45 | 2682269.6041 | 1247552.1478
46 | 2682266.5931 | 1247555.2083
47 | 2682275.2757 | 1247526.6522
48 | 2682303.6689 | 1247587.5798
49 | 2682264.1509 | 1247557.565
50 | 2682257.6555 | 1247520.5255
51 | 2682294.6342 | 1247599.6077
52 | 2682195.1332 | 1247614.372
53 | 2682189.8002 | 1247626.3736
54 | 2682243.6601 | 1247574.7347
55 | 2682153.0885 | 1247575.3497
56 | 2682336.1358 | 1247622.7341
57 | 2682284.5145 | 1247613.3262
58 | 2682255.485 | 1247546.1521
59 | 2682263.29 | 1247485.1777
60 | 2682352.1229 | 1247673.5156
61 | 2682355.1158 | 1247676.6484
62 | 2682360.5332 | 1247596.1852
63 | 2682256.6602 | 1247651.0859
64 | 2682265.4826 | 1247481.7612
65 | 2682148.9924 | 1247577.6835
66 | 2682094.742 | 1247584.3817
67 | 2682272.2197 | 1247480.7206
68 | 2682308.8599 | 1247462.3599
69 | 2682293.7823 | 1247373.7523
70 | 2682302.0519 | 1247382.0287
71 | 2682273.0583 | 1247388.2087
72 | 2682266.4258 | 1247389.8735
73 | 2682091.1146 | 1247586.1439
74 | 2682158.1118 | 1247657.3285
75 | 2682319.6655 | 1247479.4669
76 | 2682107.1868 | 1247459.7625
77 | 2682244.3112 | 1247667.8264
78 | 2681983.2544 | 1247643.8942
79 | 2681952.435 | 1247556.1038
80 | 2681986.9989 | 1247648.9497
81 | 2681964.8482 | 1247661.4257
82 | 2681977.8014 | 1247469.6799
83 | 2681967.6628 | 1247573.5715
84 | 2681991.3316 | 1247653.5241
85 | 2681942.8628 | 1247682.9869
86 | 2681974.8528 | 1247463.3234
87 | 2682030.9772 | 1247898.0852
88 | 2682027.358 | 1247891.0856
89 | 2682090.8024 | 1247871.4935
90 | 2682017.337 | 1247884.9536
91 | 2682062.412 | 1247800.4929
92 | 2682060.4871 | 1247796.0519
93 | 2681995.3887 | 1247895.5175
94 | 2681990.8586 | 1247828.5571
95 | 2682038.7194 | 1247749.65
96 | 2681968.7444 | 1247838.6936
97 | 2681910.3716 | 1247740.7137
98 | 2682338.5896 | 1247303.1335
99 | 2682337.6191 | 1247295.2365
100 | 2682354.0578 | 1247207.0444
101 | 2682364.163 | 1247143.5827
102 | 2682369.2578 | 1247226.492
103 | 2682355.5355 | 1247134.9565
104 | 2682380.4844 | 1247161.4033
105 | 2682234.76 | 1247335.2
106 | 2682180.8768 | 1247218.0503
107 | 2682405.8112 | 1247248.1935
108 | 2682326.6408 | 1247179.0919
109 | 2682329.8386 | 1247109.2809
110 | 2682043.5765 | 1247731.0702
111 | 2682045.8838 | 1247735.7278
112 | 2682032.916 | 1247737.294
113 | 2682017.1556 | 1247744.7186
114 | 2681869.8683 | 1247629.4172
115 | 2681869.5849 | 1247620.9515
116 | 2681811.8199 | 1247636.0766
117 | 2681827.4493 | 1247575.2365
118 | 2681771.7363 | 1247607.4917
119 | 2681816.9603 | 1247658.2082
120 | 2681800.3792 | 1247549.433
121 | 2681748.8021 | 1247585.2147
122 | 2681719.6667 | 1247645.6242
123 | 2681776.872 | 1247600.1508
124 | 2681712.3276 | 1247669.5295
125 | 2681696.7405 | 1247653.1727
126 | 2681810.968 | 1247669.3337
127 | 2681626.5909 | 1247695.8458
128 | 2681757.1376 | 1247577.6516
129 | 2681723.9834 | 1247705.9344
130 | 2682395.727 | 1247766.4674
131 | 2682274.1225 | 1247712.0563
132 | 2682303.9159 | 1247772.1077
133 | 2682153.5307 | 1247958.0703
134 | 2682252.6058 | 1247973.5662
135 | 2682154.9472 | 1247963.2159
136 | 2682239.4141 | 1248001.0923
137 | 2682118.0002 | 1248024.6559
138 | 2682268.5272 | 1248035.0433
139 | 2681739.4548 | 1247341.2404
140 | 2681769.326 | 1247300.9783
141 | 2681748.7017 | 1247348.8862
142 | 2681808.2549 | 1246838.7546
143 | 2681767.9702 | 1247300.1479
144 | 2681807.5762 | 1247324.1891
145 | 2681798.7801 | 1247264.2666
146 | 2681832.1804 | 1247339.8181
147 | 2681855.8419 | 1247349.4183
148 | 2681820.5267 | 1247355.5689
149 | 2681887.2086 | 1247317.7405
150 | 2681809.6057 | 1247366.1679
151 | 2682598.3277 | 1247994.3979
152 | 2682617.6473 | 1248015.0267
153 | 2682601.2232 | 1248029.4307
154 | 2682577.6725 | 1248050.0846
155 | 2682571.7468 | 1248055.2726
156 | 2682302.4152 | 1248083.5381
157 | 2682305.0638 | 1248087.5223
158 | 2682344.175 | 1248138.3805
159 | 2682186.9731 | 1248083.9929
160 | 2682518.1911 | 1248045.4421
161 | 2682373.9245 | 1248172.0962
162 | 2682326.1615 | 1248151.3587
163 | 2682519.1874 | 1248048.2024
164 | 2682366.0616 | 1248049.3411
165 | 2682544.7726 | 1248026.2312
166 | 2682376.7376 | 1248064.8119
167 | 2682395.4306 | 1248142.2978
168 | 2682186.2056 | 1248081.6028
169 | 2682560.7681 | 1248043.4525
170 | 2682520.5923 | 1247990.7019
171 | 2682190.4682 | 1248079.7605
172 | 2682168.5845 | 1248036.4365
173 | 2682134.7198 | 1248057.0047
174 | 2682196.2009 | 1248082.4753
175 | 2682197.706 | 1248086.1322
176 | 2682203.1663 | 1248100.0683
177 | 2682529.1205 | 1247982.2561
178 | 2681819.7787 | 1247677.9562
179 | 2681746.9833 | 1247877.0058
180 | 2681776.9383 | 1247861.6277
181 | 2681788.1304 | 1247856.2558
182 | 2681848.5605 | 1247825.189
183 | 2681855.2392 | 1247821.7787
184 | 2681762.7897 | 1247805.242
185 | 2681749.3748 | 1247777.497
186 | 2681769.4636 | 1247756.5095
187 | 2681747.0387 | 1247763.966
188 | 2681929.2973 | 1247690.0824
189 | 2681913.0542 | 1247746.6329
190 | 2681908.7165 | 1247699.2792
191 | 2682586.7845 | 1248070.9825
192 | 2682606.1966 | 1248090.7536
193 | 2681614.5397 | 1247699.4159
194 | 2681638.5006 | 1247732.6156
195 | 2681596.339 | 1247753.3926
196 | 2682091.1146 | 1247586.1439

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99806 | -0.037136 | 0.35067 | 0.16984
1 | 0.99806 | -0.037156 | 0 | 0
2 | 0.99807 | -0.037205 | 0 | 0
3 | 0.99801 | -0.036746 | 0 | 0
4 | 0.99792 | -0.04766 | 0 | 0
5 | 0.99789 | -0.047762 | 0.089672 | 0.04343
6 | 0.99813 | -0.046738 | 0 | 0
7 | 0.9978 | -0.046666 | 0.40235 | 0.19487
8 | 0.99817 | -0.046561 | 0.11062 | 0.053575
9 | 0.9982 | -0.036333 | 0.36714 | 0.17781
10 | 0.99798 | -0.036408 | 0 | 0
11 | 0.99801 | -0.036715 | 0.11314 | 0.054796
12 | 0.99797 | -0.036335 | 0.40112 | 0.19427
13 | 0.99787 | -0.047864 | 0 | 0
14 | 0.99765 | -0.045312 | 0 | 0
15 | 0.99831 | -0.038913 | 0.083363 | 0.040375
16 | 0.99823 | -0.036639 | 0 | 0
17 | 0.99843 | -0.038414 | 0 | 0
18 | 0.99821 | -0.036438 | 0 | 0
19 | 0.99669 | -0.045988 | 0.3739 | 0.18109
20 | 0.99669 | -0.046008 | 0 | 0
21 | 0.99671 | -0.046205 | 0 | 0
22 | 0.99657 | -0.047153 | 0 | 0
23 | 0.9965 | -0.04656 | 0 | 0
24 | 0.99653 | -0.047369 | 0.27861 | 0.13494
25 | 0.99687 | -0.047643 | 0 | 0
26 | 0.99668 | -0.045929 | 0.093071 | 0.045077
27 | 0.99716 | -0.045689 | 0.24581 | 0.11905
28 | 0.99661 | -0.046387 | 0.30123 | 0.14589
29 | 0.99717 | -0.045808 | 0 | 0
30 | 0.99725 | -0.046456 | 0 | 0
31 | 0.99737 | -0.047541 | 0.34857 | 0.16882
32 | 0.99677 | -0.037237 | 0 | 0
33 | 0.99711 | -0.040285 | 0 | 0
34 | 0.9967 | -0.036612 | 0 | 0
35 | 0.99674 | -0.036904 | 0.12313 | 0.059634
36 | 0.99667 | -0.036267 | 0 | 0
37 | 0.9967 | -0.036589 | 0.32343 | 0.15664
38 | 0.99709 | -0.040069 | 0.38939 | 0.18859
39 | 0.99749 | -0.037768 | 0 | 0
40 | 0.99806 | -0.042979 | 0 | 0
41 | 0.99728 | -0.048091 | 0 | 0
42 | 0.99671 | -0.036645 | 0 | 0
43 | 0.99666 | -0.036232 | 0.40279 | 0.19508
44 | 0.99747 | -0.037606 | 0.28277 | 0.13695
45 | 0.99902 | -0.025689 | 0.28531 | 0.13818
46 | 0.99903 | -0.025631 | 0 | 0
47 | 0.99899 | -0.025817 | 0 | 0
48 | 0.99882 | -0.036701 | 0 | 0
49 | 0.99904 | -0.025586 | 0 | 0
50 | 0.99895 | -0.025972 | 0 | 0
51 | 0.99879 | -0.036826 | 0 | 0
52 | 0.99955 | -0.0018929 | 0 | 0
53 | 0.99954 | -0.0018259 | 0 | 0
54 | 0.99913 | -0.025197 | 0.12798 | 0.061982
55 | 0.99974 | -0.0010976 | 0.39738 | 0.19246
56 | 0.99874 | -0.036376 | 0 | 0
57 | 0.99876 | -0.036962 | 0.080894 | 0.039179
58 | 0.99895 | -0.025944 | 0.082026 | 0.039727
59 | 0.99889 | -0.026224 | 0 | 0
60 | 0.99871 | -0.036057 | 0 | 0
61 | 0.99871 | -0.036038 | 0.35438 | 0.17163
62 | 0.99874 | -0.036291 | 0.19895 | 0.096354
63 | 0.99868 | -0.037332 | 0.077895 | 0.037726
64 | 0.99888 | -0.026243 | 0.26595 | 0.1288
65 | 0.99975 | -0.001032 | 0 | 0
66 | 0.99999 | -5.6299e-05 | 0 | 0
67 | 0.99887 | -0.026279 | 0 | 0
68 | 0.99881 | -0.026527 | 0 | 0
69 | 0.99861 | -0.037174 | 0 | 0
70 | 0.99862 | -0.037124 | 0.34594 | 0.16755
71 | 0.9986 | -0.037146 | 0 | 0
72 | 0.9986 | -0.037139 | 0.082618 | 0.040014
73 | 1 | 0 | -20.4048 | -9.5955
74 | 0.99952 | -0.0016466 | 0.34088 | 0.1651
75 | 0.99881 | -0.026499 | 0.11515 | 0.055771
76 | 0.99742 | -0.037945 | 0.40497 | 0.19614
77 | 0.99864 | -0.037494 | 0 | 0
78 | 0.99683 | -0.064413 | 0 | 0
79 | 0.99669 | -0.063196 | 0 | 0
80 | 0.99683 | -0.064399 | 0 | 0
81 | 0.99686 | -0.064664 | 0.16027 | 0.077623
82 | 0.99664 | -0.062738 | 0 | 0
83 | 0.99668 | -0.063294 | 0.34814 | 0.16861
84 | 0.99683 | -0.064386 | 0.17682 | 0.085636
85 | 0.9969 | -0.065026 | 0 | 0
86 | 0.99664 | -0.06271 | 0.33413 | 0.16183
87 | 0.99774 | -0.053907 | 0.23525 | 0.11394
88 | 0.99773 | -0.053932 | 0 | 0
89 | 0.99784 | -0.04797 | 0 | 0
90 | 0.99772 | -0.053982 | 0 | 0
91 | 0.99777 | -0.047315 | 0 | 0
92 | 0.99777 | -0.047274 | 0.32993 | 0.15979
93 | 0.99772 | -0.053957 | 0.085085 | 0.041208
94 | 0.99739 | -0.062228 | 0 | 0
95 | 0.99773 | -0.047516 | 0 | 0
96 | 0.99739 | -0.062201 | 0.09392 | 0.045488
97 | 0.99703 | -0.066242 | 0 | 0
98 | 0.99799 | -0.042254 | 0.37313 | 0.18071
99 | 0.99799 | -0.042293 | 0 | 0
100 | 0.99777 | -0.040366 | 0 | 0
101 | 0.99772 | -0.039903 | 0 | 0
102 | 0.99776 | -0.04023 | 0.35384 | 0.17137
103 | 0.99771 | -0.039849 | 0 | 0
104 | 0.99772 | -0.039879 | 0.086892 | 0.042084
105 | 0.99806 | -0.042913 | 0.18869 | 0.091387
106 | 0.99727 | -0.04806 | 0.41141 | 0.19925
107 | 0.99775 | -0.040152 | 0.11413 | 0.055278
108 | 0.99771 | -0.039805 | 0.071449 | 0.034604
109 | 0.9977 | -0.039712 | 0.31457 | 0.15235
110 | 0.99772 | -0.047374 | 0.30994 | 0.15011
111 | 0.99772 | -0.047394 | 0 | 0
112 | 0.99772 | -0.047455 | 0 | 0
113 | 0.99772 | -0.04744 | 0.069649 | 0.033732
114 | 0.99454 | -0.054871 | 0.30219 | 0.14636
115 | 0.99454 | -0.054902 | 0 | 0
116 | 0.99462 | -0.055627 | 0 | 0
117 | 0.9945 | -0.054534 | 0 | 0
118 | 0.9947 | -0.056363 | 0 | 0
119 | 0.99461 | -0.055573 | 0.080994 | 0.039227
120 | 0.99447 | -0.0547 | 0.36263 | 0.17563
121 | 0.99464 | -0.05589 | 0 | 0
122 | 0.99507 | -0.059541 | 0 | 0
123 | 0.9947 | -0.056355 | 0.075798 | 0.036711
124 | 0.99517 | -0.060441 | 0 | 0
125 | 0.99507 | -0.05951 | 0.10973 | 0.053147
126 | 0.99461 | -0.055555 | 0 | 0
127 | 0.99299 | -0.041404 | 0 | 0
128 | 0.99464 | -0.055871 | 0.1415 | 0.068532
129 | 0.99529 | -0.061409 | 0.089953 | 0.043566
130 | 0.9982 | -0.036325 | 0.40123 | 0.19432
131 | 0.99842 | -0.038385 | 0.087901 | 0.042573
132 | 0.99834 | -0.038773 | 0 | 0
133 | 0.99731 | -0.042317 | 0 | 0
134 | 0.99726 | -0.041832 | 0 | 0
135 | 0.99729 | -0.04214 | 0.37129 | 0.17982
136 | 0.99725 | -0.041701 | 0.088465 | 0.042846
137 | 0.99694 | -0.044562 | 0.10111 | 0.04897
138 | 0.99723 | -0.041797 | 0.17523 | 0.084869
139 | 0.99654 | -0.035147 | 0 | 0
140 | 0.99657 | -0.035433 | 0 | 0
141 | 0.99653 | -0.0351 | 0.32897 | 0.15933
142 | 0.9965 | -0.046545 | 0.25821 | 0.12506
143 | 0.99657 | -0.035432 | 0 | 0
144 | 0.99659 | -0.035641 | 0.11908 | 0.057672
145 | 0.99657 | -0.035391 | 0.076082 | 0.036848
146 | 0.99661 | -0.035817 | 0 | 0
147 | 0.99667 | -0.036284 | 0 | 0
148 | 0.99663 | -0.035934 | 0 | 0
149 | 0.99666 | -0.036206 | 0.14781 | 0.071587
150 | 0.99662 | -0.035916 | 0.098945 | 0.047921
151 | 0.9953 | -0.033645 | 0.28454 | 0.13781
152 | 0.99531 | -0.033742 | 0 | 0
153 | 0.99532 | -0.033816 | 0.071642 | 0.034698
154 | 0.99533 | -0.033947 | 0 | 0
155 | 0.99533 | -0.03398 | 0 | 0
156 | 0.99598 | -0.039678 | 0.28416 | 0.13763
157 | 0.99598 | -0.039694 | 0 | 0
158 | 0.99583 | -0.038375 | 0 | 0
159 | 0.99645 | -0.043829 | 0 | 0
160 | 0.99543 | -0.034847 | 0 | 0
161 | 0.99582 | -0.038293 | 0 | 0
162 | 0.99582 | -0.038342 | 0.12496 | 0.060521
163 | 0.99543 | -0.034831 | 0.4434 | 0.21475
164 | 0.9954 | -0.034596 | 0 | 0
165 | 0.99536 | -0.034256 | 0 | 0
166 | 0.9954 | -0.03457 | 0.11348 | 0.05496
167 | 0.99581 | -0.038211 | 0.14725 | 0.071315
168 | 0.99645 | -0.043882 | 0.22508 | 0.10901
169 | 0.99535 | -0.034083 | 0.083635 | 0.040506
170 | 0.99535 | -0.034167 | 0 | 0
171 | 0.99645 | -0.043864 | 0 | 0
172 | 0.99668 | -0.042311 | 0 | 0
173 | 0.99683 | -0.043552 | 0 | 0
174 | 0.99645 | -0.043828 | 0 | 0
175 | 0.99645 | -0.043812 | 0.24602 | 0.11916
176 | 0.99645 | -0.043796 | 0.088025 | 0.042632
177 | 0.99535 | -0.034146 | 0.15178 | 0.073512
178 | 0.99461 | -0.055537 | 0.12174 | 0.05896
179 | 0.9959 | -0.062074 | 0.13772 | 0.066699
180 | 0.99591 | -0.062129 | 0 | 0
181 | 0.99591 | -0.062164 | 0 | 0
182 | 0.99627 | -0.059627 | 0.38711 | 0.18749
183 | 0.9963 | -0.059884 | 0 | 0
184 | 0.99572 | -0.060554 | 0.094497 | 0.045767
185 | 0.99562 | -0.059718 | 0 | 0
186 | 0.99558 | -0.05931 | 0.069869 | 0.033839
187 | 0.99558 | -0.059329 | 0 | 0
188 | 0.99689 | -0.064985 | 0 | 0
189 | 0.99703 | -0.066236 | 0.072418 | 0.035074
190 | 0.99689 | -0.064945 | 0.14832 | 0.071836
191 | 0.99533 | -0.033898 | 0 | 0
192 | 0.99532 | -0.033834 | 0.19287 | 0.09341
193 | 0.99298 | -0.041341 | 0 | 0
194 | 0.99296 | -0.041074 | 0.70754 | 0.34268
195 | 0.99295 | -0.041051 | 0.42325 | 0.20499
196 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.35067 | -0.16984 | 0.35067 | 0.16973 | 7.846e-07 | -0.00010984 | 0.01127 | 0.011268 | 0.01127 | 0.99806 | -0.037136 | 0.99806 | -0.037156 | 5.1226
1 | -0.86498 | -0.41458 | 0.86499 | 0.41446 | 5.0327e-06 | -0.000115 | 0.027744 | 0.027742 | 0.027744 | 0.99806 | -0.037156 | 0.99807 | -0.037205 | 12.6107
2 | 0.51431 | 0.24485 | -0.51428 | -0.24648 | 2.4977e-05 | -0.0016298 | 0.016475 | 0.016496 | 0.016496 | 0.99806 | -0.037156 | 0.99801 | -0.036746 | 7.4981
3 | -0.86499 | -0.41446 | 0.8651 | 0.41444 | 0.00010997 | -2.6504e-05 | 0.027742 | 0.027741 | 0.027742 | 0.99807 | -0.037205 | 0.9982 | -0.036333 | 13.2105
4 | 0.40114 | 0.19223 | -0.40113 | -0.19391 | 1.5766e-05 | -0.001689 | 0.012866 | 0.012888 | 0.012888 | 0.99801 | -0.036746 | 0.99798 | -0.036408 | 5.858
5 | 0.11314 | 0.054254 | -0.11314 | -0.054796 | 4.0142e-07 | -0.00054172 | 0.0036294 | 0.0036362 | 0.0036362 | 0.99801 | -0.036746 | 0.99801 | -0.036715 | 1.6528
6 | 5.5706 | 2.6112 | -5.5705 | -2.6144 | 0.00012876 | -0.0032193 | 0.17797 | 0.17801 | 0.17801 | 0.99792 | -0.04766 | 0.99789 | -0.047762 | 13.9508
7 | -9.1721 | -4.3155 | 9.174 | 4.2985 | 0.0019242 | -0.01706 | 0.29323 | 0.29301 | 0.29323 | 0.99792 | -0.04766 | 0.99813 | -0.046738 | 22.9805
8 | 3.6015 | 1.7043 | -3.6011 | -1.7048 | 0.0004328 | -0.00045175 | 0.11526 | 0.11527 | 0.11527 | 0.99792 | -0.04766 | 0.9978 | -0.046666 | 52.3941
9 | 5.4808 | 2.571 | -5.4807 | -2.5743 | 0.00012699 | -0.0032811 | 0.17513 | 0.17517 | 0.17517 | 0.99789 | -0.047762 | 0.99787 | -0.047864 | 13.7281
10 | -9.174 | -4.2985 | 9.1744 | 4.2952 | 0.00036548 | -0.0032444 | 0.29301 | 0.29297 | 0.29301 | 0.99813 | -0.046738 | 0.99817 | -0.046561 | 22.963
11 | 3.1987 | 1.5099 | -3.1982 | -1.5106 | 0.00052657 | -0.00073892 | 0.10233 | 0.10234 | 0.10234 | 0.9978 | -0.046666 | 0.99765 | -0.045312 | 46.5203
12 | -9.285 | -4.3488 | 9.2857 | 4.3505 | 0.00068062 | 0.0017108 | 0.29652 | 0.29652 | 0.29652 | 0.99817 | -0.046561 | 0.99831 | -0.038913 | 22.986
13 | -1.2322 | -0.59225 | 1.2323 | 0.59176 | 4.4084e-05 | -0.00048956 | 0.039538 | 0.039532 | 0.039538 | 0.9982 | -0.036333 | 0.99823 | -0.036639 | 17.9719
14 | 0.40113 | 0.19391 | -0.40112 | -0.19427 | 3.3489e-06 | -0.00035803 | 0.012888 | 0.012892 | 0.012892 | 0.99798 | -0.036408 | 0.99797 | -0.036335 | 5.8601
15 | 5.4807 | 2.5743 | -5.4806 | -2.5777 | 0.00013347 | -0.0034467 | 0.17517 | 0.17521 | 0.17521 | 0.99787 | -0.047864 | 0.99784 | -0.04797 | 13.7315
16 | 3.1982 | 1.5106 | -3.197 | -1.5123 | 0.0011614 | -0.0016281 | 0.10234 | 0.10237 | 0.10237 | 0.99765 | -0.045312 | 0.99731 | -0.042317 | 46.5314
17 | -9.3691 | -4.3909 | 9.3694 | 4.3884 | 0.00029559 | -0.0025106 | 0.2992 | 0.29916 | 0.2992 | 0.99831 | -0.038913 | 0.99834 | -0.038773 | 23.448
18 | -1.6335 | -0.78452 | 1.6339 | 0.78241 | 0.00034034 | -0.0021092 | 0.052405 | 0.052377 | 0.052405 | 0.99823 | -0.036639 | 0.99843 | -0.038414 | 23.8203
19 | 0.40124 | 0.19276 | -0.40123 | -0.19376 | 9.3664e-06 | -0.0010035 | 0.012873 | 0.012886 | 0.012886 | 0.99823 | -0.036639 | 0.99821 | -0.036438 | 5.8571
20 | 0.087902 | 0.041903 | -0.087901 | -0.042573 | 2.9861e-07 | -0.00066951 | 0.0028155 | 0.0028239 | 0.0028239 | 0.99843 | -0.038414 | 0.99842 | -0.038385 | 1.2836
21 | 9.3701 | 4.382 | -9.3694 | -4.3884 | 0.00075114 | -0.0063832 | 0.29908 | 0.29916 | 0.29916 | 0.99843 | -0.038414 | 0.99834 | -0.038773 | 23.4454
22 | -11.0919 | -5.2063 | 11.0942 | 5.1927 | 0.0023017 | -0.013584 | 0.35427 | 0.35409 | 0.35427 | 0.99843 | -0.038414 | 0.99864 | -0.037494 | 27.7642
23 | 0.40123 | 0.19376 | -0.40123 | -0.19432 | 5.2405e-06 | -0.00056059 | 0.012886 | 0.012893 | 0.012893 | 0.99821 | -0.036438 | 0.9982 | -0.036325 | 5.8603
24 | -0.3739 | -0.18109 | 0.3739 | 0.18098 | 8.4904e-07 | -0.00010394 | 0.012033 | 0.012031 | 0.012033 | 0.99669 | -0.045988 | 0.99669 | -0.046008 | 5.4694
25 | -0.3739 | -0.18098 | 0.37391 | 0.17994 | 8.53e-06 | -0.0010456 | 0.012031 | 0.012018 | 0.012031 | 0.99669 | -0.046008 | 0.99671 | -0.046205 | 5.4688
26 | -1.3052 | -0.62431 | 1.3054 | 0.62213 | 0.00022241 | -0.0021864 | 0.041903 | 0.041875 | 0.041903 | 0.99671 | -0.046205 | 0.99687 | -0.047643 | 19.047
27 | 0.39434 | 0.18945 | -0.39433 | -0.19084 | 1.2613e-05 | -0.0013901 | 0.012671 | 0.012688 | 0.012688 | 0.99671 | -0.046205 | 0.99668 | -0.045929 | 5.7674
28 | 0.53692 | 0.25493 | -0.53685 | -0.25505 | 7.1906e-05 | -0.00011643 | 0.017214 | 0.017216 | 0.017216 | 0.99671 | -0.046205 | 0.99657 | -0.047153 | 8.1983
29 | 0.25823 | 0.12018 | -0.25821 | -0.12494 | 1.8397e-05 | -0.0047608 | 0.0082504 | 0.0083096 | 0.0083096 | 0.99657 | -0.047153 | 0.9965 | -0.04656 | 3.7771
30 | 0.27862 | 0.13487 | -0.27861 | -0.13494 | 9.1037e-06 | -6.9637e-05 | 0.0089666 | 0.0089675 | 0.0089675 | 0.99657 | -0.047153 | 0.99653 | -0.047369 | 4.2702
31 | 0.25821 | 0.12494 | -0.25821 | -0.12506 | 4.5074e-07 | -0.00011578 | 0.0083096 | 0.0083111 | 0.0083111 | 0.9965 | -0.04656 | 0.9965 | -0.046545 | 3.7778
32 | -1.3054 | -0.62213 | 1.3058 | 0.62222 | 0.00036471 | 8.9911e-05 | 0.041875 | 0.041874 | 0.041875 | 0.99687 | -0.047643 | 0.99716 | -0.045689 | 19.9406
33 | 0.30125 | 0.14576 | -0.30123 | -0.14589 | 2.0889e-05 | -0.00013486 | 0.0096931 | 0.009695 | 0.009695 | 0.99668 | -0.045929 | 0.99661 | -0.046387 | 4.6166
34 | -1.5516 | -0.74127 | 1.5516 | 0.74112 | 2.1847e-05 | -0.00015031 | 0.04978 | 0.049778 | 0.04978 | 0.99716 | -0.045689 | 0.99717 | -0.045808 | 22.6273
35 | -1.5516 | -0.74112 | 1.5517 | 0.7403 | 0.0001193 | -0.00082108 | 0.049778 | 0.049767 | 0.049778 | 0.99717 | -0.045808 | 0.99725 | -0.046456 | 22.6264
36 | -1.5517 | -0.7403 | 1.5519 | 0.73892 | 0.00020024 | -0.0013792 | 0.049767 | 0.04975 | 0.049767 | 0.99725 | -0.046456 | 0.99737 | -0.047541 | 22.6216
37 | -2.3119 | -1.1067 | 2.3135 | 1.1075 | 0.0015328 | 0.00077435 | 0.074188 | 0.074185 | 0.074188 | 0.99737 | -0.047541 | 0.99806 | -0.042979 | 35.3275
38 | 0.41145 | 0.19899 | -0.41141 | -0.1991 | 3.4233e-05 | -0.00010892 | 0.013228 | 0.01323 | 0.01323 | 0.99737 | -0.047541 | 0.99728 | -0.048091 | 6.3001
39 | -1.6205 | -0.77057 | 1.6211 | 0.76682 | 0.00059457 | -0.003741 | 0.051966 | 0.051917 | 0.051966 | 0.99677 | -0.037237 | 0.99711 | -0.040285 | 23.6209
40 | 0.72629 | 0.34799 | -0.72624 | -0.34971 | 5.3048e-05 | -0.0017153 | 0.023324 | 0.023346 | 0.023346 | 0.99677 | -0.037237 | 0.9967 | -0.036612 | 10.6116
41 | 0.89417 | 0.42258 | -0.89414 | -0.42334 | 3.597e-05 | -0.00076815 | 0.028642 | 0.028652 | 0.028652 | 0.99677 | -0.037237 | 0.99674 | -0.036904 | 13.0236
42 | 0.3894 | 0.18749 | -0.38939 | -0.18859 | 9.7068e-06 | -0.0010984 | 0.012512 | 0.012526 | 0.012526 | 0.99711 | -0.040285 | 0.99709 | -0.040069 | 5.6937
43 | -2.0105 | -0.95432 | 2.0112 | 0.95465 | 0.0007136 | 0.00033241 | 0.064429 | 0.064428 | 0.064429 | 0.99711 | -0.040285 | 0.99749 | -0.037768 | 30.6807
44 | 0.40281 | 0.1932 | -0.40279 | -0.19491 | 1.6129e-05 | -0.001704 | 0.012939 | 0.01296 | 0.01296 | 0.9967 | -0.036612 | 0.99667 | -0.036267 | 5.8911
45 | 0.32343 | 0.1565 | -0.32343 | -0.15664 | 8.6125e-07 | -0.00014101 | 0.010407 | 0.010408 | 0.010408 | 0.9967 | -0.036612 | 0.9967 | -0.036589 | 4.7311
46 | 0.77101 | 0.36371 | -0.77098 | -0.36441 | 2.4363e-05 | -0.00070262 | 0.02469 | 0.024699 | 0.024699 | 0.99674 | -0.036904 | 0.99671 | -0.036645 | 11.2267
47 | 0.40279 | 0.19491 | -0.40279 | -0.19508 | 1.6426e-06 | -0.00017322 | 0.01296 | 0.012963 | 0.012963 | 0.99667 | -0.036267 | 0.99666 | -0.036232 | 5.8921
48 | 0.68778 | 0.33256 | -0.68776 | -0.33302 | 1.2826e-05 | -0.00046297 | 0.022109 | 0.022115 | 0.022115 | 0.99749 | -0.037768 | 0.99747 | -0.037606 | 10.0522
49 | -2.6989 | -1.2872 | 2.7006 | 1.2837 | 0.001678 | -0.0034943 | 0.086537 | 0.086487 | 0.086537 | 0.99749 | -0.037768 | 0.99806 | -0.042979 | 39.3348
50 | 0.18869 | 0.09069 | -0.18869 | -0.091387 | 1.4377e-06 | -0.00069711 | 0.0060552 | 0.006064 | 0.006064 | 0.99806 | -0.042979 | 0.99806 | -0.042913 | 2.7564
51 | -6.5172 | -3.1017 | 6.5204 | 3.0988 | 0.0032249 | -0.0028966 | 0.20876 | 0.20869 | 0.20876 | 0.99806 | -0.042979 | 0.99861 | -0.037174 | 57.6679
52 | 0.37316 | 0.17677 | -0.37313 | -0.18051 | 3.0159e-05 | -0.0037431 | 0.011943 | 0.01199 | 0.01199 | 0.99806 | -0.042979 | 0.99799 | -0.042293 | 5.4499
53 | 0.94122 | 0.44298 | -0.94093 | -0.44872 | 0.00029663 | -0.0057339 | 0.030088 | 0.03016 | 0.03016 | 0.99806 | -0.042979 | 0.99777 | -0.040366 | 13.7091
54 | 0.41141 | 0.1991 | -0.41141 | -0.19925 | 1.4904e-06 | -0.00015099 | 0.01323 | 0.013232 | 0.013232 | 0.99728 | -0.048091 | 0.99727 | -0.04806 | 6.0146
55 | 0.77098 | 0.36441 | -0.77095 | -0.36538 | 3.3634e-05 | -0.00096909 | 0.024699 | 0.024711 | 0.024711 | 0.99671 | -0.036645 | 0.99667 | -0.036284 | 11.2322
56 | 0.40499 | 0.19607 | -0.40497 | -0.19614 | 2.0807e-05 | -6.8757e-05 | 0.013022 | 0.013023 | 0.013023 | 0.99747 | -0.037606 | 0.99742 | -0.037945 | 6.2015
57 | -19.5092 | -9.1708 | 19.5095 | 9.1704 | 0.000257 | -0.00039295 | 0.62291 | 0.62291 | 0.62291 | 0.99902 | -0.025689 | 0.99903 | -0.025631 | 48.8177
58 | 7.4143 | 3.5076 | -7.4141 | -3.5108 | 0.00022679 | -0.003149 | 0.23701 | 0.23705 | 0.23705 | 0.99902 | -0.025689 | 0.99899 | -0.025817 | 18.5775
59 | 11.8096 | 5.525 | -11.8083 | -5.5218 | 0.0012453 | 0.0032131 | 0.37675 | 0.37675 | 0.37675 | 0.99902 | -0.025689 | 0.99882 | -0.036701 | 29.2053
60 | -19.5095 | -9.1704 | 19.5097 | 9.1701 | 0.00020316 | -0.00031065 | 0.62291 | 0.6229 | 0.62291 | 0.99903 | -0.025631 | 0.99904 | -0.025586 | 48.8172
61 | 7.4141 | 3.5108 | -7.4138 | -3.5146 | 0.00027387 | -0.003801 | 0.23705 | 0.2371 | 0.2371 | 0.99899 | -0.025817 | 0.99895 | -0.025972 | 18.5814
62 | 11.8083 | 5.5218 | -11.808 | -5.5235 | 0.00032991 | -0.0017001 | 0.37675 | 0.37677 | 0.37677 | 0.99882 | -0.036701 | 0.99879 | -0.036826 | 29.5276
63 | -19.5097 | -9.1701 | 19.5114 | 9.1674 | 0.0017328 | -0.0026503 | 0.6229 | 0.62286 | 0.6229 | 0.99904 | -0.025586 | 0.99913 | -0.025197 | 48.8168
64 | 0.082026 | 0.039041 | -0.082026 | -0.039727 | 2.6559e-07 | -0.00068548 | 0.0026252 | 0.0026338 | 0.0026338 | 0.99895 | -0.025972 | 0.99895 | -0.025944 | 1.1972
65 | 7.3318 | 3.4755 | -7.3314 | -3.4819 | 0.00044606 | -0.0063314 | 0.23447 | 0.23455 | 0.23455 | 0.99895 | -0.025972 | 0.99889 | -0.026224 | 18.382
66 | 0.55337 | 0.26355 | -0.55334 | -0.26521 | 2.9476e-05 | -0.001665 | 0.017715 | 0.017736 | 0.017736 | 0.99879 | -0.036826 | 0.99874 | -0.036376 | 8.0617
67 | 11.2546 | 5.2599 | -11.2543 | -5.2619 | 0.00033958 | -0.0019458 | 0.35906 | 0.35908 | 0.35908 | 0.99879 | -0.036826 | 0.99876 | -0.036962 | 28.1413
68 | 0.34089 | 0.16364 | -0.34089 | -0.16404 | 2.6653e-06 | -0.00039836 | 0.010921 | 0.010926 | 0.010926 | 0.99955 | -0.0018929 | 0.99954 | -0.0018259 | 4.9662
69 | 19.6438 | 9.2411 | -19.6394 | -9.2294 | 0.0043964 | 0.011649 | 0.62696 | 0.62697 | 0.62697 | 0.99955 | -0.0018929 | 0.99913 | -0.025197 | 48.602
70 | -19.9847 | -9.4047 | 19.9883 | 9.3995 | 0.0036557 | -0.0052448 | 0.63788 | 0.63779 | 0.63788 | 0.99955 | -0.0018929 | 0.99974 | -0.0010976 | 49.9909
71 | 0.34089 | 0.16404 | -0.34088 | -0.1651 | 7.0685e-06 | -0.0010547 | 0.010926 | 0.010939 | 0.010939 | 0.99954 | -0.0018259 | 0.99952 | -0.0016466 | 4.9722
72 | -20.3857 | -9.5919 | 20.386 | 9.5915 | 0.00030757 | -0.00041763 | 0.65054 | 0.65054 | 0.65054 | 0.99974 | -0.0010976 | 0.99975 | -0.001032 | 50.983
73 | 0.19895 | 0.095496 | -0.19895 | -0.096354 | 1.9617e-06 | -0.00085814 | 0.0063785 | 0.0063893 | 0.0063893 | 0.99874 | -0.036376 | 0.99874 | -0.036291 | 2.9042
74 | 0.35439 | 0.16972 | -0.35438 | -0.17153 | 1.3162e-05 | -0.0018128 | 0.011357 | 0.01138 | 0.01138 | 0.99874 | -0.036376 | 0.99871 | -0.036057 | 5.1728
75 | 11.1734 | 5.2227 | -11.1725 | -5.2281 | 0.00092146 | -0.0053624 | 0.35649 | 0.35656 | 0.35656 | 0.99876 | -0.036962 | 0.99868 | -0.037332 | 27.9434
76 | 7.3314 | 3.4819 | -7.3313 | -3.4824 | 3.4485e-05 | -0.00048926 | 0.23455 | 0.23456 | 0.23456 | 0.99889 | -0.026224 | 0.99888 | -0.026243 | 18.3825
77 | 0.35438 | 0.17153 | -0.35438 | -0.17163 | 7.482e-07 | -0.00010282 | 0.01138 | 0.011381 | 0.011381 | 0.99871 | -0.036057 | 0.99871 | -0.036038 | 5.1734
78 | 11.0946 | 5.1903 | -11.0942 | -5.1927 | 0.00040293 | -0.0023802 | 0.35406 | 0.35409 | 0.35409 | 0.99868 | -0.037332 | 0.99864 | -0.037494 | 27.7499
79 | 7.0654 | 3.3536 | -7.0653 | -3.3545 | 6.1954e-05 | -0.00094923 | 0.22602 | 0.22603 | 0.22603 | 0.99888 | -0.026243 | 0.99887 | -0.026279 | 17.7142
80 | -20.386 | -9.5915 | 20.3906 | 9.5853 | 0.0045682 | -0.0062066 | 0.65054 | 0.65043 | 0.65054 | 0.99975 | -0.001032 | 0.99999 | -5.6299e-05 | 50.9824
81 | -20.3906 | -9.5853 | 20.3908 | 9.585 | 0.00026295 | -0.00035747 | 0.65043 | 0.65042 | 0.65043 | 0.99999 | -5.6299e-05 | 1 | 0 | 50.974
82 | 7.0653 | 3.3545 | -7.0649 | -3.361 | 0.00042633 | -0.0065287 | 0.22603 | 0.22612 | 0.22612 | 0.99887 | -0.026279 | 0.99881 | -0.026527 | 17.7208
83 | 0.11515 | 0.055288 | -0.11515 | -0.055771 | 3.6975e-07 | -0.00048312 | 0.0036919 | 0.0036979 | 0.0036979 | 0.99881 | -0.026527 | 0.99881 | -0.026499 | 1.6809
84 | 6.9497 | 3.3057 | -6.949 | -3.3041 | 0.00071196 | 0.0016922 | 0.22243 | 0.22243 | 0.22243 | 0.99881 | -0.026527 | 0.99862 | -0.037124 | 17.2425
85 | -6.603 | -3.1379 | 6.6031 | 3.1365 | 8.0617e-05 | -0.0014188 | 0.21134 | 0.21132 | 0.21134 | 0.99861 | -0.037174 | 0.99862 | -0.037124 | 16.5624
86 | 0.082619 | 0.039163 | -0.082618 | -0.039851 | 2.7045e-07 | -0.00068815 | 0.0026431 | 0.0026516 | 0.0026516 | 0.99861 | -0.037174 | 0.9986 | -0.037146 | 1.2053
87 | 0.082618 | 0.039851 | -0.082618 | -0.040014 | 6.4248e-08 | -0.0001628 | 0.0026516 | 0.0026537 | 0.0026537 | 0.9986 | -0.037146 | 0.9986 | -0.037139 | 1.2062
88 | 0.6824 | 0.32387 | -0.6823 | -0.32749 | 9.8503e-05 | -0.0036211 | 0.021875 | 0.02192 | 0.02192 | 0.99683 | -0.064413 | 0.99669 | -0.063196 | 9.9637
89 | 0.17682 | 0.085338 | -0.17682 | -0.085487 | 2.7134e-07 | -0.00014903 | 0.0056857 | 0.0056876 | 0.0056876 | 0.99683 | -0.064413 | 0.99683 | -0.064399 | 2.5853
90 | -0.85922 | -0.40921 | 0.85924 | 0.40861 | 2.5783e-05 | -0.00059579 | 0.02756 | 0.027553 | 0.02756 | 0.99683 | -0.064413 | 0.99686 | -0.064664 | 12.5273
91 | 0.33415 | 0.1589 | -0.33413 | -0.16166 | 1.7945e-05 | -0.0027616 | 0.010717 | 0.010751 | 0.010751 | 0.99669 | -0.063196 | 0.99664 | -0.062738 | 4.8869
92 | 0.34815 | 0.16859 | -0.34814 | -0.16861 | 5.1827e-06 | -2.4235e-05 | 0.011204 | 0.011204 | 0.011204 | 0.99669 | -0.063196 | 0.99668 | -0.063294 | 5.3352
93 | 0.17682 | 0.085487 | -0.17682 | -0.085636 | 2.718e-07 | -0.0001492 | 0.0056876 | 0.0056894 | 0.0056894 | 0.99683 | -0.064399 | 0.99683 | -0.064386 | 2.5861
94 | -1.0195 | -0.48623 | 1.0196 | 0.48552 | 4.3971e-05 | -0.0007176 | 0.032709 | 0.0327 | 0.032709 | 0.99686 | -0.064664 | 0.9969 | -0.065026 | 14.8679
95 | 0.33413 | 0.16166 | -0.33413 | -0.16183 | 1.081e-06 | -0.00016579 | 0.010751 | 0.010753 | 0.010753 | 0.99664 | -0.062738 | 0.99664 | -0.06271 | 4.8879
96 | -1.1679 | -0.55625 | 1.1681 | 0.55415 | 0.00016995 | -0.0021042 | 0.037459 | 0.037432 | 0.037459 | 0.9969 | -0.065026 | 0.99703 | -0.066242 | 17.0268
97 | 0.14832 | 0.070738 | -0.14832 | -0.071301 | 7.1905e-07 | -0.00056336 | 0.0047585 | 0.0047656 | 0.0047656 | 0.9969 | -0.065026 | 0.99689 | -0.064985 | 2.1662
98 | 4.5354 | 2.1229 | -4.5354 | -2.1238 | 2.5543e-05 | -0.00097074 | 0.14489 | 0.1449 | 0.1449 | 0.99774 | -0.053907 | 0.99773 | -0.053932 | 11.3557
99 | -4.7707 | -2.2368 | 4.771 | 2.2374 | 0.00027159 | 0.00055013 | 0.15245 | 0.15245 | 0.15245 | 0.99774 | -0.053907 | 0.99784 | -0.04797 | 11.8178
100 | 4.5354 | 2.1238 | -4.5354 | -2.1258 | 5.1185e-05 | -0.0019447 | 0.1449 | 0.14492 | 0.14492 | 0.99773 | -0.053932 | 0.99772 | -0.053982 | 11.3576
101 | 0.7096 | 0.34038 | -0.70954 | -0.34222 | 5.4191e-05 | -0.0018435 | 0.022768 | 0.022791 | 0.022791 | 0.99784 | -0.04797 | 0.99777 | -0.047315 | 10.3598
102 | 0.085085 | 0.040629 | -0.085085 | -0.041208 | 2.4266e-07 | -0.00057886 | 0.0027281 | 0.0027353 | 0.0027353 | 0.99772 | -0.053982 | 0.99772 | -0.053957 | 1.2433
103 | 4.4503 | 2.0852 | -4.4491 | -2.0839 | 0.0011564 | 0.0012448 | 0.1422 | 0.1422 | 0.1422 | 0.99772 | -0.053982 | 0.99739 | -0.062228 | 40.6275
104 | 0.70954 | 0.34222 | -0.70954 | -0.34233 | 3.3552e-06 | -0.000114 | 0.022791 | 0.022793 | 0.022793 | 0.99777 | -0.047315 | 0.99777 | -0.047274 | 10.3604
105 | 0.37961 | 0.18254 | -0.3796 | -0.18259 | 1.3563e-05 | -5.2417e-05 | 0.012187 | 0.012187 | 0.012187 | 0.99777 | -0.047274 | 0.99773 | -0.047516 | 5.8035
106 | 0.09392 | 0.04491 | -0.09392 | -0.045488 | 2.9555e-07 | -0.00057771 | 0.0030131 | 0.0030204 | 0.0030204 | 0.99739 | -0.062228 | 0.99739 | -0.062201 | 1.3729
107 | 4.3552 | 2.039 | -4.3538 | -2.0432 | 0.0014422 | -0.004208 | 0.13918 | 0.13925 | 0.13925 | 0.99739 | -0.062228 | 0.99703 | -0.066242 | 38.4662
108 | 0.3796 | 0.18259 | -0.37959 | -0.18292 | 2.7078e-06 | -0.00032365 | 0.012187 | 0.012192 | 0.012192 | 0.99773 | -0.047516 | 0.99772 | -0.047455 | 5.5416
109 | 0.072418 | 0.03492 | -0.072418 | -0.035074 | 4.7025e-08 | -0.00015417 | 0.0023278 | 0.0023297 | 0.0023297 | 0.99703 | -0.066242 | 0.99703 | -0.066236 | 1.059
110 | 3.1133 | 1.4541 | -3.1108 | -1.4578 | 0.0024583 | -0.0036808 | 0.099488 | 0.099543 | 0.099543 | 0.99703 | -0.066242 | 0.9963 | -0.059884 | 45.2466
111 | -0.37313 | -0.18071 | 0.37313 | 0.18051 | 1.6556e-06 | -0.00020461 | 0.011992 | 0.01199 | 0.011992 | 0.99799 | -0.042254 | 0.99799 | -0.042293 | 5.451
112 | 0.47295 | 0.22404 | -0.47292 | -0.22606 | 2.6139e-05 | -0.0020189 | 0.015141 | 0.015166 | 0.015166 | 0.99777 | -0.040366 | 0.99772 | -0.039903 | 6.8937
113 | 0.46798 | 0.22467 | -0.46797 | -0.22526 | 7.4286e-06 | -0.00058386 | 0.015019 | 0.015026 | 0.015026 | 0.99777 | -0.040366 | 0.99776 | -0.04023 | 6.8302
114 | 0.38603 | 0.18455 | -0.38602 | -0.18484 | 2.497e-06 | -0.00028922 | 0.01238 | 0.012384 | 0.012384 | 0.99772 | -0.039903 | 0.99771 | -0.039849 | 5.6289
115 | 0.086892 | 0.041509 | -0.086892 | -0.042084 | 2.5125e-07 | -0.00057465 | 0.0027862 | 0.0027934 | 0.0027934 | 0.99772 | -0.039903 | 0.99772 | -0.039879 | 1.2697
116 | 0.11414 | 0.053886 | -0.11413 | -0.055278 | 1.0478e-06 | -0.001392 | 0.0036518 | 0.0036691 | 0.0036691 | 0.99776 | -0.04023 | 0.99775 | -0.040152 | 1.6678
117 | 0.071449 | 0.033351 | -0.071449 | -0.034604 | 3.6903e-07 | -0.0012537 | 0.0022814 | 0.002297 | 0.002297 | 0.99771 | -0.039849 | 0.99771 | -0.039805 | 1.0441
118 | 0.31458 | 0.15149 | -0.31457 | -0.15235 | 4.9473e-06 | -0.00086062 | 0.010102 | 0.010113 | 0.010113 | 0.99771 | -0.039849 | 0.9977 | -0.039712 | 4.5969
119 | -0.30994 | -0.15011 | 0.30994 | 0.14999 | 6.8844e-07 | -0.00012327 | 0.0099641 | 0.0099626 | 0.0099641 | 0.99772 | -0.047374 | 0.99772 | -0.047394 | 4.5291
120 | -0.30994 | -0.14999 | 0.30994 | 0.1496 | 2.1813e-06 | -0.00039082 | 0.0099626 | 0.0099576 | 0.0099626 | 0.99772 | -0.047394 | 0.99772 | -0.047455 | 4.5284
121 | 0.069649 | 0.033318 | -0.069649 | -0.033732 | 1.1633e-07 | -0.00041403 | 0.0022339 | 0.0022391 | 0.0022391 | 0.99772 | -0.047455 | 0.99772 | -0.04744 | 1.0178
122 | -0.30219 | -0.14636 | 0.30219 | 0.14616 | 1.0738e-06 | -0.00019973 | 0.0097459 | 0.0097434 | 0.0097459 | 0.99454 | -0.054871 | 0.99454 | -0.054902 | 4.43
123 | -0.66485 | -0.31974 | 0.6649 | 0.31757 | 5.6677e-05 | -0.0021727 | 0.021414 | 0.021386 | 0.021414 | 0.99454 | -0.054902 | 0.99462 | -0.055627 | 9.7334
124 | 0.36266 | 0.17359 | -0.36264 | -0.17559 | 1.5511e-05 | -0.0020056 | 0.01167 | 0.011696 | 0.011696 | 0.99454 | -0.054902 | 0.9945 | -0.054534 | 5.3162
125 | -0.86764 | -0.41463 | 0.86771 | 0.41293 | 7.5894e-05 | -0.0017028 | 0.02791 | 0.027888 | 0.02791 | 0.99462 | -0.055627 | 0.9947 | -0.056363 | 12.6863
126 | 0.20273 | 0.097062 | -0.20273 | -0.097598 | 1.2923e-06 | -0.0005363 | 0.0065237 | 0.0065304 | 0.0065304 | 0.99462 | -0.055627 | 0.99461 | -0.055573 | 2.9684
127 | 0.36264 | 0.17559 | -0.36263 | -0.17563 | 9.1147e-06 | -3.8446e-05 | 0.011696 | 0.011696 | 0.011696 | 0.9945 | -0.054534 | 0.99447 | -0.0547 | 5.5696
128 | 1.2744 | 0.58621 | -1.2744 | -0.58702 | 7.7908e-05 | -0.00080845 | 0.040711 | 0.040721 | 0.040721 | 0.9947 | -0.056363 | 0.99464 | -0.05589 | 18.5095
129 | -2.2179 | -1.0356 | 2.2188 | 1.0328 | 0.00088328 | -0.002838 | 0.071039 | 0.071001 | 0.071039 | 0.9947 | -0.056363 | 0.99507 | -0.059541 | 32.2905
130 | 0.075798 | 0.036499 | -0.075798 | -0.036711 | 7.147e-08 | -0.00021188 | 0.0024415 | 0.0024442 | 0.0024442 | 0.9947 | -0.056363 | 0.9947 | -0.056355 | 1.111
131 | 0.12174 | 0.058371 | -0.12174 | -0.058669 | 2.5928e-07 | -0.00029839 | 0.0039185 | 0.0039222 | 0.0039222 | 0.99461 | -0.055573 | 0.99461 | -0.055555 | 1.7828
132 | 1.1329 | 0.51876 | -1.1308 | -0.54513 | 0.0020152 | -0.026376 | 0.036162 | 0.036495 | 0.036495 | 0.99464 | -0.05589 | 0.99299 | -0.041404 | 16.5888
133 | 0.1415 | 0.068265 | -0.1415 | -0.068532 | 3.1418e-07 | -0.00026707 | 0.0045597 | 0.0045631 | 0.0045631 | 0.99464 | -0.05589 | 0.99464 | -0.055871 | 2.0741
134 | -2.3286 | -1.0854 | 2.3288 | 1.0846 | 0.00026289 | -0.00076031 | 0.074531 | 0.074521 | 0.074531 | 0.99507 | -0.059541 | 0.99517 | -0.060441 | 33.8776
135 | 0.10974 | 0.052576 | -0.10973 | -0.053147 | 4.0234e-07 | -0.0005705 | 0.00353 | 0.0035372 | 0.0035372 | 0.99507 | -0.059541 | 0.99507 | -0.05951 | 1.6078
136 | -2.3288 | -1.0846 | 2.3291 | 1.0838 | 0.00028335 | -0.00081994 | 0.074521 | 0.074509 | 0.074521 | 0.99517 | -0.060441 | 0.99529 | -0.061409 | 33.873
137 | 0.12174 | 0.058669 | -0.12174 | -0.05896 | 2.5341e-07 | -0.0002911 | 0.0039222 | 0.0039259 | 0.0039259 | 0.99461 | -0.055555 | 0.99461 | -0.055537 | 1.7845
138 | 0.42327 | 0.20336 | -0.42327 | -0.20365 | 3.1286e-06 | -0.00029504 | 0.013651 | 0.013655 | 0.013655 | 0.99299 | -0.041404 | 0.99298 | -0.041341 | 6.2069
139 | 0.70757 | 0.34178 | -0.70754 | -0.34268 | 2.694e-05 | -0.00090191 | 0.022844 | 0.022855 | 0.022855 | 0.99299 | -0.041404 | 0.99296 | -0.041074 | 10.3888
140 | -2.4191 | -1.1274 | 2.4197 | 1.1277 | 0.00066664 | 0.00034369 | 0.077408 | 0.077407 | 0.077408 | 0.99529 | -0.061409 | 0.99558 | -0.059329 | 36.861
141 | 0.26372 | 0.12282 | -0.2637 | -0.12668 | 1.5505e-05 | -0.0038632 | 0.0084206 | 0.0084685 | 0.0084685 | 0.99731 | -0.042317 | 0.99726 | -0.041832 | 3.8493
142 | 2.9333 | 1.3894 | -2.9332 | -1.3895 | 6.2876e-05 | -0.00010807 | 0.093949 | 0.09395 | 0.09395 | 0.99731 | -0.042317 | 0.99729 | -0.04214 | 42.7047
143 | 0.2637 | 0.12668 | -0.2637 | -0.12766 | 3.979e-06 | -0.00098424 | 0.0084685 | 0.0084809 | 0.0084809 | 0.99726 | -0.041832 | 0.99725 | -0.041701 | 3.855
144 | 2.5619 | 1.2097 | -2.5611 | -1.2093 | 0.0008591 | 0.00045302 | 0.082009 | 0.08201 | 0.08201 | 0.99729 | -0.04214 | 0.99694 | -0.044562 | 39.0525
145 | 0.17524 | 0.084818 | -0.17523 | -0.084869 | 2.531e-06 | -5.1512e-05 | 0.0056355 | 0.0056362 | 0.0056362 | 0.99725 | -0.041701 | 0.99723 | -0.041797 | 2.6839
146 | 2.46 | 1.1603 | -2.4597 | -1.1611 | 0.00030266 | -0.00077735 | 0.078757 | 0.078768 | 0.078768 | 0.99694 | -0.044562 | 0.99683 | -0.043552 | 35.8037
147 | -0.32897 | -0.15904 | 0.32898 | 0.1573 | 1.0986e-05 | -0.0017421 | 0.010585 | 0.010563 | 0.010585 | 0.99654 | -0.035147 | 0.99657 | -0.035433 | 4.8113
148 | 0.32897 | 0.15904 | -0.32897 | -0.15933 | 1.7952e-06 | -0.00028396 | 0.010585 | 0.010588 | 0.010588 | 0.99654 | -0.035147 | 0.99653 | -0.0351 | 4.8129
149 | 0.076082 | 0.035689 | -0.076082 | -0.035727 | 1.2553e-08 | -3.7605e-05 | 0.0024343 | 0.0024347 | 0.0024347 | 0.99657 | -0.035433 | 0.99657 | -0.035432 | 1.1067
150 | -0.40506 | -0.19299 | 0.40507 | 0.19193 | 1.0081e-05 | -0.0010581 | 0.012997 | 0.012984 | 0.012997 | 0.99657 | -0.035433 | 0.99659 | -0.035641 | 5.9078
151 | 0.076082 | 0.035727 | -0.076082 | -0.036848 | 3.7641e-07 | -0.0011213 | 0.0024347 | 0.0024487 | 0.0024487 | 0.99657 | -0.035432 | 0.99657 | -0.035391 | 1.1131
152 | -0.52415 | -0.2496 | 0.52416 | 0.24892 | 1.0999e-05 | -0.00068797 | 0.016816 | 0.016808 | 0.016816 | 0.99659 | -0.035641 | 0.99661 | -0.035817 | 7.6438
153 | -0.52416 | -0.24892 | 0.52417 | 0.24845 | 7.4146e-06 | -0.00046421 | 0.016808 | 0.016802 | 0.016808 | 0.99661 | -0.035817 | 0.99663 | -0.035934 | 7.6399
154 | 0.62314 | 0.29485 | -0.62312 | -0.29601 | 2.6239e-05 | -0.0011605 | 0.019967 | 0.019982 | 0.019982 | 0.99667 | -0.036284 | 0.99663 | -0.035934 | 9.0826
155 | 0.14781 | 0.07053 | -0.14781 | -0.071587 | 1.3429e-06 | -0.0010569 | 0.0047436 | 0.0047568 | 0.0047568 | 0.99667 | -0.036284 | 0.99666 | -0.036206 | 2.1622
156 | 0.098945 | 0.047561 | -0.098945 | -0.047921 | 2.0573e-07 | -0.00036085 | 0.0031799 | 0.0031844 | 0.0031844 | 0.99663 | -0.035934 | 0.99662 | -0.035916 | 1.4475
157 | -0.28454 | -0.13781 | 0.28455 | 0.13714 | 3.1656e-06 | -0.00066667 | 0.0091699 | 0.0091615 | 0.0091699 | 0.9953 | -0.033645 | 0.99531 | -0.033742 | 4.1681
158 | -0.28455 | -0.13714 | 0.28455 | 0.13663 | 2.446e-06 | -0.00051598 | 0.0091615 | 0.009155 | 0.0091615 | 0.99531 | -0.033742 | 0.99532 | -0.033816 | 4.1643
159 | -0.35619 | -0.17133 | 0.3562 | 0.17059 | 5.4911e-06 | -0.0007393 | 0.011464 | 0.011454 | 0.011464 | 0.99532 | -0.033816 | 0.99533 | -0.033947 | 5.2108
160 | -0.3562 | -0.17059 | 0.3562 | 0.1704 | 1.377e-06 | -0.00018558 | 0.011454 | 0.011452 | 0.011454 | 0.99533 | -0.033947 | 0.99533 | -0.03398 | 5.2066
161 | 0.19287 | 0.091901 | -0.19287 | -0.092755 | 1.857e-06 | -0.00085492 | 0.0061964 | 0.0062071 | 0.0062071 | 0.99533 | -0.03398 | 0.99533 | -0.033898 | 2.8214
162 | -0.54907 | -0.2623 | 0.54908 | 0.26192 | 6.7061e-06 | -0.0003796 | 0.017648 | 0.017644 | 0.017648 | 0.99533 | -0.03398 | 0.99535 | -0.034083 | 8.022
163 | -0.28416 | -0.13763 | 0.28416 | 0.13751 | 5.3432e-07 | -0.00011305 | 0.0091513 | 0.0091499 | 0.0091513 | 0.99598 | -0.039678 | 0.99598 | -0.039694 | 4.1597
164 | 1.6145 | 0.7586 | -1.6142 | -0.76025 | 0.00026126 | -0.0016554 | 0.051703 | 0.051724 | 0.051724 | 0.99598 | -0.039694 | 0.99583 | -0.038375 | 23.511
165 | -1.8987 | -0.89611 | 1.8996 | 0.89178 | 0.00096183 | -0.0043293 | 0.060852 | 0.060795 | 0.060852 | 0.99598 | -0.039694 | 0.99645 | -0.043829 | 27.6601
166 | 1.342 | 0.63122 | -1.3415 | -0.63656 | 0.00057478 | -0.0053341 | 0.042992 | 0.04306 | 0.04306 | 0.99583 | -0.038375 | 0.99543 | -0.034847 | 19.5727
167 | 0.14725 | 0.069035 | -0.14725 | -0.070191 | 1.4536e-06 | -0.001156 | 0.0047144 | 0.0047287 | 0.0047287 | 0.99583 | -0.038375 | 0.99582 | -0.038293 | 2.1494
168 | 0.12496 | 0.059996 | -0.12496 | -0.060521 | 4.7938e-07 | -0.00052554 | 0.0040183 | 0.0040249 | 0.0040249 | 0.99583 | -0.038375 | 0.99582 | -0.038342 | 1.8295
169 | -1.8996 | -0.89178 | 1.8996 | 0.89173 | 1.2385e-05 | -5.5831e-05 | 0.060795 | 0.060795 | 0.060795 | 0.99645 | -0.043829 | 0.99645 | -0.043882 | 27.6342
170 | 0.4434 | 0.21468 | -0.4434 | -0.21475 | 8.1371e-07 | -7.0402e-05 | 0.014287 | 0.014287 | 0.014287 | 0.99543 | -0.034847 | 0.99543 | -0.034831 | 6.4943
171 | 0.11348 | 0.049483 | -0.11348 | -0.054516 | 3.7227e-06 | -0.0050329 | 0.0035903 | 0.0036511 | 0.0036511 | 0.99543 | -0.034847 | 0.9954 | -0.034596 | 1.6596
172 | 0.78457 | 0.3724 | -0.78451 | -0.37393 | 5.5421e-05 | -0.0015307 | 0.025185 | 0.025205 | 0.025205 | 0.99543 | -0.034847 | 0.99536 | -0.034256 | 11.4567
173 | 0.14725 | 0.070191 | -0.14725 | -0.071315 | 1.4223e-06 | -0.0011243 | 0.0047287 | 0.0047428 | 0.0047428 | 0.99582 | -0.038293 | 0.99581 | -0.038211 | 2.1558
174 | 0.11348 | 0.054516 | -0.11348 | -0.05496 | 3.347e-07 | -0.00044415 | 0.0036511 | 0.0036567 | 0.0036567 | 0.9954 | -0.034596 | 0.9954 | -0.03457 | 1.6621
175 | 0.63273 | 0.30188 | -0.63271 | -0.30243 | 1.2975e-05 | -0.00055213 | 0.020332 | 0.020339 | 0.020339 | 0.99536 | -0.034256 | 0.99535 | -0.034083 | 9.2449
176 | 0.15178 | 0.072049 | -0.15178 | -0.073228 | 1.5854e-06 | -0.0011791 | 0.0048728 | 0.0048876 | 0.0048876 | 0.99536 | -0.034256 | 0.99535 | -0.034167 | 2.2216
177 | 0.33405 | 0.16101 | -0.33405 | -0.16112 | 7.138e-07 | -0.0001096 | 0.010743 | 0.010744 | 0.010744 | 0.99645 | -0.043882 | 0.99645 | -0.043864 | 4.8839
178 | -2.4588 | -1.1618 | 2.4593 | 1.162 | 0.00053612 | 0.00027833 | 0.078782 | 0.078781 | 0.078782 | 0.99645 | -0.043882 | 0.99668 | -0.042311 | 37.5152
179 | 0.15178 | 0.073228 | -0.15178 | -0.073512 | 3.8305e-07 | -0.0002838 | 0.0048876 | 0.0048911 | 0.0048911 | 0.99535 | -0.034167 | 0.99535 | -0.034146 | 2.2232
180 | 0.33405 | 0.16112 | -0.33405 | -0.16134 | 1.4005e-06 | -0.00021496 | 0.010744 | 0.010747 | 0.010747 | 0.99645 | -0.043864 | 0.99645 | -0.043828 | 4.8851
181 | -2.4593 | -1.162 | 2.4597 | 1.1611 | 0.00037092 | -0.00095208 | 0.078781 | 0.078768 | 0.078781 | 0.99668 | -0.042311 | 0.99683 | -0.043552 | 35.8097
182 | 0.33405 | 0.16134 | -0.33405 | -0.16143 | 6.0959e-07 | -9.3532e-05 | 0.010747 | 0.010748 | 0.010748 | 0.99645 | -0.043828 | 0.99645 | -0.043812 | 4.8856
183 | 0.088025 | 0.042278 | -0.088025 | -0.042632 | 1.6019e-07 | -0.00035482 | 0.002829 | 0.0028335 | 0.0028335 | 0.99645 | -0.043812 | 0.99645 | -0.043796 | 1.2879
184 | -0.13772 | -0.066699 | 0.13772 | 0.065902 | 8.8234e-07 | -0.00079711 | 0.0044355 | 0.0044254 | 0.0044355 | 0.9959 | -0.062074 | 0.99591 | -0.062129 | 2.0161
185 | -0.13772 | -0.065902 | 0.13772 | 0.065384 | 5.7175e-07 | -0.00051845 | 0.0044254 | 0.004419 | 0.0044254 | 0.99591 | -0.062129 | 0.99591 | -0.062164 | 2.0116
186 | 2.585 | 1.2046 | -2.5845 | -1.2058 | 0.00052113 | -0.0011977 | 0.082665 | 0.082682 | 0.082682 | 0.99591 | -0.062164 | 0.99572 | -0.060554 | 37.5826
187 | -2.7227 | -1.27 | 2.7236 | 1.2705 | 0.00091809 | 0.00049458 | 0.087084 | 0.087083 | 0.087084 | 0.99591 | -0.062164 | 0.99627 | -0.059627 | 41.4685
188 | -3.1107 | -1.458 | 3.1108 | 1.4578 | 9.8975e-05 | -0.00014796 | 0.099545 | 0.099543 | 0.099545 | 0.99627 | -0.059627 | 0.9963 | -0.059884 | 45.2476
189 | 2.49 | 1.16 | -2.4897 | -1.1607 | 0.00026096 | -0.00065205 | 0.079638 | 0.079647 | 0.079647 | 0.99572 | -0.060554 | 0.99562 | -0.059718 | 36.2031
190 | 2.4897 | 1.1607 | -2.4896 | -1.161 | 0.00012136 | -0.00030313 | 0.079647 | 0.079651 | 0.079651 | 0.99562 | -0.059718 | 0.99558 | -0.059329 | 36.205
191 | -0.069869 | -0.033839 | 0.069869 | 0.03328 | 1.5936e-07 | -0.00055921 | 0.002251 | 0.002244 | 0.002251 | 0.99558 | -0.05931 | 0.99558 | -0.059329 | 1.0232
192 | 0.14832 | 0.071301 | -0.14832 | -0.071836 | 6.8442e-07 | -0.00053467 | 0.0047656 | 0.0047723 | 0.0047723 | 0.99689 | -0.064985 | 0.99689 | -0.064945 | 2.1692
193 | 0.19287 | 0.092755 | -0.19287 | -0.09341 | 1.427e-06 | -0.00065496 | 0.0062071 | 0.0062154 | 0.0062154 | 0.99533 | -0.033898 | 0.99532 | -0.033834 | 2.8252
194 | 0.42327 | 0.20365 | -0.42325 | -0.20499 | 1.4216e-05 | -0.0013386 | 0.013655 | 0.013672 | 0.013672 | 0.99298 | -0.041341 | 0.99295 | -0.041051 | 6.2146

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 20.7338 | 9.7548

## res_load
| p_mw | q_mvar
0 | 0.35067 | 0.16984
1 | 0.089672 | 0.04343
2 | 0.40235 | 0.19487
3 | 0.11062 | 0.053575
4 | 0.36714 | 0.17781
5 | 0.11314 | 0.054796
6 | 0.40112 | 0.19427
7 | 0.083363 | 0.040375
8 | 0.3739 | 0.18109
9 | 0.27861 | 0.13494
10 | 0.093071 | 0.045077
11 | 0.24581 | 0.11905
12 | 0.30123 | 0.14589
13 | 0.34857 | 0.16882
14 | 0.12313 | 0.059634
15 | 0.32343 | 0.15664
16 | 0.38939 | 0.18859
17 | 0.40279 | 0.19508
18 | 0.28277 | 0.13695
19 | 0.28531 | 0.13818
20 | 0.12798 | 0.061982
21 | 0.39738 | 0.19246
22 | 0.080894 | 0.039179
23 | 0.082026 | 0.039727
24 | 0.35438 | 0.17163
25 | 0.19895 | 0.096354
26 | 0.077895 | 0.037726
27 | 0.26595 | 0.1288
28 | 0.34594 | 0.16755
29 | 0.082618 | 0.040014
30 | 0.32896 | 0.15932
31 | 0.34088 | 0.1651
32 | 0.11515 | 0.055771
33 | 0.40497 | 0.19614
34 | 0.16027 | 0.077623
35 | 0.34814 | 0.16861
36 | 0.17682 | 0.085636
37 | 0.33413 | 0.16183
38 | 0.23525 | 0.11394
39 | 0.32993 | 0.15979
40 | 0.085085 | 0.041208
41 | 0.09392 | 0.045488
42 | 0.37313 | 0.18071
43 | 0.35384 | 0.17137
44 | 0.086892 | 0.042084
45 | 0.18869 | 0.091387
46 | 0.41141 | 0.19925
47 | 0.11413 | 0.055278
48 | 0.071449 | 0.034604
49 | 0.31457 | 0.15235
50 | 0.30994 | 0.15011
51 | 0.069649 | 0.033732
52 | 0.30219 | 0.14636
53 | 0.080994 | 0.039227
54 | 0.36263 | 0.17563
55 | 0.075798 | 0.036711
56 | 0.10973 | 0.053147
57 | 0.1415 | 0.068532
58 | 0.089953 | 0.043566
59 | 0.40123 | 0.19432
60 | 0.087901 | 0.042573
61 | 0.37129 | 0.17982
62 | 0.088465 | 0.042846
63 | 0.10111 | 0.04897
64 | 0.17523 | 0.084869
65 | 0.32897 | 0.15933
66 | 0.25821 | 0.12506
67 | 0.11908 | 0.057672
68 | 0.076082 | 0.036848
69 | 0.14781 | 0.071587
70 | 0.098945 | 0.047921
71 | 0.28454 | 0.13781
72 | 0.071642 | 0.034698
73 | 0.28416 | 0.13763
74 | 0.12496 | 0.060521
75 | 0.4434 | 0.21475
76 | 0.11348 | 0.05496
77 | 0.14725 | 0.071315
78 | 0.22508 | 0.10901
79 | 0.083635 | 0.040506
80 | 0.24602 | 0.11916
81 | 0.088025 | 0.042632
82 | 0.15178 | 0.073512
83 | 0.12174 | 0.05896
84 | 0.13772 | 0.066699
85 | 0.38711 | 0.18749
86 | 0.094497 | 0.045767
87 | 0.069869 | 0.033839
88 | 0.072418 | 0.035074
89 | 0.14832 | 0.071836
90 | 0.19287 | 0.09341
91 | 0.70754 | 0.34268
92 | 0.42325 | 0.20499

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1