## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_538_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_538_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_538_0_node_11 | 20 | n |  | TRUE
3 | bus_MV_538_0_node_12 | 20 | n |  | TRUE
4 | bus_MV_538_0_node_82 | 20 | n |  | TRUE
5 | bus_MV_538_0_node_2 | 20 | n |  | TRUE
6 | bus_MV_538_0_node_47 | 20 | n |  | TRUE
7 | bus_MV_538_0_node_79 | 20 | n |  | TRUE
8 | bus_MV_538_0_node_48 | 20 | n |  | TRUE
9 | bus_MV_538_0_node_78 | 20 | n |  | TRUE
10 | bus_MV_538_0_node_3 | 20 | n |  | TRUE
11 | bus_MV_538_0_node_4 | 20 | n |  | TRUE
12 | bus_MV_538_0_node_10 | 20 | n |  | TRUE
13 | bus_MV_538_0_node_5 | 20 | n |  | TRUE
14 | bus_MV_538_0_node_6 | 20 | n |  | TRUE
15 | bus_MV_538_0_node_9 | 20 | n |  | TRUE
16 | bus_MV_538_0_node_42 | 20 | n |  | TRUE
17 | bus_MV_538_0_node_44 | 20 | n |  | TRUE
18 | bus_MV_538_0_node_43 | 20 | n |  | TRUE
19 | bus_MV_538_0_node_26 | 20 | n |  | TRUE
20 | bus_MV_538_0_node_28 | 20 | n |  | TRUE
21 | bus_MV_538_0_node_27 | 20 | n |  | TRUE
22 | bus_MV_538_0_node_29 | 20 | n |  | TRUE
23 | bus_MV_538_0_node_191 | 20 | n |  | TRUE
24 | bus_MV_538_0_node_30 | 20 | n |  | TRUE
25 | bus_MV_538_0_node_49 | 20 | n |  | TRUE
26 | bus_MV_538_0_node_118 | 20 | n |  | TRUE
27 | bus_MV_538_0_node_45 | 20 | n |  | TRUE
28 | bus_MV_538_0_node_46 | 20 | n |  | TRUE
29 | bus_MV_538_0_node_119 | 20 | n |  | TRUE
30 | bus_MV_538_0_node_54 | 20 | n |  | TRUE
31 | bus_MV_538_0_node_61 | 20 | n |  | TRUE
32 | bus_MV_538_0_node_7 | 20 | n |  | TRUE
33 | bus_MV_538_0_node_34 | 20 | n |  | TRUE
34 | bus_MV_538_0_node_32 | 20 | n |  | TRUE
35 | bus_MV_538_0_node_70 | 20 | n |  | TRUE
36 | bus_MV_538_0_node_60 | 20 | n |  | TRUE
37 | bus_MV_538_0_node_36 | 20 | n |  | TRUE
38 | bus_MV_538_0_node_33 | 20 | n |  | TRUE
39 | bus_MV_538_0_node_69 | 20 | n |  | TRUE
40 | bus_MV_538_0_node_13 | 20 | n |  | TRUE
41 | bus_MV_538_0_node_14 | 20 | n |  | TRUE
42 | bus_MV_538_0_node_15 | 20 | n |  | TRUE
43 | bus_MV_538_0_node_16 | 20 | n |  | TRUE
44 | bus_MV_538_0_node_59 | 20 | n |  | TRUE
45 | bus_MV_538_0_node_146 | 20 | n |  | TRUE
46 | bus_MV_538_0_node_25 | 20 | n |  | TRUE
47 | bus_MV_538_0_node_58 | 20 | n |  | TRUE
48 | bus_MV_538_0_node_57 | 20 | n |  | TRUE
49 | bus_MV_538_0_node_100 | 20 | n |  | TRUE
50 | bus_MV_538_0_node_145 | 20 | n |  | TRUE
51 | bus_MV_538_0_node_17 | 20 | n |  | TRUE
52 | bus_MV_538_0_node_18 | 20 | n |  | TRUE
53 | bus_MV_538_0_node_20 | 20 | n |  | TRUE
54 | bus_MV_538_0_node_23 | 20 | n |  | TRUE
55 | bus_MV_538_0_node_19 | 20 | n |  | TRUE
56 | bus_MV_538_0_node_111 | 20 | n |  | TRUE
57 | bus_MV_538_0_node_108 | 20 | n |  | TRUE
58 | bus_MV_538_0_node_185 | 20 | n |  | TRUE
59 | bus_MV_538_0_node_21 | 20 | n |  | TRUE
60 | bus_MV_538_0_node_22 | 20 | n |  | TRUE
61 | bus_MV_538_0_node_24 | 20 | n |  | TRUE
62 | bus_MV_538_0_node_163 | 20 | n |  | TRUE
63 | bus_MV_538_0_node_177 | 20 | n |  | TRUE
64 | bus_MV_538_0_node_139 | 20 | n |  | TRUE
65 | bus_MV_538_0_node_184 | 20 | n |  | TRUE
66 | bus_MV_538_0_node_130 | 20 | n |  | TRUE
67 | bus_MV_538_0_node_126 | 20 | n |  | TRUE
68 | bus_MV_538_0_node_112 | 20 | n |  | TRUE
69 | bus_MV_538_0_node_113 | 20 | n |  | TRUE
70 | bus_MV_538_0_node_151 | 20 | n |  | TRUE
71 | bus_MV_538_0_node_155 | 20 | n |  | TRUE
72 | bus_MV_538_0_node_154 | 20 | n |  | TRUE
73 | bus_MV_538_0_node_168 | 20 | n |  | TRUE
74 | bus_MV_538_0_node_109 | 20 | n |  | TRUE
75 | bus_MV_538_0_node_41 | 20 | n |  | TRUE
76 | bus_MV_538_0_node_140 | 20 | n |  | TRUE
77 | bus_MV_538_0_node_138 | 20 | n |  | TRUE
78 | bus_MV_538_0_node_76 | 20 | n |  | TRUE
79 | bus_MV_538_0_node_125 | 20 | n |  | TRUE
80 | bus_MV_538_0_node_71 | 20 | n |  | TRUE
81 | bus_MV_538_0_node_72 | 20 | n |  | TRUE
82 | bus_MV_538_0_node_55 | 20 | n |  | TRUE
83 | bus_MV_538_0_node_35 | 20 | n |  | TRUE
84 | bus_MV_538_0_node_37 | 20 | n |  | TRUE
85 | bus_MV_538_0_node_38 | 20 | n |  | TRUE
86 | bus_MV_538_0_node_39 | 20 | n |  | TRUE
87 | bus_MV_538_0_node_40 | 20 | n |  | TRUE
88 | bus_MV_538_0_node_144 | 20 | n |  | TRUE
89 | bus_MV_538_0_node_103 | 20 | n |  | TRUE
90 | bus_MV_538_0_node_95 | 20 | n |  | TRUE
91 | bus_MV_538_0_node_104 | 20 | n |  | TRUE
92 | bus_MV_538_0_node_102 | 20 | n |  | TRUE
93 | bus_MV_538_0_node_52 | 20 | n |  | TRUE
94 | bus_MV_538_0_node_51 | 20 | n |  | TRUE
95 | bus_MV_538_0_node_50 | 20 | n |  | TRUE
96 | bus_MV_538_0_node_53 | 20 | n |  | TRUE
97 | bus_MV_538_0_node_56 | 20 | n |  | TRUE
98 | bus_MV_538_0_node_73 | 20 | n |  | TRUE
99 | bus_MV_538_0_node_187 | 20 | n |  | TRUE
100 | bus_MV_538_0_node_179 | 20 | n |  | TRUE
101 | bus_MV_538_0_node_101 | 20 | n |  | TRUE
102 | bus_MV_538_0_node_62 | 20 | n |  | TRUE
103 | bus_MV_538_0_node_63 | 20 | n |  | TRUE
104 | bus_MV_538_0_node_68 | 20 | n |  | TRUE
105 | bus_MV_538_0_node_66 | 20 | n |  | TRUE
106 | bus_MV_538_0_node_67 | 20 | n |  | TRUE
107 | bus_MV_538_0_node_170 | 20 | n |  | TRUE
108 | bus_MV_538_0_node_147 | 20 | n |  | TRUE
109 | bus_MV_538_0_node_169 | 20 | n |  | TRUE
110 | bus_MV_538_0_node_64 | 20 | n |  | TRUE
111 | bus_MV_538_0_node_65 | 20 | n |  | TRUE
112 | bus_MV_538_0_node_171 | 20 | n |  | TRUE
113 | bus_MV_538_0_node_148 | 20 | n |  | TRUE
114 | bus_MV_538_0_node_74 | 20 | n |  | TRUE
115 | bus_MV_538_0_node_75 | 20 | n |  | TRUE
116 | bus_MV_538_0_node_77 | 20 | n |  | TRUE
117 | bus_MV_538_0_node_80 | 20 | n |  | TRUE
118 | bus_MV_538_0_node_81 | 20 | n |  | TRUE
119 | bus_MV_538_0_node_136 | 20 | n |  | TRUE
120 | bus_MV_538_0_node_129 | 20 | n |  | TRUE
121 | bus_MV_538_0_node_87 | 20 | n |  | TRUE
122 | bus_MV_538_0_node_178 | 20 | n |  | TRUE
123 | bus_MV_538_0_node_84 | 20 | n |  | TRUE
124 | bus_MV_538_0_node_86 | 20 | n |  | TRUE
125 | bus_MV_538_0_node_83 | 20 | n |  | TRUE
126 | bus_MV_538_0_node_88 | 20 | n |  | TRUE
127 | bus_MV_538_0_node_128 | 20 | n |  | TRUE
128 | bus_MV_538_0_node_85 | 20 | n |  | TRUE
129 | bus_MV_538_0_node_89 | 20 | n |  | TRUE
130 | bus_MV_538_0_node_98 | 20 | n |  | TRUE
131 | bus_MV_538_0_node_90 | 20 | n |  | TRUE
132 | bus_MV_538_0_node_91 | 20 | n |  | TRUE
133 | bus_MV_538_0_node_92 | 20 | n |  | TRUE
134 | bus_MV_538_0_node_93 | 20 | n |  | TRUE
135 | bus_MV_538_0_node_94 | 20 | n |  | TRUE
136 | bus_MV_538_0_node_124 | 20 | n |  | TRUE
137 | bus_MV_538_0_node_123 | 20 | n |  | TRUE
138 | bus_MV_538_0_node_188 | 20 | n |  | TRUE
139 | bus_MV_538_0_node_96 | 20 | n |  | TRUE
140 | bus_MV_538_0_node_97 | 20 | n |  | TRUE
141 | bus_MV_538_0_node_115 | 20 | n |  | TRUE
142 | bus_MV_538_0_node_116 | 20 | n |  | TRUE
143 | bus_MV_538_0_node_164 | 20 | n |  | TRUE
144 | bus_MV_538_0_node_186 | 20 | n |  | TRUE
145 | bus_MV_538_0_node_105 | 20 | n |  | TRUE
146 | bus_MV_538_0_node_106 | 20 | n |  | TRUE
147 | bus_MV_538_0_node_107 | 20 | n |  | TRUE
148 | bus_MV_538_0_node_189 | 20 | n |  | TRUE
149 | bus_MV_538_0_node_166 | 20 | n |  | TRUE
150 | bus_MV_538_0_node_176 | 20 | n |  | TRUE
151 | bus_MV_538_0_node_165 | 20 | n |  | TRUE
152 | bus_MV_538_0_node_110 | 20 | n |  | TRUE
153 | bus_MV_538_0_node_114 | 20 | n |  | TRUE
154 | bus_MV_538_0_node_117 | 20 | n |  | TRUE
155 | bus_MV_538_0_node_131 | 20 | n |  | TRUE
156 | bus_MV_538_0_node_150 | 20 | n |  | TRUE
157 | bus_MV_538_0_node_152 | 20 | n |  | TRUE
158 | bus_MV_538_0_node_167 | 20 | n |  | TRUE
159 | bus_MV_538_0_node_132 | 20 | n |  | TRUE
160 | bus_MV_538_0_node_135 | 20 | n |  | TRUE
161 | bus_MV_538_0_node_133 | 20 | n |  | TRUE
162 | bus_MV_538_0_node_141 | 20 | n |  | TRUE
163 | bus_MV_538_0_node_142 | 20 | n |  | TRUE
164 | bus_MV_538_0_node_120 | 20 | n |  | TRUE
165 | bus_MV_538_0_node_121 | 20 | n |  | TRUE
166 | bus_MV_538_0_node_122 | 20 | n |  | TRUE
167 | bus_MV_538_0_node_175 | 20 | n |  | TRUE
168 | bus_MV_538_0_node_159 | 20 | n |  | TRUE
169 | bus_MV_538_0_node_183 | 20 | n |  | TRUE
170 | bus_MV_538_0_node_127 | 20 | n |  | TRUE
171 | bus_MV_538_0_node_162 | 20 | n |  | TRUE
172 | bus_MV_538_0_node_137 | 20 | n |  | TRUE
173 | bus_MV_538_0_node_143 | 20 | n |  | TRUE
174 | bus_MV_538_0_node_190 | 20 | n |  | TRUE
175 | bus_MV_538_0_node_149 | 20 | n |  | TRUE
176 | bus_MV_538_0_node_153 | 20 | n |  | TRUE
177 | bus_MV_538_0_node_156 | 20 | n |  | TRUE
178 | bus_MV_538_0_node_157 | 20 | n |  | TRUE
179 | bus_MV_538_0_node_158 | 20 | n |  | TRUE
180 | bus_MV_538_0_node_161 | 20 | n |  | TRUE
181 | bus_MV_538_0_node_160 | 20 | n |  | TRUE
182 | bus_MV_538_0_node_174 | 20 | n |  | TRUE
183 | bus_MV_538_0_node_173 | 20 | n |  | TRUE
184 | bus_MV_538_0_node_172 | 20 | n |  | TRUE
185 | bus_MV_538_0_node_180 | 20 | n |  | TRUE
186 | bus_MV_538_0_node_181 | 20 | n |  | TRUE
187 | bus_MV_538_0_node_182 | 20 | n |  | TRUE
188 | bus_HV_538_0_node_140 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_538_0_load_0 | 0 | 0.25647 | 0.12421 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_538_0_load_82 | 4 | 0.085466 | 0.041393 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_538_0_load_47 | 6 | 0.32369 | 0.15677 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_538_0_load_3 | 10 | 0.26001 | 0.12593 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_538_0_load_42 | 16 | 0.39469 | 0.19116 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_538_0_load_43 | 18 | 0.29035 | 0.14062 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_538_0_load_26 | 19 | 0.21518 | 0.10422 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_538_0_load_28 | 20 | 0.068285 | 0.033072 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_538_0_load_191 | 23 | 0.35392 | 0.17141 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_538_0_load_49 | 25 | 0.40525 | 0.19627 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_538_0_load_118 | 26 | 0.088442 | 0.042834 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_538_0_load_45 | 27 | 0.07102 | 0.034396 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_538_0_load_119 | 29 | 0.13725 | 0.066473 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_538_0_load_54 | 30 | 0.17618 | 0.085326 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_538_0_load_61 | 31 | 0.38992 | 0.18885 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_538_0_load_32 | 34 | 0.28375 | 0.13742 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_538_0_load_60 | 36 | 0.34095 | 0.16513 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_538_0_load_36 | 37 | 0.22456 | 0.10876 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_538_0_load_69 | 39 | 0.27707 | 0.13419 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_538_0_load_13 | 40 | 0.33856 | 0.16397 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_538_0_load_146 | 45 | 0.12545 | 0.060759 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_538_0_load_25 | 46 | 0.29606 | 0.14339 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_538_0_load_57 | 48 | 0.25409 | 0.12306 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_538_0_load_100 | 49 | 0.2489 | 0.12055 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_538_0_load_17 | 51 | 0.32963 | 0.15965 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_538_0_load_108 | 57 | 0.22201 | 0.10753 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_538_0_load_185 | 58 | 0.34386 | 0.16654 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_538_0_load_163 | 62 | 0.2294 | 0.1111 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_538_0_load_177 | 63 | 0.14504 | 0.070248 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_538_0_load_184 | 65 | 0.096934 | 0.046947 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_538_0_load_130 | 66 | 0.19074 | 0.09238 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_538_0_load_151 | 70 | 0.07608 | 0.036847 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_538_0_load_155 | 71 | 0.0842 | 0.04078 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_538_0_load_168 | 73 | 0.12211 | 0.05914 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_538_0_load_140 | 76 | 0.82488 | 0.39951 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_538_0_load_76 | 78 | 0.31052 | 0.15039 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_538_0_load_125 | 79 | 0.13742 | 0.066556 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_538_0_load_72 | 81 | 0.29038 | 0.14064 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_538_0_load_37 | 84 | 0.3885 | 0.18816 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_538_0_load_144 | 88 | 0.085133 | 0.041232 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_538_0_load_102 | 92 | 0.38245 | 0.18523 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_538_0_load_52 | 93 | 0.083875 | 0.040622 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_538_0_load_50 | 95 | 0.40865 | 0.19792 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_538_0_load_73 | 98 | 0.34885 | 0.16895 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_538_0_load_187 | 99 | 0.42224 | 0.2045 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_538_0_load_62 | 102 | 0.40967 | 0.19841 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_538_0_load_170 | 107 | 0.08331 | 0.040349 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_538_0_load_147 | 108 | 0.53468 | 0.25896 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_538_0_load_169 | 109 | 0.10318 | 0.049972 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_538_0_load_64 | 110 | 0.26827 | 0.12993 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_538_0_load_74 | 114 | 0.31656 | 0.15332 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_538_0_load_77 | 116 | 0.31464 | 0.15239 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_538_0_load_136 | 119 | 0.091825 | 0.044473 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_538_0_load_129 | 120 | 0.0942 | 0.045623 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_538_0_load_178 | 122 | 0.41857 | 0.20272 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_538_0_load_83 | 125 | 0.31754 | 0.15379 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_538_0_load_88 | 126 | 0.23657 | 0.11458 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_538_0_load_128 | 127 | 0.083344 | 0.040365 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_538_0_load_85 | 128 | 0.11141 | 0.053957 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_538_0_load_91 | 132 | 0.41163 | 0.19936 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_538_0_load_92 | 133 | 0.070964 | 0.034369 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_538_0_load_123 | 137 | 0.077385 | 0.037479 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_538_0_load_188 | 138 | 0.29993 | 0.14526 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_538_0_load_96 | 139 | 0.15513 | 0.075132 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_538_0_load_115 | 141 | 0.16054 | 0.077751 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_538_0_load_164 | 143 | 0.19941 | 0.096577 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_538_0_load_186 | 144 | 0.31387 | 0.15201 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_538_0_load_105 | 145 | 0.13114 | 0.063512 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_538_0_load_189 | 148 | 0.4107 | 0.19891 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_538_0_load_176 | 150 | 0.10577 | 0.051226 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_538_0_load_165 | 151 | 0.1166 | 0.05647 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_538_0_load_110 | 152 | 0.094348 | 0.045695 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_538_0_load_131 | 155 | 0.12323 | 0.059682 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_538_0_load_152 | 157 | 0.15251 | 0.073866 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_538_0_load_167 | 158 | 0.099942 | 0.048404 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_538_0_load_133 | 161 | 0.084866 | 0.041102 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_538_0_load_141 | 162 | 0.36082 | 0.17475 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_538_0_load_120 | 164 | 0.30518 | 0.14781 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_538_0_load_175 | 167 | 0.068275 | 0.033067 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_538_0_load_127 | 170 | 0.23349 | 0.11308 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_538_0_load_162 | 171 | 0.10467 | 0.050692 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_538_0_load_137 | 172 | 0.11082 | 0.053672 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_538_0_load_190 | 174 | 0.21592 | 0.10457 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_538_0_load_149 | 175 | 0.24685 | 0.11956 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_538_0_load_153 | 176 | 0.07019 | 0.033995 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_538_0_load_156 | 177 | 0.09241 | 0.044756 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_538_0_load_161 | 180 | 0.092401 | 0.044752 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_538_0_load_174 | 182 | 0.080786 | 0.039126 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_538_0_load_173 | 183 | 0.072009 | 0.034876 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_538_0_load_180 | 185 | 0.26802 | 0.12981 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_538_0_load_181 | 186 | 0.3921 | 0.1899 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 76 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_538_0_line_0 |  | 0 | 1 | 0.010221 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_538_0_line_1 |  | 1 | 2 | 0.084661 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_538_0_line_2 |  | 2 | 3 | 0.19793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_538_0_line_3 |  | 2 | 4 | 0.0013227 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_538_0_line_4 |  | 3 | 31 | 0.016525 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_538_0_line_5 |  | 4 | 7 | 0.036434 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_538_0_line_6 |  | 5 | 6 | 0.033499 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
7 | MV_538_0_line_7 |  | 5 | 7 | 0.10922 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
8 | MV_538_0_line_8 |  | 6 | 8 | 0.017889 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
9 | MV_538_0_line_9 |  | 7 | 9 | 0.1059 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
10 | MV_538_0_line_10 |  | 8 | 28 | 0.056054 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
11 | MV_538_0_line_11 |  | 9 | 117 | 0.058413 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
12 | MV_538_0_line_12 |  | 9 | 116 | 0.026197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_538_0_line_13 |  | 10 | 11 | 0.018522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_538_0_line_14 |  | 11 | 12 | 0.058262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_538_0_line_15 |  | 12 | 30 | 0.003811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_538_0_line_16 |  | 13 | 14 | 0.054857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_538_0_line_17 |  | 13 | 15 | 0.14065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_538_0_line_18 |  | 13 | 16 | 0.04014 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_538_0_line_19 |  | 14 | 30 | 0.033523 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_538_0_line_20 |  | 15 | 17 | 0.036285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_538_0_line_21 |  | 15 | 18 | 0.02077 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_538_0_line_22 |  | 16 | 35 | 0.078391 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_538_0_line_23 |  | 17 | 27 | 0.032866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_538_0_line_24 |  | 17 | 28 | 0.041666 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_538_0_line_25 |  | 19 | 20 | 0.043371 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_538_0_line_26 |  | 19 | 21 | 0.010519 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_538_0_line_27 |  | 20 | 23 | 0.079547 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
28 | MV_538_0_line_28 |  | 21 | 22 | 0.14875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_538_0_line_29 |  | 22 | 24 | 0.21473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_538_0_line_30 |  | 22 | 25 | 0.01942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_538_0_line_31 |  | 23 | 80 | 0.012763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_538_0_line_32 |  | 24 | 26 | 0.036148 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_538_0_line_33 |  | 27 | 29 | 0.019326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_538_0_line_34 |  | 28 | 93 | 0.025887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_538_0_line_35 |  | 30 | 36 | 0.10387 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_538_0_line_36 |  | 32 | 33 | 0.017229 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_538_0_line_37 |  | 32 | 34 | 0.027647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_538_0_line_38 |  | 33 | 37 | 0.02555 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_538_0_line_39 |  | 34 | 38 | 0.028552 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_538_0_line_40 |  | 35 | 39 | 0.048657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_538_0_line_41 |  | 35 | 80 | 0.0833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_538_0_line_42 |  | 36 | 83 | 0.01691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_538_0_line_43 |  | 38 | 83 | 0.036942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_538_0_line_44 |  | 40 | 41 | 0.008796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_538_0_line_45 |  | 41 | 42 | 0.065966 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_538_0_line_46 |  | 41 | 43 | 0.22708 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_538_0_line_47 |  | 42 | 44 | 0.065601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_538_0_line_48 |  | 42 | 45 | 0.023224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_538_0_line_49 |  | 43 | 46 | 0.002309 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_538_0_line_50 |  | 44 | 49 | 0.026936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_538_0_line_51 |  | 44 | 47 | 0.044465 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_538_0_line_52 |  | 45 | 50 | 0.031879 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_538_0_line_53 |  | 47 | 48 | 0.004036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_538_0_line_54 |  | 49 | 101 | 0.030089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_538_0_line_55 |  | 50 | 90 | 0.072143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_538_0_line_56 |  | 51 | 52 | 0.028083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_538_0_line_57 |  | 52 | 53 | 0.052427 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
58 | MV_538_0_line_58 |  | 52 | 54 | 0.11881 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
59 | MV_538_0_line_59 |  | 53 | 58 | 0.048215 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
60 | MV_538_0_line_60 |  | 53 | 55 | 0.033255 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
61 | MV_538_0_line_61 |  | 54 | 61 | 0.075936 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
62 | MV_538_0_line_62 |  | 54 | 64 | 0.042028 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
63 | MV_538_0_line_63 |  | 54 | 65 | 0.025929 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_538_0_line_64 |  | 55 | 56 | 0.083068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_538_0_line_65 |  | 55 | 57 | 0.031889 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_538_0_line_66 |  | 56 | 68 | 0.016644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_538_0_line_67 |  | 56 | 69 | 0.030426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_538_0_line_68 |  | 56 | 70 | 0.043819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_538_0_line_69 |  | 57 | 74 | 0.023606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_538_0_line_70 |  | 58 | 75 | 0.045015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_538_0_line_71 |  | 59 | 60 | 0.059108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_538_0_line_72 |  | 59 | 61 | 0.11654 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_538_0_line_73 |  | 59 | 62 | 0.037938 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_538_0_line_74 |  | 60 | 63 | 0.018697 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_538_0_line_75 |  | 61 | 66 | 0.028683 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_538_0_line_76 |  | 61 | 67 | 0.022072 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_538_0_line_77 |  | 64 | 76 | 0.028136 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
78 | MV_538_0_line_78 |  | 64 | 77 | 0.060336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_538_0_line_79 |  | 67 | 78 | 0.031658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_538_0_line_80 |  | 67 | 79 | 0.012244 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_538_0_line_81 |  | 68 | 71 | 0.015748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_538_0_line_82 |  | 68 | 72 | 0.035733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_538_0_line_83 |  | 69 | 73 | 0.017965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_538_0_line_84 |  | 72 | 156 | 0.004129 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_538_0_line_85 |  | 72 | 157 | 0.031334 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_538_0_line_86 |  | 73 | 158 | 0.040673 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_538_0_line_87 |  | 74 | 152 | 0.027404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_538_0_line_88 |  | 75 | 89 | 0.0482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_538_0_line_89 |  | 75 | 86 | 0.13762 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_538_0_line_90 |  | 77 | 172 | 0.026365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_538_0_line_91 |  | 78 | 115 | 0.017773 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_538_0_line_92 |  | 79 | 170 | 0.02573 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_538_0_line_93 |  | 81 | 82 | 0.056724 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_538_0_line_94 |  | 82 | 96 | 0.042397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_538_0_line_95 |  | 84 | 85 | 0.002175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_538_0_line_96 |  | 84 | 86 | 0.003745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_538_0_line_97 |  | 85 | 87 | 0.010982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_538_0_line_98 |  | 87 | 88 | 0.03726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_538_0_line_99 |  | 88 | 90 | 0.039292 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_538_0_line_100 |  | 89 | 91 | 0.076955 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_538_0_line_101 |  | 89 | 92 | 0.0068259 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_538_0_line_102 |  | 90 | 135 | 0.059165 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_538_0_line_103 |  | 91 | 144 | 0.042285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_538_0_line_104 |  | 93 | 94 | 0.0058691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_538_0_line_105 |  | 94 | 95 | 0.013747 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_538_0_line_106 |  | 95 | 96 | 0.049947 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_538_0_line_107 |  | 96 | 97 | 0.099419 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_538_0_line_108 |  | 97 | 98 | 0.02959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_538_0_line_109 |  | 99 | 100 | 0.031552 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_538_0_line_110 |  | 100 | 130 | 0.08849 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_538_0_line_111 |  | 100 | 121 | 0.011523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_538_0_line_112 |  | 101 | 111 | 0.092962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_538_0_line_113 |  | 102 | 103 | 0.003315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_538_0_line_114 |  | 103 | 104 | 0.017607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_538_0_line_115 |  | 104 | 109 | 0.017108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_538_0_line_116 |  | 104 | 106 | 0.02631 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_538_0_line_117 |  | 105 | 106 | 0.013315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_538_0_line_118 |  | 105 | 107 | 0.023695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_538_0_line_119 |  | 106 | 108 | 0.037443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_538_0_line_120 |  | 107 | 112 | 0.02484 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_538_0_line_121 |  | 108 | 113 | 0.046561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_538_0_line_122 |  | 110 | 111 | 0.006609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_538_0_line_123 |  | 112 | 184 | 0.008146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_538_0_line_124 |  | 113 | 175 | 0.008058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_538_0_line_125 |  | 114 | 115 | 0.028071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_538_0_line_126 |  | 117 | 118 | 0.059284 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
127 | MV_538_0_line_127 |  | 117 | 119 | 0.026897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_538_0_line_128 |  | 118 | 120 | 0.0056093 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
129 | MV_538_0_line_129 |  | 120 | 127 | 0.010573 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
130 | MV_538_0_line_130 |  | 121 | 122 | 0.029154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_538_0_line_131 |  | 121 | 123 | 0.092637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_538_0_line_132 |  | 121 | 124 | 0.026422 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_538_0_line_133 |  | 123 | 125 | 0.019325 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
134 | MV_538_0_line_134 |  | 124 | 126 | 0.001751 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_538_0_line_135 |  | 125 | 128 | 0.0019304 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_538_0_line_136 |  | 126 | 129 | 0.038657 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
137 | MV_538_0_line_137 |  | 127 | 170 | 0.023478 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
138 | MV_538_0_line_138 |  | 129 | 131 | 0.020974 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_538_0_line_139 |  | 130 | 143 | 0.021981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_538_0_line_140 |  | 130 | 140 | 0.031924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_538_0_line_141 |  | 131 | 132 | 0.032566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_538_0_line_142 |  | 133 | 134 | 0.038777 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_538_0_line_143 |  | 134 | 135 | 0.16493 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_538_0_line_144 |  | 135 | 136 | 0.1094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_538_0_line_145 |  | 135 | 137 | 0.052442 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_538_0_line_146 |  | 136 | 138 | 0.034393 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_538_0_line_147 |  | 138 | 169 | 0.005867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_538_0_line_148 |  | 139 | 140 | 0.033564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_538_0_line_149 |  | 139 | 141 | 0.094998 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
150 | MV_538_0_line_150 |  | 141 | 142 | 0.022649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_538_0_line_151 |  | 142 | 154 | 0.0097772 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_538_0_line_152 |  | 145 | 146 | 0.023344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_538_0_line_153 |  | 146 | 147 | 0.028618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_538_0_line_154 |  | 147 | 148 | 0.029366 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_538_0_line_155 |  | 147 | 149 | 0.063917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_538_0_line_156 |  | 149 | 150 | 0.077549 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
157 | MV_538_0_line_157 |  | 149 | 151 | 0.034375 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_538_0_line_158 |  | 150 | 166 | 0.020684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_538_0_line_159 |  | 152 | 153 | 0.028118 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_538_0_line_160 |  | 153 | 154 | 0.058506 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_538_0_line_161 |  | 153 | 155 | 0.018326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_538_0_line_162 |  | 154 | 162 | 0.028925 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_538_0_line_163 |  | 154 | 159 | 0.061601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_538_0_line_164 |  | 156 | 175 | 0.004135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_538_0_line_165 |  | 157 | 176 | 0.024334 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_538_0_line_166 |  | 159 | 160 | 0.086612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_538_0_line_167 |  | 159 | 161 | 0.054046 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_538_0_line_168 |  | 160 | 171 | 0.03316 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_538_0_line_169 |  | 162 | 163 | 0.034702 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_538_0_line_170 |  | 163 | 173 | 0.028253 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_538_0_line_171 |  | 164 | 165 | 0.056214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_538_0_line_172 |  | 165 | 166 | 0.046787 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_538_0_line_173 |  | 166 | 167 | 0.059342 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_538_0_line_174 |  | 167 | 168 | 0.033988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_538_0_line_175 |  | 168 | 181 | 0.031997 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_538_0_line_176 |  | 168 | 182 | 0.019436 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_538_0_line_177 |  | 168 | 178 | 0.014403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_538_0_line_178 |  | 169 | 187 | 0.11321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_538_0_line_179 |  | 173 | 174 | 0.004563 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_538_0_line_180 |  | 177 | 178 | 0.033897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_538_0_line_181 |  | 178 | 179 | 0.003078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
182 | MV_538_0_line_182 |  | 179 | 180 | 0.020572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
183 | MV_538_0_line_183 |  | 181 | 183 | 0.020842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
184 | MV_538_0_line_184 |  | 183 | 184 | 0.020667 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
185 | MV_538_0_line_185 |  | 185 | 186 | 0.028496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
186 | MV_538_0_line_186 |  | 186 | 187 | 0.006418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_538_0_trafo_140 | 25 MVA 110/20 kV | 188 | 76 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2683420.5542 | 1247295.8703
1 | 2683410.9819 | 1247292.233
2 | 2683326.5315 | 1247286.2637
3 | 2683284.3833 | 1247410.83
4 | 2683326.5639 | 1247284.9414
5 | 2683434.3803 | 1247224.3232
6 | 2683467.9398 | 1247225.0182
7 | 2683327.8779 | 1247248.5326
8 | 2683479.625 | 1247216.4875
9 | 2683276.9499 | 1247193.1654
10 | 2683417.5934 | 1247395.6688
11 | 2683399.0224 | 1247395.4297
12 | 2683414.9114 | 1247435.4159
13 | 2683472.5789 | 1247416.947
14 | 2683450.1645 | 1247443.4289
15 | 2683508.9266 | 1247287.2409
16 | 2683511.7734 | 1247425.6052
17 | 2683515.8864 | 1247251.6683
18 | 2683527.2813 | 1247296.9621
19 | 2683631.6575 | 1247334.5608
20 | 2683652.8806 | 1247372.3659
21 | 2683639.6997 | 1247327.7803
22 | 2683680.4056 | 1247241.7355
23 | 2683615.7942 | 1247442.739
24 | 2683736.7512 | 1247398.2795
25 | 2683662.2602 | 1247234.8149
26 | 2683704.0763 | 1247401.6435
27 | 2683548.2735 | 1247257.1322
28 | 2683523.1792 | 1247210.6964
29 | 2683567.1358 | 1247261.341
30 | 2683416.9889 | 1247438.6142
31 | 2683285.8996 | 1247427.0966
32 | 2683459.6963 | 1247585.0785
33 | 2683461.5631 | 1247602.1618
34 | 2683432.3699 | 1247589.2745
35 | 2683560.1227 | 1247487.3095
36 | 2683396.099 | 1247540.362
37 | 2683487.1627 | 1247601.0102
38 | 2683404.1356 | 1247593.5142
39 | 2683532.9047 | 1247527.6891
40 | 2682660.9528 | 1247157.9778
41 | 2682667.7093 | 1247152.3234
42 | 2682708.3623 | 1247122.7128
43 | 2682567.2125 | 1247117.0309
44 | 2682735.9634 | 1247082.2125
45 | 2682724.7928 | 1247139.0696
46 | 2682569.4116 | 1247116.4277
47 | 2682731.5085 | 1247048.5145
48 | 2682730.4645 | 1247052.4139
49 | 2682762.098 | 1247088.7357
50 | 2682747.0276 | 1247161.9143
51 | 2683090.5906 | 1247052.8708
52 | 2683071.4546 | 1247073.4623
53 | 2683036.1599 | 1247057.4452
54 | 2683121.6639 | 1247145.8078
55 | 2683037.486 | 1247034.5024
56 | 2682984.9709 | 1246977.2476
57 | 2683054.5154 | 1247007.5408
58 | 2682999.7065 | 1247088.9997
59 | 2683101.2172 | 1247265.8095
60 | 2683093.058 | 1247240.5655
61 | 2683129.3562 | 1247181.1861
62 | 2683137.9357 | 1247275.3065
63 | 2683075.8634 | 1247233.691
64 | 2683144.912 | 1247119.6367
65 | 2683101.8121 | 1247130.2736
66 | 2683117.4776 | 1247206.8876
67 | 2683150.985 | 1247185.8927
68 | 2682975.1956 | 1246979.4235
69 | 2682973.3125 | 1246995.7647
70 | 2683003.8155 | 1246937.7976
71 | 2682981.8483 | 1246965.1497
72 | 2682946.4331 | 1246958.1056
73 | 2682958.4944 | 1246985.6093
74 | 2683067.1211 | 1246987.5829
75 | 2682966.297 | 1247119.1684
76 | 2683172.5047 | 1247125.1381
77 | 2683138.7993 | 1247069.1249
78 | 2683177.1644 | 1247203.6931
79 | 2683155.8348 | 1247175.5353
80 | 2683605.5105 | 1247442.4383
81 | 2683587.056 | 1247123.3097
82 | 2683538.7442 | 1247093.585
83 | 2683397.9699 | 1247557.1674
84 | 2682863.3601 | 1247137.9987
85 | 2682861.364 | 1247138.1264
86 | 2682865.8132 | 1247140.835
87 | 2682854.3663 | 1247145.8899
88 | 2682826.3014 | 1247170.3987
89 | 2682960.4755 | 1247154.057
90 | 2682796.7061 | 1247196.2439
91 | 2683018.9167 | 1247170.498
92 | 2682953.6498 | 1247153.9993
93 | 2683535.7582 | 1247188.6928
94 | 2683539.6859 | 1247184.3317
95 | 2683548.9023 | 1247174.1095
96 | 2683522.403 | 1247131.7718
97 | 2683476.3858 | 1247080.1638
98 | 2683495.4987 | 1247057.5606
99 | 2683288.2454 | 1247045.9615
100 | 2683257.3689 | 1247039.4664
101 | 2682791.2926 | 1247096.017
102 | 2682835.8884 | 1246923.8244
103 | 2682839.0546 | 1246924.836
104 | 2682844.6647 | 1246926.649
105 | 2682846.2407 | 1246905.2331
106 | 2682858.6532 | 1246910.0322
107 | 2682857.4968 | 1246884.3821
108 | 2682892.6332 | 1246925.717
109 | 2682860.8808 | 1246932.1001
110 | 2682798.5634 | 1247018.4171
111 | 2682804.9946 | 1247019.8523
112 | 2682869.2966 | 1246862.5238
113 | 2682933.2274 | 1246948.4583
114 | 2683216.648 | 1247226.9995
115 | 2683191.8618 | 1247213.6864
116 | 2683276.2195 | 1247219.3411
117 | 2683251.9097 | 1247143.6219
118 | 2683205.5339 | 1247170.6688
119 | 2683278.7598 | 1247143.1991
120 | 2683201.241 | 1247174.2738
121 | 2683256.3798 | 1247050.7275
122 | 2683284.6711 | 1247057.7672
123 | 2683194.1787 | 1247082.5336
124 | 2683245.8348 | 1247039.9382
125 | 2683189.7025 | 1247101.3335
126 | 2683244.1176 | 1247039.5694
127 | 2683193.3321 | 1247181.29
128 | 2683191.5904 | 1247101.7364
129 | 2683206.3172 | 1247031.4774
130 | 2683276.2979 | 1246953.0242
131 | 2683211.2188 | 1247011.109
132 | 2683230.0925 | 1246997.4082
133 | 2682740.5351 | 1247258.9544
134 | 2682708.944 | 1247239.0842
135 | 2682838.6944 | 1247234.336
136 | 2682912.2298 | 1247272.2136
137 | 2682877.6357 | 1247199.2107
138 | 2682935.9879 | 1247247.283
139 | 2683233.6637 | 1246924.0803
140 | 2683266.4508 | 1246931.2588
141 | 2683150.1894 | 1246878.7301
142 | 2683138.0743 | 1246897.8667
143 | 2683298.1869 | 1246955.0373
144 | 2683050.678 | 1247198.413
145 | 2682979.6106 | 1246818.9341
146 | 2682990.9783 | 1246798.5449
147 | 2683015.9462 | 1246812.5268
148 | 2683002.3837 | 1246838.5894
149 | 2683047.2989 | 1246766.5542
150 | 2682975.0669 | 1246738.335
151 | 2683063.1894 | 1246736.0727
152 | 2683081.756 | 1246964.4141
153 | 2683096.7721 | 1246940.6416
154 | 2683128.8821 | 1246894.5354
155 | 2683081.5498 | 1246930.4431
156 | 2682943.0905 | 1246955.6681
157 | 2682960.9891 | 1246930.3579
158 | 2682925.1452 | 1246962.3322
159 | 2683076.988 | 1246897.4994
160 | 2683057.8971 | 1246877.106
161 | 2683047.648 | 1246942.888
162 | 2683144.2777 | 1246870.0485
163 | 2683162.7483 | 1246840.6706
164 | 2682989.8038 | 1246660.0987
165 | 2682962.9367 | 1246709.4761
166 | 2682956.7444 | 1246728.737
167 | 2682928.2443 | 1246780.7874
168 | 2682914.0076 | 1246810.8997
169 | 2682940.0359 | 1247243.0254
170 | 2683174.6505 | 1247174.8221
171 | 2683075.6494 | 1246849.0986
172 | 2683145.6804 | 1247043.6739
173 | 2683171.7371 | 1246834.8146
174 | 2683167.8656 | 1246832.3807
175 | 2682939.748 | 1246953.2196
176 | 2682972.2936 | 1246908.8086
177 | 2682937.347 | 1246838.6496
178 | 2682907.1181 | 1246823.3125
179 | 2682904.3393 | 1246824.3077
180 | 2682894.6635 | 1246842.4623
181 | 2682892.8805 | 1246818.8213
182 | 2682930.9463 | 1246820.1898
183 | 2682882.9819 | 1246837.163
184 | 2682873.1665 | 1246855.3504
185 | 2682997.7698 | 1247239.506
186 | 2683021.5015 | 1247255.063
187 | 2683017.8694 | 1247260.3605
188 | 2683172.5047 | 1247125.1381

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99927 | -0.0025749 | 0.25647 | 0.12421
1 | 0.99927 | -0.0026062 | 0 | 0
2 | 0.99932 | -0.0023414 | 0 | 0
3 | 0.99922 | -0.0014515 | 0 | 0
4 | 0.99932 | -0.0023512 | 0.085466 | 0.041393
5 | 0.99916 | -0.013071 | 0 | 0
6 | 0.99914 | -0.01318 | 0.32369 | 0.15677
7 | 0.99935 | -0.0026568 | 0 | 0
8 | 0.99912 | -0.013234 | 0 | 0
9 | 0.99945 | -0.0022581 | 0 | 0
10 | 0.99788 | -0.0060917 | 0.26001 | 0.12593
11 | 0.99789 | -0.0061493 | 0 | 0
12 | 0.9979 | -0.0063271 | 0 | 0
13 | 0.99808 | -0.0066242 | 0 | 0
14 | 0.99799 | -0.0057993 | 0 | 0
15 | 0.99863 | -0.01163 | 0 | 0
16 | 0.99794 | -0.0075527 | 0.39469 | 0.19116
17 | 0.99879 | -0.013042 | 0 | 0
18 | 0.99862 | -0.011704 | 0.29035 | 0.14062
19 | 0.99743 | -0.008245 | 0.21518 | 0.10422
20 | 0.99747 | -0.0085856 | 0.068285 | 0.033072
21 | 0.99742 | -0.008317 | 0 | 0
22 | 0.99733 | -0.0075118 | 0 | 0
23 | 0.99759 | -0.0077595 | 0.35392 | 0.17141
24 | 0.9973 | -0.0073303 | 0 | 0
25 | 0.99732 | -0.0074175 | 0.40525 | 0.19627
26 | 0.9973 | -0.0072928 | 0.088442 | 0.042834
27 | 0.99878 | -0.012962 | 0.07102 | 0.034396
28 | 0.99898 | -0.014762 | 0 | 0
29 | 0.99878 | -0.012931 | 0.13725 | 0.066473
30 | 0.99791 | -0.0063385 | 0.17618 | 0.085326
31 | 0.99921 | -0.0013745 | 0.38992 | 0.18885
32 | 0.99767 | -0.0068803 | 0 | 0
33 | 0.99767 | -0.0068347 | 0 | 0
34 | 0.99768 | -0.0069526 | 0.28375 | 0.13742
35 | 0.99773 | -0.0089905 | 0 | 0
36 | 0.99774 | -0.007442 | 0.34095 | 0.16513
37 | 0.99766 | -0.0067663 | 0.22456 | 0.10876
38 | 0.9977 | -0.0071233 | 0 | 0
39 | 0.99771 | -0.0088303 | 0.27707 | 0.13419
40 | 0.99796 | 0.0089263 | 0.33856 | 0.16397
41 | 0.99796 | 0.0088905 | 0 | 0
42 | 0.99802 | 0.0084149 | 0 | 0
43 | 0.99788 | 0.0096582 | 0 | 0
44 | 0.99795 | 0.0089989 | 0 | 0
45 | 0.99806 | 0.0080435 | 0.12545 | 0.060759
46 | 0.99788 | 0.0096664 | 0.29606 | 0.14339
47 | 0.99794 | 0.0091329 | 0 | 0
48 | 0.99794 | 0.0091452 | 0.25409 | 0.12306
49 | 0.99794 | 0.0091604 | 0.2489 | 0.12055
50 | 0.99812 | 0.007487 | 0 | 0
51 | 0.99954 | -0.0017084 | 0.32963 | 0.15965
52 | 0.99955 | -0.0018186 | 0 | 0
53 | 0.99945 | -0.0022003 | 0 | 0
54 | 0.99977 | -0.00092124 | 0 | 0
55 | 0.99935 | -0.0040226 | 0 | 0
56 | 0.99898 | -0.00071878 | 0 | 0
57 | 0.9992 | -0.0026741 | 0.22201 | 0.10753
58 | 0.99935 | -0.0033709 | 0.34386 | 0.16654
59 | 0.99962 | -0.00083714 | 0 | 0
60 | 0.99961 | -0.00073883 | 0 | 0
61 | 0.99968 | -0.0013287 | 0 | 0
62 | 0.99961 | -0.00073403 | 0.2294 | 0.1111
63 | 0.99961 | -0.00070663 | 0.14504 | 0.070248
64 | 0.99991 | -0.00037126 | 0 | 0
65 | 0.99977 | -0.00089167 | 0.096934 | 0.046947
66 | 0.99967 | -0.0012639 | 0.19074 | 0.09238
67 | 0.99965 | -0.0014379 | 0 | 0
68 | 0.99892 | -0.0001114 | 0 | 0
69 | 0.99898 | -0.0006412 | 0 | 0
70 | 0.99898 | -0.00068027 | 0.07608 | 0.036847
71 | 0.99892 | -9.5693e-05 | 0.0842 | 0.04078
72 | 0.99878 | 0.0011591 | 0 | 0
73 | 0.99897 | -0.00059474 | 0.12211 | 0.05914
74 | 0.9991 | -0.0017374 | 0 | 0
75 | 0.99913 | -0.0014353 | 0 | 0
76 | 1 | 0 | -19.754 | -9.3359
77 | 0.9999 | -0.00029644 | 0 | 0
78 | 0.99963 | -0.0012032 | 0.31052 | 0.15039
79 | 0.99964 | -0.0014936 | 0.13742 | 0.066556
80 | 0.99761 | -0.0079239 | 0 | 0
81 | 0.99881 | -0.014636 | 0.29038 | 0.14064
82 | 0.99884 | -0.014436 | 0 | 0
83 | 0.99772 | -0.0073424 | 0 | 0
84 | 0.99857 | 0.0035254 | 0.3885 | 0.18816
85 | 0.99856 | 0.0035919 | 0 | 0
86 | 0.99858 | 0.0033936 | 0 | 0
87 | 0.99852 | 0.0039276 | 0 | 0
88 | 0.99839 | 0.0050683 | 0.085133 | 0.041232
89 | 0.99908 | -0.001044 | 0 | 0
90 | 0.99826 | 0.0062336 | 0 | 0
91 | 0.99905 | -0.00076398 | 0 | 0
92 | 0.99908 | -0.0010128 | 0.38245 | 0.18523
93 | 0.99894 | -0.014419 | 0.083875 | 0.040622
94 | 0.99893 | -0.014347 | 0 | 0
95 | 0.99891 | -0.014178 | 0.40865 | 0.19792
96 | 0.99885 | -0.014582 | 0 | 0
97 | 0.99881 | -0.014178 | 0 | 0
98 | 0.9988 | -0.014055 | 0.34885 | 0.16895
99 | 0.99758 | 0.00055203 | 0.42224 | 0.2045
100 | 0.9976 | 0.00039263 | 0 | 0
101 | 0.99792 | 0.0092521 | 0 | 0
102 | 0.99844 | 0.0042282 | 0.40967 | 0.19841
103 | 0.99844 | 0.0042119 | 0 | 0
104 | 0.99845 | 0.0041257 | 0 | 0
105 | 0.99844 | 0.0042021 | 0 | 0
106 | 0.99847 | 0.0039658 | 0 | 0
107 | 0.99839 | 0.0046234 | 0.08331 | 0.040349
108 | 0.99857 | 0.003076 | 0.53468 | 0.25896
109 | 0.99845 | 0.0041466 | 0.10318 | 0.049972
110 | 0.99789 | 0.0095655 | 0.26827 | 0.12993
111 | 0.99789 | 0.0095442 | 0 | 0
112 | 0.99835 | 0.0050411 | 0 | 0
113 | 0.99872 | 0.0016741 | 0 | 0
114 | 0.99961 | -0.001031 | 0.31656 | 0.15332
115 | 0.99962 | -0.0011368 | 0 | 0
116 | 0.99944 | -0.0021599 | 0.31464 | 0.15239
117 | 0.99951 | -0.0020228 | 0 | 0
118 | 0.99957 | -0.0017773 | 0 | 0
119 | 0.99951 | -0.0019937 | 0.091825 | 0.044473
120 | 0.99957 | -0.0017539 | 0.0942 | 0.045623
121 | 0.99758 | 0.00059607 | 0 | 0
122 | 0.99756 | 0.00074214 | 0.41857 | 0.20272
123 | 0.99753 | 0.0010669 | 0 | 0
124 | 0.99756 | 0.00079915 | 0 | 0
125 | 0.99751 | 0.00096612 | 0.31754 | 0.15379
126 | 0.99755 | 0.00081264 | 0.23657 | 0.11458
127 | 0.99958 | -0.0017092 | 0.083344 | 0.040365
128 | 0.99751 | 0.0009687 | 0.11141 | 0.053957
129 | 0.99752 | 0.00061512 | 0 | 0
130 | 0.99793 | 0.0024985 | 0 | 0
131 | 0.99751 | 0.00071755 | 0 | 0
132 | 0.99749 | 0.00087792 | 0.41163 | 0.19936
133 | 0.99816 | 0.0071104 | 0.070964 | 0.034369
134 | 0.99816 | 0.0070785 | 0 | 0
135 | 0.99818 | 0.0069684 | 0 | 0
136 | 0.99804 | 0.0081892 | 0 | 0
137 | 0.99817 | 0.007015 | 0.077385 | 0.037479
138 | 0.998 | 0.0085769 | 0.29993 | 0.14526
139 | 0.9981 | 0.00086308 | 0.15513 | 0.075132
140 | 0.99801 | 0.0017004 | 0 | 0
141 | 0.99852 | 0.0035486 | 0.16054 | 0.077751
142 | 0.99859 | 0.002899 | 0 | 0
143 | 0.99792 | 0.0025508 | 0.19941 | 0.096577
144 | 0.99904 | -0.00060626 | 0.31387 | 0.15201
145 | 0.9979 | 0.0075723 | 0.13114 | 0.063512
146 | 0.9979 | 0.0075359 | 0 | 0
147 | 0.99791 | 0.0074925 | 0 | 0
148 | 0.99789 | 0.0076367 | 0.4107 | 0.19891
149 | 0.99795 | 0.0070874 | 0 | 0
150 | 0.99805 | 0.0077356 | 0.10577 | 0.051226
151 | 0.99795 | 0.0071347 | 0.1166 | 0.05647
152 | 0.99898 | -0.00064875 | 0.094348 | 0.045695
153 | 0.99886 | 0.00043794 | 0 | 0
154 | 0.99862 | 0.0026189 | 0 | 0
155 | 0.99886 | 0.00046476 | 0.12323 | 0.059682
156 | 0.99876 | 0.0012954 | 0 | 0
157 | 0.99877 | 0.0012409 | 0.15251 | 0.073866
158 | 0.99897 | -0.00054726 | 0.099942 | 0.048404
159 | 0.99861 | 0.0027398 | 0 | 0
160 | 0.9986 | 0.0028384 | 0 | 0
161 | 0.9986 | 0.0027926 | 0.084866 | 0.041102
162 | 0.9986 | 0.0028154 | 0.36082 | 0.17475
163 | 0.99859 | 0.0029027 | 0 | 0
164 | 0.99803 | 0.0079213 | 0.30518 | 0.14781
165 | 0.99805 | 0.0077176 | 0 | 0
166 | 0.99807 | 0.0075518 | 0 | 0
167 | 0.99815 | 0.00682 | 0.068275 | 0.033067
168 | 0.9982 | 0.0063755 | 0 | 0
169 | 0.998 | 0.008622 | 0 | 0
170 | 0.99961 | -0.0016083 | 0.23349 | 0.11308
171 | 0.99859 | 0.0028793 | 0.10467 | 0.050692
172 | 0.9999 | -0.00026201 | 0.11082 | 0.053672
173 | 0.99858 | 0.002975 | 0 | 0
174 | 0.99858 | 0.0029868 | 0.21592 | 0.10457
175 | 0.99875 | 0.0014319 | 0.24685 | 0.11956
176 | 0.99877 | 0.0012609 | 0.07019 | 0.033995
177 | 0.99819 | 0.0064428 | 0.09241 | 0.044756
178 | 0.9982 | 0.0064061 | 0 | 0
179 | 0.9982 | 0.0064094 | 0 | 0
180 | 0.99819 | 0.0064319 | 0.092401 | 0.044752
181 | 0.99826 | 0.0058611 | 0 | 0
182 | 0.9982 | 0.0063941 | 0.080786 | 0.039126
183 | 0.99829 | 0.0055269 | 0.072009 | 0.034876
184 | 0.99833 | 0.0051783 | 0 | 0
185 | 0.99789 | 0.0096458 | 0.26802 | 0.12981
186 | 0.9979 | 0.0095546 | 0.3921 | 0.1899
187 | 0.9979 | 0.009504 | 0 | 0
188 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.25647 | -0.12421 | 0.25647 | 0.12397 | 9.244e-07 | -0.00024341 | 0.0082323 | 0.0082293 | 0.0082323 | 0.99927 | -0.0025749 | 0.99927 | -0.0026062 | 3.742
1 | -0.25647 | -0.12397 | 0.25648 | 0.12388 | 1.0213e-05 | -9.4529e-05 | 0.0082293 | 0.008228 | 0.0082293 | 0.99927 | -0.0026062 | 0.99932 | -0.0023414 | 3.9187
2 | 0.38996 | 0.18375 | -0.38992 | -0.18845 | 4.1168e-05 | -0.0047066 | 0.012453 | 0.012512 | 0.012512 | 0.99932 | -0.0023414 | 0.99922 | -0.0014515 | 5.6871
3 | -0.64645 | -0.30762 | 0.64645 | 0.30759 | 7.5507e-07 | -3.1313e-05 | 0.020681 | 0.02068 | 0.020681 | 0.99932 | -0.0023414 | 0.99932 | -0.0023512 | 9.4003
4 | 0.38992 | 0.18845 | -0.38992 | -0.18885 | 3.4548e-06 | -0.00039291 | 0.012512 | 0.012517 | 0.012517 | 0.99922 | -0.0014515 | 0.99921 | -0.0013745 | 5.6893
5 | -0.73191 | -0.34899 | 0.73194 | 0.34812 | 2.6674e-05 | -0.00086083 | 0.023423 | 0.023413 | 0.023423 | 0.99932 | -0.0023512 | 0.99935 | -0.0026568 | 10.647
6 | 5.0477 | 2.4025 | -5.0476 | -2.4066 | 0.00013506 | -0.0041264 | 0.16151 | 0.16157 | 0.16157 | 0.99916 | -0.013071 | 0.99914 | -0.01318 | 12.6619
7 | -5.0477 | -2.4025 | 5.0482 | 2.4036 | 0.00050856 | 0.0010661 | 0.16151 | 0.16151 | 0.16151 | 0.99916 | -0.013071 | 0.99935 | -0.0026568 | 12.5204
8 | 4.7239 | 2.2499 | -4.7238 | -2.2521 | 6.3176e-05 | -0.0022085 | 0.15117 | 0.1512 | 0.1512 | 0.99914 | -0.01318 | 0.99912 | -0.013234 | 11.8497
9 | -5.7802 | -2.7517 | 5.7807 | 2.7387 | 0.000559 | -0.012977 | 0.18492 | 0.18476 | 0.18492 | 0.99935 | -0.0026568 | 0.99945 | -0.0022581 | 14.4924
10 | 4.7238 | 2.2521 | -4.7232 | -2.2536 | 0.00061908 | -0.0014695 | 0.1512 | 0.15123 | 0.15123 | 0.99912 | -0.013234 | 0.99898 | -0.014762 | 41.7753
11 | -6.0954 | -2.8905 | 6.0957 | 2.8834 | 0.00034247 | -0.0071399 | 0.19485 | 0.19476 | 0.19485 | 0.99945 | -0.0022581 | 0.99951 | -0.0020228 | 15.2702
12 | 0.31465 | 0.15176 | -0.31464 | -0.15239 | 3.5633e-06 | -0.00062373 | 0.01009 | 0.010098 | 0.010098 | 0.99945 | -0.0022581 | 0.99944 | -0.0021599 | 4.5899
13 | -0.26001 | -0.12593 | 0.26001 | 0.12549 | 1.726e-06 | -0.00043985 | 0.0083576 | 0.0083521 | 0.0083576 | 0.99788 | -0.0060917 | 0.99789 | -0.0061493 | 3.7989
14 | -0.26001 | -0.12549 | 0.26002 | 0.12411 | 5.4144e-06 | -0.0013836 | 0.0083521 | 0.0083347 | 0.0083521 | 0.99789 | -0.0061493 | 0.9979 | -0.0063271 | 3.7964
15 | -0.26002 | -0.12411 | 0.26002 | 0.12402 | 3.5339e-07 | -9.0506e-05 | 0.0083347 | 0.0083336 | 0.0083347 | 0.9979 | -0.0063271 | 0.99791 | -0.0063385 | 3.7885
16 | 1.2858 | 0.61575 | -1.2857 | -0.61702 | 0.00012457 | -0.0012677 | 0.041235 | 0.041251 | 0.041251 | 0.99808 | -0.0066242 | 0.99799 | -0.0057993 | 18.7505
17 | -3.0896 | -1.4747 | 3.0914 | 1.4719 | 0.0018402 | -0.0028013 | 0.099017 | 0.098975 | 0.099017 | 0.99808 | -0.0066242 | 0.99863 | -0.01163 | 45.0078
18 | 1.8037 | 0.85895 | -1.8035 | -0.85885 | 0.00023878 | 0.00010184 | 0.057782 | 0.057783 | 0.057783 | 0.99808 | -0.0066242 | 0.99794 | -0.0075527 | 27.5157
19 | 1.2857 | 0.61702 | -1.2856 | -0.61699 | 0.00010164 | 2.3807e-05 | 0.041251 | 0.041252 | 0.041252 | 0.99799 | -0.0057993 | 0.99791 | -0.0063385 | 19.6436
20 | -3.3817 | -1.6125 | 3.3823 | 1.6118 | 0.0005681 | -0.00069559 | 0.1083 | 0.10829 | 0.1083 | 0.99863 | -0.01163 | 0.99879 | -0.013042 | 49.2276
21 | 0.29035 | 0.1406 | -0.29035 | -0.14062 | 3.2183e-06 | -2.2711e-05 | 0.0093254 | 0.0093257 | 0.0093257 | 0.99863 | -0.01163 | 0.99862 | -0.011704 | 4.4408
22 | 1.4088 | 0.66769 | -1.4085 | -0.6676 | 0.00028406 | 8.4749e-05 | 0.045097 | 0.045098 | 0.045098 | 0.99794 | -0.0075527 | 0.99773 | -0.0089905 | 21.4755
23 | 0.20827 | 0.099627 | -0.20827 | -0.10041 | 1.9565e-06 | -0.00078223 | 0.0066728 | 0.0066826 | 0.0066826 | 0.99879 | -0.013042 | 0.99878 | -0.012962 | 3.0375
24 | -3.5906 | -1.7114 | 3.5913 | 1.7107 | 0.00073507 | -0.00077456 | 0.11496 | 0.11495 | 0.11496 | 0.99879 | -0.013042 | 0.99898 | -0.014762 | 52.2558
25 | -0.70894 | -0.33338 | 0.70897 | 0.33236 | 2.9749e-05 | -0.0010214 | 0.022673 | 0.022661 | 0.022673 | 0.99743 | -0.008245 | 0.99747 | -0.0085856 | 10.3061
26 | 0.49375 | 0.22916 | -0.49375 | -0.22917 | 4.6518e-06 | -9.5795e-06 | 0.015754 | 0.015754 | 0.015754 | 0.99743 | -0.008245 | 0.99742 | -0.008317 | 7.5021
27 | -0.77725 | -0.36543 | 0.77734 | 0.36539 | 8.7562e-05 | -3.9649e-05 | 0.024856 | 0.024855 | 0.024856 | 0.99747 | -0.0085856 | 0.99759 | -0.0077595 | 11.8363
28 | 0.49375 | 0.22917 | -0.4937 | -0.23269 | 4.9422e-05 | -0.0035182 | 0.015754 | 0.015798 | 0.015798 | 0.99742 | -0.008317 | 0.99733 | -0.0075118 | 7.1808
29 | 0.088445 | 0.036877 | -0.088442 | -0.041976 | 2.2521e-06 | -0.0050988 | 0.0027736 | 0.0028337 | 0.0028337 | 0.99733 | -0.0075118 | 0.9973 | -0.0073303 | 1.2881
30 | 0.40526 | 0.19581 | -0.40525 | -0.19627 | 4.4021e-06 | -0.0004599 | 0.013028 | 0.013033 | 0.013033 | 0.99733 | -0.0075118 | 0.99732 | -0.0074175 | 5.9243
31 | -1.1313 | -0.5368 | 1.1313 | 0.5365 | 2.2368e-05 | -0.00029663 | 0.036234 | 0.03623 | 0.036234 | 0.99759 | -0.0077595 | 0.99761 | -0.0079239 | 16.47
32 | 0.088442 | 0.041976 | -0.088442 | -0.042834 | 3.8897e-07 | -0.00085831 | 0.0028337 | 0.0028445 | 0.0028445 | 0.9973 | -0.0073303 | 0.9973 | -0.0072928 | 1.2929
33 | 0.13725 | 0.066013 | -0.13725 | -0.066473 | 5.0058e-07 | -0.00046016 | 0.0044019 | 0.0044077 | 0.0044077 | 0.99878 | -0.012962 | 0.99878 | -0.012931 | 2.0035
34 | 1.1319 | 0.5429 | -1.1319 | -0.5435 | 4.5488e-05 | -0.00060329 | 0.036276 | 0.036284 | 0.036284 | 0.99898 | -0.014762 | 0.99894 | -0.014419 | 16.4928
35 | 0.84942 | 0.40765 | -0.84928 | -0.40769 | 0.00013748 | -3.7345e-05 | 0.027255 | 0.027257 | 0.027257 | 0.99791 | -0.0063385 | 0.99774 | -0.007442 | 12.9795
36 | 0.22456 | 0.10774 | -0.22456 | -0.10815 | 1.1954e-06 | -0.00040909 | 0.0072067 | 0.0072119 | 0.0072119 | 0.99767 | -0.0068803 | 0.99767 | -0.0068347 | 3.2781
37 | -0.22456 | -0.10774 | 0.22456 | 0.10708 | 1.9147e-06 | -0.00065647 | 0.0072067 | 0.0071985 | 0.0072067 | 0.99767 | -0.0068803 | 0.99768 | -0.0069526 | 3.2758
38 | 0.22456 | 0.10815 | -0.22456 | -0.10876 | 1.7759e-06 | -0.00060666 | 0.0072119 | 0.0072195 | 0.0072195 | 0.99767 | -0.0068347 | 0.99766 | -0.0067663 | 3.2816
39 | -0.50831 | -0.24451 | 0.50832 | 0.24383 | 1.0148e-05 | -0.00067555 | 0.016321 | 0.016312 | 0.016321 | 0.99768 | -0.0069526 | 0.9977 | -0.0071233 | 7.4185
40 | 0.27707 | 0.13304 | -0.27707 | -0.13419 | 5.1454e-06 | -0.0011549 | 0.0088929 | 0.0089074 | 0.0089074 | 0.99773 | -0.0089905 | 0.99771 | -0.0088303 | 4.0488
41 | 1.1314 | 0.53457 | -1.1313 | -0.5365 | 0.00014587 | -0.0019363 | 0.036206 | 0.03623 | 0.03623 | 0.99773 | -0.0089905 | 0.99761 | -0.0079239 | 16.4683
42 | 0.50833 | 0.24256 | -0.50833 | -0.24296 | 5.997e-06 | -0.00040013 | 0.016296 | 0.016301 | 0.016301 | 0.99774 | -0.007442 | 0.99772 | -0.0073424 | 7.4097
43 | -0.50832 | -0.24383 | 0.50833 | 0.24296 | 1.3114e-05 | -0.0008741 | 0.016312 | 0.016301 | 0.016312 | 0.9977 | -0.0071233 | 0.99772 | -0.0073424 | 7.4146
44 | -0.33856 | -0.16397 | 0.33856 | 0.16376 | 1.3901e-06 | -0.00020875 | 0.010881 | 0.010879 | 0.010881 | 0.99796 | 0.0089263 | 0.99796 | 0.0088905 | 4.9461
45 | -0.63465 | -0.30171 | 0.63469 | 0.30015 | 3.6352e-05 | -0.0015579 | 0.020327 | 0.020308 | 0.020327 | 0.99796 | 0.0088905 | 0.99802 | 0.0084149 | 9.2395
46 | 0.29609 | 0.13794 | -0.29606 | -0.14333 | 2.7256e-05 | -0.0053912 | 0.0094487 | 0.0095157 | 0.0095157 | 0.99796 | 0.0088905 | 0.99788 | 0.0096582 | 4.3253
47 | 0.77134 | 0.36713 | -0.77129 | -0.36867 | 5.3512e-05 | -0.0015441 | 0.024709 | 0.024729 | 0.024729 | 0.99802 | 0.0084149 | 0.99795 | 0.0089989 | 11.2403
48 | -1.406 | -0.66727 | 1.4061 | 0.66674 | 6.282e-05 | -0.00053369 | 0.045017 | 0.04501 | 0.045017 | 0.99802 | 0.0084149 | 0.99806 | 0.0080435 | 20.4621
49 | 0.29606 | 0.14333 | -0.29606 | -0.14339 | 2.791e-07 | -5.4813e-05 | 0.0095157 | 0.0095164 | 0.0095164 | 0.99788 | 0.0096582 | 0.99788 | 0.0096664 | 4.3256
50 | 0.5172 | 0.24676 | -0.51719 | -0.2474 | 9.8857e-06 | -0.00063756 | 0.016576 | 0.016584 | 0.016584 | 0.99795 | 0.0089989 | 0.99794 | 0.0091604 | 7.5383
51 | 0.25409 | 0.12191 | -0.25409 | -0.12297 | 3.9515e-06 | -0.0010561 | 0.0081523 | 0.0081655 | 0.0081655 | 0.99795 | 0.0089989 | 0.99794 | 0.0091329 | 3.7116
52 | -1.5315 | -0.7275 | 1.5316 | 0.72677 | 0.00010234 | -0.00072788 | 0.049041 | 0.049032 | 0.049041 | 0.99806 | 0.0080435 | 0.99812 | 0.007487 | 22.2915
53 | 0.25409 | 0.12297 | -0.25409 | -0.12306 | 3.5931e-07 | -9.586e-05 | 0.0081655 | 0.0081668 | 0.0081668 | 0.99794 | 0.0091329 | 0.99794 | 0.0091452 | 3.7122
54 | 0.26829 | 0.12685 | -0.26828 | -0.12757 | 2.9633e-06 | -0.00071456 | 0.0085846 | 0.0085935 | 0.0085935 | 0.99794 | 0.0091604 | 0.99792 | 0.0092521 | 3.9061
55 | -1.5316 | -0.72677 | 1.5319 | 0.72512 | 0.00023145 | -0.0016476 | 0.049032 | 0.049011 | 0.049032 | 0.99812 | 0.007487 | 0.99826 | 0.0062336 | 22.2873
56 | -0.32963 | -0.15965 | 0.32964 | 0.15898 | 4.1916e-06 | -0.00066866 | 0.010578 | 0.010569 | 0.010578 | 0.99954 | -0.0017084 | 0.99955 | -0.0018186 | 4.8081
57 | 11.2657 | 5.3547 | -11.2646 | -5.3606 | 0.0010514 | -0.0059895 | 0.36024 | 0.36032 | 0.36032 | 0.99955 | -0.0018186 | 0.99945 | -0.0022003 | 28.2384
58 | -11.5953 | -5.5136 | 11.5978 | 5.5001 | 0.0025227 | -0.0135 | 0.37081 | 0.37062 | 0.37081 | 0.99955 | -0.0018186 | 0.99977 | -0.00092124 | 29.0603
59 | 4.1586 | 1.9697 | -4.1582 | -1.971 | 0.00041141 | -0.0013531 | 0.1329 | 0.13293 | 0.13293 | 0.99945 | -0.0022003 | 0.99935 | -0.0033709 | 36.7196
60 | 7.1061 | 3.391 | -7.1054 | -3.3917 | 0.00062953 | -0.00069095 | 0.22742 | 0.22743 | 0.22743 | 0.99945 | -0.0022003 | 0.99935 | -0.0040226 | 54.0222
61 | 7.9301 | 3.7337 | -7.9294 | -3.7428 | 0.00075181 | -0.0091138 | 0.25308 | 0.2532 | 0.2532 | 0.99977 | -0.00092124 | 0.99968 | -0.0013287 | 19.8434
62 | -19.6249 | -9.2802 | 19.6274 | 9.2763 | 0.0025509 | -0.0038433 | 0.62681 | 0.62675 | 0.62681 | 0.99977 | -0.00092124 | 0.99991 | -0.00037126 | 49.1231
63 | 0.096935 | 0.046329 | -0.096934 | -0.046947 | 3.3394e-07 | -0.0006187 | 0.0031021 | 0.0031099 | 0.0031099 | 0.99977 | -0.00092124 | 0.99977 | -0.00089167 | 1.4136
64 | 3.4616 | 1.6487 | -3.4602 | -1.6503 | 0.0013606 | -0.0015764 | 0.11075 | 0.11078 | 0.11078 | 0.99935 | -0.0040226 | 0.99898 | -0.00071878 | 50.3543
65 | 3.6438 | 1.7429 | -3.6433 | -1.7435 | 0.00057962 | -0.00058836 | 0.11668 | 0.11669 | 0.11669 | 0.99935 | -0.0040226 | 0.9992 | -0.0026741 | 53.0401
66 | 3.1621 | 1.5091 | -3.1619 | -1.5094 | 0.00022778 | -0.00032898 | 0.10125 | 0.10125 | 0.10125 | 0.99898 | -0.00071878 | 0.99892 | -0.0001114 | 46.0235
67 | 0.22206 | 0.10542 | -0.22205 | -0.10615 | 2.052e-06 | -0.00072436 | 0.0071032 | 0.0071122 | 0.0071122 | 0.99898 | -0.00071878 | 0.99898 | -0.0006412 | 3.2328
68 | 0.07608 | 0.035803 | -0.07608 | -0.036847 | 3.472e-07 | -0.001044 | 0.0024298 | 0.0024428 | 0.0024428 | 0.99898 | -0.00071878 | 0.99898 | -0.00068027 | 1.1103
69 | 3.4213 | 1.636 | -3.4209 | -1.6365 | 0.0003783 | -0.00045044 | 0.10956 | 0.10957 | 0.10957 | 0.9992 | -0.0026741 | 0.9991 | -0.0017374 | 49.8039
70 | 3.8143 | 1.8045 | -3.8134 | -1.8053 | 0.00089292 | -0.00080827 | 0.12189 | 0.1219 | 0.1219 | 0.99935 | -0.0033709 | 0.99913 | -0.0014353 | 55.41
71 | 0.14505 | 0.068392 | -0.14504 | -0.069802 | 1.6987e-06 | -0.0014097 | 0.004631 | 0.0046485 | 0.0046485 | 0.99962 | -0.00083714 | 0.99961 | -0.00073883 | 2.1129
72 | -0.37445 | -0.17859 | 0.37447 | 0.17582 | 2.2267e-05 | -0.002774 | 0.01198 | 0.011946 | 0.01198 | 0.99962 | -0.00083714 | 0.99968 | -0.0013287 | 5.4457
73 | 0.2294 | 0.1102 | -0.2294 | -0.1111 | 2.74e-06 | -0.00090431 | 0.0073495 | 0.0073609 | 0.0073609 | 0.99962 | -0.00083714 | 0.99961 | -0.00073403 | 3.3459
74 | 0.14504 | 0.069802 | -0.14504 | -0.070248 | 5.4002e-07 | -0.0004459 | 0.0046485 | 0.0046541 | 0.0046541 | 0.99961 | -0.00073883 | 0.99961 | -0.00070663 | 2.1155
75 | 0.19074 | 0.091696 | -0.19074 | -0.09238 | 1.4322e-06 | -0.00068398 | 0.0061115 | 0.0061201 | 0.0061201 | 0.99968 | -0.0013287 | 0.99967 | -0.0012639 | 2.7818
76 | 7.3642 | 3.4753 | -7.364 | -3.478 | 0.00018858 | -0.0026656 | 0.23514 | 0.23518 | 0.23518 | 0.99968 | -0.0013287 | 0.99965 | -0.0014379 | 18.4309
77 | -19.7383 | -9.3279 | 19.74 | 9.3254 | 0.0017267 | -0.002563 | 0.63028 | 0.63023 | 0.63028 | 0.99991 | -0.00037126 | 1 | 0 | 49.3946
78 | 0.11082 | 0.051602 | -0.11082 | -0.053042 | 1.0083e-06 | -0.00144 | 0.0035292 | 0.003547 | 0.003547 | 0.99991 | -0.00037126 | 0.9999 | -0.00029644 | 1.6123
79 | 0.6271 | 0.30187 | -0.62709 | -0.30262 | 1.708e-05 | -0.00075025 | 0.020098 | 0.020108 | 0.020108 | 0.99965 | -0.0014379 | 0.99963 | -0.0012032 | 9.1398
80 | 6.7369 | 3.1761 | -6.7368 | -3.1776 | 8.7514e-05 | -0.0014882 | 0.21508 | 0.2151 | 0.2151 | 0.99965 | -0.0014379 | 0.99964 | -0.0014936 | 16.8574
81 | 0.0842 | 0.040405 | -0.0842 | -0.04078 | 1.5341e-07 | -0.00037514 | 0.0026989 | 0.0027036 | 0.0027036 | 0.99892 | -0.0001114 | 0.99892 | -9.5693e-05 | 1.2289
82 | 3.0777 | 1.469 | -3.0772 | -1.4697 | 0.00046338 | -0.00071375 | 0.098553 | 0.098563 | 0.098563 | 0.99892 | -0.0001114 | 0.99878 | 0.0011591 | 44.8015
83 | 0.22205 | 0.10615 | -0.22205 | -0.10658 | 1.2141e-06 | -0.00042769 | 0.0071122 | 0.0071175 | 0.0071175 | 0.99898 | -0.0006412 | 0.99897 | -0.00059474 | 3.2352
84 | 2.8545 | 1.3632 | -2.8544 | -1.3633 | 4.6078e-05 | -8.4674e-05 | 0.091428 | 0.091429 | 0.091429 | 0.99878 | 0.0011591 | 0.99876 | 0.0012954 | 41.5587
85 | 0.22271 | 0.10654 | -0.2227 | -0.10728 | 2.1326e-06 | -0.00074566 | 0.0071354 | 0.0071448 | 0.0071448 | 0.99878 | 0.0011591 | 0.99877 | 0.0012409 | 3.2476
86 | 0.099943 | 0.047435 | -0.099942 | -0.048404 | 5.5702e-07 | -0.00096893 | 0.0031969 | 0.003209 | 0.003209 | 0.99897 | -0.00059474 | 0.99897 | -0.00054726 | 1.4586
87 | 3.4209 | 1.6365 | -3.4204 | -1.637 | 0.00043924 | -0.00052275 | 0.10957 | 0.10958 | 0.10958 | 0.9991 | -0.0017374 | 0.99898 | -0.00064875 | 49.8076
88 | 0.69636 | 0.3331 | -0.69633 | -0.33424 | 3.2029e-05 | -0.0011393 | 0.022303 | 0.022318 | 0.022318 | 0.99913 | -0.0014353 | 0.99908 | -0.001044 | 10.1443
89 | 3.117 | 1.4722 | -3.1152 | -1.4749 | 0.0018233 | -0.0027375 | 0.099599 | 0.09964 | 0.09964 | 0.99913 | -0.0014353 | 0.99858 | 0.0033936 | 45.2907
90 | 0.11082 | 0.053042 | -0.11082 | -0.053672 | 4.438e-07 | -0.00062923 | 0.003547 | 0.0035549 | 0.0035549 | 0.9999 | -0.00029644 | 0.9999 | -0.00026201 | 1.6158
91 | 0.31656 | 0.15222 | -0.31656 | -0.15265 | 2.4427e-06 | -0.00042331 | 0.010144 | 0.010149 | 0.010149 | 0.99963 | -0.0012032 | 0.99962 | -0.0011368 | 4.6133
92 | 6.5994 | 3.111 | -6.5992 | -3.1142 | 0.0001765 | -0.0031314 | 0.21069 | 0.21073 | 0.21073 | 0.99964 | -0.0014936 | 0.99961 | -0.0016083 | 16.515
93 | -0.29038 | -0.14064 | 0.29039 | 0.14058 | 8.7877e-06 | -6.2053e-05 | 0.0093252 | 0.0093243 | 0.0093252 | 0.99881 | -0.014636 | 0.99884 | -0.014436 | 4.4406
94 | -0.29039 | -0.14058 | 0.2904 | 0.13957 | 4.9142e-06 | -0.0010085 | 0.0093243 | 0.0093116 | 0.0093243 | 0.99884 | -0.014436 | 0.99885 | -0.014582 | 4.2383
95 | 2.7267 | 1.2868 | -2.7266 | -1.2869 | 2.206e-05 | -4.5238e-05 | 0.087162 | 0.087163 | 0.087163 | 0.99857 | 0.0035254 | 0.99856 | 0.0035919 | 39.6195
96 | -3.1152 | -1.475 | 3.1152 | 1.4749 | 4.9637e-05 | -7.4438e-05 | 0.099641 | 0.09964 | 0.099641 | 0.99857 | 0.0035254 | 0.99858 | 0.0033936 | 45.2912
97 | 2.7266 | 1.2869 | -2.7265 | -1.2871 | 0.00011139 | -0.00022841 | 0.087163 | 0.087166 | 0.087166 | 0.99856 | 0.0035919 | 0.99852 | 0.0039276 | 39.6209
98 | 2.7265 | 1.2871 | -2.7261 | -1.2879 | 0.00037799 | -0.00077476 | 0.087166 | 0.087177 | 0.087177 | 0.99852 | 0.0039276 | 0.99839 | 0.0050683 | 39.6259
99 | 2.641 | 1.2466 | -2.6406 | -1.2475 | 0.00037408 | -0.00082404 | 0.084442 | 0.084454 | 0.084454 | 0.99839 | 0.0050683 | 0.99826 | 0.0062336 | 38.388
100 | 0.31388 | 0.14917 | -0.31387 | -0.15101 | 1.0382e-05 | -0.0018309 | 0.010041 | 0.010064 | 0.010064 | 0.99908 | -0.001044 | 0.99905 | -0.00076398 | 4.5747
101 | 0.38245 | 0.18507 | -0.38245 | -0.18523 | 1.3736e-06 | -0.00016227 | 0.012276 | 0.012278 | 0.012278 | 0.99908 | -0.001044 | 0.99908 | -0.0010128 | 5.581
102 | 1.1088 | 0.52235 | -1.1087 | -0.52373 | 9.927e-05 | -0.0013782 | 0.035443 | 0.03546 | 0.03546 | 0.99826 | 0.0062336 | 0.99818 | 0.0069684 | 16.1183
103 | 0.31387 | 0.15101 | -0.31387 | -0.15201 | 5.725e-06 | -0.001006 | 0.010064 | 0.010077 | 0.010077 | 0.99905 | -0.00076398 | 0.99904 | -0.00060626 | 4.5804
104 | 1.048 | 0.50288 | -1.048 | -0.50302 | 8.8413e-06 | -0.00013721 | 0.033591 | 0.033593 | 0.033593 | 0.99894 | -0.014419 | 0.99893 | -0.014347 | 15.2694
105 | 1.048 | 0.50302 | -1.048 | -0.50334 | 2.0712e-05 | -0.00032137 | 0.033593 | 0.033597 | 0.033597 | 0.99893 | -0.014347 | 0.99891 | -0.014178 | 15.2713
106 | 0.6393 | 0.30542 | -0.63927 | -0.30546 | 3.7309e-05 | -3.6125e-05 | 0.020475 | 0.020476 | 0.020476 | 0.99891 | -0.014178 | 0.99885 | -0.014582 | 9.7504
107 | 0.34887 | 0.16589 | -0.34885 | -0.16825 | 1.6587e-05 | -0.0023633 | 0.011164 | 0.011194 | 0.011194 | 0.99885 | -0.014582 | 0.99881 | -0.014178 | 5.0881
108 | 0.34885 | 0.16825 | -0.34885 | -0.16895 | 4.9537e-06 | -0.00070333 | 0.011194 | 0.011203 | 0.011203 | 0.99881 | -0.014178 | 0.9988 | -0.014055 | 5.0922
109 | -0.42224 | -0.2045 | 0.42225 | 0.20375 | 7.7583e-06 | -0.00074742 | 0.013576 | 0.013567 | 0.013576 | 0.99758 | 0.00055203 | 0.9976 | 0.00039263 | 6.171
110 | -1.9181 | -0.92298 | 1.9187 | 0.92325 | 0.00059816 | 0.0002695 | 0.061595 | 0.061594 | 0.061595 | 0.9976 | 0.00039263 | 0.99793 | 0.0024985 | 29.3311
111 | 1.4958 | 0.71923 | -1.4958 | -0.71949 | 3.5487e-05 | -0.00026327 | 0.048028 | 0.048032 | 0.048032 | 0.9976 | 0.00039263 | 0.99758 | 0.00059607 | 21.8327
112 | 0.26828 | 0.12757 | -0.26827 | -0.12977 | 9.1942e-06 | -0.0022076 | 0.0085935 | 0.0086211 | 0.0086211 | 0.99792 | 0.0092521 | 0.99789 | 0.0095442 | 3.9187
113 | -0.40967 | -0.19841 | 0.40967 | 0.19833 | 7.6646e-07 | -7.8675e-05 | 0.013161 | 0.01316 | 0.013161 | 0.99844 | 0.0042282 | 0.99844 | 0.0042119 | 5.9821
114 | -0.40967 | -0.19833 | 0.40967 | 0.19791 | 4.069e-06 | -0.00041788 | 0.01316 | 0.013154 | 0.01316 | 0.99844 | 0.0042119 | 0.99845 | 0.0041257 | 5.9817
115 | 0.10318 | 0.049565 | -0.10318 | -0.049972 | 2.5054e-07 | -0.00040713 | 0.0033095 | 0.0033146 | 0.0033146 | 0.99845 | 0.0041257 | 0.99845 | 0.0041466 | 1.5066
116 | -0.51285 | -0.24748 | 0.51286 | 0.24686 | 9.516e-06 | -0.00062342 | 0.016464 | 0.016456 | 0.016464 | 0.99845 | 0.0041257 | 0.99847 | 0.0039658 | 7.4836
117 | -1.5592 | -0.74027 | 1.5593 | 0.73997 | 4.4265e-05 | -0.0003038 | 0.049904 | 0.0499 | 0.049904 | 0.99844 | 0.0042021 | 0.99847 | 0.0039658 | 22.6837
118 | 1.5592 | 0.74027 | -1.5592 | -0.74081 | 7.8791e-05 | -0.00054059 | 0.049904 | 0.049911 | 0.049911 | 0.99844 | 0.0042021 | 0.99839 | 0.0046234 | 22.6869
119 | -2.0721 | -0.98682 | 2.0724 | 0.986 | 0.00022006 | -0.00082607 | 0.066356 | 0.066345 | 0.066356 | 0.99847 | 0.0039658 | 0.99857 | 0.003076 | 30.1618
120 | 1.4758 | 0.70046 | -1.4758 | -0.70103 | 7.3998e-05 | -0.0005692 | 0.047235 | 0.047242 | 0.047242 | 0.99839 | 0.0046234 | 0.99835 | 0.0050411 | 21.4737
121 | -2.607 | -1.245 | 2.6075 | 1.244 | 0.00043351 | -0.00098009 | 0.083519 | 0.083505 | 0.083519 | 0.99857 | 0.003076 | 0.99872 | 0.0016741 | 37.9632
122 | -0.26827 | -0.12993 | 0.26827 | 0.12977 | 6.559e-07 | -0.00015694 | 0.0086231 | 0.0086211 | 0.0086231 | 0.99789 | 0.0095655 | 0.99789 | 0.0095442 | 3.9196
123 | 1.4758 | 0.70103 | -1.4757 | -0.70122 | 2.4272e-05 | -0.00018665 | 0.047242 | 0.047245 | 0.047245 | 0.99835 | 0.0050411 | 0.99833 | 0.0051783 | 21.4748
124 | -2.6075 | -1.244 | 2.6075 | 1.2438 | 7.5011e-05 | -0.00016966 | 0.083505 | 0.083503 | 0.083505 | 0.99872 | 0.0016741 | 0.99875 | 0.0014319 | 37.9569
125 | -0.31656 | -0.15332 | 0.31656 | 0.15265 | 3.8633e-06 | -0.00066856 | 0.010158 | 0.010149 | 0.010158 | 0.99961 | -0.001031 | 0.99962 | -0.0011368 | 4.6171
126 | -6.1876 | -2.9272 | 6.1879 | 2.9199 | 0.00035781 | -0.0072414 | 0.1977 | 0.1976 | 0.1977 | 0.99951 | -0.0020228 | 0.99957 | -0.0017773 | 15.4934
127 | 0.091826 | 0.043832 | -0.091825 | -0.044473 | 3.1095e-07 | -0.00064148 | 0.0029387 | 0.0029468 | 0.0029468 | 0.99951 | -0.0020228 | 0.99951 | -0.0019937 | 1.3394
128 | -6.1879 | -2.9199 | 6.1879 | 2.9193 | 3.3838e-05 | -0.00068523 | 0.1976 | 0.1976 | 0.1976 | 0.99957 | -0.0017773 | 0.99957 | -0.0017539 | 15.4862
129 | -6.2821 | -2.9649 | 6.2822 | 2.9636 | 6.5737e-05 | -0.0012904 | 0.20062 | 0.2006 | 0.20062 | 0.99957 | -0.0017539 | 0.99958 | -0.0017092 | 15.7224
130 | 0.41858 | 0.20203 | -0.41857 | -0.20272 | 7.0453e-06 | -0.00069061 | 0.01345 | 0.013459 | 0.013459 | 0.99758 | 0.00059607 | 0.99756 | 0.00074214 | 6.1175
131 | 0.42898 | 0.20549 | -0.42895 | -0.20768 | 2.3477e-05 | -0.002194 | 0.013764 | 0.013792 | 0.013792 | 0.99758 | 0.00059607 | 0.99753 | 0.0010669 | 6.2691
132 | 0.64824 | 0.31197 | -0.64822 | -0.31259 | 1.5292e-05 | -0.00062324 | 0.020818 | 0.020826 | 0.020826 | 0.99758 | 0.00059607 | 0.99756 | 0.00079915 | 9.4662
133 | 0.42895 | 0.20768 | -0.42895 | -0.2077 | 6.5497e-06 | -1.8854e-05 | 0.013792 | 0.013792 | 0.013792 | 0.99753 | 0.0010669 | 0.99751 | 0.00096612 | 6.5677
134 | 0.64822 | 0.31259 | -0.64822 | -0.31263 | 1.0139e-06 | -4.1302e-05 | 0.020826 | 0.020826 | 0.020826 | 0.99756 | 0.00079915 | 0.99755 | 0.00081264 | 9.4664
135 | 0.11141 | 0.053911 | -0.11141 | -0.053957 | 3.3028e-08 | -4.5852e-05 | 0.0035817 | 0.0035823 | 0.0035823 | 0.99751 | 0.00096612 | 0.99751 | 0.0009687 | 1.6283
136 | 0.41165 | 0.19805 | -0.41164 | -0.19809 | 1.2037e-05 | -3.8382e-05 | 0.013219 | 0.01322 | 0.01322 | 0.99755 | 0.00081264 | 0.99752 | 0.00061512 | 6.2953
137 | -6.3656 | -3.004 | 6.3657 | 3.0011 | 0.00014986 | -0.0028635 | 0.20328 | 0.20324 | 0.20328 | 0.99958 | -0.0017092 | 0.99961 | -0.0016083 | 15.9307
138 | 0.41164 | 0.19809 | -0.41163 | -0.19859 | 4.8959e-06 | -0.00049684 | 0.01322 | 0.013226 | 0.013226 | 0.99752 | 0.00061512 | 0.99751 | 0.00071755 | 6.012
139 | 0.19941 | 0.096054 | -0.19941 | -0.096577 | 1.2042e-06 | -0.0005223 | 0.0064027 | 0.0064093 | 0.0064093 | 0.99793 | 0.0024985 | 0.99792 | 0.0025508 | 2.9133
140 | -2.1181 | -1.0193 | 2.1183 | 1.0186 | 0.00019702 | -0.0007007 | 0.067997 | 0.067987 | 0.067997 | 0.99793 | 0.0024985 | 0.99801 | 0.0017004 | 30.9075
141 | 0.41163 | 0.19859 | -0.41163 | -0.19936 | 7.611e-06 | -0.00077141 | 0.013226 | 0.013236 | 0.013236 | 0.99751 | 0.00071755 | 0.99749 | 0.00087792 | 6.0164
142 | -0.070964 | -0.034369 | 0.070964 | 0.033447 | 2.6783e-07 | -0.00092237 | 0.0022804 | 0.0022689 | 0.0022804 | 0.99816 | 0.0071104 | 0.99816 | 0.0070785 | 1.0365
143 | -0.070964 | -0.033447 | 0.070965 | 0.029524 | 1.11e-06 | -0.0039232 | 0.0022689 | 0.0022229 | 0.0022689 | 0.99816 | 0.0070785 | 0.99818 | 0.0069684 | 1.0313
144 | 0.96031 | 0.45797 | -0.96018 | -0.46053 | 0.00013841 | -0.002561 | 0.030769 | 0.030801 | 0.030801 | 0.99818 | 0.0069684 | 0.99804 | 0.0081892 | 14.0007
145 | 0.077386 | 0.036232 | -0.077385 | -0.037479 | 4.302e-07 | -0.0012474 | 0.0024712 | 0.0024867 | 0.0024867 | 0.99818 | 0.0069684 | 0.99817 | 0.007015 | 1.1303
146 | 0.96018 | 0.46053 | -0.96013 | -0.46134 | 4.3575e-05 | -0.000805 | 0.030801 | 0.030812 | 0.030812 | 0.99804 | 0.0081892 | 0.998 | 0.0085769 | 14.0053
147 | 0.6602 | 0.31607 | -0.6602 | -0.31621 | 3.5113e-06 | -0.00013848 | 0.021172 | 0.021174 | 0.021174 | 0.998 | 0.0085769 | 0.998 | 0.008622 | 9.6246
148 | 2.1185 | 1.0179 | -2.1183 | -1.0186 | 0.00020708 | -0.00073684 | 0.067977 | 0.067987 | 0.067987 | 0.9981 | 0.00086308 | 0.99801 | 0.0017004 | 30.9032
149 | -2.2736 | -1.093 | 2.2745 | 1.0934 | 0.00090102 | 0.00045135 | 0.072962 | 0.072961 | 0.072962 | 0.9981 | 0.00086308 | 0.99852 | 0.0035486 | 34.7439
150 | -2.4351 | -1.1712 | 2.4352 | 1.1707 | 0.0001845 | -0.00048449 | 0.078118 | 0.078111 | 0.078118 | 0.99852 | 0.0035486 | 0.99859 | 0.002899 | 35.508
151 | -2.4352 | -1.1707 | 2.4353 | 1.1705 | 7.9634e-05 | -0.00020917 | 0.078111 | 0.078108 | 0.078111 | 0.99859 | 0.002899 | 0.99862 | 0.0026189 | 35.5049
152 | -0.13114 | -0.063512 | 0.13114 | 0.062957 | 5.5277e-07 | -0.00055486 | 0.0042151 | 0.0042081 | 0.0042151 | 0.9979 | 0.0075723 | 0.9979 | 0.0075359 | 1.9159
153 | -0.13114 | -0.062957 | 0.13114 | 0.062277 | 6.7517e-07 | -0.00068023 | 0.0042081 | 0.0041996 | 0.0042081 | 0.9979 | 0.0075359 | 0.99791 | 0.0074925 | 1.9128
154 | 0.4107 | 0.19821 | -0.4107 | -0.19891 | 6.8272e-06 | -0.00069618 | 0.013192 | 0.013201 | 0.013201 | 0.99791 | 0.0074925 | 0.99789 | 0.0076367 | 6.0004
155 | -0.54184 | -0.26049 | 0.54187 | 0.25898 | 2.5781e-05 | -0.0015121 | 0.017392 | 0.017373 | 0.017392 | 0.99791 | 0.0074925 | 0.99795 | 0.0070874 | 7.9053
156 | -0.65846 | -0.31463 | 0.65853 | 0.31458 | 6.1569e-05 | -5.3643e-05 | 0.02111 | 0.021109 | 0.02111 | 0.99795 | 0.0070874 | 0.99805 | 0.0077356 | 10.0524
157 | 0.1166 | 0.055653 | -0.1166 | -0.05647 | 6.4272e-07 | -0.00081718 | 0.0037373 | 0.0037475 | 0.0037475 | 0.99795 | 0.0070874 | 0.99795 | 0.0071347 | 1.7034
158 | -0.76429 | -0.3658 | 0.76431 | 0.36532 | 1.6581e-05 | -0.00048702 | 0.024508 | 0.024502 | 0.024508 | 0.99805 | 0.0077356 | 0.99807 | 0.0075518 | 11.1399
159 | 3.3261 | 1.5913 | -3.3257 | -1.5918 | 0.00042617 | -0.00054348 | 0.10655 | 0.10656 | 0.10656 | 0.99898 | -0.00064875 | 0.99886 | 0.00043794 | 48.4344
160 | 3.2024 | 1.5326 | -3.2016 | -1.5337 | 0.00082241 | -0.0011494 | 0.1026 | 0.10262 | 0.10262 | 0.99886 | 0.00043794 | 0.99862 | 0.0026189 | 46.6462
161 | 0.12323 | 0.059246 | -0.12323 | -0.059682 | 3.8254e-07 | -0.00043644 | 0.0039516 | 0.0039571 | 0.0039571 | 0.99886 | 0.00043794 | 0.99886 | 0.00046476 | 1.7987
162 | 0.57676 | 0.27704 | -0.57674 | -0.27772 | 1.3216e-05 | -0.00068477 | 0.018496 | 0.018505 | 0.018505 | 0.99862 | 0.0026189 | 0.9986 | 0.0028154 | 8.4112
163 | 0.18954 | 0.08619 | -0.18953 | -0.087656 | 2.9879e-06 | -0.0014658 | 0.0060189 | 0.0060366 | 0.0060366 | 0.99862 | 0.0026189 | 0.99861 | 0.0027398 | 2.7439
164 | 2.8544 | 1.3633 | -2.8544 | -1.3634 | 4.6146e-05 | -8.4794e-05 | 0.091429 | 0.09143 | 0.09143 | 0.99876 | 0.0012954 | 0.99875 | 0.0014319 | 41.5592
165 | 0.07019 | 0.033415 | -0.07019 | -0.033995 | 1.6454e-07 | -0.00057953 | 0.0022469 | 0.0022541 | 0.0022541 | 0.99877 | 0.0012409 | 0.99877 | 0.0012609 | 1.0246
166 | 0.10467 | 0.047841 | -0.10467 | -0.049902 | 1.2893e-06 | -0.0020618 | 0.0033268 | 0.003352 | 0.003352 | 0.99861 | 0.0027398 | 0.9986 | 0.0028384 | 1.5236
167 | 0.084866 | 0.039816 | -0.084866 | -0.041102 | 5.3295e-07 | -0.0012866 | 0.0027099 | 0.0027259 | 0.0027259 | 0.99861 | 0.0027398 | 0.9986 | 0.0027926 | 1.239
168 | 0.10467 | 0.049902 | -0.10467 | -0.050692 | 4.9885e-07 | -0.00078935 | 0.003352 | 0.0033619 | 0.0033619 | 0.9986 | 0.0028384 | 0.99859 | 0.0028793 | 1.5281
169 | 0.21592 | 0.10297 | -0.21592 | -0.10379 | 2.2187e-06 | -0.00082557 | 0.0069152 | 0.0069255 | 0.0069255 | 0.9986 | 0.0028154 | 0.99859 | 0.0029027 | 3.148
170 | 0.21592 | 0.10379 | -0.21592 | -0.10446 | 1.8113e-06 | -0.00067214 | 0.0069255 | 0.006934 | 0.006934 | 0.99859 | 0.0029027 | 0.99858 | 0.002975 | 3.1518
171 | -0.30518 | -0.14781 | 0.30519 | 0.14647 | 7.2068e-06 | -0.0013348 | 0.0098081 | 0.0097913 | 0.0098081 | 0.99803 | 0.0079213 | 0.99805 | 0.0077176 | 4.4582
172 | -0.30519 | -0.14647 | 0.3052 | 0.14536 | 5.9795e-06 | -0.001111 | 0.0097913 | 0.0097774 | 0.0097913 | 0.99805 | 0.0077176 | 0.99807 | 0.0075518 | 4.4506
173 | -1.0695 | -0.51068 | 1.0696 | 0.50929 | 9.3043e-05 | -0.0013839 | 0.034279 | 0.034262 | 0.034279 | 0.99807 | 0.0075518 | 0.99815 | 0.00682 | 15.5814
174 | -1.1379 | -0.54236 | 1.1379 | 0.54157 | 6.0286e-05 | -0.00079066 | 0.036455 | 0.036445 | 0.036455 | 0.99815 | 0.00682 | 0.9982 | 0.0063755 | 16.5707
175 | -1.4035 | -0.66803 | 1.4036 | 0.66729 | 8.6301e-05 | -0.00073567 | 0.044953 | 0.044943 | 0.044953 | 0.9982 | 0.0063755 | 0.99826 | 0.0058611 | 20.433
176 | 0.080786 | 0.038664 | -0.080786 | -0.039126 | 1.7445e-07 | -0.00046233 | 0.0025901 | 0.0025959 | 0.0025959 | 0.9982 | 0.0063755 | 0.9982 | 0.0063941 | 1.1799
177 | 0.18481 | 0.087797 | -0.18481 | -0.088139 | 6.7369e-07 | -0.00034244 | 0.0059171 | 0.0059214 | 0.0059214 | 0.9982 | 0.0063755 | 0.9982 | 0.0064061 | 2.6915
178 | 0.6602 | 0.31621 | -0.66013 | -0.31889 | 6.7867e-05 | -0.0026718 | 0.021174 | 0.021208 | 0.021208 | 0.998 | 0.008622 | 0.9979 | 0.009504 | 9.6399
179 | 0.21592 | 0.10446 | -0.21592 | -0.10457 | 2.9296e-07 | -0.00010855 | 0.006934 | 0.0069353 | 0.0069353 | 0.99858 | 0.002975 | 0.99858 | 0.0029868 | 3.1524
180 | -0.09241 | -0.044756 | 0.092411 | 0.04395 | 3.9765e-07 | -0.00080629 | 0.0029694 | 0.0029593 | 0.0029694 | 0.99819 | 0.0064428 | 0.9982 | 0.0064061 | 1.3497
181 | 0.092401 | 0.044189 | -0.092401 | -0.044262 | 3.6061e-08 | -7.3215e-05 | 0.0029621 | 0.002963 | 0.002963 | 0.9982 | 0.0064061 | 0.9982 | 0.0064094 | 1.3468
182 | 0.092401 | 0.044262 | -0.092401 | -0.044752 | 2.416e-07 | -0.00048934 | 0.002963 | 0.0029691 | 0.0029691 | 0.9982 | 0.0064094 | 0.99819 | 0.0064319 | 1.3496
183 | -1.4036 | -0.66729 | 1.4037 | 0.66682 | 5.6195e-05 | -0.00047925 | 0.044943 | 0.044937 | 0.044943 | 0.99826 | 0.0058611 | 0.99829 | 0.0055269 | 20.4287
184 | -1.4757 | -0.70169 | 1.4757 | 0.70122 | 6.1591e-05 | -0.00047351 | 0.047251 | 0.047245 | 0.047251 | 0.99829 | 0.0055269 | 0.99833 | 0.0051783 | 21.4776
185 | -0.26802 | -0.12981 | 0.26802 | 0.12913 | 2.8207e-06 | -0.00067668 | 0.008615 | 0.0086065 | 0.008615 | 0.99789 | 0.0096458 | 0.9979 | 0.0095546 | 3.9159
186 | -0.66013 | -0.31904 | 0.66013 | 0.31889 | 3.854e-06 | -0.00015145 | 0.02121 | 0.021208 | 0.02121 | 0.9979 | 0.0095546 | 0.9979 | 0.009504 | 9.6408

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 20.5789 | 9.7354

## res_load
| p_mw | q_mvar
0 | 0.25647 | 0.12421
1 | 0.085466 | 0.041393
2 | 0.32369 | 0.15677
3 | 0.26001 | 0.12593
4 | 0.39469 | 0.19116
5 | 0.29035 | 0.14062
6 | 0.21518 | 0.10422
7 | 0.068285 | 0.033072
8 | 0.35392 | 0.17141
9 | 0.40525 | 0.19627
10 | 0.088442 | 0.042834
11 | 0.07102 | 0.034396
12 | 0.13725 | 0.066473
13 | 0.17618 | 0.085326
14 | 0.38992 | 0.18885
15 | 0.28375 | 0.13742
16 | 0.34095 | 0.16513
17 | 0.22456 | 0.10876
18 | 0.27707 | 0.13419
19 | 0.33856 | 0.16397
20 | 0.12545 | 0.060759
21 | 0.29606 | 0.14339
22 | 0.25409 | 0.12306
23 | 0.2489 | 0.12055
24 | 0.32963 | 0.15965
25 | 0.22201 | 0.10753
26 | 0.34386 | 0.16654
27 | 0.2294 | 0.1111
28 | 0.14504 | 0.070248
29 | 0.096934 | 0.046947
30 | 0.19074 | 0.09238
31 | 0.07608 | 0.036847
32 | 0.0842 | 0.04078
33 | 0.12211 | 0.05914
34 | 0.82488 | 0.39951
35 | 0.31052 | 0.15039
36 | 0.13742 | 0.066556
37 | 0.29038 | 0.14064
38 | 0.3885 | 0.18816
39 | 0.085133 | 0.041232
40 | 0.38245 | 0.18523
41 | 0.083875 | 0.040622
42 | 0.40865 | 0.19792
43 | 0.34885 | 0.16895
44 | 0.42224 | 0.2045
45 | 0.40967 | 0.19841
46 | 0.08331 | 0.040349
47 | 0.53468 | 0.25896
48 | 0.10318 | 0.049972
49 | 0.26827 | 0.12993
50 | 0.31656 | 0.15332
51 | 0.31464 | 0.15239
52 | 0.091825 | 0.044473
53 | 0.0942 | 0.045623
54 | 0.41857 | 0.20272
55 | 0.31754 | 0.15379
56 | 0.23657 | 0.11458
57 | 0.083344 | 0.040365
58 | 0.11141 | 0.053957
59 | 0.41163 | 0.19936
60 | 0.070964 | 0.034369
61 | 0.077385 | 0.037479
62 | 0.29993 | 0.14526
63 | 0.15513 | 0.075132
64 | 0.16054 | 0.077751
65 | 0.19941 | 0.096577
66 | 0.31387 | 0.15201
67 | 0.13114 | 0.063512
68 | 0.4107 | 0.19891
69 | 0.10577 | 0.051226
70 | 0.1166 | 0.05647
71 | 0.094348 | 0.045695
72 | 0.12323 | 0.059682
73 | 0.15251 | 0.073866
74 | 0.099942 | 0.048404
75 | 0.084866 | 0.041102
76 | 0.36082 | 0.17475
77 | 0.30518 | 0.14781
78 | 0.068275 | 0.033067
79 | 0.23349 | 0.11308
80 | 0.10467 | 0.050692
81 | 0.11082 | 0.053672
82 | 0.21592 | 0.10457
83 | 0.24685 | 0.11956
84 | 0.07019 | 0.033995
85 | 0.09241 | 0.044756
86 | 0.092401 | 0.044752
87 | 0.080786 | 0.039126
88 | 0.072009 | 0.034876
89 | 0.26802 | 0.12981
90 | 0.3921 | 0.1899

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1