## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_539_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_539_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_539_0_node_1 | 20 | n |  | TRUE
3 | bus_MV_539_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_539_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_539_0_node_144 | 20 | n |  | TRUE
6 | bus_MV_539_0_node_143 | 20 | n |  | TRUE
7 | bus_MV_539_0_node_145 | 20 | n |  | TRUE
8 | bus_MV_539_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_539_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_539_0_node_103 | 20 | n |  | TRUE
11 | bus_MV_539_0_node_53 | 20 | n |  | TRUE
12 | bus_MV_539_0_node_102 | 20 | n |  | TRUE
13 | bus_MV_539_0_node_176 | 20 | n |  | TRUE
14 | bus_MV_539_0_node_54 | 20 | n |  | TRUE
15 | bus_MV_539_0_node_97 | 20 | n |  | TRUE
16 | bus_MV_539_0_node_96 | 20 | n |  | TRUE
17 | bus_MV_539_0_node_7 | 20 | n |  | TRUE
18 | bus_MV_539_0_node_8 | 20 | n |  | TRUE
19 | bus_MV_539_0_node_9 | 20 | n |  | TRUE
20 | bus_MV_539_0_node_77 | 20 | n |  | TRUE
21 | bus_MV_539_0_node_78 | 20 | n |  | TRUE
22 | bus_MV_539_0_node_10 | 20 | n |  | TRUE
23 | bus_MV_539_0_node_42 | 20 | n |  | TRUE
24 | bus_MV_539_0_node_79 | 20 | n |  | TRUE
25 | bus_MV_539_0_node_60 | 20 | n |  | TRUE
26 | bus_MV_539_0_node_61 | 20 | n |  | TRUE
27 | bus_MV_539_0_node_11 | 20 | n |  | TRUE
28 | bus_MV_539_0_node_12 | 20 | n |  | TRUE
29 | bus_MV_539_0_node_13 | 20 | n |  | TRUE
30 | bus_MV_539_0_node_29 | 20 | n |  | TRUE
31 | bus_MV_539_0_node_120 | 20 | n |  | TRUE
32 | bus_MV_539_0_node_169 | 20 | n |  | TRUE
33 | bus_MV_539_0_node_15 | 20 | n |  | TRUE
34 | bus_MV_539_0_node_30 | 20 | n |  | TRUE
35 | bus_MV_539_0_node_18 | 20 | n |  | TRUE
36 | bus_MV_539_0_node_14 | 20 | n |  | TRUE
37 | bus_MV_539_0_node_16 | 20 | n |  | TRUE
38 | bus_MV_539_0_node_20 | 20 | n |  | TRUE
39 | bus_MV_539_0_node_19 | 20 | n |  | TRUE
40 | bus_MV_539_0_node_21 | 20 | n |  | TRUE
41 | bus_MV_539_0_node_22 | 20 | n |  | TRUE
42 | bus_MV_539_0_node_27 | 20 | n |  | TRUE
43 | bus_MV_539_0_node_17 | 20 | n |  | TRUE
44 | bus_MV_539_0_node_38 | 20 | n |  | TRUE
45 | bus_MV_539_0_node_123 | 20 | n |  | TRUE
46 | bus_MV_539_0_node_28 | 20 | n |  | TRUE
47 | bus_MV_539_0_node_171 | 20 | n |  | TRUE
48 | bus_MV_539_0_node_148 | 20 | n |  | TRUE
49 | bus_MV_539_0_node_152 | 20 | n |  | TRUE
50 | bus_MV_539_0_node_76 | 20 | n |  | TRUE
51 | bus_MV_539_0_node_25 | 20 | n |  | TRUE
52 | bus_MV_539_0_node_158 | 20 | n |  | TRUE
53 | bus_MV_539_0_node_160 | 20 | n |  | TRUE
54 | bus_MV_539_0_node_26 | 20 | n |  | TRUE
55 | bus_MV_539_0_node_24 | 20 | n |  | TRUE
56 | bus_MV_539_0_node_164 | 20 | n |  | TRUE
57 | bus_MV_539_0_node_23 | 20 | n |  | TRUE
58 | bus_MV_539_0_node_36 | 20 | n |  | TRUE
59 | bus_MV_539_0_node_150 | 20 | n |  | TRUE
60 | bus_MV_539_0_node_146 | 20 | n |  | TRUE
61 | bus_MV_539_0_node_170 | 20 | n |  | TRUE
62 | bus_MV_539_0_node_37 | 20 | n |  | TRUE
63 | bus_MV_539_0_node_159 | 20 | n |  | TRUE
64 | bus_MV_539_0_node_151 | 20 | n |  | TRUE
65 | bus_MV_539_0_node_156 | 20 | n |  | TRUE
66 | bus_MV_539_0_node_31 | 20 | n |  | TRUE
67 | bus_MV_539_0_node_32 | 20 | n |  | TRUE
68 | bus_MV_539_0_node_33 | 20 | n |  | TRUE
69 | bus_MV_539_0_node_175 | 20 | n |  | TRUE
70 | bus_MV_539_0_node_34 | 20 | n |  | TRUE
71 | bus_MV_539_0_node_69 | 20 | n |  | TRUE
72 | bus_MV_539_0_node_126 | 20 | n |  | TRUE
73 | bus_MV_539_0_node_35 | 20 | n |  | TRUE
74 | bus_MV_539_0_node_161 | 20 | n |  | TRUE
75 | bus_MV_539_0_node_127 | 20 | n |  | TRUE
76 | bus_MV_539_0_node_67 | 20 | n |  | TRUE
77 | bus_MV_539_0_node_168 | 20 | n |  | TRUE
78 | bus_MV_539_0_node_147 | 20 | n |  | TRUE
79 | bus_MV_539_0_node_149 | 20 | n |  | TRUE
80 | bus_MV_539_0_node_153 | 20 | n |  | TRUE
81 | bus_MV_539_0_node_154 | 20 | n |  | TRUE
82 | bus_MV_539_0_node_155 | 20 | n |  | TRUE
83 | bus_MV_539_0_node_157 | 20 | n |  | TRUE
84 | bus_MV_539_0_node_172 | 20 | n |  | TRUE
85 | bus_MV_539_0_node_40 | 20 | n |  | TRUE
86 | bus_MV_539_0_node_52 | 20 | n |  | TRUE
87 | bus_MV_539_0_node_41 | 20 | n |  | TRUE
88 | bus_MV_539_0_node_137 | 20 | n |  | TRUE
89 | bus_MV_539_0_node_47 | 20 | n |  | TRUE
90 | bus_MV_539_0_node_50 | 20 | n |  | TRUE
91 | bus_MV_539_0_node_45 | 20 | n |  | TRUE
92 | bus_MV_539_0_node_43 | 20 | n |  | TRUE
93 | bus_MV_539_0_node_44 | 20 | n |  | TRUE
94 | bus_MV_539_0_node_130 | 20 | n |  | TRUE
95 | bus_MV_539_0_node_131 | 20 | n |  | TRUE
96 | bus_MV_539_0_node_132 | 20 | n |  | TRUE
97 | bus_MV_539_0_node_46 | 20 | n |  | TRUE
98 | bus_MV_539_0_node_109 | 20 | n |  | TRUE
99 | bus_MV_539_0_node_110 | 20 | n |  | TRUE
100 | bus_MV_539_0_node_48 | 20 | n |  | TRUE
101 | bus_MV_539_0_node_51 | 20 | n |  | TRUE
102 | bus_MV_539_0_node_173 | 20 | n |  | TRUE
103 | bus_MV_539_0_node_49 | 20 | n |  | TRUE
104 | bus_MV_539_0_node_100 | 20 | n |  | TRUE
105 | bus_MV_539_0_node_139 | 20 | n |  | TRUE
106 | bus_MV_539_0_node_101 | 20 | n |  | TRUE
107 | bus_MV_539_0_node_142 | 20 | n |  | TRUE
108 | bus_MV_539_0_node_108 | 20 | n |  | TRUE
109 | bus_MV_539_0_node_55 | 20 | n |  | TRUE
110 | bus_MV_539_0_node_99 | 20 | n |  | TRUE
111 | bus_MV_539_0_node_135 | 20 | n |  | TRUE
112 | bus_MV_539_0_node_111 | 20 | n |  | TRUE
113 | bus_MV_539_0_node_112 | 20 | n |  | TRUE
114 | bus_MV_539_0_node_56 | 20 | n |  | TRUE
115 | bus_MV_539_0_node_57 | 20 | n |  | TRUE
116 | bus_MV_539_0_node_58 | 20 | n |  | TRUE
117 | bus_MV_539_0_node_59 | 20 | n |  | TRUE
118 | bus_MV_539_0_node_129 | 20 | n |  | TRUE
119 | bus_MV_539_0_node_75 | 20 | n |  | TRUE
120 | bus_MV_539_0_node_128 | 20 | n |  | TRUE
121 | bus_MV_539_0_node_73 | 20 | n |  | TRUE
122 | bus_MV_539_0_node_74 | 20 | n |  | TRUE
123 | bus_MV_539_0_node_122 | 20 | n |  | TRUE
124 | bus_MV_539_0_node_62 | 20 | n |  | TRUE
125 | bus_MV_539_0_node_89 | 20 | n |  | TRUE
126 | bus_MV_539_0_node_90 | 20 | n |  | TRUE
127 | bus_MV_539_0_node_63 | 20 | n |  | TRUE
128 | bus_MV_539_0_node_64 | 20 | n |  | TRUE
129 | bus_MV_539_0_node_65 | 20 | n |  | TRUE
130 | bus_MV_539_0_node_66 | 20 | n |  | TRUE
131 | bus_MV_539_0_node_165 | 20 | n |  | TRUE
132 | bus_MV_539_0_node_68 | 20 | n |  | TRUE
133 | bus_MV_539_0_node_121 | 20 | n |  | TRUE
134 | bus_MV_539_0_node_162 | 20 | n |  | TRUE
135 | bus_MV_539_0_node_70 | 20 | n |  | TRUE
136 | bus_MV_539_0_node_71 | 20 | n |  | TRUE
137 | bus_MV_539_0_node_72 | 20 | n |  | TRUE
138 | bus_MV_539_0_node_163 | 20 | n |  | TRUE
139 | bus_MV_539_0_node_125 | 20 | n |  | TRUE
140 | bus_MV_539_0_node_118 | 20 | n |  | TRUE
141 | bus_MV_539_0_node_80 | 20 | n |  | TRUE
142 | bus_MV_539_0_node_81 | 20 | n |  | TRUE
143 | bus_MV_539_0_node_138 | 20 | n |  | TRUE
144 | bus_MV_539_0_node_82 | 20 | n |  | TRUE
145 | bus_MV_539_0_node_83 | 20 | n |  | TRUE
146 | bus_MV_539_0_node_84 | 20 | n |  | TRUE
147 | bus_MV_539_0_node_85 | 20 | n |  | TRUE
148 | bus_MV_539_0_node_86 | 20 | n |  | TRUE
149 | bus_MV_539_0_node_174 | 20 | n |  | TRUE
150 | bus_MV_539_0_node_87 | 20 | n |  | TRUE
151 | bus_MV_539_0_node_88 | 20 | n |  | TRUE
152 | bus_MV_539_0_node_94 | 20 | n |  | TRUE
153 | bus_MV_539_0_node_91 | 20 | n |  | TRUE
154 | bus_MV_539_0_node_98 | 20 | n |  | TRUE
155 | bus_MV_539_0_node_95 | 20 | n |  | TRUE
156 | bus_MV_539_0_node_104 | 20 | n |  | TRUE
157 | bus_MV_539_0_node_105 | 20 | n |  | TRUE
158 | bus_MV_539_0_node_106 | 20 | n |  | TRUE
159 | bus_MV_539_0_node_107 | 20 | n |  | TRUE
160 | bus_MV_539_0_node_141 | 20 | n |  | TRUE
161 | bus_MV_539_0_node_140 | 20 | n |  | TRUE
162 | bus_MV_539_0_node_113 | 20 | n |  | TRUE
163 | bus_MV_539_0_node_115 | 20 | n |  | TRUE
164 | bus_MV_539_0_node_114 | 20 | n |  | TRUE
165 | bus_MV_539_0_node_116 | 20 | n |  | TRUE
166 | bus_MV_539_0_node_133 | 20 | n |  | TRUE
167 | bus_MV_539_0_node_119 | 20 | n |  | TRUE
168 | bus_MV_539_0_node_134 | 20 | n |  | TRUE
169 | bus_MV_539_0_node_136 | 20 | n |  | TRUE
170 | bus_MV_539_0_node_166 | 20 | n |  | TRUE
171 | bus_MV_539_0_node_167 | 20 | n |  | TRUE
172 | bus_HV_539_0_node_132 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_539_0_load_0 | 0 | 0.38256 | 0.18528 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_539_0_load_143 | 6 | 0.1147 | 0.055552 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_539_0_load_145 | 7 | 0.1383 | 0.066982 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_539_0_load_103 | 10 | 0.37219 | 0.18026 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_539_0_load_53 | 11 | 0.36964 | 0.17903 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_539_0_load_102 | 12 | 0.3756 | 0.18191 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_539_0_load_176 | 13 | 0.35505 | 0.17196 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_539_0_load_7 | 17 | 0.31228 | 0.15124 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_539_0_load_8 | 18 | 0.13702 | 0.066361 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_539_0_load_77 | 20 | 0.31298 | 0.15158 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_539_0_load_78 | 21 | 0.32652 | 0.15814 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_539_0_load_60 | 25 | 0.23189 | 0.11231 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_539_0_load_11 | 27 | 0.39561 | 0.1916 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_539_0_load_29 | 30 | 0.40073 | 0.19408 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_539_0_load_120 | 31 | 0.25129 | 0.12171 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_539_0_load_15 | 33 | 0.26043 | 0.12613 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_539_0_load_18 | 35 | 0.26205 | 0.12692 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_539_0_load_27 | 42 | 0.37298 | 0.18064 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_539_0_load_38 | 44 | 0.2094 | 0.10142 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_539_0_load_123 | 45 | 0.22187 | 0.10746 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_539_0_load_171 | 47 | 0.31263 | 0.15141 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_539_0_load_76 | 50 | 0.27425 | 0.13283 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_539_0_load_158 | 52 | 0.086996 | 0.042134 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_539_0_load_160 | 53 | 0.27453 | 0.13296 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_539_0_load_164 | 56 | 0.29517 | 0.14296 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_539_0_load_23 | 57 | 0.21972 | 0.10641 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_539_0_load_150 | 59 | 0.10726 | 0.051948 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_539_0_load_146 | 60 | 0.09334 | 0.045207 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_539_0_load_170 | 61 | 0.18945 | 0.091757 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_539_0_load_159 | 63 | 0.22727 | 0.11007 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_539_0_load_31 | 66 | 0.39481 | 0.19121 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_539_0_load_175 | 69 | 0.21234 | 0.10284 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_539_0_load_69 | 71 | 0.30348 | 0.14698 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_539_0_load_126 | 72 | 0.34766 | 0.16838 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_539_0_load_161 | 74 | 0.39878 | 0.19314 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_539_0_load_147 | 78 | 0.25475 | 0.12338 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_539_0_load_149 | 79 | 0.10309 | 0.04993 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_539_0_load_153 | 80 | 0.11368 | 0.055059 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_539_0_load_154 | 81 | 0.13947 | 0.067548 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_539_0_load_157 | 83 | 0.16362 | 0.079244 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_539_0_load_172 | 84 | 0.35964 | 0.17418 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_539_0_load_40 | 85 | 0.31327 | 0.15172 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_539_0_load_52 | 86 | 0.2348 | 0.11372 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_539_0_load_137 | 88 | 0.089837 | 0.04351 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_539_0_load_130 | 94 | 0.24333 | 0.11785 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_539_0_load_131 | 95 | 0.22835 | 0.11059 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_539_0_load_132 | 96 | 0.61164 | 0.29623 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_539_0_load_110 | 99 | 0.32442 | 0.15712 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_539_0_load_173 | 102 | 0.39013 | 0.18895 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_539_0_load_100 | 104 | 0.31019 | 0.15023 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_539_0_load_139 | 105 | 0.11158 | 0.054042 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_539_0_load_101 | 106 | 0.32856 | 0.15913 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_539_0_load_142 | 107 | 0.1179 | 0.057101 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_539_0_load_108 | 108 | 0.2921 | 0.14147 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_539_0_load_112 | 113 | 0.11331 | 0.054879 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_539_0_load_56 | 114 | 0.32439 | 0.15711 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_539_0_load_129 | 118 | 0.3201 | 0.15503 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_539_0_load_73 | 121 | 0.21372 | 0.10351 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_539_0_load_122 | 123 | 0.28287 | 0.137 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_539_0_load_89 | 125 | 0.35617 | 0.1725 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_539_0_load_63 | 127 | 0.093909 | 0.045482 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_539_0_load_165 | 131 | 0.15099 | 0.073129 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_539_0_load_121 | 133 | 0.29807 | 0.14436 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_539_0_load_162 | 134 | 0.12256 | 0.05936 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_539_0_load_70 | 135 | 0.28089 | 0.13604 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_539_0_load_163 | 138 | 0.26361 | 0.12767 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_539_0_load_138 | 143 | 0.14362 | 0.069556 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_539_0_load_82 | 144 | 0.29723 | 0.14395 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_539_0_load_86 | 148 | 0.37645 | 0.18232 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_539_0_load_174 | 149 | 0.33015 | 0.1599 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_539_0_load_94 | 152 | 0.33643 | 0.16294 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_539_0_load_98 | 154 | 0.37403 | 0.18115 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_539_0_load_95 | 155 | 0.26944 | 0.1305 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_539_0_load_104 | 156 | 0.16656 | 0.080671 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_539_0_load_105 | 157 | 0.072284 | 0.035009 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_539_0_load_140 | 161 | 0.089589 | 0.04339 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_539_0_load_113 | 162 | 0.37927 | 0.18369 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_539_0_load_133 | 166 | 0.19632 | 0.095081 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_539_0_load_119 | 167 | 0.37102 | 0.1797 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_539_0_load_136 | 169 | 0.24155 | 0.11699 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_539_0_load_166 | 170 | 0.25298 | 0.12253 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 96 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_539_0_line_0 |  | 0 | 1 | 0.006798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_539_0_line_1 |  | 0 | 2 | 0.049344 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_539_0_line_2 |  | 1 | 3 | 0.082048 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_539_0_line_3 |  | 2 | 4 | 0.1301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_539_0_line_4 |  | 3 | 7 | 0.014799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_539_0_line_5 |  | 4 | 5 | 0.30629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_539_0_line_6 |  | 4 | 6 | 0.036156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_539_0_line_7 |  | 5 | 13 | 0.035415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_539_0_line_8 |  | 8 | 9 | 0.22238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_539_0_line_9 |  | 8 | 10 | 0.004565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_539_0_line_10 |  | 8 | 11 | 0.074994 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_539_0_line_11 |  | 9 | 12 | 0.007037 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_539_0_line_12 |  | 11 | 14 | 0.047461 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_539_0_line_13 |  | 12 | 15 | 0.040975 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_539_0_line_14 |  | 13 | 139 | 0.036544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_539_0_line_15 |  | 14 | 109 | 0.027725 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_539_0_line_16 |  | 15 | 16 | 0.13297 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_539_0_line_17 |  | 16 | 155 | 0.006081 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_539_0_line_18 |  | 17 | 18 | 0.027344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_539_0_line_19 |  | 17 | 19 | 0.050308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_539_0_line_20 |  | 17 | 20 | 0.24221 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_539_0_line_21 |  | 19 | 21 | 0.20763 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_539_0_line_22 |  | 20 | 22 | 0.12103 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
23 | MV_539_0_line_23 |  | 20 | 23 | 0.072035 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
24 | MV_539_0_line_24 |  | 21 | 24 | 0.005601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_539_0_line_25 |  | 22 | 25 | 0.061648 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_539_0_line_26 |  | 23 | 91 | 0.47963 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
27 | MV_539_0_line_27 |  | 24 | 141 | 0.050282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_539_0_line_28 |  | 24 | 142 | 0.047548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_539_0_line_29 |  | 25 | 26 | 0.006293 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
30 | MV_539_0_line_30 |  | 26 | 124 | 0.073203 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
31 | MV_539_0_line_31 |  | 27 | 28 | 0.064443 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_539_0_line_32 |  | 28 | 29 | 0.2554 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_539_0_line_33 |  | 28 | 30 | 0.14411 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
34 | MV_539_0_line_34 |  | 29 | 35 | 0.006919 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
35 | MV_539_0_line_35 |  | 30 | 38 | 0.006577 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
36 | MV_539_0_line_36 |  | 31 | 32 | 0.14495 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
37 | MV_539_0_line_37 |  | 31 | 33 | 0.22231 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_539_0_line_38 |  | 31 | 34 | 0.080265 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
39 | MV_539_0_line_39 |  | 32 | 61 | 0.037562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_539_0_line_40 |  | 32 | 46 | 0.14149 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
41 | MV_539_0_line_41 |  | 33 | 36 | 0.035257 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_539_0_line_42 |  | 34 | 38 | 0.00755 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
43 | MV_539_0_line_43 |  | 35 | 39 | 0.064599 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
44 | MV_539_0_line_44 |  | 36 | 37 | 0.168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_539_0_line_45 |  | 37 | 42 | 0.045494 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_539_0_line_46 |  | 39 | 40 | 0.11123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_539_0_line_47 |  | 39 | 41 | 0.275 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
48 | MV_539_0_line_48 |  | 40 | 50 | 0.01924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_539_0_line_49 |  | 41 | 51 | 0.27044 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
50 | MV_539_0_line_50 |  | 41 | 52 | 0.0028239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_539_0_line_51 |  | 43 | 44 | 0.083535 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
52 | MV_539_0_line_52 |  | 43 | 45 | 0.045668 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_539_0_line_53 |  | 45 | 49 | 0.23441 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_539_0_line_54 |  | 46 | 47 | 0.005413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_539_0_line_55 |  | 46 | 48 | 0.046939 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
56 | MV_539_0_line_56 |  | 48 | 59 | 0.050945 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_539_0_line_57 |  | 48 | 60 | 0.034186 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
58 | MV_539_0_line_58 |  | 49 | 59 | 0.028761 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_539_0_line_59 |  | 49 | 80 | 0.042145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_539_0_line_60 |  | 51 | 53 | 0.004989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_539_0_line_61 |  | 51 | 54 | 0.37715 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_539_0_line_62 |  | 51 | 55 | 0.028093 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_539_0_line_63 |  | 53 | 58 | 0.075745 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_539_0_line_64 |  | 54 | 56 | 0.053169 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_539_0_line_65 |  | 55 | 57 | 0.018924 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_539_0_line_66 |  | 58 | 70 | 0.33949 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_539_0_line_67 |  | 58 | 73 | 0.17067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_539_0_line_68 |  | 60 | 78 | 0.015245 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
69 | MV_539_0_line_69 |  | 62 | 63 | 0.005634 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_539_0_line_70 |  | 62 | 64 | 0.1244 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
71 | MV_539_0_line_71 |  | 62 | 65 | 0.17133 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
72 | MV_539_0_line_72 |  | 63 | 77 | 0.024664 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_539_0_line_73 |  | 64 | 79 | 0.027888 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
74 | MV_539_0_line_74 |  | 65 | 84 | 0.024735 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
75 | MV_539_0_line_75 |  | 65 | 82 | 0.17391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_539_0_line_76 |  | 66 | 67 | 0.003964 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_539_0_line_77 |  | 67 | 68 | 0.19316 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_539_0_line_78 |  | 68 | 69 | 0.002352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_539_0_line_79 |  | 68 | 70 | 0.098733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_539_0_line_80 |  | 68 | 71 | 0.094313 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
81 | MV_539_0_line_81 |  | 70 | 72 | 0.004877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_539_0_line_82 |  | 72 | 75 | 0.0463 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_539_0_line_83 |  | 73 | 74 | 0.019536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_539_0_line_84 |  | 74 | 76 | 0.036967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_539_0_line_85 |  | 75 | 120 | 0.048766 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_539_0_line_86 |  | 76 | 130 | 0.32061 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_539_0_line_87 |  | 77 | 171 | 0.060908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_539_0_line_88 |  | 78 | 79 | 0.013888 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
89 | MV_539_0_line_89 |  | 80 | 81 | 0.030459 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_539_0_line_90 |  | 82 | 83 | 0.058067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_539_0_line_91 |  | 84 | 95 | 0.16511 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
92 | MV_539_0_line_92 |  | 85 | 86 | 0.089401 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
93 | MV_539_0_line_93 |  | 85 | 87 | 0.069222 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_539_0_line_94 |  | 86 | 88 | 0.11656 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_539_0_line_95 |  | 87 | 89 | 0.15344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_539_0_line_96 |  | 87 | 90 | 0.16841 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
97 | MV_539_0_line_97 |  | 88 | 111 | 0.0085596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_539_0_line_98 |  | 89 | 99 | 0.00712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_539_0_line_99 |  | 89 | 97 | 0.1029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_539_0_line_100 |  | 90 | 101 | 0.1326 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_539_0_line_101 |  | 90 | 105 | 0.034218 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_539_0_line_102 |  | 91 | 96 | 0.03768 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
103 | MV_539_0_line_103 |  | 91 | 93 | 0.4835 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
104 | MV_539_0_line_104 |  | 92 | 93 | 0.041217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_539_0_line_105 |  | 92 | 94 | 0.04617 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_539_0_line_106 |  | 93 | 95 | 0.004845 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
107 | MV_539_0_line_107 |  | 97 | 98 | 0.027011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_539_0_line_108 |  | 98 | 107 | 0.020304 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_539_0_line_109 |  | 98 | 108 | 0.020831 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_539_0_line_110 |  | 99 | 109 | 0.004632 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_539_0_line_111 |  | 100 | 101 | 0.3665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_539_0_line_112 |  | 100 | 102 | 0.007314 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_539_0_line_113 |  | 101 | 106 | 0.025054 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_539_0_line_114 |  | 101 | 103 | 0.14025 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
115 | MV_539_0_line_115 |  | 103 | 104 | 0.003007 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
116 | MV_539_0_line_116 |  | 104 | 110 | 0.032307 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
117 | MV_539_0_line_117 |  | 107 | 160 | 0.017652 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_539_0_line_118 |  | 109 | 112 | 0.050731 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
119 | MV_539_0_line_119 |  | 110 | 153 | 0.03125 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
120 | MV_539_0_line_120 |  | 111 | 169 | 0.074306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_539_0_line_121 |  | 111 | 168 | 0.056904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_539_0_line_122 |  | 112 | 113 | 0.014097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_539_0_line_123 |  | 114 | 115 | 0.039545 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_539_0_line_124 |  | 115 | 116 | 0.13203 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_539_0_line_125 |  | 116 | 117 | 0.16212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_539_0_line_126 |  | 116 | 118 | 0.049152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_539_0_line_127 |  | 117 | 119 | 0.055475 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
128 | MV_539_0_line_128 |  | 118 | 120 | 0.056065 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_539_0_line_129 |  | 119 | 123 | 0.003732 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_539_0_line_130 |  | 119 | 122 | 0.10923 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_539_0_line_131 |  | 121 | 122 | 0.070037 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
132 | MV_539_0_line_132 |  | 124 | 125 | 0.040543 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
133 | MV_539_0_line_133 |  | 125 | 126 | 0.008036 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
134 | MV_539_0_line_134 |  | 126 | 153 | 0.20098 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
135 | MV_539_0_line_135 |  | 127 | 128 | 0.003083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_539_0_line_136 |  | 128 | 129 | 0.23464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_539_0_line_137 |  | 129 | 130 | 0.44156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_539_0_line_138 |  | 129 | 131 | 0.025422 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
139 | MV_539_0_line_139 |  | 130 | 132 | 0.23437 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_539_0_line_140 |  | 130 | 133 | 0.003936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_539_0_line_141 |  | 132 | 134 | 0.027695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_539_0_line_142 |  | 135 | 136 | 0.004146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_539_0_line_143 |  | 136 | 137 | 0.064094 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_539_0_line_144 |  | 137 | 138 | 0.041825 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_539_0_line_145 |  | 137 | 139 | 0.16053 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_539_0_line_146 |  | 139 | 140 | 0.085965 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
147 | MV_539_0_line_147 |  | 140 | 167 | 0.004595 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_539_0_line_148 |  | 140 | 163 | 0.13772 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_539_0_line_149 |  | 141 | 143 | 0.025627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_539_0_line_150 |  | 142 | 144 | 0.020153 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_539_0_line_151 |  | 144 | 145 | 0.020264 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_539_0_line_152 |  | 145 | 146 | 0.12269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_539_0_line_153 |  | 145 | 147 | 0.61944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_539_0_line_154 |  | 146 | 148 | 0.01337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_539_0_line_155 |  | 147 | 149 | 0.024954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_539_0_line_156 |  | 148 | 150 | 0.024758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_539_0_line_157 |  | 150 | 151 | 0.11397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_539_0_line_158 |  | 151 | 152 | 0.002475 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_539_0_line_159 |  | 153 | 154 | 0.006093 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_539_0_line_160 |  | 156 | 157 | 0.013415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_539_0_line_161 |  | 156 | 158 | 0.017784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_539_0_line_162 |  | 158 | 159 | 0.0074764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_539_0_line_163 |  | 159 | 160 | 0.050521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_539_0_line_164 |  | 159 | 161 | 0.018055 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_539_0_line_165 |  | 162 | 163 | 0.004596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_539_0_line_166 |  | 162 | 164 | 0.08479 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
167 | MV_539_0_line_167 |  | 164 | 165 | 0.10962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_539_0_line_168 |  | 165 | 166 | 0.028848 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_539_0_line_169 |  | 166 | 168 | 0.0085826 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_539_0_line_170 |  | 170 | 171 | 0.01151 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_539_0_trafo_132 | 25 MVA 110/20 kV | 172 | 96 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2683915.4703 | 1245826.3383
1 | 2683920.997 | 1245822.358
2 | 2683896.3679 | 1245871.8348
3 | 2683973.3208 | 1245788.1622
4 | 2683819.3324 | 1245922.4941
5 | 2683951.1159 | 1246013.7357
6 | 2683850.9247 | 1245922.6237
7 | 2683965.2609 | 1245775.7502
8 | 2684179.3199 | 1245742.9375
9 | 2684266.9519 | 1245572.8458
10 | 2684175.4697 | 1245744.8398
11 | 2684245.2828 | 1245778.6177
12 | 2684273.2125 | 1245570.9555
13 | 2683983.02 | 1246021.3818
14 | 2684287.4654 | 1245800.3597
15 | 2684296.87 | 1245537.5004
16 | 2684371.8134 | 1245449.7236
17 | 2684889.3983 | 1245387.1129
18 | 2684896.1914 | 1245360.6257
19 | 2684849.5764 | 1245369.3786
20 | 2684799.4758 | 1245612.0071
21 | 2684664.8805 | 1245274.5147
22 | 2684694.3916 | 1245551.9507
23 | 2684757.0628 | 1245670.2327
24 | 2684661.7986 | 1245279.1964
25 | 2684641.5638 | 1245519.9177
26 | 2684636.3401 | 1245516.385
27 | 2684665.6989 | 1246614.801
28 | 2684724.7183 | 1246641.0743
29 | 2684949.248 | 1246705.0107
30 | 2684824.7683 | 1246537.35
31 | 2684766.1639 | 1246471.4525
32 | 2684621.592 | 1246461.0027
33 | 2684566.9248 | 1246570.0812
34 | 2684823.9216 | 1246527.3638
35 | 2684946.027 | 1246698.8823
36 | 2684534.9302 | 1246555.2698
37 | 2684450.7354 | 1246486.6643
38 | 2684829.3537 | 1246532.6232
39 | 2685003.6344 | 1246669.6527
40 | 2685080.349 | 1246676.1574
41 | 2685058.5318 | 1246576.6266
42 | 2684434.8049 | 1246444.0506
43 | 2684301.631 | 1246280.1803
44 | 2684360.0581 | 1246220.4781
45 | 2684269.5839 | 1246247.6454
46 | 2684594.6691 | 1246357.5869
47 | 2684598.8584 | 1246354.1442
48 | 2684563.0288 | 1246328.4588
49 | 2684502.0496 | 1246277.7524
50 | 2685088.8431 | 1246659.656
51 | 2685232.1145 | 1246497.4933
52 | 2685060.8759 | 1246578.2011
53 | 2685236.453 | 1246499.9797
54 | 2685367.5309 | 1246586.4508
55 | 2685212.6365 | 1246501.8055
56 | 2685373.4709 | 1246639.2865
57 | 2685201.7793 | 1246486.6272
58 | 2685279.1021 | 1246437.3576
59 | 2684523.2754 | 1246296.5993
60 | 2684579.7911 | 1246298.6643
61 | 2684596.2044 | 1246488.7499
62 | 2684739.3351 | 1246260.7027
63 | 2684744.4758 | 1246258.3633
64 | 2684616.6137 | 1246281.0436
65 | 2684616.6086 | 1246141.1516
66 | 2684960.4563 | 1246414.279
67 | 2684962.3046 | 1246410.7695
68 | 2685075.1207 | 1246291.4319
69 | 2685076.8045 | 1246293.0794
70 | 2685124.9527 | 1246227.8888
71 | 2684989.3977 | 1246252.1073
72 | 2685121.443 | 1246224.4915
73 | 2685361.4209 | 1246330.3293
74 | 2685375.0112 | 1246316.2589
75 | 2685118.1601 | 1246180.045
76 | 2685400.7121 | 1246289.6204
77 | 2684763.2078 | 1246242.3192
78 | 2684587.0118 | 1246285.2441
79 | 2684592.8792 | 1246272.656
80 | 2684523.326 | 1246241.5081
81 | 2684539.1389 | 1246215.4758
82 | 2684557.4534 | 1246167.9723
83 | 2684528.3227 | 1246217.9707
84 | 2684627.6232 | 1246118.9925
85 | 2684391.9651 | 1245932.7427
86 | 2684414.7683 | 1246019.1862
87 | 2684417.6176 | 1245868.4493
88 | 2684302.868 | 1245986.5487
89 | 2684304.061 | 1245822.4451
90 | 2684483.8808 | 1245783.0744
91 | 2684714.38 | 1245907.0638
92 | 2684813.5135 | 1246126.9755
93 | 2684796.9464 | 1246132.6651
94 | 2684847.8781 | 1246157.9008
95 | 2684792.2656 | 1246131.3639
96 | 2684699.2707 | 1245932.5479
97 | 2684340.5669 | 1245763.7209
98 | 2684363.5933 | 1245761.8469
99 | 2684298.2848 | 1245822.1739
100 | 2684666.2946 | 1245734.1946
101 | 2684511.0338 | 1245706.9163
102 | 2684670.9898 | 1245728.6909
103 | 2684432.2362 | 1245622.9437
104 | 2684433.9115 | 1245620.4435
105 | 2684514.3787 | 1245798.2608
106 | 2684534.2836 | 1245716.4212
107 | 2684378.5407 | 1245749.027
108 | 2684374.5387 | 1245779.5711
109 | 2684294.299 | 1245819.7933
110 | 2684451.922 | 1245593.5913
111 | 2684297.3427 | 1245993.0861
112 | 2684270.0615 | 1245864.3594
113 | 2684262.6379 | 1245876.343
114 | 2685090.3288 | 1246029.3568
115 | 2685118.3692 | 1246056.0454
116 | 2685118.1842 | 1246118.3887
117 | 2685245.0691 | 1246113.6184
118 | 2685069.2074 | 1246122.8116
119 | 2685300.4569 | 1246110.5012
120 | 2685069.2649 | 1246178.8204
121 | 2685424.0543 | 1246019.8463
122 | 2685372.1584 | 1246066.8783
123 | 2685301.084 | 1246114.1796
124 | 2684594.0556 | 1245465.0664
125 | 2684565.9632 | 1245435.8334
126 | 2684563.0813 | 1245428.6314
127 | 2685656.1771 | 1246516.8052
128 | 2685658.5279 | 1246518.8073
129 | 2685709.3376 | 1246337.2848
130 | 2685571.1384 | 1246180.407
131 | 2685732.939 | 1246346.7329
132 | 2685738.8939 | 1246131.9603
133 | 2685570.908 | 1246176.4785
134 | 2685737.1101 | 1246104.3252
135 | 2684169.541 | 1246124.579
136 | 2684170.9037 | 1246120.6621
137 | 2684120.9238 | 1246089.8972
138 | 2684142.6845 | 1246054.1462
139 | 2684017.8003 | 1246032.9161
140 | 2684070.9812 | 1245965.3755
141 | 2684630.4706 | 1245307.7259
142 | 2684671.3726 | 1245241.6277
143 | 2684612.7785 | 1245289.1854
144 | 2684657.0136 | 1245227.4862
145 | 2684642.2916 | 1245213.8479
146 | 2684562.4525 | 1245236.4482
147 | 2684815.4972 | 1245085.772
148 | 2684553.4566 | 1245246.2493
149 | 2684836.3913 | 1245099.503
150 | 2684535.2774 | 1245263.0915
151 | 2684469.6807 | 1245345.2619
152 | 2684467.2134 | 1245345.5381
153 | 2684461.2883 | 1245568.8843
154 | 2684456.2755 | 1245565.3992
155 | 2684367.3001 | 1245445.6342
156 | 2684332.2673 | 1245715.2489
157 | 2684326.3451 | 1245727.2856
158 | 2684348.2246 | 1245723.0999
159 | 2684352.2808 | 1245716.8196
160 | 2684381.7507 | 1245732.0611
161 | 2684335.9448 | 1245709.131
162 | 2684123.4749 | 1245923.4445
163 | 2684121.9175 | 1245927.77
164 | 2684204.4058 | 1245948.7335
165 | 2684205.7124 | 1245995.5754
166 | 2684234.4363 | 1245992.9047
167 | 2684073.5213 | 1245961.542
168 | 2684242.9801 | 1245992.0908
169 | 2684258.7977 | 1246056.3168
170 | 2684821.9409 | 1246248.7079
171 | 2684811.5929 | 1246253.8081
172 | 2684699.2707 | 1245932.5479

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99332 | -0.055834 | 0.38256 | 0.18528
1 | 0.99332 | -0.055824 | 0 | 0
2 | 0.99337 | -0.055509 | 0 | 0
3 | 0.99331 | -0.055693 | 0 | 0
4 | 0.99346 | -0.056297 | 0 | 0
5 | 0.99371 | -0.058458 | 0 | 0
6 | 0.99346 | -0.056247 | 0.1147 | 0.055552
7 | 0.99331 | -0.055669 | 0.1383 | 0.066982
8 | 0.99621 | -0.047608 | 0 | 0
9 | 0.99602 | -0.045966 | 0 | 0
10 | 0.99621 | -0.047587 | 0.37219 | 0.18026
11 | 0.99636 | -0.046621 | 0.36964 | 0.17903
12 | 0.99602 | -0.045913 | 0.3756 | 0.18191
13 | 0.99374 | -0.058698 | 0.35505 | 0.17196
14 | 0.99644 | -0.047386 | 0 | 0
15 | 0.996 | -0.046059 | 0 | 0
16 | 0.99595 | -0.045642 | 0 | 0
17 | 0.99773 | -0.026032 | 0.31228 | 0.15124
18 | 0.99773 | -0.025988 | 0.13702 | 0.066361
19 | 0.99762 | -0.025022 | 0 | 0
20 | 0.99879 | -0.01881 | 0.31298 | 0.15158
21 | 0.99689 | -0.030054 | 0.32652 | 0.15814
22 | 0.99846 | -0.037321 | 0 | 0
23 | 0.99905 | -0.0042868 | 0 | 0
24 | 0.99688 | -0.029963 | 0 | 0
25 | 0.99838 | -0.037679 | 0.23189 | 0.11231
26 | 0.99837 | -0.037714 | 0 | 0
27 | 0.99668 | -0.11669 | 0.39561 | 0.1916
28 | 0.99672 | -0.117 | 0 | 0
29 | 0.99651 | -0.118 | 0 | 0
30 | 0.99697 | -0.10241 | 0.40073 | 0.19408
31 | 0.99706 | -0.10198 | 0.25129 | 0.12171
32 | 0.99737 | -0.083772 | 0 | 0
33 | 0.99678 | -0.10377 | 0.26043 | 0.12613
34 | 0.99698 | -0.10234 | 0 | 0
35 | 0.99651 | -0.11802 | 0.26205 | 0.12692
36 | 0.99676 | -0.10394 | 0 | 0
37 | 0.99668 | -0.10321 | 0 | 0
38 | 0.99697 | -0.10238 | 0 | 0
39 | 0.99641 | -0.12374 | 0 | 0
40 | 0.99637 | -0.12339 | 0 | 0
41 | 0.99621 | -0.12466 | 0 | 0
42 | 0.99664 | -0.10342 | 0.37298 | 0.18064
43 | 0.99729 | -0.083407 | 0 | 0
44 | 0.99726 | -0.08362 | 0.2094 | 0.10142
45 | 0.99731 | -0.08329 | 0.22187 | 0.10746
46 | 0.99753 | -0.083023 | 0 | 0
47 | 0.99753 | -0.083003 | 0.31263 | 0.15141
48 | 0.99758 | -0.082762 | 0 | 0
49 | 0.99751 | -0.082056 | 0 | 0
50 | 0.99636 | -0.12332 | 0.27425 | 0.13283
51 | 0.99559 | -0.13167 | 0 | 0
52 | 0.99621 | -0.12465 | 0.086996 | 0.042134
53 | 0.99557 | -0.13147 | 0.27453 | 0.13296
54 | 0.99545 | -0.13044 | 0 | 0
55 | 0.99558 | -0.1316 | 0 | 0
56 | 0.99542 | -0.13063 | 0.29517 | 0.14296
57 | 0.99558 | -0.13155 | 0.21972 | 0.10641
58 | 0.99523 | -0.12863 | 0 | 0
59 | 0.99753 | -0.082288 | 0.10726 | 0.051948
60 | 0.99763 | -0.082554 | 0.09334 | 0.045207
61 | 0.99736 | -0.083688 | 0.18945 | 0.091757
62 | 0.99805 | -0.062444 | 0 | 0
63 | 0.99804 | -0.062412 | 0.22727 | 0.11007
64 | 0.9977 | -0.082193 | 0 | 0
65 | 0.99855 | -0.033711 | 0 | 0
66 | 0.99398 | -0.1174 | 0.39481 | 0.19121
67 | 0.99398 | -0.11742 | 0 | 0
68 | 0.99408 | -0.11831 | 0 | 0
69 | 0.99408 | -0.11831 | 0.21234 | 0.10284
70 | 0.99419 | -0.11936 | 0 | 0
71 | 0.99402 | -0.11866 | 0.30348 | 0.14698
72 | 0.99418 | -0.11928 | 0.34766 | 0.16838
73 | 0.995 | -0.1268 | 0 | 0
74 | 0.99498 | -0.12659 | 0.39878 | 0.19314
75 | 0.99412 | -0.11868 | 0 | 0
76 | 0.99495 | -0.12636 | 0 | 0
77 | 0.99803 | -0.062491 | 0 | 0
78 | 0.99765 | -0.08246 | 0.25475 | 0.12338
79 | 0.99766 | -0.082372 | 0.10309 | 0.04993
80 | 0.99749 | -0.081931 | 0.11368 | 0.055059
81 | 0.99749 | -0.081881 | 0.13947 | 0.067548
82 | 0.99851 | -0.033408 | 0 | 0
83 | 0.9985 | -0.033297 | 0.16362 | 0.079244
84 | 0.99859 | -0.033543 | 0.35964 | 0.17418
85 | 0.99656 | -0.055631 | 0.31327 | 0.15172
86 | 0.99604 | -0.059203 | 0.2348 | 0.11372
87 | 0.99701 | -0.052604 | 0 | 0
88 | 0.9954 | -0.063531 | 0.089837 | 0.04351
89 | 0.99651 | -0.048062 | 0 | 0
90 | 0.99756 | -0.046764 | 0 | 0
91 | 0.99988 | -0.00058949 | 0 | 0
92 | 0.99909 | -0.004093 | 0 | 0
93 | 0.99911 | -0.0042091 | 0 | 0
94 | 0.99908 | -0.00396 | 0.24333 | 0.11785
95 | 0.9991 | -0.0042435 | 0.22835 | 0.11059
96 | 1 | 0 | -20.4577 | -9.3996
97 | 0.99642 | -0.047182 | 0 | 0
98 | 0.99639 | -0.046948 | 0 | 0
99 | 0.9965 | -0.047911 | 0.32442 | 0.15712
100 | 0.99751 | -0.044616 | 0 | 0
101 | 0.99769 | -0.046228 | 0 | 0
102 | 0.9975 | -0.044581 | 0.39013 | 0.18895
103 | 0.99784 | -0.045575 | 0 | 0
104 | 0.99785 | -0.045561 | 0.31019 | 0.15023
105 | 0.99755 | -0.046719 | 0.11158 | 0.054042
106 | 0.99768 | -0.04613 | 0.32856 | 0.15913
107 | 0.99638 | -0.046843 | 0.1179 | 0.057101
108 | 0.99638 | -0.047022 | 0.2921 | 0.14147
109 | 0.99649 | -0.047831 | 0 | 0
110 | 0.99788 | -0.045402 | 0 | 0
111 | 0.99537 | -0.063267 | 0 | 0
112 | 0.99648 | -0.047902 | 0 | 0
113 | 0.99647 | -0.047883 | 0.11331 | 0.054879
114 | 0.99384 | -0.11622 | 0.32439 | 0.15711
115 | 0.99386 | -0.11637 | 0 | 0
116 | 0.99391 | -0.11687 | 0 | 0
117 | 0.99381 | -0.11594 | 0 | 0
118 | 0.99396 | -0.11732 | 0.3201 | 0.15503
119 | 0.99376 | -0.11629 | 0 | 0
120 | 0.99405 | -0.11805 | 0 | 0
121 | 0.9937 | -0.11621 | 0.21372 | 0.10351
122 | 0.99373 | -0.11602 | 0 | 0
123 | 0.99376 | -0.11628 | 0.28287 | 0.137
124 | 0.99828 | -0.038124 | 0 | 0
125 | 0.99817 | -0.044145 | 0.35617 | 0.1725
126 | 0.99816 | -0.044188 | 0 | 0
127 | 0.99451 | -0.1231 | 0.093909 | 0.045482
128 | 0.99451 | -0.1231 | 0 | 0
129 | 0.99454 | -0.12332 | 0 | 0
130 | 0.99468 | -0.12432 | 0 | 0
131 | 0.99453 | -0.12337 | 0.15099 | 0.073129
132 | 0.99464 | -0.12403 | 0 | 0
133 | 0.99467 | -0.12431 | 0.29807 | 0.14436
134 | 0.99463 | -0.12399 | 0.12256 | 0.05936
135 | 0.99365 | -0.05786 | 0.28089 | 0.13604
136 | 0.99365 | -0.057875 | 0 | 0
137 | 0.99367 | -0.058089 | 0 | 0
138 | 0.99366 | -0.057957 | 0.26361 | 0.12767
139 | 0.99378 | -0.059102 | 0 | 0
140 | 0.99404 | -0.057325 | 0 | 0
141 | 0.99687 | -0.02988 | 0 | 0
142 | 0.9968 | -0.029267 | 0 | 0
143 | 0.99687 | -0.029836 | 0.14362 | 0.069556
144 | 0.99677 | -0.028971 | 0.29723 | 0.14395
145 | 0.99674 | -0.028746 | 0 | 0
146 | 0.99663 | -0.027733 | 0 | 0
147 | 0.99648 | -0.026598 | 0 | 0
148 | 0.99662 | -0.027621 | 0.37645 | 0.18232
149 | 0.99647 | -0.026499 | 0.33015 | 0.1599
150 | 0.99661 | -0.027525 | 0 | 0
151 | 0.99656 | -0.027074 | 0 | 0
152 | 0.99656 | -0.027064 | 0.33643 | 0.16294
153 | 0.99792 | -0.045248 | 0 | 0
154 | 0.99792 | -0.045221 | 0.37403 | 0.18115
155 | 0.99595 | -0.045622 | 0.26944 | 0.1305
156 | 0.99634 | -0.046511 | 0.16656 | 0.080671
157 | 0.99634 | -0.0465 | 0.072284 | 0.035009
158 | 0.99635 | -0.046562 | 0 | 0
159 | 0.99635 | -0.046583 | 0 | 0
160 | 0.99637 | -0.046776 | 0 | 0
161 | 0.99635 | -0.046564 | 0.089589 | 0.04339
162 | 0.99439 | -0.060393 | 0.37927 | 0.18369
163 | 0.99437 | -0.060295 | 0 | 0
164 | 0.99476 | -0.057839 | 0 | 0
165 | 0.99508 | -0.060681 | 0 | 0
166 | 0.99516 | -0.061426 | 0.19632 | 0.095081
167 | 0.99404 | -0.057305 | 0.37102 | 0.1797
168 | 0.99519 | -0.061668 | 0 | 0
169 | 0.99535 | -0.063054 | 0.24155 | 0.11699
170 | 0.99801 | -0.062275 | 0.25298 | 0.12253
171 | 0.99801 | -0.06231 | 0 | 0
172 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.1383 | 0.064541 | -0.1383 | -0.064701 | 1.7862e-07 | -0.0001601 | 0.0044354 | 0.0044374 | 0.0044374 | 0.99332 | -0.055834 | 0.99332 | -0.055824 | 2.017
1 | -0.52086 | -0.24982 | 0.52089 | 0.24978 | 2.4777e-05 | -4.2606e-05 | 0.016788 | 0.016787 | 0.016788 | 0.99332 | -0.055834 | 0.99337 | -0.055509 | 7.9943
2 | 0.1383 | 0.064701 | -0.1383 | -0.066633 | 2.1684e-06 | -0.0019322 | 0.0044374 | 0.0044615 | 0.0044615 | 0.99332 | -0.055824 | 0.99331 | -0.055693 | 2.0279
3 | -0.52089 | -0.24978 | 0.52093 | 0.24673 | 4.8835e-05 | -0.0030511 | 0.016787 | 0.016749 | 0.016787 | 0.99337 | -0.055509 | 0.99346 | -0.056297 | 7.6306
4 | 0.1383 | 0.066633 | -0.1383 | -0.066982 | 3.9364e-07 | -0.00034852 | 0.0044615 | 0.0044659 | 0.0044659 | 0.99331 | -0.055693 | 0.99331 | -0.055669 | 2.0299
5 | -0.63564 | -0.30143 | 0.63581 | 0.29426 | 0.00017011 | -0.0071691 | 0.020442 | 0.020353 | 0.020442 | 0.99346 | -0.056297 | 0.99371 | -0.058458 | 9.2916
6 | 0.1147 | 0.0547 | -0.1147 | -0.055552 | 6.6003e-07 | -0.00085182 | 0.0036925 | 0.0037032 | 0.0037032 | 0.99346 | -0.056297 | 0.99346 | -0.056247 | 1.6833
7 | -0.63581 | -0.29426 | 0.63582 | 0.29343 | 1.9574e-05 | -0.00082918 | 0.020353 | 0.020342 | 0.020353 | 0.99371 | -0.058458 | 0.99374 | -0.058698 | 9.2512
8 | 0.64519 | 0.30368 | -0.64506 | -0.30891 | 0.00012716 | -0.0052307 | 0.020663 | 0.020729 | 0.020729 | 0.99621 | -0.047608 | 0.99602 | -0.045966 | 9.4222
9 | 0.37219 | 0.18015 | -0.37219 | -0.18026 | 8.7505e-07 | -0.00010791 | 0.011982 | 0.011983 | 0.011983 | 0.99621 | -0.047608 | 0.99621 | -0.047587 | 5.447
10 | -1.0174 | -0.48383 | 1.0175 | 0.48383 | 0.00014239 | 3.2512e-07 | 0.032645 | 0.032644 | 0.032645 | 0.99621 | -0.047608 | 0.99636 | -0.046621 | 15.5453
11 | 0.64506 | 0.30891 | -0.64506 | -0.30907 | 4.037e-06 | -0.00016548 | 0.020729 | 0.020731 | 0.020731 | 0.99602 | -0.045966 | 0.99602 | -0.045913 | 9.4232
12 | -1.3872 | -0.66286 | 1.3873 | 0.66177 | 0.00012567 | -0.0010877 | 0.044543 | 0.044529 | 0.044543 | 0.99636 | -0.046621 | 0.99644 | -0.047386 | 20.247
13 | 0.26946 | 0.12716 | -0.26945 | -0.12721 | 5.4447e-06 | -4.5116e-05 | 0.0086357 | 0.0086363 | 0.0086363 | 0.99602 | -0.045913 | 0.996 | -0.046059 | 4.1125
14 | -0.99088 | -0.46539 | 0.99093 | 0.46454 | 4.9322e-05 | -0.00084704 | 0.031801 | 0.031791 | 0.031801 | 0.99374 | -0.058698 | 0.99378 | -0.059102 | 14.4551
15 | -1.3873 | -0.66177 | 1.3874 | 0.66113 | 7.3378e-05 | -0.00063553 | 0.044529 | 0.044521 | 0.044529 | 0.99644 | -0.047386 | 0.99649 | -0.047831 | 20.2406
16 | 0.26945 | 0.12721 | -0.26944 | -0.13035 | 1.33e-05 | -0.0031452 | 0.0086363 | 0.0086756 | 0.0086756 | 0.996 | -0.046059 | 0.99595 | -0.045642 | 3.9435
17 | 0.26944 | 0.13035 | -0.26944 | -0.1305 | 6.1115e-07 | -0.00014384 | 0.0086756 | 0.0086774 | 0.0086774 | 0.99595 | -0.045642 | 0.99595 | -0.045622 | 3.9443
18 | 0.13702 | 0.065712 | -0.13702 | -0.066361 | 7.0699e-07 | -0.00064971 | 0.0043967 | 0.0044049 | 0.0044049 | 0.99773 | -0.026032 | 0.99773 | -0.025988 | 2.0022
19 | 1.8123 | 0.85047 | -1.8121 | -0.8516 | 0.00022538 | -0.0011287 | 0.057922 | 0.057937 | 0.057937 | 0.99773 | -0.026032 | 0.99762 | -0.025022 | 26.3348
20 | -2.2616 | -1.0674 | 2.2638 | 1.0685 | 0.0022592 | 0.001127 | 0.072357 | 0.072353 | 0.072357 | 0.99773 | -0.026032 | 0.99879 | -0.01881 | 34.4557
21 | 1.8121 | 0.8516 | -1.8108 | -0.85107 | 0.0012418 | 0.00053133 | 0.057937 | 0.05794 | 0.05794 | 0.99762 | -0.025022 | 0.99689 | -0.030054 | 27.5903
22 | 8.0479 | 3.746 | -8.0464 | -3.7425 | 0.0014222 | 0.0034907 | 0.25657 | 0.25657 | 0.25657 | 0.99879 | -0.01881 | 0.99846 | -0.037321 | 19.8892
23 | -10.6247 | -4.9661 | 10.6262 | 4.9699 | 0.0014774 | 0.0037741 | 0.33897 | 0.33897 | 0.33897 | 0.99879 | -0.01881 | 0.99905 | -0.0042868 | 26.2767
24 | 1.4843 | 0.69292 | -1.4843 | -0.69305 | 1.6825e-05 | -0.00012791 | 0.047435 | 0.047436 | 0.047436 | 0.99689 | -0.030054 | 0.99688 | -0.029963 | 21.562
25 | 8.0464 | 3.7425 | -8.0458 | -3.7499 | 0.00062722 | -0.0073693 | 0.25657 | 0.25666 | 0.25666 | 0.99846 | -0.037321 | 0.99838 | -0.037679 | 20.1148
26 | -10.6262 | -4.9699 | 10.6347 | 4.9145 | 0.0084959 | -0.055423 | 0.33897 | 0.33823 | 0.33897 | 0.99905 | -0.0042868 | 0.99988 | -0.00058949 | 26.5648
27 | 0.14362 | 0.067756 | -0.14362 | -0.068948 | 1.424e-06 | -0.0011926 | 0.0045984 | 0.0046133 | 0.0046133 | 0.99688 | -0.029963 | 0.99687 | -0.02988 | 2.097
28 | 1.3407 | 0.6253 | -1.3406 | -0.62639 | 0.00011652 | -0.0010935 | 0.042838 | 0.042852 | 0.042852 | 0.99688 | -0.029963 | 0.9968 | -0.029267 | 19.4781
29 | 7.8139 | 3.6375 | -7.8139 | -3.6383 | 6.0388e-05 | -0.00075423 | 0.24922 | 0.24923 | 0.24923 | 0.99838 | -0.037679 | 0.99837 | -0.037714 | 19.5318
30 | 7.8139 | 3.6383 | -7.8132 | -3.6471 | 0.00070281 | -0.0087725 | 0.24923 | 0.24934 | 0.24934 | 0.99837 | -0.037714 | 0.99828 | -0.038124 | 19.5405
31 | -0.39561 | -0.1916 | 0.39562 | 0.19008 | 1.3924e-05 | -0.0015244 | 0.012731 | 0.012712 | 0.012731 | 0.99668 | -0.11669 | 0.99672 | -0.117 | 5.787
32 | 4.8861 | 2.2092 | -4.8852 | -2.2405 | 0.00095413 | -0.031341 | 0.15531 | 0.15569 | 0.15569 | 0.99672 | -0.117 | 0.99651 | -0.118 | 12.2015
33 | -5.2818 | -2.3993 | 5.2825 | 2.4008 | 0.00072617 | 0.0015568 | 0.16802 | 0.16801 | 0.16802 | 0.99672 | -0.117 | 0.99697 | -0.10241 | 13.0246
34 | 4.8852 | 2.2405 | -4.8852 | -2.2414 | 2.5914e-05 | -0.00084882 | 0.15569 | 0.1557 | 0.1557 | 0.99651 | -0.118 | 0.99651 | -0.11802 | 12.2023
35 | -5.6832 | -2.5949 | 5.6833 | 2.5941 | 3.3252e-05 | -0.00080277 | 0.1809 | 0.18089 | 0.1809 | 0.99697 | -0.10241 | 0.99697 | -0.10238 | 14.1772
36 | -6.5686 | -3.0076 | 6.5697 | 3.0103 | 0.001132 | 0.0026454 | 0.20917 | 0.20916 | 0.20917 | 0.99706 | -0.10198 | 0.99737 | -0.083772 | 16.2145
37 | 0.63362 | 0.30255 | -0.63345 | -0.30271 | 0.00016372 | -0.00016122 | 0.020329 | 0.020332 | 0.020332 | 0.99706 | -0.10198 | 0.99678 | -0.10377 | 9.6821
38 | 5.6837 | 2.5834 | -5.6833 | -2.5932 | 0.00040546 | -0.009798 | 0.18076 | 0.18088 | 0.18088 | 0.99706 | -0.10198 | 0.99698 | -0.10234 | 14.1756
39 | 0.18946 | 0.090865 | -0.18945 | -0.091757 | 1.8581e-06 | -0.00089157 | 0.0060816 | 0.0060928 | 0.0060928 | 0.99737 | -0.083772 | 0.99736 | -0.083688 | 2.7695
40 | -6.7592 | -3.1012 | 6.7602 | 3.084 | 0.0010118 | -0.01712 | 0.21524 | 0.21503 | 0.21524 | 0.99737 | -0.083772 | 0.99753 | -0.083023 | 16.8686
41 | 0.37303 | 0.17658 | -0.37302 | -0.17662 | 8.9744e-06 | -3.6197e-05 | 0.011952 | 0.011953 | 0.011953 | 0.99678 | -0.10377 | 0.99676 | -0.10394 | 5.6919
42 | 5.6833 | 2.5932 | -5.6833 | -2.5941 | 3.8167e-05 | -0.00092154 | 0.18088 | 0.18089 | 0.18089 | 0.99698 | -0.10234 | 0.99697 | -0.10238 | 14.1765
43 | 4.6231 | 2.1145 | -4.6229 | -2.114 | 0.00025009 | 0.00049517 | 0.14727 | 0.14727 | 0.14727 | 0.99651 | -0.11802 | 0.99641 | -0.12374 | 11.4163
44 | 0.37302 | 0.17662 | -0.37299 | -0.18059 | 3.2177e-05 | -0.0039754 | 0.011953 | 0.012003 | 0.012003 | 0.99676 | -0.10394 | 0.99668 | -0.10321 | 5.4558
45 | 0.37299 | 0.18059 | -0.37298 | -0.18064 | 1.1678e-05 | -4.6634e-05 | 0.012003 | 0.012003 | 0.012003 | 0.99668 | -0.10321 | 0.99664 | -0.10342 | 5.7159
46 | 0.27426 | 0.12974 | -0.27425 | -0.13237 | 1.1516e-05 | -0.0026333 | 0.00879 | 0.008823 | 0.008823 | 0.99641 | -0.12374 | 0.99637 | -0.12339 | 4.0104
47 | 4.3486 | 1.9842 | -4.3478 | -2.0181 | 0.00081722 | -0.033843 | 0.13848 | 0.1389 | 0.1389 | 0.99641 | -0.12374 | 0.99621 | -0.12466 | 10.8853
48 | 0.27425 | 0.13237 | -0.27425 | -0.13283 | 2.0008e-06 | -0.00045545 | 0.008823 | 0.0088287 | 0.0088287 | 0.99637 | -0.12339 | 0.99636 | -0.12332 | 4.013
49 | 4.2608 | 1.976 | -4.2584 | -1.9835 | 0.0024215 | -0.0074424 | 0.1361 | 0.13621 | 0.13621 | 0.99621 | -0.12466 | 0.99559 | -0.13167 | 37.627
50 | 0.086996 | 0.042067 | -0.086996 | -0.042134 | 2.9595e-08 | -6.6905e-05 | 0.0028002 | 0.002801 | 0.002801 | 0.99621 | -0.12466 | 0.99621 | -0.12465 | 1.2732
51 | 0.20941 | 0.10132 | -0.2094 | -0.10142 | 6.7498e-06 | -9.4954e-05 | 0.0067337 | 0.0067349 | 0.0067349 | 0.99729 | -0.083407 | 0.99726 | -0.08362 | 3.2071
52 | -0.20941 | -0.10132 | 0.20941 | 0.10127 | 3.689e-06 | -5.1914e-05 | 0.0067337 | 0.006733 | 0.0067337 | 0.99729 | -0.083407 | 0.99731 | -0.08329 | 3.2065
53 | -0.43128 | -0.20873 | 0.43136 | 0.2085 | 8.031e-05 | -0.00022808 | 0.013869 | 0.013865 | 0.013869 | 0.99731 | -0.08329 | 0.99751 | -0.082056 | 6.6042
54 | 0.31263 | 0.15129 | -0.31263 | -0.15141 | 7.3013e-07 | -0.00012839 | 0.010051 | 0.010053 | 0.010053 | 0.99753 | -0.083023 | 0.99753 | -0.083003 | 4.5693
55 | -7.0728 | -3.2353 | 7.0732 | 3.2297 | 0.00036728 | -0.0056629 | 0.22508 | 0.22501 | 0.22508 | 0.99753 | -0.083023 | 0.99758 | -0.082762 | 17.6394
56 | 0.79184 | 0.37946 | -0.7918 | -0.38065 | 4.3935e-05 | -0.0011974 | 0.025409 | 0.025424 | 0.025424 | 0.99758 | -0.082762 | 0.99753 | -0.082288 | 11.5564
57 | -7.8651 | -3.6091 | 7.8654 | 3.605 | 0.00033113 | -0.0040889 | 0.25041 | 0.25036 | 0.25041 | 0.99758 | -0.082762 | 0.99763 | -0.082554 | 19.6249
58 | -0.68452 | -0.32938 | 0.68454 | 0.3287 | 1.8549e-05 | -0.00067779 | 0.021984 | 0.021975 | 0.021984 | 0.99751 | -0.082056 | 0.99753 | -0.082288 | 9.9927
59 | 0.25316 | 0.12088 | -0.25315 | -0.12188 | 3.7142e-06 | -0.0010001 | 0.0081187 | 0.0081312 | 0.0081312 | 0.99751 | -0.082056 | 0.99749 | -0.081931 | 3.696
60 | 3.7434 | 1.7442 | -3.7433 | -1.7442 | 9.5503e-05 | -8.9738e-05 | 0.11975 | 0.11975 | 0.11975 | 0.99559 | -0.13167 | 0.99557 | -0.13147 | 54.4303
61 | 0.29523 | 0.13399 | -0.29518 | -0.1429 | 4.5009e-05 | -0.0089111 | 0.0094005 | 0.0095104 | 0.0095104 | 0.99559 | -0.13167 | 0.99545 | -0.13044 | 4.3229
62 | 0.21972 | 0.1053 | -0.21972 | -0.10597 | 1.8741e-06 | -0.00066429 | 0.0070648 | 0.0070731 | 0.0070731 | 0.99559 | -0.13167 | 0.99558 | -0.1316 | 3.215
63 | 3.4688 | 1.6113 | -3.4676 | -1.6127 | 0.001244 | -0.0014229 | 0.1109 | 0.11092 | 0.11092 | 0.99557 | -0.13147 | 0.99523 | -0.12863 | 50.4204
64 | 0.29518 | 0.1429 | -0.29517 | -0.14296 | 8.5689e-06 | -5.7527e-05 | 0.0095104 | 0.0095112 | 0.0095112 | 0.99545 | -0.13044 | 0.99542 | -0.13063 | 4.5291
65 | 0.21972 | 0.10597 | -0.21972 | -0.10641 | 1.2649e-06 | -0.00044747 | 0.0070731 | 0.0070788 | 0.0070788 | 0.99558 | -0.1316 | 0.99558 | -0.13155 | 3.2176
66 | 2.4027 | 1.1324 | -2.4 | -1.1396 | 0.0026937 | -0.0072211 | 0.077044 | 0.077144 | 0.077144 | 0.99523 | -0.12863 | 0.99419 | -0.11936 | 35.0653
67 | 1.0649 | 0.48033 | -1.0646 | -0.48429 | 0.00026198 | -0.0039576 | 0.033884 | 0.033932 | 0.033932 | 0.99523 | -0.12863 | 0.995 | -0.1268 | 15.4238
68 | -7.9587 | -3.6502 | 7.9589 | 3.6484 | 0.00015118 | -0.0018215 | 0.25336 | 0.25334 | 0.25336 | 0.99763 | -0.082554 | 0.99765 | -0.08246 | 19.856
69 | 0.48027 | 0.23072 | -0.48027 | -0.23085 | 1.7866e-06 | -0.00013346 | 0.015411 | 0.015413 | 0.015413 | 0.99805 | -0.062444 | 0.99804 | -0.062412 | 7.0058
70 | 8.3187 | 3.8206 | -8.3172 | -3.8167 | 0.0015567 | 0.0038436 | 0.26477 | 0.26478 | 0.26478 | 0.99805 | -0.062444 | 0.9977 | -0.082193 | 20.5255
71 | -8.799 | -4.0513 | 8.8014 | 4.0573 | 0.0024008 | 0.0059838 | 0.28018 | 0.28018 | 0.28018 | 0.99805 | -0.062444 | 0.99855 | -0.033711 | 21.7196
72 | 0.25299 | 0.12078 | -0.25299 | -0.12081 | 2.8895e-06 | -2.7518e-05 | 0.0081087 | 0.0081091 | 0.0081091 | 0.99804 | -0.062412 | 0.99803 | -0.062491 | 3.8615
73 | 8.3172 | 3.8167 | -8.3169 | -3.8201 | 0.00030212 | -0.0033182 | 0.26478 | 0.26482 | 0.26482 | 0.9977 | -0.082193 | 0.99766 | -0.082372 | 20.754
74 | -8.965 | -4.131 | 8.9653 | 4.1281 | 0.00031116 | -0.0029242 | 0.28537 | 0.28533 | 0.28537 | 0.99855 | -0.033711 | 0.99859 | -0.033543 | 22.3641
75 | 0.16363 | 0.073724 | -0.16362 | -0.077862 | 6.3096e-06 | -0.0041381 | 0.0051883 | 0.0052386 | 0.0052386 | 0.99855 | -0.033711 | 0.99851 | -0.033408 | 2.3812
76 | -0.39481 | -0.19121 | 0.39481 | 0.19112 | 8.5887e-07 | -9.3254e-05 | 0.01274 | 0.012739 | 0.01274 | 0.99398 | -0.1174 | 0.99398 | -0.11742 | 5.791
77 | -0.39481 | -0.19112 | 0.39485 | 0.18658 | 4.1658e-05 | -0.0045446 | 0.012739 | 0.012682 | 0.012739 | 0.99398 | -0.11742 | 0.99408 | -0.11831 | 5.7904
78 | 0.21234 | 0.10279 | -0.21234 | -0.10284 | 1.4736e-07 | -5.545e-05 | 0.0068507 | 0.0068514 | 0.0068514 | 0.99408 | -0.11831 | 0.99408 | -0.11831 | 3.1143
79 | -0.91069 | -0.43624 | 0.9108 | 0.43395 | 0.00011323 | -0.0022962 | 0.029324 | 0.029294 | 0.029324 | 0.99408 | -0.11831 | 0.99419 | -0.11936 | 13.3289
80 | 0.3035 | 0.14688 | -0.30348 | -0.14698 | 1.6112e-05 | -0.00010116 | 0.0097914 | 0.0097928 | 0.0097928 | 0.99408 | -0.11831 | 0.99402 | -0.11866 | 4.6632
81 | 1.4892 | 0.70565 | -1.4892 | -0.70576 | 1.4907e-05 | -0.00011067 | 0.047849 | 0.047851 | 0.047851 | 0.99419 | -0.11936 | 0.99418 | -0.11928 | 21.7503
82 | 1.1415 | 0.53738 | -1.1414 | -0.53845 | 8.2986e-05 | -0.001068 | 0.036635 | 0.036648 | 0.036648 | 0.99418 | -0.11928 | 0.99412 | -0.11868 | 16.6582
83 | 1.0646 | 0.48429 | -1.0646 | -0.48474 | 3.0034e-05 | -0.00045287 | 0.033932 | 0.033938 | 0.033938 | 0.995 | -0.1268 | 0.99498 | -0.12659 | 15.4264
84 | 0.6658 | 0.29161 | -0.66577 | -0.29247 | 2.1958e-05 | -0.00086724 | 0.021088 | 0.021099 | 0.021099 | 0.99498 | -0.12659 | 0.99495 | -0.12636 | 9.5903
85 | 1.1414 | 0.53845 | -1.1413 | -0.53957 | 8.7472e-05 | -0.0011247 | 0.036648 | 0.036662 | 0.036662 | 0.99412 | -0.11868 | 0.99405 | -0.11805 | 16.6647
86 | 0.66577 | 0.29247 | -0.66558 | -0.29999 | 0.00019134 | -0.007519 | 0.021099 | 0.021188 | 0.021188 | 0.99495 | -0.12636 | 0.99468 | -0.12432 | 9.6309
87 | 0.25299 | 0.12081 | -0.25298 | -0.12225 | 5.3588e-06 | -0.0014469 | 0.0081091 | 0.0081272 | 0.0081272 | 0.99803 | -0.062491 | 0.99801 | -0.06231 | 3.6942
88 | -8.2136 | -3.7718 | 8.2138 | 3.7701 | 0.00014675 | -0.0016545 | 0.26153 | 0.26151 | 0.26153 | 0.99765 | -0.08246 | 0.99766 | -0.082372 | 20.4959
89 | 0.13947 | 0.066825 | -0.13947 | -0.067548 | 8.1619e-07 | -0.00072334 | 0.0044757 | 0.0044848 | 0.0044848 | 0.99749 | -0.081931 | 0.99749 | -0.081881 | 2.0385
90 | 0.16362 | 0.077862 | -0.16362 | -0.079244 | 2.1344e-06 | -0.0013816 | 0.0052386 | 0.0052559 | 0.0052559 | 0.99851 | -0.033408 | 0.9985 | -0.033297 | 2.3891
91 | -9.325 | -4.3023 | 9.3276 | 4.3088 | 0.0025975 | 0.0065294 | 0.29688 | 0.29687 | 0.29688 | 0.99859 | -0.033543 | 0.9991 | -0.0042435 | 23.0138
92 | 3.0551 | 1.4474 | -3.0535 | -1.4465 | 0.0015275 | 0.00085082 | 0.097925 | 0.097927 | 0.097927 | 0.99656 | -0.055631 | 0.99604 | -0.059203 | 46.6317
93 | -3.3683 | -1.5991 | 3.3698 | 1.5999 | 0.0014388 | 0.00081908 | 0.10801 | 0.10801 | 0.10801 | 0.99656 | -0.055631 | 0.99701 | -0.052604 | 51.4323
94 | 2.8187 | 1.3328 | -2.817 | -1.3319 | 0.0016959 | 0.00092432 | 0.090366 | 0.090367 | 0.090367 | 0.99604 | -0.059203 | 0.9954 | -0.063531 | 43.0321
95 | 2.5651 | 1.2204 | -2.5637 | -1.2236 | 0.0013864 | -0.0032285 | 0.082247 | 0.082292 | 0.082292 | 0.99701 | -0.052604 | 0.99651 | -0.048062 | 37.4054
96 | -5.9349 | -2.8203 | 5.9378 | 2.8167 | 0.0029432 | -0.0036073 | 0.19025 | 0.19018 | 0.19025 | 0.99701 | -0.052604 | 0.99756 | -0.046764 | 52.5562
97 | 2.7272 | 1.2883 | -2.7271 | -1.2885 | 8.7437e-05 | -0.00017655 | 0.087473 | 0.087475 | 0.087475 | 0.9954 | -0.063531 | 0.99537 | -0.063267 | 39.7615
98 | 1.8251 | 0.87248 | -1.8251 | -0.87264 | 3.2644e-05 | -0.00015913 | 0.058602 | 0.058604 | 0.058604 | 0.99651 | -0.048062 | 0.9965 | -0.047911 | 26.6383
99 | 0.73855 | 0.35113 | -0.73848 | -0.35355 | 7.7192e-05 | -0.0024166 | 0.02369 | 0.02372 | 0.02372 | 0.99651 | -0.048062 | 0.99642 | -0.047182 | 10.7819
100 | -6.0494 | -2.8699 | 6.0502 | 2.8537 | 0.00076829 | -0.016151 | 0.19376 | 0.19355 | 0.19376 | 0.99756 | -0.046764 | 0.99769 | -0.046228 | 15.1849
101 | 0.11158 | 0.053229 | -0.11158 | -0.054042 | 5.8634e-07 | -0.00081282 | 0.0035776 | 0.0035878 | 0.0035878 | 0.99756 | -0.046764 | 0.99755 | -0.046719 | 1.6308
102 | -20.4412 | -9.3924 | 20.4437 | 9.3891 | 0.0024554 | -0.0033517 | 0.64948 | 0.64942 | 0.64948 | 0.99988 | -0.00058949 | 1 | 0 | 50.8997
103 | 9.8066 | 4.478 | -9.7993 | -4.5346 | 0.0072536 | -0.056612 | 0.31125 | 0.31198 | 0.31198 | 0.99988 | -0.00058949 | 0.99911 | -0.0042091 | 24.4498
104 | -0.24333 | -0.11675 | 0.24334 | 0.11577 | 3.3409e-06 | -0.00098135 | 0.0077982 | 0.0077859 | 0.0077982 | 0.99909 | -0.004093 | 0.99911 | -0.0042091 | 3.5446
105 | 0.24333 | 0.11675 | -0.24333 | -0.11785 | 3.7548e-06 | -0.0010992 | 0.0077982 | 0.007812 | 0.007812 | 0.99909 | -0.004093 | 0.99908 | -0.00396 | 3.5509
106 | 9.556 | 4.4188 | -9.5559 | -4.4194 | 6.9269e-05 | -0.00056874 | 0.30419 | 0.3042 | 0.3042 | 0.99911 | -0.0042091 | 0.9991 | -0.0042435 | 23.8403
107 | 0.73848 | 0.35355 | -0.73846 | -0.35418 | 2.0295e-05 | -0.00063426 | 0.02372 | 0.023728 | 0.023728 | 0.99642 | -0.047182 | 0.99639 | -0.046948 | 10.7855
108 | 0.44635 | 0.21273 | -0.44635 | -0.21321 | 5.5649e-06 | -0.00047963 | 0.014325 | 0.014331 | 0.014331 | 0.99639 | -0.046948 | 0.99638 | -0.046843 | 6.5143
109 | 0.2921 | 0.14145 | -0.2921 | -0.14147 | 3.2816e-06 | -2.2634e-05 | 0.0094028 | 0.0094031 | 0.0094031 | 0.99639 | -0.046948 | 0.99638 | -0.047022 | 4.4777
110 | 1.5007 | 0.71551 | -1.5007 | -0.71562 | 1.4344e-05 | -0.00010556 | 0.048162 | 0.048164 | 0.048164 | 0.9965 | -0.047911 | 0.99649 | -0.047831 | 21.8925
111 | -0.39013 | -0.18878 | 0.39021 | 0.18009 | 7.6305e-05 | -0.008686 | 0.012543 | 0.012435 | 0.012543 | 0.99751 | -0.044616 | 0.99769 | -0.046228 | 5.7012
112 | 0.39013 | 0.18878 | -0.39013 | -0.18895 | 1.5363e-06 | -0.0001733 | 0.012543 | 0.012545 | 0.012545 | 0.99751 | -0.044616 | 0.9975 | -0.044581 | 5.7022
113 | 0.32857 | 0.15854 | -0.32856 | -0.15913 | 3.7294e-06 | -0.00059432 | 0.010556 | 0.010563 | 0.010563 | 0.99769 | -0.046228 | 0.99768 | -0.04613 | 4.8014
114 | -6.7689 | -3.1924 | 6.77 | 3.1754 | 0.0010151 | -0.016975 | 0.21654 | 0.21633 | 0.21654 | 0.99769 | -0.046228 | 0.99784 | -0.045575 | 16.9705
115 | -6.77 | -3.1754 | 6.77 | 3.175 | 2.1741e-05 | -0.000364 | 0.21633 | 0.21632 | 0.21633 | 0.99784 | -0.045575 | 0.99785 | -0.045561 | 16.9536
116 | -7.0802 | -3.3253 | 7.0804 | 3.3214 | 0.00025555 | -0.0038986 | 0.22629 | 0.22624 | 0.22629 | 0.99785 | -0.045561 | 0.99788 | -0.045402 | 17.7346
117 | 0.32845 | 0.15611 | -0.32845 | -0.15653 | 2.6173e-06 | -0.00041763 | 0.010536 | 0.010541 | 0.010541 | 0.99638 | -0.046843 | 0.99637 | -0.046776 | 4.7916
118 | 0.11331 | 0.054486 | -0.11331 | -0.054545 | 1.1994e-06 | -5.9386e-05 | 0.0036424 | 0.0036431 | 0.0036431 | 0.99649 | -0.047831 | 0.99648 | -0.047902 | 1.7348
119 | -7.0804 | -3.3214 | 7.0807 | 3.3176 | 0.00024708 | -0.0037714 | 0.22624 | 0.2262 | 0.22624 | 0.99788 | -0.045402 | 0.99792 | -0.045248 | 17.7307
120 | 0.24155 | 0.11523 | -0.24155 | -0.11699 | 5.9932e-06 | -0.0017559 | 0.0077618 | 0.0077839 | 0.0077839 | 0.99537 | -0.063267 | 0.99535 | -0.063054 | 3.5381
121 | 2.4856 | 1.1733 | -2.4851 | -1.1745 | 0.00048281 | -0.0012026 | 0.079714 | 0.07973 | 0.07973 | 0.99537 | -0.063267 | 0.99519 | -0.061668 | 36.241
122 | 0.11331 | 0.054545 | -0.11331 | -0.054879 | 2.5006e-07 | -0.00033413 | 0.0036431 | 0.0036473 | 0.0036473 | 0.99648 | -0.047902 | 0.99647 | -0.047883 | 1.6579
123 | -0.32439 | -0.15711 | 0.3244 | 0.15618 | 5.7799e-06 | -0.00093089 | 0.010469 | 0.010458 | 0.010469 | 0.99384 | -0.11622 | 0.99386 | -0.11637 | 4.7588
124 | -0.3244 | -0.15618 | 0.32442 | 0.15307 | 1.9204e-05 | -0.0031083 | 0.010458 | 0.010419 | 0.010458 | 0.99386 | -0.11637 | 0.99391 | -0.11687 | 4.7534
125 | 0.49668 | 0.23391 | -0.49662 | -0.23772 | 5.5194e-05 | -0.0038071 | 0.015945 | 0.015993 | 0.015993 | 0.99391 | -0.11687 | 0.99381 | -0.11594 | 7.2696
126 | -0.82109 | -0.38698 | 0.82114 | 0.38583 | 4.5584e-05 | -0.0011459 | 0.026364 | 0.02635 | 0.026364 | 0.99391 | -0.11687 | 0.99396 | -0.11732 | 11.9836
127 | 0.49662 | 0.23772 | -0.4966 | -0.23777 | 2.5282e-05 | -4.957e-05 | 0.015993 | 0.015994 | 0.015994 | 0.99381 | -0.11594 | 0.99376 | -0.11629 | 7.6161
128 | -1.1412 | -0.54087 | 1.1413 | 0.53957 | 0.00010065 | -0.0012928 | 0.036679 | 0.036662 | 0.036679 | 0.99396 | -0.11732 | 0.99405 | -0.11805 | 16.6722
129 | 0.28287 | 0.13691 | -0.28287 | -0.137 | 4.1524e-07 | -8.7873e-05 | 0.0091288 | 0.0091299 | 0.0091299 | 0.99376 | -0.11629 | 0.99376 | -0.11628 | 4.15
130 | 0.21373 | 0.10086 | -0.21373 | -0.10343 | 6.9052e-06 | -0.0025735 | 0.0068652 | 0.0068975 | 0.0068975 | 0.99376 | -0.11629 | 0.99373 | -0.11602 | 3.1352
131 | -0.21372 | -0.10351 | 0.21373 | 0.10343 | 5.9376e-06 | -7.8843e-05 | 0.0068985 | 0.0068975 | 0.0068985 | 0.9937 | -0.11621 | 0.99373 | -0.11602 | 3.285
132 | 7.8132 | 3.6471 | -7.8127 | -3.646 | 0.00044992 | 0.0010982 | 0.24934 | 0.24934 | 0.24934 | 0.99828 | -0.038124 | 0.99817 | -0.044145 | 19.3286
133 | 7.4565 | 3.4735 | -7.4565 | -3.4744 | 7.0268e-05 | -0.00096657 | 0.23789 | 0.23791 | 0.23791 | 0.99817 | -0.044145 | 0.99816 | -0.044188 | 18.6447
134 | 7.4565 | 3.4744 | -7.4547 | -3.4986 | 0.0017598 | -0.024167 | 0.23791 | 0.23822 | 0.23822 | 0.99816 | -0.044188 | 0.99792 | -0.045248 | 18.6689
135 | -0.093909 | -0.045482 | 0.093909 | 0.045409 | 3.7742e-08 | -7.2793e-05 | 0.0030288 | 0.0030278 | 0.0030288 | 0.99451 | -0.1231 | 0.99451 | -0.1231 | 1.3767
136 | -0.093909 | -0.045409 | 0.093912 | 0.039869 | 2.8074e-06 | -0.0055403 | 0.0030278 | 0.0029614 | 0.0030278 | 0.99451 | -0.1231 | 0.99454 | -0.12332 | 1.3763
137 | -0.2449 | -0.11297 | 0.24494 | 0.10255 | 3.5555e-05 | -0.010419 | 0.0078284 | 0.0077065 | 0.0078284 | 0.99454 | -0.12332 | 0.99468 | -0.12432 | 3.5584
138 | 0.15099 | 0.073099 | -0.15099 | -0.073129 | 1.074e-06 | -2.9346e-05 | 0.0048693 | 0.0048697 | 0.0048697 | 0.99454 | -0.12332 | 0.99453 | -0.12337 | 2.3189
139 | 0.12257 | 0.053171 | -0.12256 | -0.058706 | 4.7837e-06 | -0.0055348 | 0.0038775 | 0.0039442 | 0.0039442 | 0.99468 | -0.12432 | 0.99464 | -0.12403 | 1.7928
140 | 0.29808 | 0.14427 | -0.29807 | -0.14436 | 4.8542e-07 | -9.2834e-05 | 0.0096108 | 0.0096119 | 0.0096119 | 0.99468 | -0.12432 | 0.99467 | -0.12431 | 4.3691
141 | 0.12256 | 0.058706 | -0.12256 | -0.05936 | 5.7637e-07 | -0.000654 | 0.0039442 | 0.0039524 | 0.0039524 | 0.99464 | -0.12403 | 0.99463 | -0.12399 | 1.7965
142 | -0.28089 | -0.13604 | 0.28089 | 0.13594 | 4.55e-07 | -9.7602e-05 | 0.0090672 | 0.009066 | 0.0090672 | 0.99365 | -0.05786 | 0.99365 | -0.057875 | 4.1215
143 | -0.28089 | -0.13594 | 0.2809 | 0.13444 | 7.018e-06 | -0.0015089 | 0.009066 | 0.0090469 | 0.009066 | 0.99365 | -0.057875 | 0.99367 | -0.058089 | 4.1209
144 | 0.26361 | 0.12669 | -0.26361 | -0.12767 | 4.037e-06 | -0.00098481 | 0.0084967 | 0.0085092 | 0.0085092 | 0.99367 | -0.058089 | 0.99366 | -0.057957 | 3.8678
145 | -0.54451 | -0.26112 | 0.54458 | 0.25736 | 6.5781e-05 | -0.0037654 | 0.017544 | 0.017496 | 0.017544 | 0.99367 | -0.058089 | 0.99378 | -0.059102 | 7.9744
146 | -1.5355 | -0.7219 | 1.5359 | 0.72203 | 0.00037205 | 0.00013166 | 0.049287 | 0.049286 | 0.049287 | 0.99378 | -0.059102 | 0.99404 | -0.057325 | 23.4699
147 | 0.37103 | 0.17959 | -0.37102 | -0.1797 | 8.7911e-07 | -0.00010815 | 0.011971 | 0.011972 | 0.011972 | 0.99404 | -0.057325 | 0.99404 | -0.057305 | 5.4418
148 | -1.9069 | -0.90162 | 1.9076 | 0.89857 | 0.00068941 | -0.0030457 | 0.061256 | 0.061215 | 0.061256 | 0.99404 | -0.057325 | 0.99437 | -0.060295 | 27.8435
149 | 0.14362 | 0.068948 | -0.14362 | -0.069556 | 7.2933e-07 | -0.00060784 | 0.0046133 | 0.0046209 | 0.0046209 | 0.99687 | -0.02988 | 0.99687 | -0.029836 | 2.1004
150 | 1.3406 | 0.62639 | -1.3405 | -0.62685 | 4.9411e-05 | -0.00046344 | 0.042852 | 0.042858 | 0.042858 | 0.9968 | -0.029267 | 0.99677 | -0.028971 | 19.4808
151 | 1.0433 | 0.4829 | -1.0433 | -0.48337 | 2.9993e-05 | -0.00047179 | 0.033294 | 0.0333 | 0.0333 | 0.99677 | -0.028971 | 0.99674 | -0.028746 | 15.1364
152 | 0.713 | 0.33872 | -0.71291 | -0.34161 | 8.5741e-05 | -0.0028845 | 0.022862 | 0.022898 | 0.022898 | 0.99674 | -0.028746 | 0.99663 | -0.027733 | 10.4082
153 | 0.33025 | 0.14465 | -0.33016 | -0.15931 | 9.1677e-05 | -0.014662 | 0.010442 | 0.01062 | 0.01062 | 0.99674 | -0.028746 | 0.99648 | -0.026598 | 4.8272
154 | 0.71291 | 0.34161 | -0.71291 | -0.34192 | 9.3601e-06 | -0.00031429 | 0.022898 | 0.022902 | 0.022902 | 0.99663 | -0.027733 | 0.99662 | -0.027621 | 10.41
155 | 0.33016 | 0.15931 | -0.33015 | -0.1599 | 3.7597e-06 | -0.0005905 | 0.01062 | 0.010627 | 0.010627 | 0.99648 | -0.026598 | 0.99647 | -0.026499 | 4.8306
156 | 0.33645 | 0.1596 | -0.33645 | -0.16018 | 3.8481e-06 | -0.00058598 | 0.010786 | 0.010794 | 0.010794 | 0.99662 | -0.027621 | 0.99661 | -0.027525 | 4.9062
157 | 0.33645 | 0.16018 | -0.33643 | -0.16288 | 1.7782e-05 | -0.0026974 | 0.010794 | 0.010828 | 0.010828 | 0.99661 | -0.027525 | 0.99656 | -0.027074 | 4.9216
158 | 0.33643 | 0.16288 | -0.33643 | -0.16294 | 3.8739e-07 | -5.8572e-05 | 0.010828 | 0.010828 | 0.010828 | 0.99656 | -0.027074 | 0.99656 | -0.027064 | 4.922
159 | 0.37403 | 0.18101 | -0.37403 | -0.18115 | 1.1755e-06 | -0.00014452 | 0.01202 | 0.012022 | 0.012022 | 0.99792 | -0.045248 | 0.99792 | -0.045221 | 5.4646
160 | 0.072284 | 0.034691 | -0.072284 | -0.035009 | 9.6812e-08 | -0.00031793 | 0.002323 | 0.002327 | 0.002327 | 0.99634 | -0.046511 | 0.99634 | -0.0465 | 1.0577
161 | -0.23885 | -0.11536 | 0.23885 | 0.11494 | 1.4013e-06 | -0.0004211 | 0.0076852 | 0.0076799 | 0.0076852 | 0.99634 | -0.046511 | 0.99635 | -0.046562 | 3.4933
162 | -0.23885 | -0.11494 | 0.23885 | 0.11476 | 5.8851e-07 | -0.00017703 | 0.0076799 | 0.0076777 | 0.0076799 | 0.99635 | -0.046562 | 0.99635 | -0.046583 | 3.4909
163 | -0.32844 | -0.15773 | 0.32845 | 0.15653 | 7.5053e-06 | -0.0011953 | 0.010556 | 0.010541 | 0.010556 | 0.99635 | -0.046583 | 0.99637 | -0.046776 | 4.7984
164 | 0.08959 | 0.042962 | -0.089589 | -0.04339 | 2.0011e-07 | -0.00042788 | 0.0028787 | 0.0028841 | 0.0028841 | 0.99635 | -0.046583 | 0.99635 | -0.046564 | 1.311
165 | 1.9076 | 0.89847 | -1.9076 | -0.89857 | 2.2992e-05 | -0.00010168 | 0.061214 | 0.061215 | 0.061215 | 0.99439 | -0.060393 | 0.99437 | -0.060295 | 27.8252
166 | -2.2869 | -1.0822 | 2.2877 | 1.0826 | 0.00081494 | 0.00041032 | 0.073447 | 0.073446 | 0.073447 | 0.99439 | -0.060393 | 0.99476 | -0.057839 | 34.9749
167 | -2.2877 | -1.0826 | 2.2885 | 1.0802 | 0.00078909 | -0.0023568 | 0.073446 | 0.073414 | 0.073446 | 0.99476 | -0.057839 | 0.99508 | -0.060681 | 33.3846
168 | -2.2885 | -1.0802 | 2.2887 | 1.0796 | 0.00020754 | -0.00062051 | 0.073414 | 0.073405 | 0.073414 | 0.99508 | -0.060681 | 0.99516 | -0.061426 | 33.37
169 | -2.485 | -1.1747 | 2.4851 | 1.1745 | 7.2838e-05 | -0.00018134 | 0.079733 | 0.07973 | 0.079733 | 0.99516 | -0.061426 | 0.99519 | -0.061668 | 36.2421
170 | -0.25298 | -0.12253 | 0.25298 | 0.12225 | 1.0154e-06 | -0.00027342 | 0.0081307 | 0.0081272 | 0.0081307 | 0.99801 | -0.062275 | 0.99801 | -0.06231 | 3.6958

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.0693 | 9.6958

## res_load
| p_mw | q_mvar
0 | 0.38256 | 0.18528
1 | 0.1147 | 0.055552
2 | 0.1383 | 0.066982
3 | 0.37219 | 0.18026
4 | 0.36964 | 0.17903
5 | 0.3756 | 0.18191
6 | 0.35505 | 0.17196
7 | 0.31228 | 0.15124
8 | 0.13702 | 0.066361
9 | 0.31298 | 0.15158
10 | 0.32652 | 0.15814
11 | 0.23189 | 0.11231
12 | 0.39561 | 0.1916
13 | 0.40073 | 0.19408
14 | 0.25129 | 0.12171
15 | 0.26043 | 0.12613
16 | 0.26205 | 0.12692
17 | 0.37298 | 0.18064
18 | 0.2094 | 0.10142
19 | 0.22187 | 0.10746
20 | 0.31263 | 0.15141
21 | 0.27425 | 0.13283
22 | 0.086996 | 0.042134
23 | 0.27453 | 0.13296
24 | 0.29517 | 0.14296
25 | 0.21972 | 0.10641
26 | 0.10726 | 0.051948
27 | 0.09334 | 0.045207
28 | 0.18945 | 0.091757
29 | 0.22727 | 0.11007
30 | 0.39481 | 0.19121
31 | 0.21234 | 0.10284
32 | 0.30348 | 0.14698
33 | 0.34766 | 0.16838
34 | 0.39878 | 0.19314
35 | 0.25475 | 0.12338
36 | 0.10309 | 0.04993
37 | 0.11368 | 0.055059
38 | 0.13947 | 0.067548
39 | 0.16362 | 0.079244
40 | 0.35964 | 0.17418
41 | 0.31327 | 0.15172
42 | 0.2348 | 0.11372
43 | 0.089837 | 0.04351
44 | 0.24333 | 0.11785
45 | 0.22835 | 0.11059
46 | 0.61164 | 0.29623
47 | 0.32442 | 0.15712
48 | 0.39013 | 0.18895
49 | 0.31019 | 0.15023
50 | 0.11158 | 0.054042
51 | 0.32856 | 0.15913
52 | 0.1179 | 0.057101
53 | 0.2921 | 0.14147
54 | 0.11331 | 0.054879
55 | 0.32439 | 0.15711
56 | 0.3201 | 0.15503
57 | 0.21372 | 0.10351
58 | 0.28287 | 0.137
59 | 0.35617 | 0.1725
60 | 0.093909 | 0.045482
61 | 0.15099 | 0.073129
62 | 0.29807 | 0.14436
63 | 0.12256 | 0.05936
64 | 0.28089 | 0.13604
65 | 0.26361 | 0.12767
66 | 0.14362 | 0.069556
67 | 0.29723 | 0.14395
68 | 0.37645 | 0.18232
69 | 0.33015 | 0.1599
70 | 0.33643 | 0.16294
71 | 0.37403 | 0.18115
72 | 0.26944 | 0.1305
73 | 0.16656 | 0.080671
74 | 0.072284 | 0.035009
75 | 0.089589 | 0.04339
76 | 0.37927 | 0.18369
77 | 0.19632 | 0.095081
78 | 0.37102 | 0.1797
79 | 0.24155 | 0.11699
80 | 0.25298 | 0.12253

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1