## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_540_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_540_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_540_0_node_54 | 20 | n |  | TRUE
3 | bus_MV_540_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_540_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_540_0_node_55 | 20 | n |  | TRUE
6 | bus_MV_540_0_node_22 | 20 | n |  | TRUE
7 | bus_MV_540_0_node_146 | 20 | n |  | TRUE
8 | bus_MV_540_0_node_4 | 20 | n |  | TRUE
9 | bus_MV_540_0_node_97 | 20 | n |  | TRUE
10 | bus_MV_540_0_node_91 | 20 | n |  | TRUE
11 | bus_MV_540_0_node_24 | 20 | n |  | TRUE
12 | bus_MV_540_0_node_96 | 20 | n |  | TRUE
13 | bus_MV_540_0_node_5 | 20 | n |  | TRUE
14 | bus_MV_540_0_node_6 | 20 | n |  | TRUE
15 | bus_MV_540_0_node_7 | 20 | n |  | TRUE
16 | bus_MV_540_0_node_11 | 20 | n |  | TRUE
17 | bus_MV_540_0_node_103 | 20 | n |  | TRUE
18 | bus_MV_540_0_node_8 | 20 | n |  | TRUE
19 | bus_MV_540_0_node_171 | 20 | n |  | TRUE
20 | bus_MV_540_0_node_9 | 20 | n |  | TRUE
21 | bus_MV_540_0_node_10 | 20 | n |  | TRUE
22 | bus_MV_540_0_node_75 | 20 | n |  | TRUE
23 | bus_MV_540_0_node_73 | 20 | n |  | TRUE
24 | bus_MV_540_0_node_104 | 20 | n |  | TRUE
25 | bus_MV_540_0_node_122 | 20 | n |  | TRUE
26 | bus_MV_540_0_node_125 | 20 | n |  | TRUE
27 | bus_MV_540_0_node_12 | 20 | n |  | TRUE
28 | bus_MV_540_0_node_77 | 20 | n |  | TRUE
29 | bus_MV_540_0_node_74 | 20 | n |  | TRUE
30 | bus_MV_540_0_node_59 | 20 | n |  | TRUE
31 | bus_MV_540_0_node_121 | 20 | n |  | TRUE
32 | bus_MV_540_0_node_78 | 20 | n |  | TRUE
33 | bus_MV_540_0_node_76 | 20 | n |  | TRUE
34 | bus_MV_540_0_node_13 | 20 | n |  | TRUE
35 | bus_MV_540_0_node_14 | 20 | n |  | TRUE
36 | bus_MV_540_0_node_18 | 20 | n |  | TRUE
37 | bus_MV_540_0_node_19 | 20 | n |  | TRUE
38 | bus_MV_540_0_node_17 | 20 | n |  | TRUE
39 | bus_MV_540_0_node_20 | 20 | n |  | TRUE
40 | bus_MV_540_0_node_102 | 20 | n |  | TRUE
41 | bus_MV_540_0_node_34 | 20 | n |  | TRUE
42 | bus_MV_540_0_node_21 | 20 | n |  | TRUE
43 | bus_MV_540_0_node_32 | 20 | n |  | TRUE
44 | bus_MV_540_0_node_89 | 20 | n |  | TRUE
45 | bus_MV_540_0_node_31 | 20 | n |  | TRUE
46 | bus_MV_540_0_node_15 | 20 | n |  | TRUE
47 | bus_MV_540_0_node_16 | 20 | n |  | TRUE
48 | bus_MV_540_0_node_144 | 20 | n |  | TRUE
49 | bus_MV_540_0_node_49 | 20 | n |  | TRUE
50 | bus_MV_540_0_node_50 | 20 | n |  | TRUE
51 | bus_MV_540_0_node_51 | 20 | n |  | TRUE
52 | bus_MV_540_0_node_53 | 20 | n |  | TRUE
53 | bus_MV_540_0_node_36 | 20 | n |  | TRUE
54 | bus_MV_540_0_node_143 | 20 | n |  | TRUE
55 | bus_MV_540_0_node_38 | 20 | n |  | TRUE
56 | bus_MV_540_0_node_33 | 20 | n |  | TRUE
57 | bus_MV_540_0_node_101 | 20 | n |  | TRUE
58 | bus_MV_540_0_node_35 | 20 | n |  | TRUE
59 | bus_MV_540_0_node_48 | 20 | n |  | TRUE
60 | bus_MV_540_0_node_27 | 20 | n |  | TRUE
61 | bus_MV_540_0_node_148 | 20 | n |  | TRUE
62 | bus_MV_540_0_node_149 | 20 | n |  | TRUE
63 | bus_MV_540_0_node_147 | 20 | n |  | TRUE
64 | bus_MV_540_0_node_114 | 20 | n |  | TRUE
65 | bus_MV_540_0_node_23 | 20 | n |  | TRUE
66 | bus_MV_540_0_node_25 | 20 | n |  | TRUE
67 | bus_MV_540_0_node_26 | 20 | n |  | TRUE
68 | bus_MV_540_0_node_145 | 20 | n |  | TRUE
69 | bus_MV_540_0_node_129 | 20 | n |  | TRUE
70 | bus_MV_540_0_node_70 | 20 | n |  | TRUE
71 | bus_MV_540_0_node_29 | 20 | n |  | TRUE
72 | bus_MV_540_0_node_30 | 20 | n |  | TRUE
73 | bus_MV_540_0_node_111 | 20 | n |  | TRUE
74 | bus_MV_540_0_node_112 | 20 | n |  | TRUE
75 | bus_MV_540_0_node_113 | 20 | n |  | TRUE
76 | bus_MV_540_0_node_37 | 20 | n |  | TRUE
77 | bus_MV_540_0_node_39 | 20 | n |  | TRUE
78 | bus_MV_540_0_node_52 | 20 | n |  | TRUE
79 | bus_MV_540_0_node_40 | 20 | n |  | TRUE
80 | bus_MV_540_0_node_41 | 20 | n |  | TRUE
81 | bus_MV_540_0_node_83 | 20 | n |  | TRUE
82 | bus_MV_540_0_node_142 | 20 | n |  | TRUE
83 | bus_MV_540_0_node_45 | 20 | n |  | TRUE
84 | bus_MV_540_0_node_90 | 20 | n |  | TRUE
85 | bus_MV_540_0_node_86 | 20 | n |  | TRUE
86 | bus_MV_540_0_node_84 | 20 | n |  | TRUE
87 | bus_MV_540_0_node_85 | 20 | n |  | TRUE
88 | bus_MV_540_0_node_87 | 20 | n |  | TRUE
89 | bus_MV_540_0_node_88 | 20 | n |  | TRUE
90 | bus_MV_540_0_node_138 | 20 | n |  | TRUE
91 | bus_MV_540_0_node_161 | 20 | n |  | TRUE
92 | bus_MV_540_0_node_141 | 20 | n |  | TRUE
93 | bus_MV_540_0_node_135 | 20 | n |  | TRUE
94 | bus_MV_540_0_node_136 | 20 | n |  | TRUE
95 | bus_MV_540_0_node_137 | 20 | n |  | TRUE
96 | bus_MV_540_0_node_140 | 20 | n |  | TRUE
97 | bus_MV_540_0_node_139 | 20 | n |  | TRUE
98 | bus_MV_540_0_node_162 | 20 | n |  | TRUE
99 | bus_MV_540_0_node_163 | 20 | n |  | TRUE
100 | bus_MV_540_0_node_110 | 20 | n |  | TRUE
101 | bus_MV_540_0_node_42 | 20 | n |  | TRUE
102 | bus_MV_540_0_node_44 | 20 | n |  | TRUE
103 | bus_MV_540_0_node_131 | 20 | n |  | TRUE
104 | bus_MV_540_0_node_132 | 20 | n |  | TRUE
105 | bus_MV_540_0_node_133 | 20 | n |  | TRUE
106 | bus_MV_540_0_node_130 | 20 | n |  | TRUE
107 | bus_MV_540_0_node_166 | 20 | n |  | TRUE
108 | bus_MV_540_0_node_173 | 20 | n |  | TRUE
109 | bus_MV_540_0_node_128 | 20 | n |  | TRUE
110 | bus_MV_540_0_node_168 | 20 | n |  | TRUE
111 | bus_MV_540_0_node_124 | 20 | n |  | TRUE
112 | bus_MV_540_0_node_56 | 20 | n |  | TRUE
113 | bus_MV_540_0_node_95 | 20 | n |  | TRUE
114 | bus_MV_540_0_node_100 | 20 | n |  | TRUE
115 | bus_MV_540_0_node_93 | 20 | n |  | TRUE
116 | bus_MV_540_0_node_92 | 20 | n |  | TRUE
117 | bus_MV_540_0_node_57 | 20 | n |  | TRUE
118 | bus_MV_540_0_node_58 | 20 | n |  | TRUE
119 | bus_MV_540_0_node_66 | 20 | n |  | TRUE
120 | bus_MV_540_0_node_67 | 20 | n |  | TRUE
121 | bus_MV_540_0_node_158 | 20 | n |  | TRUE
122 | bus_MV_540_0_node_94 | 20 | n |  | TRUE
123 | bus_MV_540_0_node_68 | 20 | n |  | TRUE
124 | bus_MV_540_0_node_69 | 20 | n |  | TRUE
125 | bus_MV_540_0_node_71 | 20 | n |  | TRUE
126 | bus_MV_540_0_node_72 | 20 | n |  | TRUE
127 | bus_MV_540_0_node_115 | 20 | n |  | TRUE
128 | bus_MV_540_0_node_172 | 20 | n |  | TRUE
129 | bus_MV_540_0_node_164 | 20 | n |  | TRUE
130 | bus_MV_540_0_node_165 | 20 | n |  | TRUE
131 | bus_MV_540_0_node_60 | 20 | n |  | TRUE
132 | bus_MV_540_0_node_61 | 20 | n |  | TRUE
133 | bus_MV_540_0_node_62 | 20 | n |  | TRUE
134 | bus_MV_540_0_node_65 | 20 | n |  | TRUE
135 | bus_MV_540_0_node_159 | 20 | n |  | TRUE
136 | bus_MV_540_0_node_63 | 20 | n |  | TRUE
137 | bus_MV_540_0_node_64 | 20 | n |  | TRUE
138 | bus_MV_540_0_node_154 | 20 | n |  | TRUE
139 | bus_MV_540_0_node_118 | 20 | n |  | TRUE
140 | bus_MV_540_0_node_156 | 20 | n |  | TRUE
141 | bus_MV_540_0_node_160 | 20 | n |  | TRUE
142 | bus_MV_540_0_node_157 | 20 | n |  | TRUE
143 | bus_MV_540_0_node_155 | 20 | n |  | TRUE
144 | bus_MV_540_0_node_152 | 20 | n |  | TRUE
145 | bus_MV_540_0_node_119 | 20 | n |  | TRUE
146 | bus_MV_540_0_node_116 | 20 | n |  | TRUE
147 | bus_MV_540_0_node_134 | 20 | n |  | TRUE
148 | bus_MV_540_0_node_79 | 20 | n |  | TRUE
149 | bus_MV_540_0_node_174 | 20 | n |  | TRUE
150 | bus_MV_540_0_node_81 | 20 | n |  | TRUE
151 | bus_MV_540_0_node_80 | 20 | n |  | TRUE
152 | bus_MV_540_0_node_82 | 20 | n |  | TRUE
153 | bus_MV_540_0_node_175 | 20 | n |  | TRUE
154 | bus_MV_540_0_node_170 | 20 | n |  | TRUE
155 | bus_MV_540_0_node_98 | 20 | n |  | TRUE
156 | bus_MV_540_0_node_99 | 20 | n |  | TRUE
157 | bus_MV_540_0_node_108 | 20 | n |  | TRUE
158 | bus_MV_540_0_node_109 | 20 | n |  | TRUE
159 | bus_MV_540_0_node_105 | 20 | n |  | TRUE
160 | bus_MV_540_0_node_151 | 20 | n |  | TRUE
161 | bus_MV_540_0_node_150 | 20 | n |  | TRUE
162 | bus_MV_540_0_node_117 | 20 | n |  | TRUE
163 | bus_MV_540_0_node_120 | 20 | n |  | TRUE
164 | bus_MV_540_0_node_153 | 20 | n |  | TRUE
165 | bus_MV_540_0_node_123 | 20 | n |  | TRUE
166 | bus_MV_540_0_node_126 | 20 | n |  | TRUE
167 | bus_MV_540_0_node_127 | 20 | n |  | TRUE
168 | bus_MV_540_0_node_169 | 20 | n |  | TRUE
169 | bus_MV_540_0_node_167 | 20 | n |  | TRUE
170 | bus_HV_540_0_node_126 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_540_0_load_0 | 0 | 0.34861 | 0.16884 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_540_0_load_54 | 2 | 0.34635 | 0.16774 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_540_0_load_55 | 5 | 0.17602 | 0.085251 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_540_0_load_22 | 6 | 0.40197 | 0.19468 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_540_0_load_146 | 7 | 0.11731 | 0.056814 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_540_0_load_97 | 9 | 0.27715 | 0.13423 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_540_0_load_91 | 10 | 0.26241 | 0.12709 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_540_0_load_5 | 13 | 0.24177 | 0.1171 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_540_0_load_103 | 17 | 0.12517 | 0.060622 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_540_0_load_171 | 19 | 0.079648 | 0.038575 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_540_0_load_104 | 24 | 0.1315 | 0.063688 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_540_0_load_125 | 26 | 0.10653 | 0.051593 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_540_0_load_12 | 27 | 0.23744 | 0.115 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_540_0_load_74 | 29 | 0.37317 | 0.18073 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_540_0_load_59 | 30 | 0.070374 | 0.034084 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_540_0_load_121 | 31 | 0.11312 | 0.054785 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_540_0_load_78 | 32 | 0.076661 | 0.037129 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_540_0_load_13 | 34 | 0.33695 | 0.16319 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_540_0_load_18 | 36 | 0.080165 | 0.038826 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_540_0_load_102 | 40 | 0.11331 | 0.054877 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_540_0_load_32 | 43 | 0.18808 | 0.091094 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_540_0_load_89 | 44 | 0.36927 | 0.17884 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_540_0_load_31 | 45 | 0.25244 | 0.12226 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_540_0_load_16 | 47 | 0.27794 | 0.13461 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_540_0_load_144 | 48 | 0.13174 | 0.063803 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_540_0_load_49 | 49 | 0.25832 | 0.12511 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_540_0_load_51 | 51 | 0.069726 | 0.03377 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_540_0_load_143 | 54 | 0.3273 | 0.15852 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_540_0_load_38 | 55 | 0.15822 | 0.076628 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_540_0_load_101 | 57 | 0.11729 | 0.056808 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_540_0_load_35 | 58 | 0.36291 | 0.17577 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_540_0_load_27 | 60 | 0.35885 | 0.1738 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_540_0_load_147 | 63 | 0.12392 | 0.060017 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_540_0_load_114 | 64 | 0.33435 | 0.16193 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_540_0_load_145 | 68 | 0.13298 | 0.064404 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_540_0_load_129 | 69 | 0.19662 | 0.095227 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_540_0_load_111 | 73 | 0.096701 | 0.046834 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_540_0_load_52 | 78 | 0.32139 | 0.15566 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_540_0_load_41 | 80 | 0.17937 | 0.086875 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_540_0_load_83 | 81 | 0.37875 | 0.18344 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_540_0_load_142 | 82 | 0.078495 | 0.038017 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_540_0_load_86 | 85 | 0.30721 | 0.14879 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_540_0_load_85 | 87 | 0.13035 | 0.063133 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_540_0_load_88 | 89 | 0.13098 | 0.063435 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_540_0_load_138 | 90 | 0.10543 | 0.051064 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_540_0_load_141 | 92 | 0.18454 | 0.089377 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_540_0_load_135 | 93 | 0.47155 | 0.22838 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_540_0_load_140 | 96 | 0.12615 | 0.061095 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_540_0_load_163 | 99 | 0.1042 | 0.050467 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_540_0_load_110 | 100 | 0.094464 | 0.045751 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_540_0_load_42 | 101 | 0.27744 | 0.13437 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_540_0_load_130 | 106 | 0.1941 | 0.094007 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_540_0_load_166 | 107 | 0.37632 | 0.18226 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_540_0_load_173 | 108 | 0.23413 | 0.11339 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_540_0_load_168 | 110 | 0.19424 | 0.094072 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_540_0_load_95 | 113 | 0.36937 | 0.17889 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_540_0_load_92 | 116 | 0.28853 | 0.13974 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_540_0_load_57 | 117 | 0.35543 | 0.17214 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_540_0_load_158 | 121 | 0.15039 | 0.072835 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_540_0_load_94 | 122 | 0.11567 | 0.056023 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_540_0_load_115 | 127 | 0.67418 | 0.32652 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_540_0_load_172 | 128 | 1.6429 | 0.79567 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_540_0_load_164 | 129 | 0.27961 | 0.13542 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_540_0_load_165 | 130 | 0.24419 | 0.11827 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_540_0_load_61 | 132 | 0.1515 | 0.073375 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_540_0_load_154 | 138 | 0.21718 | 0.10519 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_540_0_load_118 | 139 | 0.26004 | 0.12594 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_540_0_load_156 | 140 | 0.10865 | 0.052622 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_540_0_load_157 | 142 | 0.13931 | 0.067469 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_540_0_load_155 | 143 | 0.10429 | 0.050508 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_540_0_load_174 | 149 | 0.37903 | 0.18357 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_540_0_load_80 | 151 | 0.27782 | 0.13456 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_540_0_load_175 | 153 | 0.35478 | 0.17183 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_540_0_load_170 | 154 | 0.28952 | 0.14022 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_540_0_load_108 | 157 | 0.093285 | 0.04518 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_540_0_load_109 | 158 | 0.089075 | 0.043141 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_540_0_load_105 | 159 | 0.09418 | 0.045614 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_540_0_load_150 | 161 | 0.13459 | 0.065184 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_540_0_load_117 | 162 | 0.073172 | 0.035439 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_540_0_load_153 | 164 | 0.17612 | 0.085299 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_540_0_load_123 | 165 | 0.33703 | 0.16323 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_540_0_load_127 | 167 | 0.11928 | 0.057769 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_540_0_load_169 | 168 | 0.090304 | 0.043736 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_540_0_load_167 | 169 | 0.16486 | 0.079844 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 166 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_540_0_line_0 |  | 0 | 1 | 0.014639 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
1 | MV_540_0_line_1 |  | 0 | 2 | 0.067451 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
2 | MV_540_0_line_2 |  | 1 | 3 | 0.059106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_540_0_line_3 |  | 1 | 4 | 0.051954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_540_0_line_4 |  | 2 | 5 | 0.024542 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
5 | MV_540_0_line_5 |  | 3 | 6 | 0.004293 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_540_0_line_6 |  | 3 | 7 | 0.043478 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_540_0_line_7 |  | 4 | 8 | 0.039547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_540_0_line_8 |  | 4 | 9 | 0.035602 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_540_0_line_9 |  | 5 | 112 | 0.023753 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
10 | MV_540_0_line_10 |  | 7 | 11 | 0.013694 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_540_0_line_11 |  | 8 | 10 | 0.030026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_540_0_line_12 |  | 9 | 12 | 0.039898 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_540_0_line_13 |  | 11 | 65 | 0.0096545 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_540_0_line_14 |  | 12 | 114 | 0.082498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_540_0_line_15 |  | 12 | 113 | 0.014164 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_540_0_line_16 |  | 13 | 14 | 0.034111 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_540_0_line_17 |  | 14 | 15 | 0.082989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_540_0_line_18 |  | 14 | 16 | 0.12322 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_540_0_line_19 |  | 15 | 17 | 0.024086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_540_0_line_20 |  | 16 | 27 | 0.01025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_540_0_line_21 |  | 18 | 19 | 0.01212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_540_0_line_22 |  | 18 | 20 | 0.20568 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
23 | MV_540_0_line_23 |  | 18 | 21 | 0.091347 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
24 | MV_540_0_line_24 |  | 18 | 22 | 0.064772 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_540_0_line_25 |  | 20 | 23 | 0.057355 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_540_0_line_26 |  | 20 | 24 | 0.045701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_540_0_line_27 |  | 21 | 25 | 0.020288 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
28 | MV_540_0_line_28 |  | 21 | 26 | 0.015696 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_540_0_line_29 |  | 22 | 28 | 0.047108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_540_0_line_30 |  | 22 | 29 | 0.017458 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_540_0_line_31 |  | 23 | 30 | 0.020087 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
32 | MV_540_0_line_32 |  | 25 | 31 | 0.046864 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_540_0_line_33 |  | 27 | 32 | 0.031586 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_540_0_line_34 |  | 28 | 148 | 0.037821 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_540_0_line_35 |  | 28 | 149 | 0.045524 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
36 | MV_540_0_line_36 |  | 29 | 33 | 0.018449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_540_0_line_37 |  | 30 | 117 | 0.024039 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
38 | MV_540_0_line_38 |  | 31 | 165 | 0.033398 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
39 | MV_540_0_line_39 |  | 32 | 33 | 0.016301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_540_0_line_40 |  | 34 | 35 | 0.026469 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_540_0_line_41 |  | 35 | 36 | 0.031634 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_540_0_line_42 |  | 35 | 37 | 0.087596 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
43 | MV_540_0_line_43 |  | 36 | 38 | 0.032649 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_540_0_line_44 |  | 37 | 39 | 0.10116 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
45 | MV_540_0_line_45 |  | 37 | 40 | 0.0075395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_540_0_line_46 |  | 38 | 48 | 0.080616 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_540_0_line_47 |  | 38 | 46 | 0.03523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_540_0_line_48 |  | 39 | 41 | 0.021537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_540_0_line_49 |  | 39 | 42 | 0.11653 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
50 | MV_540_0_line_50 |  | 39 | 43 | 0.00476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_540_0_line_51 |  | 41 | 58 | 0.004628 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_540_0_line_52 |  | 41 | 56 | 0.044711 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_540_0_line_53 |  | 42 | 44 | 0.037452 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
54 | MV_540_0_line_54 |  | 42 | 45 | 0.072144 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_540_0_line_55 |  | 44 | 59 | 0.00441 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
56 | MV_540_0_line_56 |  | 45 | 60 | 0.036779 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_540_0_line_57 |  | 46 | 47 | 0.058122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_540_0_line_58 |  | 48 | 55 | 0.056524 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_540_0_line_59 |  | 48 | 54 | 0.071829 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_540_0_line_60 |  | 49 | 50 | 0.004576 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_540_0_line_61 |  | 49 | 51 | 0.022269 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_540_0_line_62 |  | 50 | 52 | 0.006463 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_540_0_line_63 |  | 51 | 53 | 0.071367 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_540_0_line_64 |  | 52 | 54 | 0.035455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_540_0_line_65 |  | 53 | 76 | 0.019169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_540_0_line_66 |  | 53 | 77 | 0.047169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_540_0_line_67 |  | 56 | 57 | 0.029859 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_540_0_line_68 |  | 58 | 100 | 0.16818 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_540_0_line_69 |  | 59 | 102 | 0.031223 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
70 | MV_540_0_line_70 |  | 60 | 71 | 0.026487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_540_0_line_71 |  | 61 | 62 | 0.051417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_540_0_line_72 |  | 61 | 63 | 0.028684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_540_0_line_73 |  | 62 | 64 | 0.015374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_540_0_line_74 |  | 64 | 75 | 0.015701 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_540_0_line_75 |  | 65 | 66 | 0.090508 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_540_0_line_76 |  | 66 | 67 | 0.057403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_540_0_line_77 |  | 66 | 68 | 0.016612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_540_0_line_78 |  | 67 | 69 | 0.030114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_540_0_line_79 |  | 68 | 70 | 0.025626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_540_0_line_80 |  | 70 | 125 | 0.076255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_540_0_line_81 |  | 71 | 72 | 0.030936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_540_0_line_82 |  | 72 | 73 | 0.017083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_540_0_line_83 |  | 73 | 74 | 0.023249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_540_0_line_84 |  | 74 | 75 | 0.023047 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_540_0_line_85 |  | 76 | 78 | 0.003411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_540_0_line_86 |  | 77 | 79 | 0.008357 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_540_0_line_87 |  | 77 | 80 | 0.027446 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_540_0_line_88 |  | 79 | 81 | 0.007844 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_540_0_line_89 |  | 80 | 82 | 0.048435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_540_0_line_90 |  | 81 | 86 | 0.031809 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_540_0_line_91 |  | 81 | 87 | 0.03351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_540_0_line_92 |  | 82 | 84 | 0.034522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_540_0_line_93 |  | 83 | 84 | 0.008614 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_540_0_line_94 |  | 83 | 85 | 0.008339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_540_0_line_95 |  | 84 | 92 | 0.0081315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_540_0_line_96 |  | 86 | 88 | 0.046346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_540_0_line_97 |  | 87 | 89 | 0.029854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_540_0_line_98 |  | 88 | 90 | 0.018036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_540_0_line_99 |  | 89 | 91 | 0.016351 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_540_0_line_100 |  | 90 | 97 | 0.020989 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_540_0_line_101 |  | 91 | 96 | 0.014782 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_540_0_line_102 |  | 93 | 94 | 0.034216 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_540_0_line_103 |  | 94 | 95 | 0.017569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_540_0_line_104 |  | 95 | 96 | 0.051834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_540_0_line_105 |  | 97 | 98 | 0.007487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_540_0_line_106 |  | 98 | 99 | 0.060646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_540_0_line_107 |  | 101 | 102 | 0.02447 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
108 | MV_540_0_line_108 |  | 101 | 103 | 0.083237 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_540_0_line_109 |  | 101 | 104 | 0.029456 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
110 | MV_540_0_line_110 |  | 101 | 105 | 0.050329 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_540_0_line_111 |  | 103 | 106 | 0.041201 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_540_0_line_112 |  | 104 | 107 | 0.048122 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
113 | MV_540_0_line_113 |  | 105 | 108 | 0.016519 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_540_0_line_114 |  | 107 | 109 | 0.044706 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
115 | MV_540_0_line_115 |  | 109 | 166 | 0.039227 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
116 | MV_540_0_line_116 |  | 109 | 111 | 0.027117 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
117 | MV_540_0_line_117 |  | 110 | 111 | 0.051037 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_540_0_line_118 |  | 111 | 165 | 0.019685 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
119 | MV_540_0_line_119 |  | 112 | 115 | 0.015579 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
120 | MV_540_0_line_120 |  | 114 | 157 | 0.02101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_540_0_line_121 |  | 114 | 158 | 0.024835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_540_0_line_122 |  | 114 | 159 | 0.052691 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
123 | MV_540_0_line_123 |  | 115 | 116 | 0.029967 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
124 | MV_540_0_line_124 |  | 116 | 142 | 0.055915 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
125 | MV_540_0_line_125 |  | 116 | 133 | 0.017784 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
126 | MV_540_0_line_126 |  | 117 | 118 | 0.007035 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
127 | MV_540_0_line_127 |  | 118 | 119 | 0.035161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_540_0_line_128 |  | 118 | 120 | 0.041484 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
129 | MV_540_0_line_129 |  | 119 | 121 | 0.0082092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_540_0_line_130 |  | 120 | 122 | 0.020676 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
131 | MV_540_0_line_131 |  | 122 | 133 | 0.018084 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
132 | MV_540_0_line_132 |  | 123 | 124 | 0.054977 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_540_0_line_133 |  | 123 | 125 | 0.063024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_540_0_line_134 |  | 123 | 126 | 0.053651 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_540_0_line_135 |  | 123 | 127 | 0.018747 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_540_0_line_136 |  | 124 | 128 | 0.023236 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_540_0_line_137 |  | 125 | 129 | 0.0021444 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_540_0_line_138 |  | 126 | 130 | 0.0024335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_540_0_line_139 |  | 127 | 146 | 0.032097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_540_0_line_140 |  | 128 | 147 | 0.20504 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_540_0_line_141 |  | 131 | 132 | 0.018955 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_540_0_line_142 |  | 131 | 133 | 0.061471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
143 | MV_540_0_line_143 |  | 131 | 134 | 0.059305 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_540_0_line_144 |  | 132 | 135 | 0.030111 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_540_0_line_145 |  | 134 | 140 | 0.0038272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_540_0_line_146 |  | 135 | 141 | 0.025684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_540_0_line_147 |  | 136 | 137 | 0.032948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_540_0_line_148 |  | 136 | 138 | 0.036492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_540_0_line_149 |  | 137 | 139 | 0.013832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_540_0_line_150 |  | 138 | 143 | 0.068176 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
151 | MV_540_0_line_151 |  | 138 | 144 | 0.030415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_540_0_line_152 |  | 139 | 145 | 0.028038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_540_0_line_153 |  | 141 | 169 | 0.026505 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_540_0_line_154 |  | 142 | 155 | 0.038365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_540_0_line_155 |  | 143 | 156 | 0.016048 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_540_0_line_156 |  | 144 | 160 | 0.047619 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_540_0_line_157 |  | 145 | 163 | 0.012802 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_540_0_line_158 |  | 146 | 162 | 0.01765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_540_0_line_159 |  | 147 | 168 | 0.012192 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_540_0_line_160 |  | 148 | 150 | 0.25541 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_540_0_line_161 |  | 148 | 151 | 0.016674 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
162 | MV_540_0_line_162 |  | 150 | 152 | 0.4145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_540_0_line_163 |  | 150 | 153 | 0.00527 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_540_0_line_164 |  | 152 | 154 | 0.018627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_540_0_line_165 |  | 155 | 156 | 0.01007 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_540_0_line_166 |  | 160 | 161 | 0.019759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_540_0_line_167 |  | 163 | 164 | 0.02837 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_540_0_line_168 |  | 166 | 167 | 0.025068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_540_0_trafo_126 | 25 MVA 110/20 kV | 170 | 166 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2683030.7814 | 1247861.2835
1 | 2683018.4427 | 1247869.161
2 | 2683093.1883 | 1247886.8765
3 | 2683023.5071 | 1247912.5528
4 | 2682997.9755 | 1247822.1399
5 | 2683116.5218 | 1247879.2688
6 | 2683025.7976 | 1247916.1876
7 | 2682984.6069 | 1247931.9718
8 | 2682982.1713 | 1247848.2491
9 | 2683030.3146 | 1247815.8807
10 | 2682957.0249 | 1247864.6571
11 | 2682972.8729 | 1247938.9191
12 | 2683064.2144 | 1247799.0837
13 | 2683578.9226 | 1247919.5599
14 | 2683545.5355 | 1247912.2619
15 | 2683567.2813 | 1247851.1565
16 | 2683531.0994 | 1247882.9591
17 | 2683577.4004 | 1247829.2992
18 | 2683479.1414 | 1247886.7636
19 | 2683491.164 | 1247885.8211
20 | 2683322.4776 | 1247917.3162
21 | 2683470.4865 | 1247946.219
22 | 2683481.373 | 1247823.793
23 | 2683265.3128 | 1247920.8158
24 | 2683325.9607 | 1247872.0568
25 | 2683488.5435 | 1247952.2665
26 | 2683463.7951 | 1247960.2498
27 | 2683523.2469 | 1247876.3436
28 | 2683478.181 | 1247776.9357
29 | 2683498.6243 | 1247826.4712
30 | 2683245.2468 | 1247921.7382
31 | 2683490.565 | 1247998.735
32 | 2683516.255 | 1247845.5411
33 | 2683516.9164 | 1247829.253
34 | 2683581.3892 | 1248286.577
35 | 2683557.4194 | 1248275.1974
36 | 2683544.4975 | 1248304.0718
37 | 2683538.3762 | 1248227.7496
38 | 2683528.2603 | 1248331.3615
39 | 2683486.0254 | 1248254.8212
40 | 2683543.0222 | 1248224.3828
41 | 2683484.0632 | 1248267.0471
42 | 2683533.8289 | 1248177.971
43 | 2683481.3487 | 1248253.8658
44 | 2683504.8389 | 1248155.1347
45 | 2683602.688 | 1248156.4477
46 | 2683559.0598 | 1248339.3569
47 | 2683611.5557 | 1248364.5933
48 | 2683468.1798 | 1248385.1139
49 | 2683442.5924 | 1248489.0609
50 | 2683447.1125 | 1248489.8584
51 | 2683445.01 | 1248466.9239
52 | 2683453.518 | 1248490.8493
53 | 2683376.3877 | 1248447.3209
54 | 2683458.6566 | 1248455.7684
55 | 2683412.3857 | 1248376.0581
56 | 2683489.5948 | 1248305.9537
57 | 2683514.7592 | 1248302.1639
58 | 2683479.5306 | 1248266.0492
59 | 2683500.4246 | 1248154.8501
60 | 2683635.8463 | 1248172.3604
61 | 2683592.3404 | 1248092.2322
62 | 2683620.0802 | 1248062.9016
63 | 2683604.2127 | 1248066.1206
64 | 2683634.2339 | 1248068.885
65 | 2682978.9232 | 1247946.4427
66 | 2683028.1851 | 1248008.3111
67 | 2682999.583 | 1248026.602
68 | 2683043.7642 | 1248002.5642
69 | 2682971.293 | 1248036.9026
70 | 2683067.4131 | 1247992.7935
71 | 2683646.7158 | 1248148.1958
72 | 2683653.0112 | 1248122.7659
73 | 2683659.7987 | 1248107.089
74 | 2683669.0095 | 1248085.742
75 | 2683647.5677 | 1248077.1442
76 | 2683370.8284 | 1248465.623
77 | 2683335.3913 | 1248424.4055
78 | 2683367.5651 | 1248464.5985
79 | 2683327.9691 | 1248420.5205
80 | 2683349.4561 | 1248400.9826
81 | 2683321.0043 | 1248416.8755
82 | 2683371.1285 | 1248357.6739
83 | 2683377.7424 | 1248323.1371
84 | 2683385.7399 | 1248326.3964
85 | 2683370.0002 | 1248319.9814
86 | 2683295.3337 | 1248398.6236
87 | 2683305.776 | 1248446.725
88 | 2683274.0761 | 1248439.8332
89 | 2683292.5683 | 1248473.4972
90 | 2683257.7595 | 1248432.1682
91 | 2683285.4495 | 1248488.2176
92 | 2683388.7436 | 1248318.84
93 | 2683250.1151 | 1248485.9215
94 | 2683236.3629 | 1248517.0386
95 | 2683238.0056 | 1248534.4968
96 | 2683276.2692 | 1248499.6936
97 | 2683238.4641 | 1248423.9103
98 | 2683231.5884 | 1248420.9005
99 | 2683203.9118 | 1248474.8629
100 | 2683311.8911 | 1248279.5409
101 | 2683447.1304 | 1248147.5167
102 | 2683471.6058 | 1248149.3292
103 | 2683363.9124 | 1248149.3031
104 | 2683435.1531 | 1248120.6061
105 | 2683401.1267 | 1248167.929
106 | 2683351.1326 | 1248188.4668
107 | 2683439.7078 | 1248072.7002
108 | 2683407.1882 | 1248180.5013
109 | 2683443.9392 | 1248028.1948
110 | 2683453.3827 | 1248082.8641
111 | 2683458.3181 | 1248032.0667
112 | 2683139.1162 | 1247871.9426
113 | 2683068.7622 | 1247812.5017
114 | 2683049.6791 | 1247757.2715
115 | 2683153.942 | 1247867.158
116 | 2683182.4562 | 1247857.9392
117 | 2683227.2244 | 1247911.5855
118 | 2683220.2668 | 1247912.7554
119 | 2683193.1442 | 1247911.1291
120 | 2683221.6025 | 1247880.5726
121 | 2683185.3754 | 1247913.7817
122 | 2683204.7511 | 1247869.6306
123 | 2683155.0035 | 1247927.6842
124 | 2683178.9829 | 1247969.2067
125 | 2683131.4353 | 1247966.1265
126 | 2683126.4133 | 1247952.6128
127 | 2683137.3053 | 1247933.8677
128 | 2683187.1138 | 1247990.9812
129 | 2683129.432 | 1247966.8917
130 | 2683124.1419 | 1247953.4862
131 | 2683251.9317 | 1247834.064
132 | 2683270.4315 | 1247838.1943
133 | 2683199.3469 | 1247852.3728
134 | 2683242.8388 | 1247799.5776
135 | 2683299.819 | 1247844.7555
136 | 2683226.7115 | 1247760.4224
137 | 2683253.699 | 1247751.8171
138 | 2683197.4211 | 1247738.6566
139 | 2683251.9288 | 1247738.0998
140 | 2683243.6104 | 1247795.829
141 | 2683305.3831 | 1247819.6818
142 | 2683169.8522 | 1247803.4631
143 | 2683146.9025 | 1247784.4371
144 | 2683173.7857 | 1247719.572
145 | 2683250.0241 | 1247711.2467
146 | 2683107.0253 | 1247944.5129
147 | 2683170.748 | 1248195.3691
148 | 2683470.3861 | 1247739.932
149 | 2683523.6719 | 1247778.6664
150 | 2683528.9119 | 1247638.4034
151 | 2683486.9203 | 1247737.7743
152 | 2683418.5965 | 1247654.9629
153 | 2683533.6062 | 1247640.8269
154 | 2683421.3661 | 1247673.3821
155 | 2683134.0935 | 1247796.0273
156 | 2683131.5867 | 1247786.2739
157 | 2683029.7987 | 1247764.0677
158 | 2683073.2524 | 1247749.4573
159 | 2683032.6353 | 1247707.4137
160 | 2683150.7958 | 1247705.9618
161 | 2683150.3204 | 1247686.2082
162 | 2683090.5779 | 1247950.9168
163 | 2683237.3065 | 1247712.7137
164 | 2683211.288 | 1247705.3742
165 | 2683460.1199 | 1248012.4664
166 | 2683420.6326 | 1248007.1625
167 | 2683423.5612 | 1247985.0849
168 | 2683181.9476 | 1248200.1868
169 | 2683309.8898 | 1247793.5745
170 | 2683420.6326 | 1248007.1625

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99846 | -0.025466 | 0.34861 | 0.16884
1 | 0.99837 | -0.027624 | 0 | 0
2 | 0.99871 | -0.011725 | 0.34635 | 0.16774
3 | 0.99808 | -0.024946 | 0 | 0
4 | 0.9983 | -0.02691 | 0 | 0
5 | 0.99876 | -0.011552 | 0.17602 | 0.085251
6 | 0.99808 | -0.024926 | 0.40197 | 0.19468
7 | 0.99779 | -0.026826 | 0.11731 | 0.056814
8 | 0.99828 | -0.026788 | 0 | 0
9 | 0.99825 | -0.026526 | 0.27715 | 0.13423
10 | 0.99827 | -0.026694 | 0.26241 | 0.12709
11 | 0.99773 | -0.02629 | 0 | 0
12 | 0.99822 | -0.026227 | 0 | 0
13 | 0.99901 | -0.0069501 | 0.24177 | 0.1171
14 | 0.99902 | -0.0070481 | 0 | 0
15 | 0.99901 | -0.0069319 | 0 | 0
16 | 0.99908 | -0.0075521 | 0 | 0
17 | 0.999 | -0.0068962 | 0.12517 | 0.060622
18 | 0.99938 | -0.0090955 | 0 | 0
19 | 0.99938 | -0.009084 | 0.079648 | 0.038575
20 | 0.99909 | -0.010244 | 0 | 0
21 | 0.99954 | -0.0084244 | 0 | 0
22 | 0.99918 | -0.0073784 | 0 | 0
23 | 0.99902 | -0.010553 | 0 | 0
24 | 0.99909 | -0.010174 | 0.1315 | 0.063688
25 | 0.99958 | -0.0082731 | 0 | 0
26 | 0.99954 | -0.0084046 | 0.10653 | 0.051593
27 | 0.99908 | -0.0075929 | 0.23744 | 0.115
28 | 0.99911 | -0.0066982 | 0 | 0
29 | 0.99915 | -0.0076123 | 0.37317 | 0.18073
30 | 0.99899 | -0.010661 | 0.070374 | 0.034084
31 | 0.99966 | -0.007922 | 0.11312 | 0.054785
32 | 0.99912 | -0.0073441 | 0.076661 | 0.037129
33 | 0.99913 | -0.0074702 | 0 | 0
34 | 0.99921 | -0.0080795 | 0.33695 | 0.16319
35 | 0.99922 | -0.0081858 | 0 | 0
36 | 0.99907 | -0.0067783 | 0.080165 | 0.038826
37 | 0.99942 | -0.0060949 | 0 | 0
38 | 0.99891 | -0.005355 | 0 | 0
39 | 0.99949 | -0.0058192 | 0 | 0
40 | 0.99942 | -0.0060848 | 0.11331 | 0.054877
41 | 0.99948 | -0.0056742 | 0 | 0
42 | 0.99959 | -0.0054358 | 0 | 0
43 | 0.99949 | -0.0058085 | 0.18808 | 0.091094
44 | 0.99963 | -0.005283 | 0.36927 | 0.17884
45 | 0.99943 | -0.0064881 | 0.25244 | 0.12226
46 | 0.9989 | -0.0052416 | 0 | 0
47 | 0.99888 | -0.0050505 | 0.27794 | 0.13461
48 | 0.99837 | -0.0088666 | 0.13174 | 0.063803
49 | 0.99791 | -0.0046617 | 0.25832 | 0.12511
50 | 0.99793 | -0.0048139 | 0 | 0
51 | 0.99784 | -0.0039899 | 0.069726 | 0.03377
52 | 0.99795 | -0.0050287 | 0 | 0
53 | 0.99749 | -0.0062608 | 0 | 0
54 | 0.99808 | -0.0062061 | 0.3273 | 0.15852
55 | 0.99836 | -0.0089752 | 0.15822 | 0.076628
56 | 0.99947 | -0.0056149 | 0 | 0
57 | 0.99947 | -0.0055737 | 0.11729 | 0.056808
58 | 0.99947 | -0.0056489 | 0.36291 | 0.17577
59 | 0.99963 | -0.0052639 | 0 | 0
60 | 0.99936 | -0.0069122 | 0.35885 | 0.1738
61 | 0.99926 | -0.0060176 | 0 | 0
62 | 0.99927 | -0.0060897 | 0 | 0
63 | 0.99926 | -0.0059757 | 0.12392 | 0.060017
64 | 0.99927 | -0.0061105 | 0.33435 | 0.16193
65 | 0.99769 | -0.025912 | 0 | 0
66 | 0.99731 | -0.022358 | 0 | 0
67 | 0.99729 | -0.022228 | 0 | 0
68 | 0.99724 | -0.021741 | 0.13298 | 0.064404
69 | 0.99729 | -0.022157 | 0.19662 | 0.095227
70 | 0.99714 | -0.02083 | 0 | 0
71 | 0.99934 | -0.0067449 | 0 | 0
72 | 0.99932 | -0.0065482 | 0 | 0
73 | 0.99931 | -0.0064389 | 0.096701 | 0.046834
74 | 0.99929 | -0.0063165 | 0 | 0
75 | 0.99928 | -0.0061942 | 0 | 0
76 | 0.99749 | -0.0061871 | 0 | 0
77 | 0.99736 | -0.0050547 | 0 | 0
78 | 0.99748 | -0.006174 | 0.32139 | 0.15566
79 | 0.99735 | -0.0049142 | 0 | 0
80 | 0.99734 | -0.0048123 | 0.17937 | 0.086875
81 | 0.99733 | -0.0047823 | 0.37875 | 0.18344
82 | 0.9973 | -0.0044863 | 0.078495 | 0.038017
83 | 0.99727 | -0.0042526 | 0 | 0
84 | 0.99728 | -0.0042843 | 0 | 0
85 | 0.99727 | -0.0042219 | 0.30721 | 0.14879
86 | 0.99732 | -0.0047103 | 0 | 0
87 | 0.99729 | -0.0044453 | 0.13035 | 0.063133
88 | 0.99731 | -0.0046026 | 0 | 0
89 | 0.99727 | -0.0041904 | 0.13098 | 0.063435
90 | 0.99731 | -0.0045598 | 0.10543 | 0.051064
91 | 0.99725 | -0.004076 | 0 | 0
92 | 0.99728 | -0.0042663 | 0.18454 | 0.089377
93 | 0.99718 | -0.0033925 | 0.47155 | 0.22838
94 | 0.9972 | -0.0035858 | 0 | 0
95 | 0.99721 | -0.0036843 | 0 | 0
96 | 0.99724 | -0.0039722 | 0.12615 | 0.061095
97 | 0.9973 | -0.004536 | 0 | 0
98 | 0.9973 | -0.0045274 | 0 | 0
99 | 0.99729 | -0.0044542 | 0.1042 | 0.050467
100 | 0.99944 | -0.0058425 | 0.094464 | 0.045751
101 | 0.99969 | -0.0050221 | 0.27744 | 0.13437
102 | 0.99966 | -0.0051287 | 0 | 0
103 | 0.99966 | -0.0052248 | 0 | 0
104 | 0.99976 | -0.00096908 | 0 | 0
105 | 0.99967 | -0.0051664 | 0 | 0
106 | 0.99965 | -0.0051303 | 0.1941 | 0.094007
107 | 0.99982 | -0.00073774 | 0.37632 | 0.18226
108 | 0.99966 | -0.0051203 | 0.23413 | 0.11339
109 | 0.99988 | -0.00051114 | 0 | 0
110 | 0.99981 | -0.00060905 | 0.19424 | 0.094072
111 | 0.99982 | -0.00072571 | 0 | 0
112 | 0.99878 | -0.011465 | 0 | 0
113 | 0.99821 | -0.026164 | 0.36937 | 0.17889
114 | 0.99819 | -0.025964 | 0 | 0
115 | 0.99879 | -0.011408 | 0 | 0
116 | 0.99882 | -0.011298 | 0.28853 | 0.13974
117 | 0.99896 | -0.010788 | 0.35543 | 0.17214
118 | 0.99895 | -0.010823 | 0 | 0
119 | 0.99894 | -0.010761 | 0 | 0
120 | 0.99889 | -0.011028 | 0 | 0
121 | 0.99894 | -0.010746 | 0.15039 | 0.072835
122 | 0.99887 | -0.01113 | 0.11567 | 0.056023
123 | 0.99663 | -0.016067 | 0 | 0
124 | 0.99651 | -0.014926 | 0 | 0
125 | 0.99685 | -0.018111 | 0 | 0
126 | 0.99662 | -0.015912 | 0 | 0
127 | 0.99661 | -0.0159 | 0.67418 | 0.32652
128 | 0.99646 | -0.014442 | 1.6429 | 0.79567
129 | 0.99685 | -0.018103 | 0.27961 | 0.13542
130 | 0.99662 | -0.015905 | 0.24419 | 0.11827
131 | 0.99881 | -0.010922 | 0 | 0
132 | 0.9988 | -0.010853 | 0.1515 | 0.073375
133 | 0.99884 | -0.011218 | 0 | 0
134 | 0.9988 | -0.010848 | 0 | 0
135 | 0.9988 | -0.010797 | 0 | 0
136 | 0.99851 | -0.011873 | 0 | 0
137 | 0.9985 | -0.011706 | 0 | 0
138 | 0.99854 | -0.012057 | 0.21718 | 0.10519
139 | 0.99849 | -0.011635 | 0.26004 | 0.12594
140 | 0.9988 | -0.010843 | 0.10865 | 0.052622
141 | 0.99879 | -0.010748 | 0 | 0
142 | 0.99871 | -0.012033 | 0.13931 | 0.067469
143 | 0.99864 | -0.011371 | 0.10429 | 0.050508
144 | 0.99853 | -0.012012 | 0 | 0
145 | 0.99848 | -0.011578 | 0 | 0
146 | 0.99661 | -0.015874 | 0 | 0
147 | 0.99642 | -0.014674 | 0 | 0
148 | 0.99906 | -0.0063212 | 0 | 0
149 | 0.99907 | -0.0069072 | 0.37903 | 0.18357
150 | 0.99885 | -0.0045683 | 0 | 0
151 | 0.99905 | -0.0063773 | 0.27782 | 0.13456
152 | 0.9987 | -0.0032715 | 0 | 0
153 | 0.99885 | -0.0045459 | 0.35478 | 0.17183
154 | 0.9987 | -0.0032071 | 0.28952 | 0.14022
155 | 0.99867 | -0.01164 | 0 | 0
156 | 0.99866 | -0.011536 | 0 | 0
157 | 0.99819 | -0.025941 | 0.093285 | 0.04518
158 | 0.99819 | -0.025938 | 0.089075 | 0.043141
159 | 0.99818 | -0.026024 | 0.09418 | 0.045614
160 | 0.99852 | -0.011938 | 0 | 0
161 | 0.99852 | -0.011906 | 0.13459 | 0.065184
162 | 0.99661 | -0.015858 | 0.073172 | 0.035439
163 | 0.99848 | -0.011552 | 0 | 0
164 | 0.99847 | -0.011493 | 0.17612 | 0.085299
165 | 0.99979 | -0.00087866 | 0.33703 | 0.16323
166 | 1 | 0 | -19.4804 | -9.1935
167 | 1 | 3.5295e-05 | 0.11928 | 0.057769
168 | 0.99642 | -0.014661 | 0.090304 | 0.043736
169 | 0.99879 | -0.010696 | 0.16486 | 0.079844
170 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 5.0456 | 2.4188 | -5.0452 | -2.4184 | 0.0003517 | 0.00038393 | 0.16177 | 0.16177 | 0.16177 | 0.99846 | -0.025466 | 0.99837 | -0.027624 | 46.2213
1 | -5.3942 | -2.5876 | 5.3949 | 2.5895 | 0.00072046 | 0.0018444 | 0.17297 | 0.17297 | 0.17297 | 0.99846 | -0.025466 | 0.99871 | -0.011725 | 26.8175
2 | 3.8596 | 1.8524 | -3.8584 | -1.8534 | 0.0012092 | -0.0010475 | 0.12379 | 0.1238 | 0.1238 | 0.99837 | -0.027624 | 0.99808 | -0.024946 | 56.274
3 | 1.1857 | 0.56606 | -1.1856 | -0.56727 | 0.00010014 | -0.0012066 | 0.037989 | 0.038005 | 0.038005 | 0.99837 | -0.027624 | 0.9983 | -0.02691 | 17.2748
4 | -5.7413 | -2.7572 | 5.7415 | 2.7558 | 0.00025699 | -0.0013934 | 0.1841 | 0.18408 | 0.1841 | 0.99871 | -0.011725 | 0.99876 | -0.011552 | 28.855
5 | 0.40197 | 0.19458 | -0.40197 | -0.19468 | 9.5632e-07 | -0.00010182 | 0.012917 | 0.012918 | 0.012918 | 0.99808 | -0.024946 | 0.99808 | -0.024926 | 5.8718
6 | 3.4564 | 1.6588 | -3.4555 | -1.6583 | 0.00095249 | 0.00054492 | 0.11089 | 0.11089 | 0.11089 | 0.99808 | -0.024946 | 0.99779 | -0.026826 | 52.8033
7 | 0.26241 | 0.12544 | -0.26241 | -0.12638 | 3.7398e-06 | -0.0009399 | 0.0084105 | 0.0084223 | 0.0084223 | 0.9983 | -0.02691 | 0.99828 | -0.026788 | 3.8283
8 | 0.92314 | 0.44183 | -0.92309 | -0.44267 | 4.1641e-05 | -0.00083476 | 0.029594 | 0.029605 | 0.029605 | 0.9983 | -0.02691 | 0.99825 | -0.026526 | 13.4567
9 | -5.9175 | -2.8411 | 5.9177 | 2.8382 | 0.00013207 | -0.0029031 | 0.18973 | 0.18969 | 0.18973 | 0.99876 | -0.011552 | 0.99878 | -0.011465 | 14.869
10 | 3.3381 | 1.6015 | -3.3379 | -1.6017 | 0.00020977 | -0.00026328 | 0.10712 | 0.10712 | 0.10712 | 0.99779 | -0.026826 | 0.99773 | -0.02629 | 48.6909
11 | 0.26241 | 0.12638 | -0.26241 | -0.12709 | 2.8465e-06 | -0.0007136 | 0.0084223 | 0.0084313 | 0.0084313 | 0.99828 | -0.026788 | 0.99827 | -0.026694 | 3.8324
12 | 0.64594 | 0.30844 | -0.64592 | -0.30938 | 2.2835e-05 | -0.00094248 | 0.0207 | 0.020712 | 0.020712 | 0.99825 | -0.026526 | 0.99822 | -0.026227 | 9.4143
13 | 3.3379 | 1.6017 | -3.3378 | -1.6019 | 0.0001479 | -0.00018559 | 0.10712 | 0.10712 | 0.10712 | 0.99773 | -0.02629 | 0.99769 | -0.025912 | 48.6922
14 | 0.27655 | 0.13082 | -0.27654 | -0.13278 | 8.6444e-06 | -0.0019601 | 0.0088472 | 0.0088716 | 0.0088716 | 0.99822 | -0.026227 | 0.99819 | -0.025964 | 4.0326
15 | 0.36937 | 0.17856 | -0.36937 | -0.17889 | 2.6627e-06 | -0.00033619 | 0.011864 | 0.011869 | 0.011869 | 0.99822 | -0.026227 | 0.99821 | -0.026164 | 5.3949
16 | -0.24177 | -0.1171 | 0.24177 | 0.11628 | 2.7404e-06 | -0.00081202 | 0.0077625 | 0.0077523 | 0.0077625 | 0.99901 | -0.0069501 | 0.99902 | -0.0070481 | 3.5284
17 | 0.12517 | 0.058072 | -0.12517 | -0.060049 | 1.7721e-06 | -0.001977 | 0.0039872 | 0.0040116 | 0.0040116 | 0.99902 | -0.0070481 | 0.99901 | -0.0069319 | 1.8235
18 | -0.36695 | -0.17436 | 0.36697 | 0.17143 | 2.26e-05 | -0.0029298 | 0.011739 | 0.011703 | 0.011739 | 0.99902 | -0.0070481 | 0.99908 | -0.0075521 | 5.336
19 | 0.12517 | 0.060049 | -0.12517 | -0.060622 | 5.1841e-07 | -0.00057379 | 0.0040116 | 0.0040188 | 0.0040188 | 0.99901 | -0.0069319 | 0.999 | -0.0068962 | 1.8267
20 | -0.36697 | -0.17143 | 0.36697 | 0.17118 | 1.8737e-06 | -0.00024372 | 0.011703 | 0.0117 | 0.011703 | 0.99908 | -0.0075521 | 0.99908 | -0.0075929 | 5.3196
21 | 0.079648 | 0.038286 | -0.079648 | -0.038575 | 1.0557e-07 | -0.00028899 | 0.0025527 | 0.0025563 | 0.0025563 | 0.99938 | -0.0090955 | 0.99938 | -0.009084 | 1.162
22 | 8.4911 | 4.0124 | -8.4888 | -4.0368 | 0.0023413 | -0.024489 | 0.27127 | 0.27159 | 0.27159 | 0.99938 | -0.0090955 | 0.99909 | -0.010244 | 21.2847
23 | -10.9271 | -5.1641 | 10.9288 | 5.1536 | 0.0017193 | -0.010498 | 0.34911 | 0.34897 | 0.34911 | 0.99938 | -0.0090955 | 0.99954 | -0.0084244 | 27.3594
24 | 2.3563 | 1.1135 | -2.3558 | -1.1149 | 0.00049016 | -0.0013989 | 0.07528 | 0.075299 | 0.075299 | 0.99938 | -0.0090955 | 0.99918 | -0.0073784 | 34.2268
25 | 8.3573 | 3.9742 | -8.3566 | -3.9811 | 0.00063375 | -0.006837 | 0.26739 | 0.26747 | 0.26747 | 0.99909 | -0.010244 | 0.99902 | -0.010553 | 20.962
26 | 0.1315 | 0.062599 | -0.1315 | -0.063688 | 1.0839e-06 | -0.0010889 | 0.0042081 | 0.0042217 | 0.0042217 | 0.99909 | -0.010244 | 0.99909 | -0.010174 | 1.919
27 | -11.0353 | -5.2048 | 11.0357 | 5.2025 | 0.00038919 | -0.0023281 | 0.35238 | 0.35235 | 0.35238 | 0.99954 | -0.0084244 | 0.99958 | -0.0082731 | 27.6159
28 | 0.10653 | 0.051219 | -0.10653 | -0.051593 | 2.4452e-07 | -0.00037433 | 0.0034137 | 0.0034184 | 0.0034184 | 0.99954 | -0.0084244 | 0.99954 | -0.0084046 | 1.5538
29 | 1.3015 | 0.61166 | -1.3014 | -0.61275 | 0.0001086 | -0.0010906 | 0.041548 | 0.041561 | 0.041561 | 0.99918 | -0.0073784 | 0.99911 | -0.0066982 | 18.8916
30 | 1.0543 | 0.50319 | -1.0543 | -0.50319 | 3.5434e-05 | 1.3881e-06 | 0.033752 | 0.033752 | 0.033752 | 0.99918 | -0.0073784 | 0.99915 | -0.0076123 | 16.0723
31 | 8.3566 | 3.9811 | -8.3564 | -3.9835 | 0.00022206 | -0.0023942 | 0.26747 | 0.26751 | 0.26751 | 0.99902 | -0.010553 | 0.99899 | -0.010661 | 20.9644
32 | -11.0357 | -5.2025 | 11.0366 | 5.1971 | 0.0008987 | -0.0053785 | 0.35235 | 0.35227 | 0.35235 | 0.99958 | -0.0082731 | 0.99966 | -0.007922 | 27.6134
33 | -0.60441 | -0.28618 | 0.60443 | 0.28615 | 2.1011e-05 | -2.4479e-05 | 0.019322 | 0.019322 | 0.019322 | 0.99908 | -0.0075929 | 0.99912 | -0.0073441 | 9.2012
34 | 0.92236 | 0.42923 | -0.92232 | -0.43012 | 4.3643e-05 | -0.00088843 | 0.029394 | 0.029405 | 0.029405 | 0.99911 | -0.0066982 | 0.99906 | -0.0063212 | 13.3661
35 | 0.37904 | 0.18353 | -0.37903 | -0.18357 | 1.201e-05 | -4.6725e-05 | 0.012168 | 0.012169 | 0.012169 | 0.99911 | -0.0066982 | 0.99907 | -0.0069072 | 5.7946
36 | 0.68111 | 0.32246 | -0.6811 | -0.3229 | 1.1679e-05 | -0.00043627 | 0.021773 | 0.021778 | 0.021778 | 0.99915 | -0.0076123 | 0.99913 | -0.0074702 | 9.8992
37 | 8.286 | 3.9494 | -8.2858 | -3.9523 | 0.00026134 | -0.0028674 | 0.26525 | 0.26528 | 0.26528 | 0.99899 | -0.010661 | 0.99896 | -0.010788 | 20.7903
38 | -11.1497 | -5.2519 | 11.1505 | 5.2538 | 0.00075514 | 0.0019384 | 0.3559 | 0.3559 | 0.3559 | 0.99966 | -0.007922 | 0.99979 | -0.00087866 | 27.5895
39 | -0.68109 | -0.32328 | 0.6811 | 0.3229 | 1.0324e-05 | -0.00038547 | 0.021783 | 0.021778 | 0.021783 | 0.99912 | -0.0073441 | 0.99913 | -0.0074702 | 9.9014
40 | -0.33695 | -0.16319 | 0.33695 | 0.16256 | 4.1309e-06 | -0.00062976 | 0.010816 | 0.010808 | 0.010816 | 0.99921 | -0.0080795 | 0.99922 | -0.0081858 | 4.9164
41 | 3.8279 | 1.832 | -3.8273 | -1.8325 | 0.00063483 | -0.0005657 | 0.1226 | 0.12261 | 0.12261 | 0.99922 | -0.0081858 | 0.99907 | -0.0067783 | 55.7321
42 | -4.1649 | -1.9945 | 4.1657 | 1.9921 | 0.00075281 | -0.002454 | 0.13341 | 0.13337 | 0.13341 | 0.99922 | -0.0081858 | 0.99942 | -0.0060949 | 36.8534
43 | 3.7471 | 1.7937 | -3.7465 | -1.7943 | 0.00062808 | -0.00059165 | 0.12004 | 0.12005 | 0.12005 | 0.99907 | -0.0067783 | 0.99891 | -0.005355 | 54.5667
44 | -4.279 | -2.0468 | 4.2793 | 2.0342 | 0.00029304 | -0.012534 | 0.13701 | 0.13685 | 0.13701 | 0.99942 | -0.0060949 | 0.99949 | -0.0058192 | 10.7372
45 | 0.11331 | 0.054697 | -0.11331 | -0.054877 | 1.3303e-07 | -0.00017977 | 0.0036342 | 0.0036364 | 0.0036364 | 0.99942 | -0.0060949 | 0.99942 | -0.0060848 | 1.6529
46 | 3.4686 | 1.6619 | -3.4668 | -1.6609 | 0.0017745 | 0.0010155 | 0.11115 | 0.11115 | 0.11115 | 0.99891 | -0.005355 | 0.99837 | -0.0088666 | 52.929
47 | 0.27795 | 0.13239 | -0.27794 | -0.13323 | 3.7273e-06 | -0.00083822 | 0.008897 | 0.0089074 | 0.0089074 | 0.99891 | -0.005355 | 0.9989 | -0.0052416 | 4.0488
48 | 0.57469 | 0.27573 | -0.57468 | -0.27624 | 9.748e-06 | -0.0005108 | 0.01841 | 0.018416 | 0.018416 | 0.99949 | -0.0058192 | 0.99948 | -0.0056742 | 8.371
49 | -5.042 | -2.4009 | 5.0425 | 2.3866 | 0.00046786 | -0.014367 | 0.16129 | 0.16111 | 0.16129 | 0.99949 | -0.0058192 | 0.99959 | -0.0054358 | 12.6405
50 | 0.18809 | 0.09098 | -0.18808 | -0.091094 | 2.3145e-07 | -0.00011347 | 0.0060345 | 0.0060359 | 0.0060359 | 0.99949 | -0.0058192 | 0.99949 | -0.0058085 | 2.7436
51 | 0.45738 | 0.22121 | -0.45738 | -0.22132 | 1.3306e-06 | -0.00010999 | 0.014674 | 0.014676 | 0.014676 | 0.99948 | -0.0056742 | 0.99947 | -0.0056489 | 6.6708
52 | 0.11729 | 0.05503 | -0.11729 | -0.056096 | 8.3878e-07 | -0.0010662 | 0.0037421 | 0.0037553 | 0.0037553 | 0.99948 | -0.0056742 | 0.99947 | -0.0056149 | 1.7069
53 | -6.209 | -2.9459 | 6.2093 | 2.9413 | 0.00022786 | -0.0045743 | 0.19847 | 0.19841 | 0.19847 | 0.99959 | -0.0054358 | 0.99963 | -0.005283 | 15.5543
54 | 1.1665 | 0.55935 | -1.1664 | -0.55932 | 0.00017943 | 2.6349e-05 | 0.037362 | 0.037363 | 0.037363 | 0.99959 | -0.0054358 | 0.99943 | -0.0064881 | 17.7918
55 | -6.5785 | -3.1202 | 6.5786 | 3.1196 | 3.0122e-05 | -0.0005368 | 0.21026 | 0.21026 | 0.21026 | 0.99963 | -0.005283 | 0.99963 | -0.0052639 | 16.4782
56 | 0.91393 | 0.43706 | -0.91387 | -0.43707 | 5.6108e-05 | -8.7093e-06 | 0.029261 | 0.029262 | 0.029262 | 0.99943 | -0.0064881 | 0.99936 | -0.0069122 | 13.9342
57 | 0.27794 | 0.13323 | -0.27794 | -0.13461 | 6.1684e-06 | -0.0013828 | 0.0089074 | 0.0089248 | 0.0089248 | 0.9989 | -0.0052416 | 0.99888 | -0.0050505 | 4.0567
58 | 0.15822 | 0.076563 | -0.15822 | -0.076628 | 2.6018e-06 | -6.5629e-05 | 0.0050823 | 0.0050832 | 0.0050832 | 0.99837 | -0.0088666 | 0.99836 | -0.0089752 | 2.4206
59 | 3.1768 | 1.5205 | -3.1758 | -1.5219 | 0.00099467 | -0.0014139 | 0.10184 | 0.10186 | 0.10186 | 0.99837 | -0.0088666 | 0.99808 | -0.0062061 | 46.2989
60 | -2.848 | -1.3644 | 2.8481 | 1.3643 | 5.0981e-05 | -9.3681e-05 | 0.091353 | 0.091352 | 0.091353 | 0.99791 | -0.0046617 | 0.99793 | -0.0048139 | 41.5242
61 | 2.5897 | 1.2393 | -2.5895 | -1.2397 | 0.00020507 | -0.0004686 | 0.083051 | 0.083057 | 0.083057 | 0.99791 | -0.0046617 | 0.99784 | -0.0039899 | 37.7533
62 | -2.8481 | -1.3643 | 2.8482 | 1.3641 | 7.2001e-05 | -0.00013232 | 0.091352 | 0.09135 | 0.091352 | 0.99793 | -0.0048139 | 0.99795 | -0.0050287 | 41.5236
63 | 2.5198 | 1.206 | -2.519 | -1.2055 | 0.00083049 | 0.00043539 | 0.080816 | 0.080817 | 0.080817 | 0.99784 | -0.0039899 | 0.99749 | -0.0062608 | 38.4843
64 | -2.8482 | -1.3641 | 2.8485 | 1.3634 | 0.00039494 | -0.00072604 | 0.09135 | 0.091339 | 0.09135 | 0.99795 | -0.0050287 | 0.99808 | -0.0062061 | 41.5227
65 | 0.3214 | 0.15512 | -0.32139 | -0.15558 | 2.7312e-06 | -0.00045458 | 0.010328 | 0.010334 | 0.010334 | 0.99749 | -0.0062608 | 0.99749 | -0.0061871 | 4.6971
66 | 2.1976 | 1.0504 | -2.1972 | -1.0514 | 0.00031295 | -0.0010276 | 0.070489 | 0.070503 | 0.070503 | 0.99749 | -0.0062608 | 0.99736 | -0.0050547 | 32.0468
67 | 0.11729 | 0.056096 | -0.11729 | -0.056808 | 5.6348e-07 | -0.000712 | 0.0037553 | 0.0037642 | 0.0037642 | 0.99947 | -0.0056149 | 0.99947 | -0.0055737 | 1.711
68 | 0.094467 | 0.045552 | -0.094464 | -0.045751 | 2.7517e-06 | -0.00019884 | 0.0030291 | 0.0030316 | 0.0030316 | 0.99947 | -0.0056489 | 0.99944 | -0.0058425 | 1.4436
69 | -6.5786 | -3.1196 | 6.5788 | 3.1158 | 0.0002132 | -0.0038008 | 0.21026 | 0.21021 | 0.21026 | 0.99963 | -0.0052639 | 0.99966 | -0.0051287 | 16.4777
70 | 0.55502 | 0.26327 | -0.55501 | -0.26389 | 1.1139e-05 | -0.00062828 | 0.017744 | 0.017752 | 0.017752 | 0.99936 | -0.0069122 | 0.99934 | -0.0067449 | 8.0692
71 | -0.12392 | -0.059333 | 0.12392 | 0.058108 | 1.0772e-06 | -0.0012255 | 0.0039691 | 0.0039539 | 0.0039691 | 0.99926 | -0.0060176 | 0.99927 | -0.0060897 | 1.8041
72 | 0.12392 | 0.059333 | -0.12392 | -0.060017 | 6.0456e-07 | -0.00068367 | 0.0039691 | 0.0039777 | 0.0039777 | 0.99926 | -0.0060176 | 0.99926 | -0.0059757 | 1.808
73 | -0.12392 | -0.058108 | 0.12392 | 0.057741 | 3.205e-07 | -0.00036643 | 0.0039539 | 0.0039494 | 0.0039539 | 0.99927 | -0.0060897 | 0.99927 | -0.0061105 | 1.7972
74 | -0.45827 | -0.21967 | 0.45827 | 0.2193 | 4.5162e-06 | -0.00037299 | 0.014681 | 0.014676 | 0.014681 | 0.99927 | -0.0061105 | 0.99928 | -0.0061942 | 6.6732
75 | 3.3378 | 1.6019 | -3.3364 | -1.6036 | 0.0013869 | -0.0017388 | 0.10712 | 0.10715 | 0.10715 | 0.99769 | -0.025912 | 0.99731 | -0.022358 | 48.7045
76 | 0.19662 | 0.09315 | -0.19662 | -0.094512 | 3.0476e-06 | -0.0013623 | 0.0062977 | 0.0063147 | 0.0063147 | 0.99731 | -0.022358 | 0.99729 | -0.022228 | 2.8703
77 | 3.1398 | 1.5105 | -3.1396 | -1.5108 | 0.00022558 | -0.00032756 | 0.10085 | 0.10086 | 0.10086 | 0.99731 | -0.022358 | 0.99724 | -0.021741 | 45.8442
78 | 0.19662 | 0.094512 | -0.19662 | -0.095227 | 1.6054e-06 | -0.00071464 | 0.0063147 | 0.0063237 | 0.0063237 | 0.99729 | -0.022228 | 0.99729 | -0.022157 | 2.8744
79 | 3.0066 | 1.4464 | -3.0063 | -1.4469 | 0.00031913 | -0.00051375 | 0.09658 | 0.096588 | 0.096588 | 0.99724 | -0.021741 | 0.99714 | -0.02083 | 43.9035
80 | 3.0063 | 1.4469 | -3.0053 | -1.4485 | 0.00094993 | -0.001528 | 0.096588 | 0.09661 | 0.09661 | 0.99714 | -0.02083 | 0.99685 | -0.018111 | 43.9139
81 | 0.55501 | 0.26389 | -0.55499 | -0.26463 | 1.3022e-05 | -0.00073379 | 0.017752 | 0.017761 | 0.017761 | 0.99934 | -0.0067449 | 0.99932 | -0.0065482 | 8.0734
82 | 0.55499 | 0.26463 | -0.55499 | -0.26503 | 7.1966e-06 | -0.00040518 | 0.017761 | 0.017766 | 0.017766 | 0.99932 | -0.0065482 | 0.99931 | -0.0064389 | 8.0757
83 | 0.45828 | 0.2182 | -0.45828 | -0.21875 | 6.6761e-06 | -0.00055235 | 0.014663 | 0.01467 | 0.01467 | 0.99931 | -0.0064389 | 0.99929 | -0.0063165 | 6.668
84 | 0.45828 | 0.21875 | -0.45827 | -0.2193 | 6.6242e-06 | -0.00054752 | 0.01467 | 0.014676 | 0.014676 | 0.99929 | -0.0063165 | 0.99928 | -0.0061942 | 6.6711
85 | 0.32139 | 0.15558 | -0.32139 | -0.15566 | 4.8631e-07 | -8.0888e-05 | 0.010334 | 0.010335 | 0.010335 | 0.99749 | -0.0061871 | 0.99748 | -0.006174 | 4.6976
86 | 1.4476 | 0.69157 | -1.4475 | -0.69176 | 2.4057e-05 | -0.00019134 | 0.046434 | 0.046437 | 0.046437 | 0.99736 | -0.0050547 | 0.99735 | -0.0049142 | 21.1076
87 | 0.74967 | 0.35985 | -0.74965 | -0.3605 | 2.1233e-05 | -0.00064553 | 0.024069 | 0.024077 | 0.024077 | 0.99736 | -0.0050547 | 0.99734 | -0.0048123 | 10.9441
88 | 1.4475 | 0.69176 | -1.4475 | -0.69194 | 2.2582e-05 | -0.00017959 | 0.046437 | 0.046439 | 0.046439 | 0.99735 | -0.0049142 | 0.99733 | -0.0047823 | 21.1087
89 | 0.57028 | 0.27362 | -0.57025 | -0.27477 | 2.1691e-05 | -0.0011438 | 0.018308 | 0.018323 | 0.018323 | 0.99734 | -0.0048123 | 0.9973 | -0.0044863 | 8.3284
90 | 0.20964 | 0.097132 | -0.20964 | -0.097887 | 1.9019e-06 | -0.00075486 | 0.0066877 | 0.0066969 | 0.0066969 | 0.99733 | -0.0047823 | 0.99732 | -0.0047103 | 3.0441
91 | 0.85913 | 0.41137 | -0.8591 | -0.41216 | 3.4019e-05 | -0.00078569 | 0.027571 | 0.027581 | 0.027581 | 0.99733 | -0.0047823 | 0.99729 | -0.0044453 | 12.5368
92 | 0.49176 | 0.23675 | -0.49175 | -0.23757 | 1.151e-05 | -0.00081637 | 0.015798 | 0.015808 | 0.015808 | 0.9973 | -0.0044863 | 0.99728 | -0.0042843 | 7.1856
93 | -0.30721 | -0.14859 | 0.30721 | 0.14838 | 1.1218e-06 | -0.00020422 | 0.0098781 | 0.0098755 | 0.0098781 | 0.99727 | -0.0042526 | 0.99728 | -0.0042843 | 4.49
94 | 0.30721 | 0.14859 | -0.30721 | -0.14879 | 1.0865e-06 | -0.0001977 | 0.0098781 | 0.0098806 | 0.0098806 | 0.99727 | -0.0042526 | 0.99727 | -0.0042219 | 4.4912
95 | 0.18454 | 0.089184 | -0.18454 | -0.089377 | 3.8228e-07 | -0.00019298 | 0.0059329 | 0.0059353 | 0.0059353 | 0.99728 | -0.0042843 | 0.99728 | -0.0042663 | 2.6979
96 | 0.20964 | 0.097887 | -0.20964 | -0.098987 | 2.7805e-06 | -0.0010998 | 0.0066969 | 0.0067105 | 0.0067105 | 0.99732 | -0.0047103 | 0.99731 | -0.0046026 | 3.0502
97 | 0.72875 | 0.34903 | -0.72872 | -0.34973 | 2.181e-05 | -0.00070247 | 0.023389 | 0.023398 | 0.023398 | 0.99729 | -0.0044453 | 0.99727 | -0.0041904 | 10.6352
98 | 0.20964 | 0.098987 | -0.20964 | -0.099415 | 1.0851e-06 | -0.000428 | 0.0067105 | 0.0067158 | 0.0067158 | 0.99731 | -0.0046026 | 0.99731 | -0.0045598 | 3.0526
99 | 0.59775 | 0.28629 | -0.59774 | -0.28668 | 8.0365e-06 | -0.00038589 | 0.019185 | 0.01919 | 0.01919 | 0.99727 | -0.0041904 | 0.99725 | -0.004076 | 8.7227
100 | 0.1042 | 0.048351 | -0.1042 | -0.048849 | 3.1037e-07 | -0.00049834 | 0.0033251 | 0.0033312 | 0.0033312 | 0.99731 | -0.0045598 | 0.9973 | -0.004536 | 1.5142
101 | 0.59774 | 0.28668 | -0.59773 | -0.28703 | 7.2689e-06 | -0.00034885 | 0.01919 | 0.019194 | 0.019194 | 0.99725 | -0.004076 | 0.99724 | -0.0039722 | 8.7246
102 | -0.47155 | -0.22838 | 0.47156 | 0.22757 | 1.0502e-05 | -0.00080926 | 0.015168 | 0.015158 | 0.015168 | 0.99718 | -0.0033925 | 0.9972 | -0.0035858 | 6.8945
103 | -0.47156 | -0.22757 | 0.47157 | 0.22716 | 5.3869e-06 | -0.00041554 | 0.015158 | 0.015152 | 0.015158 | 0.9972 | -0.0035858 | 0.99721 | -0.0036843 | 6.8898
104 | -0.47157 | -0.22716 | 0.47159 | 0.22593 | 1.5871e-05 | -0.001226 | 0.015152 | 0.015137 | 0.015152 | 0.99721 | -0.0036843 | 0.99724 | -0.0039722 | 6.8874
105 | 0.1042 | 0.048849 | -0.1042 | -0.049027 | 1.1099e-07 | -0.00017776 | 0.0033312 | 0.0033334 | 0.0033334 | 0.9973 | -0.004536 | 0.9973 | -0.0045274 | 1.5152
106 | 0.1042 | 0.049027 | -0.1042 | -0.050467 | 9.0442e-07 | -0.0014399 | 0.0033334 | 0.0033513 | 0.0033513 | 0.9973 | -0.0045274 | 0.99729 | -0.0044542 | 1.5233
107 | 6.5789 | 3.1129 | -6.5788 | -3.1158 | 0.00016702 | -0.002979 | 0.21017 | 0.21021 | 0.21021 | 0.99969 | -0.0050221 | 0.99966 | -0.0051287 | 16.4739
108 | 0.19411 | 0.092929 | -0.1941 | -0.093025 | 5.7284e-06 | -9.5716e-05 | 0.0062144 | 0.0062156 | 0.0062156 | 0.99969 | -0.0050221 | 0.99966 | -0.0052248 | 2.9598
109 | -7.2846 | -3.4531 | 7.2849 | 3.4538 | 0.00028493 | 0.00068481 | 0.23279 | 0.23279 | 0.23279 | 0.99969 | -0.0050221 | 0.99976 | -0.00096908 | 18.0458
110 | 0.23413 | 0.11294 | -0.23413 | -0.113 | 5.0532e-06 | -5.6879e-05 | 0.0075064 | 0.0075072 | 0.0075072 | 0.99969 | -0.0050221 | 0.99967 | -0.0051664 | 3.5749
111 | 0.1941 | 0.093025 | -0.1941 | -0.094007 | 2.1292e-06 | -0.0009824 | 0.0062156 | 0.006228 | 0.006228 | 0.99966 | -0.0052248 | 0.99965 | -0.0051303 | 2.8309
112 | -7.2849 | -3.4538 | 7.2853 | 3.448 | 0.00040277 | -0.0058179 | 0.23279 | 0.23272 | 0.23279 | 0.99976 | -0.00096908 | 0.99982 | -0.00073774 | 18.2437
113 | 0.23413 | 0.113 | -0.23413 | -0.11339 | 1.2437e-06 | -0.00039378 | 0.0075072 | 0.0075121 | 0.0075121 | 0.99967 | -0.0051664 | 0.99966 | -0.0051203 | 3.4146
114 | -7.6616 | -3.6302 | 7.662 | 3.6249 | 0.00041376 | -0.0053832 | 0.24479 | 0.24472 | 0.24479 | 0.99982 | -0.00073774 | 0.99988 | -0.00051114 | 19.184
115 | -19.3448 | -9.1295 | 19.3471 | 9.1258 | 0.0023113 | -0.0036273 | 0.61758 | 0.61752 | 0.61758 | 0.99988 | -0.00051114 | 1 | 0 | 48.3994
116 | 11.6827 | 5.5046 | -11.6822 | -5.5077 | 0.00058252 | -0.0030786 | 0.37286 | 0.3729 | 0.3729 | 0.99988 | -0.00051114 | 0.99982 | -0.00072571 | 29.2242
117 | -0.19424 | -0.094072 | 0.19424 | 0.092855 | 2.6391e-06 | -0.0012173 | 0.0062313 | 0.006216 | 0.0062313 | 0.99981 | -0.00060905 | 0.99982 | -0.00072571 | 2.8324
118 | 11.4879 | 5.4148 | -11.4875 | -5.4171 | 0.00040896 | -0.0022424 | 0.36668 | 0.36672 | 0.36672 | 0.99982 | -0.00072571 | 0.99979 | -0.00087866 | 28.7394
119 | -5.9177 | -2.8382 | 5.9178 | 2.8363 | 8.6596e-05 | -0.0019042 | 0.18969 | 0.18967 | 0.18969 | 0.99878 | -0.011465 | 0.99879 | -0.011408 | 14.8661
120 | 0.093285 | 0.04468 | -0.093285 | -0.04518 | 2.5149e-07 | -0.00049975 | 0.0029913 | 0.0029975 | 0.0029975 | 0.99819 | -0.025964 | 0.99819 | -0.025941 | 1.3625
121 | 0.089075 | 0.04255 | -0.089075 | -0.043141 | 2.7091e-07 | -0.00059073 | 0.0028549 | 0.0028623 | 0.0028623 | 0.99819 | -0.025964 | 0.99819 | -0.025938 | 1.301
122 | 0.094181 | 0.045551 | -0.09418 | -0.045614 | 8.5958e-07 | -6.2136e-05 | 0.0030255 | 0.0030263 | 0.0030263 | 0.99819 | -0.025964 | 0.99818 | -0.026024 | 1.4411
123 | -5.9178 | -2.8363 | 5.9179 | 2.8326 | 0.00016652 | -0.0036631 | 0.18967 | 0.18962 | 0.18967 | 0.99879 | -0.011408 | 0.99882 | -0.011298 | 14.8642
124 | 1.0318 | 0.4921 | -1.0317 | -0.49209 | 0.00010875 | 1.5291e-06 | 0.033039 | 0.03304 | 0.03304 | 0.99882 | -0.011298 | 0.99871 | -0.012033 | 15.7331
125 | -7.2383 | -3.4644 | 7.2384 | 3.4623 | 0.00014778 | -0.0021464 | 0.23192 | 0.2319 | 0.23192 | 0.99882 | -0.011298 | 0.99884 | -0.011218 | 18.1759
126 | 7.9303 | 3.7801 | -7.9303 | -3.781 | 7.0055e-05 | -0.00084274 | 0.25387 | 0.25388 | 0.25388 | 0.99896 | -0.010788 | 0.99895 | -0.010823 | 19.8968
127 | 0.15039 | 0.071802 | -0.15039 | -0.07264 | 1.091e-06 | -0.00083741 | 0.0048158 | 0.0048263 | 0.0048263 | 0.99895 | -0.010823 | 0.99894 | -0.010761 | 2.1938
128 | 7.7799 | 3.7092 | -7.7795 | -3.7141 | 0.00039769 | -0.0049778 | 0.24907 | 0.24913 | 0.24913 | 0.99895 | -0.010823 | 0.99889 | -0.011028 | 19.5244
129 | 0.15039 | 0.07264 | -0.15039 | -0.072835 | 2.554e-07 | -0.00019551 | 0.0048263 | 0.0048287 | 0.0048287 | 0.99894 | -0.010761 | 0.99894 | -0.010746 | 2.1949
130 | 7.7795 | 3.7141 | -7.7793 | -3.7166 | 0.00019829 | -0.0024807 | 0.24913 | 0.24916 | 0.24916 | 0.99889 | -0.011028 | 0.99887 | -0.01113 | 19.5269
131 | 7.6636 | 3.6606 | -7.6634 | -3.6628 | 0.00016835 | -0.0021725 | 0.24545 | 0.24548 | 0.24548 | 0.99887 | -0.01113 | 0.99884 | -0.011218 | 19.2381
132 | 1.7335 | 0.83712 | -1.7333 | -0.83835 | 0.00022825 | -0.0012359 | 0.055759 | 0.055775 | 0.055775 | 0.99663 | -0.016067 | 0.99651 | -0.014926 | 25.3523
133 | -2.7251 | -1.3144 | 2.7257 | 1.3131 | 0.00064599 | -0.0013033 | 0.087633 | 0.087614 | 0.087633 | 0.99663 | -0.016067 | 0.99685 | -0.018111 | 39.8333
134 | 0.2442 | 0.11694 | -0.24419 | -0.11821 | 4.414e-06 | -0.001271 | 0.0078424 | 0.0078583 | 0.0078583 | 0.99663 | -0.016067 | 0.99662 | -0.015912 | 3.572
135 | 0.74737 | 0.36034 | -0.74735 | -0.36078 | 1.4458e-05 | -0.00044031 | 0.024032 | 0.024038 | 0.024038 | 0.99663 | -0.016067 | 0.99661 | -0.0159 | 10.9263
136 | 1.7333 | 0.83835 | -1.7332 | -0.83888 | 9.6511e-05 | -0.00052226 | 0.055775 | 0.055782 | 0.055782 | 0.99651 | -0.014926 | 0.99646 | -0.014442 | 25.3554
137 | 0.27961 | 0.13537 | -0.27961 | -0.13542 | 2.3164e-07 | -5.081e-05 | 0.0089961 | 0.0089967 | 0.0089967 | 0.99685 | -0.018111 | 0.99685 | -0.018103 | 4.0894
138 | 0.24419 | 0.11821 | -0.24419 | -0.11827 | 2.0063e-07 | -5.7651e-05 | 0.0078583 | 0.0078591 | 0.0078591 | 0.99662 | -0.015912 | 0.99662 | -0.015905 | 3.5723
139 | 0.073173 | 0.034259 | -0.073172 | -0.03502 | 2.3563e-07 | -0.0007611 | 0.0023403 | 0.0023497 | 0.0023497 | 0.99661 | -0.0159 | 0.99661 | -0.015874 | 1.0681
140 | 0.090307 | 0.043206 | -0.090304 | -0.043447 | 3.076e-06 | -0.00024111 | 0.0029002 | 0.0029033 | 0.0029033 | 0.99646 | -0.014442 | 0.99642 | -0.014674 | 1.3825
141 | 0.31636 | 0.15081 | -0.31636 | -0.15126 | 2.5978e-06 | -0.00045073 | 0.010129 | 0.010135 | 0.010135 | 0.99881 | -0.010922 | 0.9988 | -0.010853 | 4.6067
142 | -0.42501 | -0.20193 | 0.42503 | 0.20047 | 1.5157e-05 | -0.0014597 | 0.0136 | 0.013581 | 0.0136 | 0.99881 | -0.010922 | 0.99884 | -0.011218 | 6.1816
143 | 0.10865 | 0.051118 | -0.10865 | -0.052531 | 9.5834e-07 | -0.0014123 | 0.0034704 | 0.003488 | 0.003488 | 0.99881 | -0.010922 | 0.9988 | -0.010848 | 1.5855
144 | 0.16486 | 0.077884 | -0.16486 | -0.078601 | 1.1182e-06 | -0.00071688 | 0.0052698 | 0.0052787 | 0.0052787 | 0.9988 | -0.010853 | 0.9988 | -0.010797 | 2.3994
145 | 0.10865 | 0.052531 | -0.10865 | -0.052622 | 6.2163e-08 | -9.1142e-05 | 0.003488 | 0.0034891 | 0.0034891 | 0.9988 | -0.010848 | 0.9988 | -0.010843 | 1.586
146 | 0.16486 | 0.078601 | -0.16486 | -0.079213 | 9.5678e-07 | -0.00061146 | 0.0052787 | 0.0052863 | 0.0052863 | 0.9988 | -0.010797 | 0.99879 | -0.010748 | 2.4029
147 | 0.43618 | 0.20849 | -0.43617 | -0.20927 | 8.5985e-06 | -0.00078178 | 0.013977 | 0.013986 | 0.013986 | 0.99851 | -0.011873 | 0.9985 | -0.011706 | 6.3575
148 | -0.43618 | -0.20849 | 0.43619 | 0.20762 | 9.5093e-06 | -0.0008659 | 0.013977 | 0.013966 | 0.013977 | 0.99851 | -0.011873 | 0.99854 | -0.012057 | 6.353
149 | 0.43617 | 0.20927 | -0.43617 | -0.2096 | 3.6133e-06 | -0.00032818 | 0.013986 | 0.013991 | 0.013991 | 0.9985 | -0.011706 | 0.99849 | -0.011635 | 6.3593
150 | -0.78796 | -0.37566 | 0.78804 | 0.37563 | 7.7357e-05 | -3.2705e-05 | 0.025236 | 0.025235 | 0.025236 | 0.99854 | -0.012057 | 0.99864 | -0.011371 | 12.0173
151 | 0.13459 | 0.062857 | -0.13459 | -0.063581 | 7.5038e-07 | -0.00072385 | 0.0042944 | 0.0043033 | 0.0043033 | 0.99854 | -0.012057 | 0.99853 | -0.012012 | 1.9561
152 | 0.17612 | 0.083653 | -0.17612 | -0.08432 | 1.1912e-06 | -0.00066705 | 0.0056371 | 0.0056454 | 0.0056454 | 0.99849 | -0.011635 | 0.99848 | -0.011578 | 2.5661
153 | 0.16486 | 0.079213 | -0.16486 | -0.079844 | 9.9028e-07 | -0.00063101 | 0.0052863 | 0.0052942 | 0.0052942 | 0.99879 | -0.010748 | 0.99879 | -0.010696 | 2.4065
154 | 0.8924 | 0.42463 | -0.89235 | -0.42553 | 4.181e-05 | -0.0009012 | 0.028566 | 0.028577 | 0.028577 | 0.99871 | -0.012033 | 0.99867 | -0.01164 | 12.9896
155 | -0.89233 | -0.42614 | 0.89234 | 0.42576 | 1.7502e-05 | -0.00037693 | 0.028585 | 0.02858 | 0.028585 | 0.99864 | -0.011371 | 0.99866 | -0.011536 | 12.9931
156 | 0.13459 | 0.063581 | -0.13459 | -0.064714 | 1.1811e-06 | -0.0011332 | 0.0043033 | 0.0043174 | 0.0043174 | 0.99853 | -0.012012 | 0.99852 | -0.011938 | 1.9625
157 | 0.17612 | 0.08432 | -0.17612 | -0.084624 | 5.4506e-07 | -0.00030458 | 0.0056454 | 0.0056492 | 0.0056492 | 0.99848 | -0.011578 | 0.99848 | -0.011552 | 2.5678
158 | 0.073172 | 0.03502 | -0.073172 | -0.035439 | 1.3038e-07 | -0.00041853 | 0.0023497 | 0.002355 | 0.002355 | 0.99661 | -0.015874 | 0.99661 | -0.015858 | 1.0704
159 | 0.090304 | 0.043447 | -0.090304 | -0.043736 | 1.3737e-07 | -0.00028897 | 0.0029033 | 0.0029069 | 0.0029069 | 0.99642 | -0.014674 | 0.99642 | -0.014661 | 1.3213
160 | 0.6445 | 0.29558 | -0.64435 | -0.30162 | 0.00014363 | -0.0060429 | 0.020488 | 0.020561 | 0.020561 | 0.99906 | -0.0063212 | 0.99885 | -0.0045683 | 9.3461
161 | 0.27782 | 0.13454 | -0.27782 | -0.13456 | 2.3635e-06 | -1.8388e-05 | 0.0089193 | 0.0089196 | 0.0089196 | 0.99906 | -0.0063212 | 0.99905 | -0.0063773 | 4.2474
162 | 0.28957 | 0.12992 | -0.28953 | -0.13978 | 4.7161e-05 | -0.0098585 | 0.0091726 | 0.009293 | 0.009293 | 0.99885 | -0.0045683 | 0.9987 | -0.0032715 | 4.2241
163 | 0.35478 | 0.1717 | -0.35478 | -0.17183 | 9.13e-07 | -0.00012527 | 0.011391 | 0.011393 | 0.011393 | 0.99885 | -0.0045683 | 0.99885 | -0.0045459 | 5.1785
164 | 0.28953 | 0.13978 | -0.28952 | -0.14022 | 2.1488e-06 | -0.00044295 | 0.009293 | 0.0092986 | 0.0092986 | 0.9987 | -0.0032715 | 0.9987 | -0.0032071 | 4.2266
165 | 0.89235 | 0.42553 | -0.89234 | -0.42576 | 1.098e-05 | -0.00023654 | 0.028577 | 0.02858 | 0.02858 | 0.99867 | -0.01164 | 0.99866 | -0.011536 | 12.9909
166 | 0.13459 | 0.064714 | -0.13459 | -0.065184 | 4.9237e-07 | -0.00047023 | 0.0043174 | 0.0043233 | 0.0043233 | 0.99852 | -0.011938 | 0.99852 | -0.011906 | 1.9652
167 | 0.17612 | 0.084624 | -0.17612 | -0.085299 | 1.2105e-06 | -0.00067495 | 0.0056492 | 0.0056577 | 0.0056577 | 0.99848 | -0.011552 | 0.99847 | -0.011493 | 2.5717
168 | 0.11928 | 0.057171 | -0.11928 | -0.057769 | 4.889e-07 | -0.00059839 | 0.0038184 | 0.0038259 | 0.0038259 | 1 | 0 | 1 | 3.5295e-05 | 1.739

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 19.4804 | 9.1935

## res_load
| p_mw | q_mvar
0 | 0.34861 | 0.16884
1 | 0.34635 | 0.16774
2 | 0.17602 | 0.085251
3 | 0.40197 | 0.19468
4 | 0.11731 | 0.056814
5 | 0.27715 | 0.13423
6 | 0.26241 | 0.12709
7 | 0.24177 | 0.1171
8 | 0.12517 | 0.060622
9 | 0.079648 | 0.038575
10 | 0.1315 | 0.063688
11 | 0.10653 | 0.051593
12 | 0.23744 | 0.115
13 | 0.37317 | 0.18073
14 | 0.070374 | 0.034084
15 | 0.11312 | 0.054785
16 | 0.076661 | 0.037129
17 | 0.33695 | 0.16319
18 | 0.080165 | 0.038826
19 | 0.11331 | 0.054877
20 | 0.18808 | 0.091094
21 | 0.36927 | 0.17884
22 | 0.25244 | 0.12226
23 | 0.27794 | 0.13461
24 | 0.13174 | 0.063803
25 | 0.25832 | 0.12511
26 | 0.069726 | 0.03377
27 | 0.3273 | 0.15852
28 | 0.15822 | 0.076628
29 | 0.11729 | 0.056808
30 | 0.36291 | 0.17577
31 | 0.35885 | 0.1738
32 | 0.12392 | 0.060017
33 | 0.33435 | 0.16193
34 | 0.13298 | 0.064404
35 | 0.19662 | 0.095227
36 | 0.096701 | 0.046834
37 | 0.32139 | 0.15566
38 | 0.17937 | 0.086875
39 | 0.37875 | 0.18344
40 | 0.078495 | 0.038017
41 | 0.30721 | 0.14879
42 | 0.13035 | 0.063133
43 | 0.13098 | 0.063435
44 | 0.10543 | 0.051064
45 | 0.18454 | 0.089377
46 | 0.47155 | 0.22838
47 | 0.12615 | 0.061095
48 | 0.1042 | 0.050467
49 | 0.094464 | 0.045751
50 | 0.27744 | 0.13437
51 | 0.1941 | 0.094007
52 | 0.37632 | 0.18226
53 | 0.23413 | 0.11339
54 | 0.19424 | 0.094072
55 | 0.36937 | 0.17889
56 | 0.28853 | 0.13974
57 | 0.35543 | 0.17214
58 | 0.15039 | 0.072835
59 | 0.11567 | 0.056023
60 | 0.67418 | 0.32652
61 | 1.6429 | 0.79567
62 | 0.27961 | 0.13542
63 | 0.24419 | 0.11827
64 | 0.1515 | 0.073375
65 | 0.21718 | 0.10519
66 | 0.26004 | 0.12594
67 | 0.10865 | 0.052622
68 | 0.13931 | 0.067469
69 | 0.10429 | 0.050508
70 | 0.37903 | 0.18357
71 | 0.27782 | 0.13456
72 | 0.35478 | 0.17183
73 | 0.28952 | 0.14022
74 | 0.093285 | 0.04518
75 | 0.089075 | 0.043141
76 | 0.09418 | 0.045614
77 | 0.13459 | 0.065184
78 | 0.073172 | 0.035439
79 | 0.17612 | 0.085299
80 | 0.33703 | 0.16323
81 | 0.11928 | 0.057769
82 | 0.090304 | 0.043736
83 | 0.16486 | 0.079844

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1