## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_545_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_545_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_545_0_node_4 | 20 | n |  | TRUE
3 | bus_MV_545_0_node_5 | 20 | n |  | TRUE
4 | bus_MV_545_0_node_2 | 20 | n |  | TRUE
5 | bus_MV_545_0_node_91 | 20 | n |  | TRUE
6 | bus_MV_545_0_node_61 | 20 | n |  | TRUE
7 | bus_MV_545_0_node_75 | 20 | n |  | TRUE
8 | bus_MV_545_0_node_3 | 20 | n |  | TRUE
9 | bus_MV_545_0_node_70 | 20 | n |  | TRUE
10 | bus_MV_545_0_node_58 | 20 | n |  | TRUE
11 | bus_MV_545_0_node_71 | 20 | n |  | TRUE
12 | bus_MV_545_0_node_51 | 20 | n |  | TRUE
13 | bus_MV_545_0_node_50 | 20 | n |  | TRUE
14 | bus_MV_545_0_node_81 | 20 | n |  | TRUE
15 | bus_MV_545_0_node_90 | 20 | n |  | TRUE
16 | bus_MV_545_0_node_60 | 20 | n |  | TRUE
17 | bus_MV_545_0_node_59 | 20 | n |  | TRUE
18 | bus_MV_545_0_node_64 | 20 | n |  | TRUE
19 | bus_MV_545_0_node_6 | 20 | n |  | TRUE
20 | bus_MV_545_0_node_62 | 20 | n |  | TRUE
21 | bus_MV_545_0_node_8 | 20 | n |  | TRUE
22 | bus_MV_545_0_node_12 | 20 | n |  | TRUE
23 | bus_MV_545_0_node_63 | 20 | n |  | TRUE
24 | bus_MV_545_0_node_9 | 20 | n |  | TRUE
25 | bus_MV_545_0_node_10 | 20 | n |  | TRUE
26 | bus_MV_545_0_node_11 | 20 | n |  | TRUE
27 | bus_MV_545_0_node_69 | 20 | n |  | TRUE
28 | bus_MV_545_0_node_68 | 20 | n |  | TRUE
29 | bus_MV_545_0_node_27 | 20 | n |  | TRUE
30 | bus_MV_545_0_node_78 | 20 | n |  | TRUE
31 | bus_MV_545_0_node_26 | 20 | n |  | TRUE
32 | bus_MV_545_0_node_67 | 20 | n |  | TRUE
33 | bus_MV_545_0_node_24 | 20 | n |  | TRUE
34 | bus_MV_545_0_node_66 | 20 | n |  | TRUE
35 | bus_MV_545_0_node_65 | 20 | n |  | TRUE
36 | bus_MV_545_0_node_72 | 20 | n |  | TRUE
37 | bus_MV_545_0_node_73 | 20 | n |  | TRUE
38 | bus_MV_545_0_node_13 | 20 | n |  | TRUE
39 | bus_MV_545_0_node_15 | 20 | n |  | TRUE
40 | bus_MV_545_0_node_14 | 20 | n |  | TRUE
41 | bus_MV_545_0_node_18 | 20 | n |  | TRUE
42 | bus_MV_545_0_node_20 | 20 | n |  | TRUE
43 | bus_MV_545_0_node_16 | 20 | n |  | TRUE
44 | bus_MV_545_0_node_17 | 20 | n |  | TRUE
45 | bus_MV_545_0_node_74 | 20 | n |  | TRUE
46 | bus_MV_545_0_node_19 | 20 | n |  | TRUE
47 | bus_MV_545_0_node_109 | 20 | n |  | TRUE
48 | bus_MV_545_0_node_21 | 20 | n |  | TRUE
49 | bus_MV_545_0_node_22 | 20 | n |  | TRUE
50 | bus_MV_545_0_node_108 | 20 | n |  | TRUE
51 | bus_MV_545_0_node_57 | 20 | n |  | TRUE
52 | bus_MV_545_0_node_56 | 20 | n |  | TRUE
53 | bus_MV_545_0_node_41 | 20 | n |  | TRUE
54 | bus_MV_545_0_node_23 | 20 | n |  | TRUE
55 | bus_MV_545_0_node_40 | 20 | n |  | TRUE
56 | bus_MV_545_0_node_94 | 20 | n |  | TRUE
57 | bus_MV_545_0_node_93 | 20 | n |  | TRUE
58 | bus_MV_545_0_node_107 | 20 | n |  | TRUE
59 | bus_MV_545_0_node_101 | 20 | n |  | TRUE
60 | bus_MV_545_0_node_100 | 20 | n |  | TRUE
61 | bus_MV_545_0_node_88 | 20 | n |  | TRUE
62 | bus_MV_545_0_node_37 | 20 | n |  | TRUE
63 | bus_MV_545_0_node_111 | 20 | n |  | TRUE
64 | bus_MV_545_0_node_33 | 20 | n |  | TRUE
65 | bus_MV_545_0_node_36 | 20 | n |  | TRUE
66 | bus_MV_545_0_node_44 | 20 | n |  | TRUE
67 | bus_MV_545_0_node_92 | 20 | n |  | TRUE
68 | bus_MV_545_0_node_25 | 20 | n |  | TRUE
69 | bus_MV_545_0_node_79 | 20 | n |  | TRUE
70 | bus_MV_545_0_node_28 | 20 | n |  | TRUE
71 | bus_MV_545_0_node_29 | 20 | n |  | TRUE
72 | bus_MV_545_0_node_30 | 20 | n |  | TRUE
73 | bus_MV_545_0_node_31 | 20 | n |  | TRUE
74 | bus_MV_545_0_node_113 | 20 | n |  | TRUE
75 | bus_MV_545_0_node_112 | 20 | n |  | TRUE
76 | bus_MV_545_0_node_32 | 20 | n |  | TRUE
77 | bus_MV_545_0_node_39 | 20 | n |  | TRUE
78 | bus_MV_545_0_node_34 | 20 | n |  | TRUE
79 | bus_MV_545_0_node_38 | 20 | n |  | TRUE
80 | bus_MV_545_0_node_35 | 20 | n |  | TRUE
81 | bus_MV_545_0_node_48 | 20 | n |  | TRUE
82 | bus_MV_545_0_node_89 | 20 | n |  | TRUE
83 | bus_MV_545_0_node_42 | 20 | n |  | TRUE
84 | bus_MV_545_0_node_43 | 20 | n |  | TRUE
85 | bus_MV_545_0_node_45 | 20 | n |  | TRUE
86 | bus_MV_545_0_node_47 | 20 | n |  | TRUE
87 | bus_MV_545_0_node_114 | 20 | n |  | TRUE
88 | bus_MV_545_0_node_87 | 20 | n |  | TRUE
89 | bus_MV_545_0_node_49 | 20 | n |  | TRUE
90 | bus_MV_545_0_node_53 | 20 | n |  | TRUE
91 | bus_MV_545_0_node_54 | 20 | n |  | TRUE
92 | bus_MV_545_0_node_55 | 20 | n |  | TRUE
93 | bus_MV_545_0_node_110 | 20 | n |  | TRUE
94 | bus_MV_545_0_node_105 | 20 | n |  | TRUE
95 | bus_MV_545_0_node_98 | 20 | n |  | TRUE
96 | bus_MV_545_0_node_106 | 20 | n |  | TRUE
97 | bus_MV_545_0_node_80 | 20 | n |  | TRUE
98 | bus_MV_545_0_node_76 | 20 | n |  | TRUE
99 | bus_MV_545_0_node_77 | 20 | n |  | TRUE
100 | bus_MV_545_0_node_82 | 20 | n |  | TRUE
101 | bus_MV_545_0_node_83 | 20 | n |  | TRUE
102 | bus_MV_545_0_node_84 | 20 | n |  | TRUE
103 | bus_MV_545_0_node_85 | 20 | n |  | TRUE
104 | bus_MV_545_0_node_86 | 20 | n |  | TRUE
105 | bus_MV_545_0_node_95 | 20 | n |  | TRUE
106 | bus_MV_545_0_node_96 | 20 | n |  | TRUE
107 | bus_MV_545_0_node_97 | 20 | n |  | TRUE
108 | bus_MV_545_0_node_99 | 20 | n |  | TRUE
109 | bus_MV_545_0_node_102 | 20 | n |  | TRUE
110 | bus_MV_545_0_node_103 | 20 | n |  | TRUE
111 | bus_MV_545_0_node_104 | 20 | n |  | TRUE
112 | bus_MV_545_0_node_115 | 20 | n |  | TRUE
113 | bus_HV_545_0_node_25 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_545_0_load_0 | 0 | 0.33021 | 0.15993 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_545_0_load_91 | 5 | 0.27423 | 0.13282 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_545_0_load_75 | 7 | 0.16789 | 0.081315 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_545_0_load_3 | 8 | 0.082394 | 0.039905 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_545_0_load_70 | 9 | 0.075339 | 0.036488 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_545_0_load_58 | 10 | 0.24383 | 0.11809 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_545_0_load_71 | 11 | 0.090469 | 0.043816 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_545_0_load_90 | 15 | 0.070015 | 0.03391 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_545_0_load_59 | 17 | 0.25708 | 0.12451 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_545_0_load_6 | 19 | 0.21173 | 0.10254 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_545_0_load_62 | 20 | 0.50073 | 0.24251 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_545_0_load_8 | 21 | 0.30088 | 0.14572 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_545_0_load_10 | 25 | 0.18743 | 0.090778 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_545_0_load_11 | 26 | 0.12965 | 0.062791 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_545_0_load_78 | 30 | 0.082988 | 0.040193 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_545_0_load_24 | 33 | 0.27151 | 0.1315 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_545_0_load_65 | 35 | 0.14426 | 0.069871 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_545_0_load_72 | 36 | 0.16735 | 0.081052 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_545_0_load_73 | 37 | 0.17437 | 0.084452 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_545_0_load_13 | 38 | 0.23592 | 0.11426 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_545_0_load_18 | 41 | 0.29101 | 0.14094 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_545_0_load_17 | 44 | 0.076293 | 0.03695 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_545_0_load_74 | 45 | 0.1093 | 0.052934 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_545_0_load_109 | 47 | 0.21664 | 0.10492 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_545_0_load_108 | 50 | 0.097582 | 0.047261 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_545_0_load_56 | 52 | 0.26158 | 0.12669 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_545_0_load_40 | 55 | 0.35338 | 0.17115 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_545_0_load_94 | 56 | 0.21446 | 0.10387 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_545_0_load_107 | 58 | 0.11655 | 0.056447 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_545_0_load_101 | 59 | 0.15023 | 0.072758 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_545_0_load_100 | 60 | 0.21775 | 0.10546 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_545_0_load_88 | 61 | 0.076 | 0.036809 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_545_0_load_111 | 63 | 1.6741 | 0.81082 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_545_0_load_92 | 67 | 0.14579 | 0.07061 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_545_0_load_25 | 68 | 0.35607 | 0.17245 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_545_0_load_79 | 69 | 0.083191 | 0.040291 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_545_0_load_28 | 70 | 0.24138 | 0.11691 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_545_0_load_113 | 74 | 0.2606 | 0.12621 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_545_0_load_112 | 75 | 0.21244 | 0.10289 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_545_0_load_39 | 77 | 0.2224 | 0.10772 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_545_0_load_38 | 79 | 0.25829 | 0.12509 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_545_0_load_35 | 80 | 0.36703 | 0.17776 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_545_0_load_48 | 81 | 0.34059 | 0.16495 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_545_0_load_42 | 83 | 0.28724 | 0.13912 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_545_0_load_45 | 85 | 0.2822 | 0.13668 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_545_0_load_114 | 87 | 0.24055 | 0.1165 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_545_0_load_49 | 89 | 0.35245 | 0.1707 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_545_0_load_53 | 90 | 0.2503 | 0.12122 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_545_0_load_110 | 93 | 0.068664 | 0.033256 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_545_0_load_106 | 96 | 0.073913 | 0.035798 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_545_0_load_77 | 99 | 0.16165 | 0.078292 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_545_0_load_82 | 100 | 0.071927 | 0.034836 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_545_0_load_85 | 103 | 0.72312 | 0.35022 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_545_0_load_95 | 105 | 0.086956 | 0.042115 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_545_0_load_102 | 109 | 0.078406 | 0.037974 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_545_0_load_115 | 112 | 0.29836 | 0.1445 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 68 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_545_0_line_0 |  | 0 | 1 | 0.006841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_545_0_line_1 |  | 1 | 2 | 0.11425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_545_0_line_2 |  | 1 | 3 | 0.080508 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_545_0_line_3 |  | 1 | 4 | 0.072531 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_545_0_line_4 |  | 2 | 5 | 0.001212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_545_0_line_5 |  | 3 | 6 | 0.058476 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
6 | MV_545_0_line_6 |  | 3 | 7 | 0.045693 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
7 | MV_545_0_line_7 |  | 4 | 8 | 0.028315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_545_0_line_8 |  | 6 | 14 | 0.010676 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
9 | MV_545_0_line_9 |  | 6 | 15 | 0.020304 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_545_0_line_10 |  | 6 | 16 | 0.056271 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_545_0_line_11 |  | 7 | 18 | 0.041693 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
12 | MV_545_0_line_12 |  | 8 | 9 | 0.059604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_545_0_line_13 |  | 8 | 10 | 0.16756 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_545_0_line_14 |  | 9 | 11 | 0.025537 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
15 | MV_545_0_line_15 |  | 10 | 12 | 0.024392 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_545_0_line_16 |  | 12 | 13 | 0.13975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_545_0_line_17 |  | 13 | 89 | 0.003673 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_545_0_line_18 |  | 14 | 96 | 0.041043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_545_0_line_19 |  | 14 | 97 | 0.006216 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
20 | MV_545_0_line_20 |  | 16 | 17 | 0.052012 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_545_0_line_21 |  | 18 | 98 | 0.007582 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_545_0_line_22 |  | 18 | 23 | 0.024033 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
23 | MV_545_0_line_23 |  | 19 | 20 | 0.01894 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_545_0_line_24 |  | 20 | 23 | 0.076352 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
25 | MV_545_0_line_25 |  | 20 | 21 | 0.041286 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
26 | MV_545_0_line_26 |  | 21 | 22 | 0.053168 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
27 | MV_545_0_line_27 |  | 22 | 27 | 0.020106 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
28 | MV_545_0_line_28 |  | 22 | 28 | 0.072541 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_545_0_line_29 |  | 24 | 25 | 0.034705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_545_0_line_30 |  | 24 | 26 | 0.023372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_545_0_line_31 |  | 26 | 29 | 0.0043939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_545_0_line_32 |  | 27 | 32 | 0.011413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_545_0_line_33 |  | 27 | 33 | 0.034767 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
34 | MV_545_0_line_34 |  | 28 | 37 | 0.044887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_545_0_line_35 |  | 28 | 34 | 0.076244 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_545_0_line_36 |  | 29 | 30 | 0.045702 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
37 | MV_545_0_line_37 |  | 29 | 31 | 0.0049 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
38 | MV_545_0_line_38 |  | 30 | 69 | 0.044051 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
39 | MV_545_0_line_39 |  | 31 | 68 | 0.062383 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
40 | MV_545_0_line_40 |  | 32 | 36 | 0.020567 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_545_0_line_41 |  | 33 | 43 | 0.021713 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
42 | MV_545_0_line_42 |  | 34 | 35 | 0.02039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_545_0_line_43 |  | 37 | 45 | 0.044623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_545_0_line_44 |  | 38 | 39 | 0.057533 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_545_0_line_45 |  | 38 | 40 | 0.044832 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
46 | MV_545_0_line_46 |  | 39 | 41 | 0.055365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_545_0_line_47 |  | 39 | 42 | 0.024848 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
48 | MV_545_0_line_48 |  | 40 | 43 | 0.015657 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
49 | MV_545_0_line_49 |  | 40 | 44 | 0.026388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_545_0_line_50 |  | 42 | 48 | 0.1564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_545_0_line_51 |  | 42 | 49 | 0.28769 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
52 | MV_545_0_line_52 |  | 42 | 50 | 0.0075337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_545_0_line_53 |  | 42 | 46 | 0.033713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_545_0_line_54 |  | 46 | 47 | 0.017669 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_545_0_line_55 |  | 48 | 51 | 0.36239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_545_0_line_56 |  | 48 | 52 | 0.00558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_545_0_line_57 |  | 49 | 53 | 0.19127 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
58 | MV_545_0_line_58 |  | 49 | 54 | 0.12371 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_545_0_line_59 |  | 49 | 55 | 0.03426 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
60 | MV_545_0_line_60 |  | 50 | 58 | 0.033034 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_545_0_line_61 |  | 51 | 59 | 0.027786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_545_0_line_62 |  | 51 | 60 | 0.030495 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_545_0_line_63 |  | 53 | 61 | 0.013176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_545_0_line_64 |  | 53 | 62 | 0.37021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_545_0_line_65 |  | 54 | 56 | 0.030405 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_545_0_line_66 |  | 54 | 57 | 0.008077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_545_0_line_67 |  | 56 | 66 | 0.017604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_545_0_line_68 |  | 57 | 67 | 0.0042866 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_545_0_line_69 |  | 58 | 102 | 0.033987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_545_0_line_70 |  | 59 | 95 | 0.046347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_545_0_line_71 |  | 61 | 82 | 0.039605 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_545_0_line_72 |  | 62 | 63 | 0.056489 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_545_0_line_73 |  | 62 | 64 | 0.87779 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_545_0_line_74 |  | 62 | 65 | 0.4417 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_545_0_line_75 |  | 64 | 78 | 0.20987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_545_0_line_76 |  | 64 | 79 | 0.004749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_545_0_line_77 |  | 64 | 72 | 0.8558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_545_0_line_78 |  | 65 | 81 | 0.039706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_545_0_line_79 |  | 66 | 84 | 0.13383 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_545_0_line_80 |  | 69 | 97 | 0.054109 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
81 | MV_545_0_line_81 |  | 70 | 71 | 0.003988 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_545_0_line_82 |  | 71 | 72 | 0.62036 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_545_0_line_83 |  | 71 | 73 | 0.38331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_545_0_line_84 |  | 72 | 74 | 0.01897 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_545_0_line_85 |  | 73 | 75 | 0.015916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_545_0_line_86 |  | 73 | 76 | 0.32707 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_545_0_line_87 |  | 76 | 77 | 0.007266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_545_0_line_88 |  | 78 | 80 | 0.001601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_545_0_line_89 |  | 82 | 86 | 0.14091 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_545_0_line_90 |  | 82 | 85 | 0.088581 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
91 | MV_545_0_line_91 |  | 83 | 84 | 0.083589 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_545_0_line_92 |  | 86 | 87 | 0.043258 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_545_0_line_93 |  | 87 | 88 | 0.054017 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_545_0_line_94 |  | 88 | 104 | 0.42464 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_545_0_line_95 |  | 90 | 91 | 0.057162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_545_0_line_96 |  | 91 | 92 | 0.059692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_545_0_line_97 |  | 92 | 93 | 0.012375 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_545_0_line_98 |  | 93 | 94 | 0.013971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_545_0_line_99 |  | 94 | 110 | 0.052592 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_545_0_line_100 |  | 95 | 106 | 0.11479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_545_0_line_101 |  | 98 | 99 | 0.024015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_545_0_line_102 |  | 100 | 101 | 0.032904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_545_0_line_103 |  | 101 | 102 | 0.069842 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_545_0_line_104 |  | 103 | 104 | 0.012157 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_545_0_line_105 |  | 105 | 106 | 0.011542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_545_0_line_106 |  | 105 | 107 | 0.013901 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_545_0_line_107 |  | 107 | 108 | 0.073119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_545_0_line_108 |  | 108 | 109 | 0.012913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_545_0_line_109 |  | 109 | 110 | 0.024668 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_545_0_line_110 |  | 110 | 111 | 0.15812 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_545_0_line_111 |  | 111 | 112 | 0.035486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_545_0_trafo_25 | 25 MVA 110/20 kV | 113 | 68 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2681009.2155 | 1246250.0698
1 | 2681003.6107 | 1246246.1237
2 | 2680913.3231 | 1246217.1593
3 | 2681055.7085 | 1246202.0477
4 | 2680992.1583 | 1246293.0459
5 | 2680912.712 | 1246218.2072
6 | 2681077.4579 | 1246162.9498
7 | 2681097.9274 | 1246219.1333
8 | 2681018.4247 | 1246303.5249
9 | 2681074.1365 | 1246324.71
10 | 2680948.7707 | 1246455.9253
11 | 2681048.7677 | 1246327.6326
12 | 2680935.4709 | 1246476.3723
13 | 2680963.6976 | 1246585.7149
14 | 2681084.113 | 1246168.5449
15 | 2681061.3538 | 1246150.6672
16 | 2681034.2102 | 1246144.8679
17 | 2681007.0657 | 1246189.2348
18 | 2681129.4388 | 1246237.3591
19 | 2681207.7961 | 1246259.6809
20 | 2681213.8682 | 1246277.6214
21 | 2681255.1547 | 1246277.652
22 | 2681304.8639 | 1246296.5152
23 | 2681142.511 | 1246250.4586
24 | 2681254.031 | 1246192.0203
25 | 2681287.9402 | 1246199.4087
26 | 2681231.1988 | 1246187.0276
27 | 2681310.6346 | 1246302.1206
28 | 2681281.9225 | 1246348.0828
29 | 2681226.9063 | 1246186.089
30 | 2681182.2575 | 1246176.3348
31 | 2681228.0445 | 1246181.3233
32 | 2681306.2216 | 1246312.6455
33 | 2681343.7097 | 1246312.4256
34 | 2681240.8083 | 1246387.2481
35 | 2681221.5467 | 1246380.7643
36 | 2681325.4572 | 1246319.9258
37 | 2681323.9179 | 1246363.9338
38 | 2681395.0072 | 1246284.0534
39 | 2681436.0499 | 1246243.6206
40 | 2681378.6442 | 1246325.7927
41 | 2681459.233 | 1246278.897
42 | 2681448.9752 | 1246223.9282
43 | 2681363.9578 | 1246320.265
44 | 2681403.3167 | 1246335.1489
45 | 2681365.6664 | 1246379.6916
46 | 2681422.2335 | 1246227.5415
47 | 2681404.7881 | 1246224.8742
48 | 2681555.1537 | 1246245.9253
49 | 2681440.9489 | 1246041.0181
50 | 2681441.4419 | 1246224.0076
51 | 2681476.1194 | 1246444.9621
52 | 2681550.3546 | 1246248.7947
53 | 2681483.3687 | 1245887.3443
54 | 2681396.8946 | 1246024.4569
55 | 2681457.1692 | 1246010.841
56 | 2681366.5031 | 1246025.3566
57 | 2681396.7562 | 1246016.3825
58 | 2681408.5984 | 1246220.9887
59 | 2681460.207 | 1246467.7404
60 | 2681492.8573 | 1246419.4714
61 | 2681495.9047 | 1245883.2892
62 | 2681293.2122 | 1245696.6967
63 | 2681334.421 | 1245663.1149
64 | 2680746.194 | 1245940.6588
65 | 2681114.0814 | 1245815.9314
66 | 2681348.9064 | 1246025.8774
67 | 2681396.6834 | 1246012.0965
68 | 2681234.2658 | 1246119.8749
69 | 2681139.3737 | 1246169.7606
70 | 2681153.0986 | 1245505.1726
71 | 2681151.3569 | 1245508.7625
72 | 2680844.7781 | 1245557.7457
73 | 2681068.928 | 1245316.5294
74 | 2680862.2975 | 1245565.1454
75 | 2681063.2013 | 1245331.3841
76 | 2680857.5766 | 1245195.5019
77 | 2680856.2551 | 1245202.6446
78 | 2680717.8226 | 1245991.2205
79 | 2680748.7944 | 1245936.6802
80 | 2680716.988 | 1245992.5879
81 | 2681086.1058 | 1245816.8385
82 | 2681533.5869 | 1245871.1002
83 | 2681291.4518 | 1245913.7749
84 | 2681329.5988 | 1245988.1519
85 | 2681542.2115 | 1245959.2607
86 | 2681561.8536 | 1245759.5187
87 | 2681520.2549 | 1245747.2268
88 | 2681537.0397 | 1245695.8757
89 | 2680967.2968 | 1246584.9302
90 | 2681434.5788 | 1246571.206
91 | 2681408.1286 | 1246621.9132
92 | 2681368.8432 | 1246598.9241
93 | 2681358.4726 | 1246592.1854
94 | 2681347.6768 | 1246583.4002
95 | 2681433.6652 | 1246505.7345
96 | 2681124.4335 | 1246162.0136
97 | 2681086.0494 | 1246174.4534
98 | 2681126.8105 | 1246244.4728
99 | 2681104.3855 | 1246235.8788
100 | 2681314.8678 | 1246167.0291
101 | 2681307.1231 | 1246199.0084
102 | 2681375.4168 | 1246213.6333
103 | 2681408.3785 | 1245478.6146
104 | 2681406.5181 | 1245468.896
105 | 2681382.8715 | 1246489.2833
106 | 2681392.1708 | 1246496.1136
107 | 2681371.3925 | 1246481.4622
108 | 2681325.937 | 1246522.6578
109 | 2681318.4742 | 1246533.1956
110 | 2681304.4292 | 1246553.4743
111 | 2681286.5583 | 1246670.5592
112 | 2681307.7917 | 1246642.085
113 | 2681234.2658 | 1246119.8749

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99906 | -0.012933 | 0.33021 | 0.15993
1 | 0.99907 | -0.01296 | 0 | 0
2 | 0.99903 | -0.012595 | 0 | 0
3 | 0.99922 | -0.014297 | 0 | 0
4 | 0.99899 | -0.012259 | 0 | 0
5 | 0.99903 | -0.012591 | 0.27423 | 0.13282
6 | 0.99937 | -0.011488 | 0 | 0
7 | 0.99911 | -0.016235 | 0.16789 | 0.081315
8 | 0.99896 | -0.011983 | 0.082394 | 0.039905
9 | 0.99895 | -0.011868 | 0.075339 | 0.036488
10 | 0.99877 | -0.013252 | 0.24383 | 0.11809
11 | 0.99894 | -0.011896 | 0.090469 | 0.043816
12 | 0.99876 | -0.013155 | 0 | 0
13 | 0.99869 | -0.01258 | 0 | 0
14 | 0.9994 | -0.010961 | 0 | 0
15 | 0.99937 | -0.011471 | 0.070015 | 0.03391
16 | 0.99935 | -0.011321 | 0 | 0
17 | 0.99933 | -0.011163 | 0.25708 | 0.12451
18 | 0.99901 | -0.017976 | 0 | 0
19 | 0.99878 | -0.02215 | 0.21173 | 0.10254
20 | 0.99879 | -0.022101 | 0.50073 | 0.24251
21 | 0.99859 | -0.028772 | 0.30088 | 0.14572
22 | 0.99848 | -0.030751 | 0 | 0
23 | 0.99896 | -0.018964 | 0 | 0
24 | 0.9998 | -0.0034004 | 0 | 0
25 | 0.99979 | -0.0033235 | 0.18743 | 0.090778
26 | 0.99981 | -0.0034512 | 0.12965 | 0.062791
27 | 0.99845 | -0.031466 | 0 | 0
28 | 0.99845 | -0.030403 | 0 | 0
29 | 0.99981 | -0.0034675 | 0 | 0
30 | 0.99968 | -0.0057662 | 0.082988 | 0.040193
31 | 0.99982 | -0.003215 | 0 | 0
32 | 0.99844 | -0.031443 | 0 | 0
33 | 0.99838 | -0.032678 | 0.27151 | 0.1315
34 | 0.99843 | -0.030278 | 0 | 0
35 | 0.99843 | -0.030243 | 0.14426 | 0.069871
36 | 0.99844 | -0.031402 | 0.16735 | 0.081052
37 | 0.99843 | -0.030255 | 0.17437 | 0.084452
38 | 0.99813 | -0.04026 | 0.23592 | 0.11426
39 | 0.99802 | -0.042136 | 0 | 0
40 | 0.99831 | -0.033942 | 0 | 0
41 | 0.998 | -0.041945 | 0.29101 | 0.14094
42 | 0.99798 | -0.042918 | 0 | 0
43 | 0.99834 | -0.033412 | 0 | 0
44 | 0.99831 | -0.033918 | 0.076293 | 0.03695
45 | 0.99842 | -0.030198 | 0.1093 | 0.052934
46 | 0.99797 | -0.042832 | 0 | 0
47 | 0.99797 | -0.042787 | 0.21664 | 0.10492
48 | 0.9977 | -0.040548 | 0 | 0
49 | 0.99761 | -0.049758 | 0 | 0
50 | 0.99798 | -0.042895 | 0.097582 | 0.047261
51 | 0.99717 | -0.036043 | 0 | 0
52 | 0.9977 | -0.04053 | 0.26158 | 0.12669
53 | 0.99711 | -0.05558 | 0 | 0
54 | 0.99751 | -0.048844 | 0 | 0
55 | 0.99759 | -0.049905 | 0.35338 | 0.17115
56 | 0.99749 | -0.048668 | 0.21446 | 0.10387
57 | 0.99751 | -0.04883 | 0 | 0
58 | 0.99797 | -0.042827 | 0.11655 | 0.056447
59 | 0.99714 | -0.035761 | 0.15023 | 0.072758
60 | 0.99716 | -0.035964 | 0.21775 | 0.10546
61 | 0.99708 | -0.055385 | 0.076 | 0.036809
62 | 0.99542 | -0.041888 | 0 | 0
63 | 0.9953 | -0.040749 | 1.6741 | 0.81082
64 | 0.99369 | -0.029147 | 0 | 0
65 | 0.99523 | -0.040247 | 0 | 0
66 | 0.99748 | -0.048612 | 0 | 0
67 | 0.99751 | -0.048822 | 0.14579 | 0.07061
68 | 1 | 0 | -13.0105 | -6.0422
69 | 0.99956 | -0.0079673 | 0.083191 | 0.040291
70 | 0.99214 | -0.01765 | 0.24138 | 0.11691
71 | 0.99214 | -0.017662 | 0 | 0
72 | 0.99267 | -0.021769 | 0 | 0
73 | 0.99192 | -0.015952 | 0 | 0
74 | 0.99266 | -0.02171 | 0.2606 | 0.12621
75 | 0.99192 | -0.015911 | 0.21244 | 0.10289
76 | 0.99183 | -0.015152 | 0 | 0
77 | 0.99183 | -0.015132 | 0.2224 | 0.10772
78 | 0.99359 | -0.028248 | 0 | 0
79 | 0.99368 | -0.029132 | 0.25829 | 0.12509
80 | 0.99359 | -0.028241 | 0.36703 | 0.17776
81 | 0.99521 | -0.040084 | 0.34059 | 0.16495
82 | 0.99702 | -0.054834 | 0 | 0
83 | 0.99739 | -0.048456 | 0.28724 | 0.13912
84 | 0.99744 | -0.048164 | 0 | 0
85 | 0.99697 | -0.055138 | 0.2822 | 0.13668
86 | 0.99685 | -0.053329 | 0 | 0
87 | 0.9968 | -0.05286 | 0.24055 | 0.1165
88 | 0.99675 | -0.052428 | 0 | 0
89 | 0.99869 | -0.012564 | 0.35245 | 0.1707
90 | 0.99679 | -0.032742 | 0.2503 | 0.12122
91 | 0.99681 | -0.032912 | 0 | 0
92 | 0.99683 | -0.033084 | 0 | 0
93 | 0.99683 | -0.033119 | 0.068664 | 0.033256
94 | 0.99684 | -0.033169 | 0 | 0
95 | 0.99709 | -0.035371 | 0 | 0
96 | 0.9994 | -0.010926 | 0.073913 | 0.035798
97 | 0.99942 | -0.010653 | 0 | 0
98 | 0.99901 | -0.017961 | 0 | 0
99 | 0.99901 | -0.017915 | 0.16165 | 0.078292
100 | 0.99796 | -0.042724 | 0.071927 | 0.034836
101 | 0.99796 | -0.042751 | 0 | 0
102 | 0.99797 | -0.042804 | 0 | 0
103 | 0.99634 | -0.048768 | 0.72312 | 0.35022
104 | 0.99635 | -0.048874 | 0 | 0
105 | 0.99697 | -0.034292 | 0.086956 | 0.042115
106 | 0.99698 | -0.034392 | 0 | 0
107 | 0.99696 | -0.034187 | 0 | 0
108 | 0.99689 | -0.033626 | 0 | 0
109 | 0.99688 | -0.033526 | 0.078406 | 0.037974
110 | 0.99686 | -0.033358 | 0 | 0
111 | 0.9968 | -0.032817 | 0 | 0
112 | 0.99679 | -0.032691 | 0.29836 | 0.1445
113 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.33021 | -0.15993 | 0.33021 | 0.15977 | 1.0262e-06 | -0.00016273 | 0.010601 | 0.010599 | 0.010601 | 0.99906 | -0.012933 | 0.99907 | -0.01296 | 4.8189
1 | 0.27424 | 0.13007 | -0.27423 | -0.13279 | 1.1777e-05 | -0.0027191 | 0.0087702 | 0.0088042 | 0.0088042 | 0.99907 | -0.01296 | 0.99903 | -0.012595 | 4.0019
2 | -1.4492 | -0.69089 | 1.4494 | 0.68904 | 0.00023116 | -0.0018504 | 0.046388 | 0.046365 | 0.046388 | 0.99907 | -0.01296 | 0.99922 | -0.014297 | 21.0856
3 | 0.84472 | 0.40106 | -0.84465 | -0.40276 | 7.0743e-05 | -0.0017074 | 0.027019 | 0.02704 | 0.02704 | 0.99907 | -0.01296 | 0.99899 | -0.012259 | 12.2911
4 | 0.27423 | 0.13279 | -0.27423 | -0.13282 | 1.2547e-07 | -2.8844e-05 | 0.0088042 | 0.0088046 | 0.0088046 | 0.99903 | -0.012595 | 0.99903 | -0.012591 | 4.0021
5 | -12.1038 | -5.6231 | 12.1054 | 5.6201 | 0.0015907 | -0.0030012 | 0.38557 | 0.38552 | 0.38557 | 0.99922 | -0.014297 | 0.99937 | -0.011488 | 45.7927
6 | 10.6544 | 4.934 | -10.6535 | -4.9366 | 0.00096227 | -0.0026019 | 0.33921 | 0.33925 | 0.33925 | 0.99922 | -0.014297 | 0.99911 | -0.016235 | 40.2915
7 | 0.84465 | 0.40276 | -0.84462 | -0.40343 | 2.7648e-05 | -0.00066648 | 0.02704 | 0.027049 | 0.027049 | 0.99899 | -0.012259 | 0.99896 | -0.011983 | 12.2949
8 | -12.4325 | -5.7754 | 12.4328 | 5.7749 | 0.00030635 | -0.00053348 | 0.39598 | 0.39597 | 0.39598 | 0.99937 | -0.011488 | 0.9994 | -0.010961 | 47.0285
9 | 0.070015 | 0.033425 | -0.070015 | -0.03391 | 1.3651e-07 | -0.00048413 | 0.0022411 | 0.0022471 | 0.0022471 | 0.99937 | -0.011488 | 0.99937 | -0.011471 | 1.0214
10 | 0.25709 | 0.12193 | -0.25709 | -0.12327 | 5.0851e-06 | -0.0013403 | 0.0082191 | 0.0082358 | 0.0082358 | 0.99937 | -0.011488 | 0.99935 | -0.011321 | 3.7436
11 | 10.4856 | 4.8553 | -10.4847 | -4.8577 | 0.00085056 | -0.0023987 | 0.33387 | 0.3339 | 0.3339 | 0.99911 | -0.016235 | 0.99901 | -0.017976 | 39.656
12 | 0.16581 | 0.078854 | -0.16581 | -0.080274 | 2.2475e-06 | -0.0014195 | 0.0053057 | 0.0053235 | 0.0053235 | 0.99896 | -0.011983 | 0.99895 | -0.011868 | 2.4198
13 | 0.59642 | 0.28467 | -0.59631 | -0.2848 | 0.0001089 | -0.00013137 | 0.019098 | 0.0191 | 0.0191 | 0.99896 | -0.011983 | 0.99877 | -0.013252 | 9.0953
14 | 0.090469 | 0.043786 | -0.090469 | -0.043816 | 3.8387e-07 | -3.0181e-05 | 0.0029045 | 0.0029049 | 0.0029049 | 0.99895 | -0.011868 | 0.99894 | -0.011896 | 1.3833
15 | 0.35247 | 0.16671 | -0.35247 | -0.16729 | 4.1383e-06 | -0.00057971 | 0.01127 | 0.011277 | 0.011277 | 0.99877 | -0.013252 | 0.99876 | -0.013155 | 5.1258
16 | 0.35247 | 0.16729 | -0.35245 | -0.17061 | 2.3812e-05 | -0.003321 | 0.011277 | 0.011318 | 0.011318 | 0.99876 | -0.013155 | 0.99869 | -0.01258 | 5.1447
17 | 0.35245 | 0.17061 | -0.35245 | -0.1707 | 6.2825e-07 | -8.7281e-05 | 0.011318 | 0.01132 | 0.01132 | 0.99869 | -0.01258 | 0.99869 | -0.012564 | 5.1452
18 | 0.073913 | 0.034819 | -0.073913 | -0.035798 | 3.0674e-07 | -0.00097868 | 0.00236 | 0.0023722 | 0.0023722 | 0.9994 | -0.010961 | 0.9994 | -0.010926 | 1.0783
19 | -12.5067 | -5.8097 | 12.5069 | 5.8094 | 0.00018049 | -0.00030867 | 0.39833 | 0.39832 | 0.39833 | 0.9994 | -0.010961 | 0.99942 | -0.010653 | 47.3076
20 | 0.25709 | 0.12327 | -0.25708 | -0.12451 | 4.7187e-06 | -0.0012388 | 0.0082358 | 0.0082514 | 0.0082514 | 0.99935 | -0.011321 | 0.99933 | -0.011163 | 3.7506
21 | 0.16165 | 0.077539 | -0.16165 | -0.07772 | 2.7179e-07 | -0.00018059 | 0.0051807 | 0.005183 | 0.005183 | 0.99901 | -0.017976 | 0.99901 | -0.017961 | 2.3559
22 | 10.3231 | 4.7802 | -10.3226 | -4.7816 | 0.00047528 | -0.0013962 | 0.32872 | 0.32875 | 0.32875 | 0.99901 | -0.017976 | 0.99896 | -0.018964 | 39.0434
23 | -0.21173 | -0.10254 | 0.21173 | 0.10252 | 1.5601e-06 | -2.1579e-05 | 0.0067994 | 0.0067992 | 0.0067994 | 0.99878 | -0.02215 | 0.99879 | -0.022101 | 3.2378
24 | -10.3211 | -4.786 | 10.3226 | 4.7816 | 0.0015104 | -0.0044339 | 0.32882 | 0.32875 | 0.32882 | 0.99879 | -0.022101 | 0.99896 | -0.018964 | 39.0518
25 | 9.6086 | 4.441 | -9.6072 | -4.4391 | 0.0013773 | 0.0018874 | 0.30594 | 0.30594 | 0.30594 | 0.99879 | -0.022101 | 0.99859 | -0.028772 | 37.31
26 | 9.3064 | 4.2934 | -9.3055 | -4.2966 | 0.00085423 | -0.0032661 | 0.29628 | 0.29633 | 0.29633 | 0.99859 | -0.028772 | 0.99848 | -0.030751 | 35.1934
27 | 8.8776 | 4.0955 | -8.8773 | -4.0968 | 0.00029399 | -0.0012616 | 0.28266 | 0.28268 | 0.28268 | 0.99848 | -0.030751 | 0.99845 | -0.031466 | 33.572
28 | 0.42796 | 0.20111 | -0.42794 | -0.20283 | 1.8127e-05 | -0.0017213 | 0.013671 | 0.013692 | 0.013692 | 0.99848 | -0.030751 | 0.99845 | -0.030403 | 6.2237
29 | 0.18744 | 0.089951 | -0.18743 | -0.090778 | 1.6724e-06 | -0.00082778 | 0.0060028 | 0.0060132 | 0.0060132 | 0.9998 | -0.0034004 | 0.99979 | -0.0033235 | 2.7333
30 | -0.18744 | -0.089951 | 0.18744 | 0.089393 | 1.123e-06 | -0.00055747 | 0.0060028 | 0.0059959 | 0.0060028 | 0.9998 | -0.0034004 | 0.99981 | -0.0034512 | 2.7285
31 | -0.31708 | -0.15218 | 0.31708 | 0.15208 | 6.0485e-07 | -0.00010469 | 0.010155 | 0.010154 | 0.010155 | 0.99981 | -0.0034512 | 0.99981 | -0.0034675 | 4.6159
32 | 0.16735 | 0.080291 | -0.16735 | -0.080563 | 4.3908e-07 | -0.00027151 | 0.0053666 | 0.00537 | 0.00537 | 0.99845 | -0.031466 | 0.99844 | -0.031443 | 2.4409
33 | 8.7099 | 4.0165 | -8.7094 | -4.0187 | 0.00048934 | -0.0021987 | 0.27731 | 0.27734 | 0.27734 | 0.99845 | -0.031466 | 0.99838 | -0.032678 | 32.9385
34 | 0.28367 | 0.13526 | -0.28367 | -0.13632 | 4.9546e-06 | -0.0010669 | 0.0090863 | 0.0090996 | 0.0090996 | 0.99845 | -0.030403 | 0.99843 | -0.030255 | 4.1362
35 | 0.14427 | 0.067571 | -0.14427 | -0.069386 | 2.1699e-06 | -0.0018141 | 0.004606 | 0.0046285 | 0.0046285 | 0.99845 | -0.030403 | 0.99843 | -0.030278 | 2.1039
36 | 12.6773 | 5.8828 | -12.676 | -5.885 | 0.001362 | -0.0022397 | 0.40352 | 0.40356 | 0.40356 | 0.99981 | -0.0034675 | 0.99968 | -0.0057662 | 47.9293
37 | -12.9944 | -6.0349 | 12.9946 | 6.0346 | 0.00015345 | -0.00023337 | 0.41368 | 0.41367 | 0.41368 | 0.99981 | -0.0034675 | 0.99982 | -0.003215 | 49.1301
38 | 12.593 | 5.8448 | -12.5917 | -5.847 | 0.0012958 | -0.0021736 | 0.4009 | 0.40094 | 0.40094 | 0.99968 | -0.0057662 | 0.99956 | -0.0079673 | 47.618
39 | -12.9946 | -6.0346 | 12.9965 | 6.0317 | 0.0019533 | -0.0029723 | 0.41367 | 0.41361 | 0.41367 | 0.99982 | -0.003215 | 1 | 0 | 49.1295
40 | 0.16735 | 0.080563 | -0.16735 | -0.081052 | 7.9269e-07 | -0.0004893 | 0.00537 | 0.0053762 | 0.0053762 | 0.99844 | -0.031443 | 0.99844 | -0.031402 | 2.4437
41 | 8.4379 | 3.8872 | -8.4376 | -3.8886 | 0.00028673 | -0.0013903 | 0.26862 | 0.26864 | 0.26864 | 0.99838 | -0.032678 | 0.99834 | -0.033412 | 31.9051
42 | 0.14427 | 0.069386 | -0.14426 | -0.069871 | 5.8391e-07 | -0.00048513 | 0.0046285 | 0.0046346 | 0.0046346 | 0.99843 | -0.030278 | 0.99843 | -0.030243 | 2.1066
43 | 0.1093 | 0.051872 | -0.1093 | -0.052934 | 7.3165e-07 | -0.0010619 | 0.0034979 | 0.0035112 | 0.0035112 | 0.99843 | -0.030255 | 0.99842 | -0.030198 | 1.596
44 | 8.1241 | 3.7375 | -8.1234 | -3.7412 | 0.00070441 | -0.0037321 | 0.25863 | 0.25869 | 0.25869 | 0.99813 | -0.04026 | 0.99802 | -0.042136 | 30.7229
45 | -8.36 | -3.8517 | 8.3611 | 3.8533 | 0.0011324 | 0.0015238 | 0.26621 | 0.26621 | 0.26621 | 0.99813 | -0.04026 | 0.99831 | -0.033942 | 32.4651
46 | 0.29101 | 0.13963 | -0.29101 | -0.14094 | 6.454e-06 | -0.0013148 | 0.0093362 | 0.0093528 | 0.0093528 | 0.99802 | -0.042136 | 0.998 | -0.041945 | 4.2513
47 | 7.8324 | 3.6016 | -7.8321 | -3.6032 | 0.00028275 | -0.0016313 | 0.24935 | 0.24937 | 0.24937 | 0.99802 | -0.042136 | 0.99798 | -0.042918 | 29.617
48 | -8.4374 | -3.8896 | 8.4376 | 3.8886 | 0.00020679 | -0.0010024 | 0.26866 | 0.26864 | 0.26866 | 0.99831 | -0.033942 | 0.99834 | -0.033412 | 31.9068
49 | 0.076293 | 0.036322 | -0.076293 | -0.03695 | 2.1099e-07 | -0.00062785 | 0.0024434 | 0.0024512 | 0.0024512 | 0.99831 | -0.033942 | 0.99831 | -0.033918 | 1.1142
50 | 1.4136 | 0.65425 | -1.4132 | -0.65784 | 0.00042431 | -0.0035923 | 0.045057 | 0.045103 | 0.045103 | 0.99798 | -0.042918 | 0.9977 | -0.040548 | 20.5011
51 | 5.9157 | 2.7109 | -5.9139 | -2.7311 | 0.0018679 | -0.020169 | 0.18823 | 0.18849 | 0.18849 | 0.99798 | -0.042918 | 0.99761 | -0.049758 | 22.3865
52 | 0.28606 | 0.13433 | -0.28606 | -0.13451 | 8.4066e-07 | -0.0001789 | 0.0091414 | 0.0091436 | 0.0091436 | 0.99798 | -0.042918 | 0.99798 | -0.042895 | 4.1562
53 | 0.21664 | 0.1037 | -0.21664 | -0.1045 | 2.1756e-06 | -0.00080104 | 0.0069476 | 0.0069576 | 0.0069576 | 0.99798 | -0.042918 | 0.99797 | -0.042832 | 3.1626
54 | 0.21664 | 0.1045 | -0.21664 | -0.10492 | 1.1427e-06 | -0.00041981 | 0.0069576 | 0.0069629 | 0.0069629 | 0.99797 | -0.042832 | 0.99797 | -0.042787 | 3.165
55 | 1.1516 | 0.53129 | -1.151 | -0.5397 | 0.00065333 | -0.0084144 | 0.036696 | 0.036801 | 0.036801 | 0.9977 | -0.040548 | 0.99717 | -0.036043 | 16.7277
56 | 0.26158 | 0.12655 | -0.26158 | -0.12669 | 5.2671e-07 | -0.00013246 | 0.0084077 | 0.0084094 | 0.0084094 | 0.9977 | -0.040548 | 0.9977 | -0.04053 | 3.8224
57 | 4.9129 | 2.254 | -4.9106 | -2.2589 | 0.0022613 | -0.0048839 | 0.15641 | 0.15649 | 0.15649 | 0.99761 | -0.049758 | 0.99711 | -0.05558 | 43.2291
58 | 0.6476 | 0.30598 | -0.64753 | -0.3089 | 7.1066e-05 | -0.0029182 | 0.020726 | 0.020762 | 0.020762 | 0.99761 | -0.049758 | 0.99751 | -0.048844 | 9.4373
59 | 0.35339 | 0.17111 | -0.35338 | -0.17115 | 7.8797e-06 | -3.5768e-05 | 0.011361 | 0.011362 | 0.011362 | 0.99761 | -0.049758 | 0.99759 | -0.049905 | 5.4105
60 | 0.18848 | 0.087246 | -0.18848 | -0.088031 | 1.5942e-06 | -0.00078507 | 0.0060077 | 0.0060172 | 0.0060172 | 0.99798 | -0.042895 | 0.99797 | -0.042827 | 2.7351
61 | 0.93321 | 0.43497 | -0.93318 | -0.43562 | 3.2964e-05 | -0.00064987 | 0.029806 | 0.029814 | 0.029814 | 0.99717 | -0.036043 | 0.99714 | -0.035761 | 13.552
62 | 0.21775 | 0.10474 | -0.21775 | -0.10546 | 1.9946e-06 | -0.00072339 | 0.0069951 | 0.0070042 | 0.0070042 | 0.99717 | -0.036043 | 0.99716 | -0.035964 | 3.1837
63 | 1.3226 | 0.62306 | -1.3226 | -0.62336 | 3.1515e-05 | -0.00030341 | 0.042327 | 0.04233 | 0.04233 | 0.99711 | -0.05558 | 0.99708 | -0.055385 | 19.2411
64 | 3.5881 | 1.6358 | -3.5816 | -1.6427 | 0.0064476 | -0.0068607 | 0.11417 | 0.11427 | 0.11427 | 0.99711 | -0.05558 | 0.99542 | -0.041888 | 51.9414
65 | 0.50174 | 0.23858 | -0.50173 | -0.2393 | 1.0499e-05 | -0.00071921 | 0.016078 | 0.016087 | 0.016087 | 0.99751 | -0.048844 | 0.99749 | -0.048668 | 7.3123
66 | 0.14579 | 0.070316 | -0.14579 | -0.070508 | 2.3672e-07 | -0.00019182 | 0.0046842 | 0.0046866 | 0.0046866 | 0.99751 | -0.048844 | 0.99751 | -0.04883 | 2.1303
67 | 0.28727 | 0.13543 | -0.28727 | -0.13585 | 1.9865e-06 | -0.00041763 | 0.0091911 | 0.0091963 | 0.0091963 | 0.99749 | -0.048668 | 0.99748 | -0.048612 | 4.1801
68 | 0.14579 | 0.070508 | -0.14579 | -0.07061 | 1.2575e-07 | -0.0001018 | 0.0046866 | 0.0046879 | 0.0046879 | 0.99751 | -0.04883 | 0.99751 | -0.048822 | 2.1309
69 | 0.071928 | 0.031585 | -0.071928 | -0.032393 | 2.3526e-07 | -0.00080812 | 0.0022724 | 0.0022819 | 0.0022819 | 0.99797 | -0.042827 | 0.99797 | -0.042804 | 1.0372
70 | 0.78295 | 0.36286 | -0.78291 | -0.36395 | 3.8638e-05 | -0.0010887 | 0.024983 | 0.024996 | 0.024996 | 0.99714 | -0.035761 | 0.99709 | -0.035371 | 11.3619
71 | 1.2465 | 0.58655 | -1.2465 | -0.58747 | 8.4137e-05 | -0.00091508 | 0.039886 | 0.039897 | 0.039897 | 0.99708 | -0.055385 | 0.99702 | -0.054834 | 18.1352
72 | 1.6743 | 0.80955 | -1.6741 | -0.81082 | 0.00021944 | -0.0012712 | 0.053934 | 0.053951 | 0.053951 | 0.99542 | -0.041888 | 0.9953 | -0.040749 | 24.5232
73 | 1.5666 | 0.67956 | -1.5637 | -0.69943 | 0.0028879 | -0.019874 | 0.049522 | 0.049764 | 0.049764 | 0.99542 | -0.041888 | 0.99369 | -0.029147 | 22.6202
74 | 0.34066 | 0.15359 | -0.34059 | -0.16402 | 7.006e-05 | -0.010427 | 0.010837 | 0.010965 | 0.010965 | 0.99542 | -0.041888 | 0.99523 | -0.040247 | 4.9841
75 | 0.36707 | 0.17279 | -0.36703 | -0.17772 | 3.9123e-05 | -0.0049356 | 0.011786 | 0.011848 | 0.011848 | 0.99369 | -0.029147 | 0.99359 | -0.028248 | 5.3855
76 | 0.25829 | 0.12498 | -0.25829 | -0.12509 | 4.4059e-07 | -0.00011183 | 0.0083359 | 0.0083373 | 0.0083373 | 0.99369 | -0.029147 | 0.99368 | -0.029132 | 3.7897
77 | 0.93835 | 0.40166 | -0.93734 | -0.42152 | 0.0010125 | -0.019855 | 0.029652 | 0.029888 | 0.029888 | 0.99369 | -0.029147 | 0.99267 | -0.021769 | 13.5853
78 | 0.34059 | 0.16402 | -0.34059 | -0.16495 | 6.38e-06 | -0.0009371 | 0.010965 | 0.010977 | 0.010977 | 0.99523 | -0.040247 | 0.99521 | -0.040084 | 4.9895
79 | 0.28727 | 0.13585 | -0.28725 | -0.13902 | 1.5175e-05 | -0.0031747 | 0.0091963 | 0.009236 | 0.009236 | 0.99748 | -0.048612 | 0.99744 | -0.048164 | 4.1982
80 | 12.5085 | 5.8067 | -12.5069 | -5.8094 | 0.0015709 | -0.0026878 | 0.39827 | 0.39832 | 0.39832 | 0.99956 | -0.0079673 | 0.99942 | -0.010653 | 47.3069
81 | -0.24138 | -0.11691 | 0.24138 | 0.11681 | 3.2416e-07 | -9.363e-05 | 0.0078037 | 0.0078025 | 0.0078037 | 0.99214 | -0.01765 | 0.99214 | -0.017662 | 3.5471
82 | -0.67635 | -0.31022 | 0.67674 | 0.29575 | 0.00038507 | -0.014473 | 0.021651 | 0.021477 | 0.021651 | 0.99214 | -0.017662 | 0.99267 | -0.021769 | 9.8412
83 | 0.43497 | 0.19341 | -0.43487 | -0.20239 | 9.8933e-05 | -0.0089773 | 0.013851 | 0.013959 | 0.013959 | 0.99214 | -0.017662 | 0.99192 | -0.015952 | 6.3451
84 | 0.2606 | 0.12577 | -0.2606 | -0.12621 | 1.7945e-06 | -0.00044578 | 0.0084149 | 0.0084205 | 0.0084205 | 0.99267 | -0.021769 | 0.99266 | -0.02171 | 3.8275
85 | 0.21244 | 0.10252 | -0.21244 | -0.10289 | 1.002e-06 | -0.0003736 | 0.0068648 | 0.0068696 | 0.0068696 | 0.99192 | -0.015952 | 0.99192 | -0.015911 | 3.1225
86 | 0.22243 | 0.099869 | -0.22241 | -0.10755 | 2.2274e-05 | -0.0076763 | 0.0070958 | 0.0071902 | 0.0071902 | 0.99192 | -0.015952 | 0.99183 | -0.015152 | 3.2683
87 | 0.22241 | 0.10755 | -0.2224 | -0.10772 | 5.0164e-07 | -0.00017051 | 0.0071902 | 0.0071924 | 0.0071924 | 0.99183 | -0.015152 | 0.99183 | -0.015132 | 3.2693
88 | 0.36703 | 0.17772 | -0.36703 | -0.17776 | 3.0001e-07 | -3.7648e-05 | 0.011848 | 0.011849 | 0.011849 | 0.99359 | -0.028248 | 0.99359 | -0.028241 | 5.3857
89 | 0.96425 | 0.45089 | -0.96407 | -0.45418 | 0.00017892 | -0.0032907 | 0.03082 | 0.030861 | 0.030861 | 0.99702 | -0.054834 | 0.99685 | -0.053329 | 14.0279
90 | 0.28221 | 0.13658 | -0.2822 | -0.13668 | 1.3008e-05 | -9.6967e-05 | 0.0090777 | 0.0090791 | 0.0090791 | 0.99702 | -0.054834 | 0.99697 | -0.055138 | 4.3234
91 | -0.28724 | -0.13912 | 0.28725 | 0.13902 | 1.2706e-05 | -9.1315e-05 | 0.0092373 | 0.009236 | 0.0092373 | 0.99739 | -0.048456 | 0.99744 | -0.048164 | 4.3987
92 | 0.96407 | 0.45418 | -0.96402 | -0.45519 | 5.5025e-05 | -0.00101 | 0.030861 | 0.030874 | 0.030874 | 0.99685 | -0.053329 | 0.9968 | -0.05286 | 14.0337
93 | 0.72347 | 0.33869 | -0.72343 | -0.33996 | 3.862e-05 | -0.0012699 | 0.023134 | 0.02315 | 0.02315 | 0.9968 | -0.05286 | 0.99675 | -0.052428 | 10.5227
94 | 0.72343 | 0.33996 | -0.72313 | -0.34994 | 0.00030545 | -0.0099783 | 0.02315 | 0.023275 | 0.023275 | 0.99675 | -0.052428 | 0.99635 | -0.048874 | 10.5798
95 | -0.2503 | -0.12122 | 0.2503 | 0.11987 | 4.9398e-06 | -0.0013546 | 0.0080542 | 0.0080371 | 0.0080542 | 0.99679 | -0.032742 | 0.99681 | -0.032912 | 3.661
96 | -0.2503 | -0.11987 | 0.25031 | 0.11846 | 5.1362e-06 | -0.0014146 | 0.0080371 | 0.0080195 | 0.0080371 | 0.99681 | -0.032912 | 0.99683 | -0.033084 | 3.6532
97 | -0.25031 | -0.11846 | 0.25031 | 0.11816 | 1.0619e-06 | -0.00029327 | 0.0080195 | 0.0080158 | 0.0080195 | 0.99683 | -0.033084 | 0.99683 | -0.033119 | 3.6452
98 | -0.31897 | -0.15142 | 0.31898 | 0.15109 | 1.9493e-06 | -0.00033088 | 0.010225 | 0.010221 | 0.010225 | 0.99683 | -0.033119 | 0.99684 | -0.033169 | 4.6478
99 | -0.31898 | -0.15109 | 0.31898 | 0.14984 | 7.3238e-06 | -0.0012456 | 0.010221 | 0.010206 | 0.010221 | 0.99684 | -0.033169 | 0.99686 | -0.033358 | 4.6459
100 | 0.78291 | 0.36395 | -0.78282 | -0.36664 | 9.5876e-05 | -0.0026961 | 0.024996 | 0.025029 | 0.025029 | 0.99709 | -0.035371 | 0.99698 | -0.034392 | 11.377
101 | 0.16165 | 0.07772 | -0.16165 | -0.078292 | 8.6243e-07 | -0.000572 | 0.005183 | 0.0051901 | 0.0051901 | 0.99901 | -0.017961 | 0.99901 | -0.017915 | 2.3592
102 | -0.071927 | -0.034836 | 0.071927 | 0.034053 | 2.3376e-07 | -0.00078234 | 0.0023118 | 0.002302 | 0.0023118 | 0.99796 | -0.042724 | 0.99796 | -0.042751 | 1.0508
103 | -0.071927 | -0.034053 | 0.071928 | 0.032393 | 4.8973e-07 | -0.0016606 | 0.002302 | 0.0022819 | 0.002302 | 0.99796 | -0.042751 | 0.99797 | -0.042804 | 1.0464
104 | -0.72312 | -0.35022 | 0.72313 | 0.34994 | 8.7936e-06 | -0.00028553 | 0.023279 | 0.023275 | 0.023279 | 0.99634 | -0.048768 | 0.99635 | -0.048874 | 10.5814
105 | -0.78281 | -0.36691 | 0.78282 | 0.36664 | 9.6547e-06 | -0.00027106 | 0.025033 | 0.025029 | 0.025033 | 0.99697 | -0.034292 | 0.99698 | -0.034392 | 11.3785
106 | 0.69585 | 0.3248 | -0.69584 | -0.32513 | 9.1769e-06 | -0.00032716 | 0.022235 | 0.022239 | 0.022239 | 0.99697 | -0.034292 | 0.99696 | -0.034187 | 10.1089
107 | 0.69584 | 0.32513 | -0.6958 | -0.32685 | 4.8325e-05 | -0.0017207 | 0.022239 | 0.022261 | 0.022261 | 0.99696 | -0.034187 | 0.99689 | -0.033626 | 10.1185
108 | 0.6958 | 0.32685 | -0.69579 | -0.32715 | 8.5439e-06 | -0.00030385 | 0.022261 | 0.022265 | 0.022265 | 0.99689 | -0.033626 | 0.99688 | -0.033526 | 10.1203
109 | 0.61738 | 0.28918 | -0.61737 | -0.28976 | 1.284e-05 | -0.00058148 | 0.019742 | 0.019749 | 0.019749 | 0.99688 | -0.033526 | 0.99686 | -0.033358 | 8.9769
110 | 0.29838 | 0.13992 | -0.29837 | -0.14366 | 1.9319e-05 | -0.0037456 | 0.0095436 | 0.0095902 | 0.0095902 | 0.99686 | -0.033358 | 0.9968 | -0.032817 | 4.3592
111 | 0.29837 | 0.14366 | -0.29836 | -0.1445 | 4.3619e-06 | -0.00084055 | 0.0095902 | 0.0096008 | 0.0096008 | 0.9968 | -0.032817 | 0.99679 | -0.032691 | 4.364

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 13.3666 | 6.2146

## res_load
| p_mw | q_mvar
0 | 0.33021 | 0.15993
1 | 0.27423 | 0.13282
2 | 0.16789 | 0.081315
3 | 0.082394 | 0.039905
4 | 0.075339 | 0.036488
5 | 0.24383 | 0.11809
6 | 0.090469 | 0.043816
7 | 0.070015 | 0.03391
8 | 0.25708 | 0.12451
9 | 0.21173 | 0.10254
10 | 0.50073 | 0.24251
11 | 0.30088 | 0.14572
12 | 0.18743 | 0.090778
13 | 0.12965 | 0.062791
14 | 0.082988 | 0.040193
15 | 0.27151 | 0.1315
16 | 0.14426 | 0.069871
17 | 0.16735 | 0.081052
18 | 0.17437 | 0.084452
19 | 0.23592 | 0.11426
20 | 0.29101 | 0.14094
21 | 0.076293 | 0.03695
22 | 0.1093 | 0.052934
23 | 0.21664 | 0.10492
24 | 0.097582 | 0.047261
25 | 0.26158 | 0.12669
26 | 0.35338 | 0.17115
27 | 0.21446 | 0.10387
28 | 0.11655 | 0.056447
29 | 0.15023 | 0.072758
30 | 0.21775 | 0.10546
31 | 0.076 | 0.036809
32 | 1.6741 | 0.81082
33 | 0.14579 | 0.07061
34 | 0.35607 | 0.17245
35 | 0.083191 | 0.040291
36 | 0.24138 | 0.11691
37 | 0.2606 | 0.12621
38 | 0.21244 | 0.10289
39 | 0.2224 | 0.10772
40 | 0.25829 | 0.12509
41 | 0.36703 | 0.17776
42 | 0.34059 | 0.16495
43 | 0.28724 | 0.13912
44 | 0.2822 | 0.13668
45 | 0.24055 | 0.1165
46 | 0.35245 | 0.1707
47 | 0.2503 | 0.12122
48 | 0.068664 | 0.033256
49 | 0.073913 | 0.035798
50 | 0.16165 | 0.078292
51 | 0.071927 | 0.034836
52 | 0.72312 | 0.35022
53 | 0.086956 | 0.042115
54 | 0.078406 | 0.037974
55 | 0.29836 | 0.1445

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1