## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_54_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_54_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_54_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_54_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_54_0_node_5 | 20 | n |  | TRUE
5 | bus_MV_54_0_node_16 | 20 | n |  | TRUE
6 | bus_MV_54_0_node_14 | 20 | n |  | TRUE
7 | bus_MV_54_0_node_15 | 20 | n |  | TRUE
8 | bus_MV_54_0_node_120 | 20 | n |  | TRUE
9 | bus_MV_54_0_node_119 | 20 | n |  | TRUE
10 | bus_MV_54_0_node_13 | 20 | n |  | TRUE
11 | bus_MV_54_0_node_4 | 20 | n |  | TRUE
12 | bus_MV_54_0_node_154 | 20 | n |  | TRUE
13 | bus_MV_54_0_node_12 | 20 | n |  | TRUE
14 | bus_MV_54_0_node_10 | 20 | n |  | TRUE
15 | bus_MV_54_0_node_115 | 20 | n |  | TRUE
16 | bus_MV_54_0_node_6 | 20 | n |  | TRUE
17 | bus_MV_54_0_node_101 | 20 | n |  | TRUE
18 | bus_MV_54_0_node_114 | 20 | n |  | TRUE
19 | bus_MV_54_0_node_82 | 20 | n |  | TRUE
20 | bus_MV_54_0_node_7 | 20 | n |  | TRUE
21 | bus_MV_54_0_node_8 | 20 | n |  | TRUE
22 | bus_MV_54_0_node_11 | 20 | n |  | TRUE
23 | bus_MV_54_0_node_9 | 20 | n |  | TRUE
24 | bus_MV_54_0_node_162 | 20 | n |  | TRUE
25 | bus_MV_54_0_node_17 | 20 | n |  | TRUE
26 | bus_MV_54_0_node_18 | 20 | n |  | TRUE
27 | bus_MV_54_0_node_19 | 20 | n |  | TRUE
28 | bus_MV_54_0_node_20 | 20 | n |  | TRUE
29 | bus_MV_54_0_node_21 | 20 | n |  | TRUE
30 | bus_MV_54_0_node_22 | 20 | n |  | TRUE
31 | bus_MV_54_0_node_28 | 20 | n |  | TRUE
32 | bus_MV_54_0_node_29 | 20 | n |  | TRUE
33 | bus_MV_54_0_node_26 | 20 | n |  | TRUE
34 | bus_MV_54_0_node_23 | 20 | n |  | TRUE
35 | bus_MV_54_0_node_24 | 20 | n |  | TRUE
36 | bus_MV_54_0_node_25 | 20 | n |  | TRUE
37 | bus_MV_54_0_node_27 | 20 | n |  | TRUE
38 | bus_MV_54_0_node_147 | 20 | n |  | TRUE
39 | bus_MV_54_0_node_148 | 20 | n |  | TRUE
40 | bus_MV_54_0_node_149 | 20 | n |  | TRUE
41 | bus_MV_54_0_node_30 | 20 | n |  | TRUE
42 | bus_MV_54_0_node_31 | 20 | n |  | TRUE
43 | bus_MV_54_0_node_157 | 20 | n |  | TRUE
44 | bus_MV_54_0_node_156 | 20 | n |  | TRUE
45 | bus_MV_54_0_node_40 | 20 | n |  | TRUE
46 | bus_MV_54_0_node_32 | 20 | n |  | TRUE
47 | bus_MV_54_0_node_33 | 20 | n |  | TRUE
48 | bus_MV_54_0_node_34 | 20 | n |  | TRUE
49 | bus_MV_54_0_node_110 | 20 | n |  | TRUE
50 | bus_MV_54_0_node_112 | 20 | n |  | TRUE
51 | bus_MV_54_0_node_35 | 20 | n |  | TRUE
52 | bus_MV_54_0_node_172 | 20 | n |  | TRUE
53 | bus_MV_54_0_node_46 | 20 | n |  | TRUE
54 | bus_MV_54_0_node_36 | 20 | n |  | TRUE
55 | bus_MV_54_0_node_37 | 20 | n |  | TRUE
56 | bus_MV_54_0_node_38 | 20 | n |  | TRUE
57 | bus_MV_54_0_node_41 | 20 | n |  | TRUE
58 | bus_MV_54_0_node_39 | 20 | n |  | TRUE
59 | bus_MV_54_0_node_113 | 20 | n |  | TRUE
60 | bus_MV_54_0_node_158 | 20 | n |  | TRUE
61 | bus_MV_54_0_node_155 | 20 | n |  | TRUE
62 | bus_MV_54_0_node_150 | 20 | n |  | TRUE
63 | bus_MV_54_0_node_151 | 20 | n |  | TRUE
64 | bus_MV_54_0_node_153 | 20 | n |  | TRUE
65 | bus_MV_54_0_node_42 | 20 | n |  | TRUE
66 | bus_MV_54_0_node_43 | 20 | n |  | TRUE
67 | bus_MV_54_0_node_44 | 20 | n |  | TRUE
68 | bus_MV_54_0_node_45 | 20 | n |  | TRUE
69 | bus_MV_54_0_node_109 | 20 | n |  | TRUE
70 | bus_MV_54_0_node_48 | 20 | n |  | TRUE
71 | bus_MV_54_0_node_52 | 20 | n |  | TRUE
72 | bus_MV_54_0_node_173 | 20 | n |  | TRUE
73 | bus_MV_54_0_node_47 | 20 | n |  | TRUE
74 | bus_MV_54_0_node_182 | 20 | n |  | TRUE
75 | bus_MV_54_0_node_49 | 20 | n |  | TRUE
76 | bus_MV_54_0_node_181 | 20 | n |  | TRUE
77 | bus_MV_54_0_node_122 | 20 | n |  | TRUE
78 | bus_MV_54_0_node_121 | 20 | n |  | TRUE
79 | bus_MV_54_0_node_50 | 20 | n |  | TRUE
80 | bus_MV_54_0_node_51 | 20 | n |  | TRUE
81 | bus_MV_54_0_node_170 | 20 | n |  | TRUE
82 | bus_MV_54_0_node_126 | 20 | n |  | TRUE
83 | bus_MV_54_0_node_134 | 20 | n |  | TRUE
84 | bus_MV_54_0_node_111 | 20 | n |  | TRUE
85 | bus_MV_54_0_node_174 | 20 | n |  | TRUE
86 | bus_MV_54_0_node_131 | 20 | n |  | TRUE
87 | bus_MV_54_0_node_128 | 20 | n |  | TRUE
88 | bus_MV_54_0_node_124 | 20 | n |  | TRUE
89 | bus_MV_54_0_node_53 | 20 | n |  | TRUE
90 | bus_MV_54_0_node_55 | 20 | n |  | TRUE
91 | bus_MV_54_0_node_54 | 20 | n |  | TRUE
92 | bus_MV_54_0_node_58 | 20 | n |  | TRUE
93 | bus_MV_54_0_node_60 | 20 | n |  | TRUE
94 | bus_MV_54_0_node_56 | 20 | n |  | TRUE
95 | bus_MV_54_0_node_133 | 20 | n |  | TRUE
96 | bus_MV_54_0_node_57 | 20 | n |  | TRUE
97 | bus_MV_54_0_node_105 | 20 | n |  | TRUE
98 | bus_MV_54_0_node_125 | 20 | n |  | TRUE
99 | bus_MV_54_0_node_64 | 20 | n |  | TRUE
100 | bus_MV_54_0_node_79 | 20 | n |  | TRUE
101 | bus_MV_54_0_node_62 | 20 | n |  | TRUE
102 | bus_MV_54_0_node_63 | 20 | n |  | TRUE
103 | bus_MV_54_0_node_65 | 20 | n |  | TRUE
104 | bus_MV_54_0_node_73 | 20 | n |  | TRUE
105 | bus_MV_54_0_node_61 | 20 | n |  | TRUE
106 | bus_MV_54_0_node_169 | 20 | n |  | TRUE
107 | bus_MV_54_0_node_72 | 20 | n |  | TRUE
108 | bus_MV_54_0_node_77 | 20 | n |  | TRUE
109 | bus_MV_54_0_node_78 | 20 | n |  | TRUE
110 | bus_MV_54_0_node_76 | 20 | n |  | TRUE
111 | bus_MV_54_0_node_146 | 20 | n |  | TRUE
112 | bus_MV_54_0_node_132 | 20 | n |  | TRUE
113 | bus_MV_54_0_node_106 | 20 | n |  | TRUE
114 | bus_MV_54_0_node_123 | 20 | n |  | TRUE
115 | bus_MV_54_0_node_80 | 20 | n |  | TRUE
116 | bus_MV_54_0_node_166 | 20 | n |  | TRUE
117 | bus_MV_54_0_node_138 | 20 | n |  | TRUE
118 | bus_MV_54_0_node_75 | 20 | n |  | TRUE
119 | bus_MV_54_0_node_85 | 20 | n |  | TRUE
120 | bus_MV_54_0_node_107 | 20 | n |  | TRUE
121 | bus_MV_54_0_node_71 | 20 | n |  | TRUE
122 | bus_MV_54_0_node_68 | 20 | n |  | TRUE
123 | bus_MV_54_0_node_66 | 20 | n |  | TRUE
124 | bus_MV_54_0_node_67 | 20 | n |  | TRUE
125 | bus_MV_54_0_node_69 | 20 | n |  | TRUE
126 | bus_MV_54_0_node_171 | 20 | n |  | TRUE
127 | bus_MV_54_0_node_70 | 20 | n |  | TRUE
128 | bus_MV_54_0_node_81 | 20 | n |  | TRUE
129 | bus_MV_54_0_node_90 | 20 | n |  | TRUE
130 | bus_MV_54_0_node_159 | 20 | n |  | TRUE
131 | bus_MV_54_0_node_92 | 20 | n |  | TRUE
132 | bus_MV_54_0_node_161 | 20 | n |  | TRUE
133 | bus_MV_54_0_node_91 | 20 | n |  | TRUE
134 | bus_MV_54_0_node_99 | 20 | n |  | TRUE
135 | bus_MV_54_0_node_160 | 20 | n |  | TRUE
136 | bus_MV_54_0_node_87 | 20 | n |  | TRUE
137 | bus_MV_54_0_node_89 | 20 | n |  | TRUE
138 | bus_MV_54_0_node_88 | 20 | n |  | TRUE
139 | bus_MV_54_0_node_86 | 20 | n |  | TRUE
140 | bus_MV_54_0_node_117 | 20 | n |  | TRUE
141 | bus_MV_54_0_node_108 | 20 | n |  | TRUE
142 | bus_MV_54_0_node_118 | 20 | n |  | TRUE
143 | bus_MV_54_0_node_83 | 20 | n |  | TRUE
144 | bus_MV_54_0_node_84 | 20 | n |  | TRUE
145 | bus_MV_54_0_node_95 | 20 | n |  | TRUE
146 | bus_MV_54_0_node_97 | 20 | n |  | TRUE
147 | bus_MV_54_0_node_136 | 20 | n |  | TRUE
148 | bus_MV_54_0_node_135 | 20 | n |  | TRUE
149 | bus_MV_54_0_node_96 | 20 | n |  | TRUE
150 | bus_MV_54_0_node_98 | 20 | n |  | TRUE
151 | bus_MV_54_0_node_137 | 20 | n |  | TRUE
152 | bus_MV_54_0_node_180 | 20 | n |  | TRUE
153 | bus_MV_54_0_node_163 | 20 | n |  | TRUE
154 | bus_MV_54_0_node_140 | 20 | n |  | TRUE
155 | bus_MV_54_0_node_141 | 20 | n |  | TRUE
156 | bus_MV_54_0_node_143 | 20 | n |  | TRUE
157 | bus_MV_54_0_node_142 | 20 | n |  | TRUE
158 | bus_MV_54_0_node_164 | 20 | n |  | TRUE
159 | bus_MV_54_0_node_145 | 20 | n |  | TRUE
160 | bus_MV_54_0_node_144 | 20 | n |  | TRUE
161 | bus_MV_54_0_node_167 | 20 | n |  | TRUE
162 | bus_MV_54_0_node_168 | 20 | n |  | TRUE
163 | bus_MV_54_0_node_165 | 20 | n |  | TRUE
164 | bus_MV_54_0_node_177 | 20 | n |  | TRUE
165 | bus_MV_54_0_node_93 | 20 | n |  | TRUE
166 | bus_MV_54_0_node_94 | 20 | n |  | TRUE
167 | bus_MV_54_0_node_179 | 20 | n |  | TRUE
168 | bus_MV_54_0_node_103 | 20 | n |  | TRUE
169 | bus_MV_54_0_node_116 | 20 | n |  | TRUE
170 | bus_MV_54_0_node_104 | 20 | n |  | TRUE
171 | bus_MV_54_0_node_102 | 20 | n |  | TRUE
172 | bus_MV_54_0_node_139 | 20 | n |  | TRUE
173 | bus_MV_54_0_node_178 | 20 | n |  | TRUE
174 | bus_MV_54_0_node_130 | 20 | n |  | TRUE
175 | bus_MV_54_0_node_127 | 20 | n |  | TRUE
176 | bus_MV_54_0_node_129 | 20 | n |  | TRUE
177 | bus_MV_54_0_node_152 | 20 | n |  | TRUE
178 | bus_MV_54_0_node_176 | 20 | n |  | TRUE
179 | bus_MV_54_0_node_175 | 20 | n |  | TRUE
180 | bus_HV_54_0_node_114 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_54_0_load_0 | 0 | 0.40546 | 0.19637 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_54_0_load_14 | 6 | 0.1203 | 0.058265 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_54_0_load_15 | 7 | 0.05048 | 0.024449 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_54_0_load_120 | 8 | 0.10372 | 0.050235 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_54_0_load_13 | 10 | 0.14112 | 0.068349 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_54_0_load_154 | 12 | 0.1699 | 0.082285 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_54_0_load_12 | 13 | 0.257 | 0.12447 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_54_0_load_115 | 15 | 0.10491 | 0.050809 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_54_0_load_6 | 16 | 0.18523 | 0.089711 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_54_0_load_114 | 18 | 0.20016 | 0.096944 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_54_0_load_9 | 23 | 0.30435 | 0.1474 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_54_0_load_162 | 24 | 0.11434 | 0.055377 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_54_0_load_17 | 25 | 0.11999 | 0.058114 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_54_0_load_20 | 28 | 0.13431 | 0.065047 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_54_0_load_28 | 31 | 0.10722 | 0.051929 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_54_0_load_23 | 34 | 0.13946 | 0.067546 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_54_0_load_147 | 38 | 0.12225 | 0.059209 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_54_0_load_148 | 39 | 0.12982 | 0.062873 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_54_0_load_30 | 41 | 0.27674 | 0.13403 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_54_0_load_156 | 44 | 0.27489 | 0.13314 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_54_0_load_110 | 49 | 0.33623 | 0.16284 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_54_0_load_112 | 50 | 0.36499 | 0.17677 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_54_0_load_172 | 52 | 0.23725 | 0.11491 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_54_0_load_36 | 54 | 0.28277 | 0.13695 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_54_0_load_113 | 59 | 0.2954 | 0.14307 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_54_0_load_158 | 60 | 0.095851 | 0.046423 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_54_0_load_155 | 61 | 0.052956 | 0.025648 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_54_0_load_151 | 63 | 0.050946 | 0.024674 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_54_0_load_42 | 65 | 0.29914 | 0.14488 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_54_0_load_109 | 69 | 0.21386 | 0.10358 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_54_0_load_173 | 72 | 0.34399 | 0.1666 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_54_0_load_182 | 74 | 0.15945 | 0.077226 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_54_0_load_181 | 76 | 0.33511 | 0.1623 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_54_0_load_121 | 78 | 0.28223 | 0.13669 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_54_0_load_170 | 81 | 0.17982 | 0.087089 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_54_0_load_134 | 83 | 0.11144 | 0.053972 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_54_0_load_111 | 84 | 0.27534 | 0.13335 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_54_0_load_174 | 85 | 0.15968 | 0.077335 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_54_0_load_128 | 87 | 0.10954 | 0.053053 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_54_0_load_53 | 89 | 0.26651 | 0.12908 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_54_0_load_133 | 95 | 0.34046 | 0.16489 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_54_0_load_105 | 97 | 0.32399 | 0.15692 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_54_0_load_125 | 98 | 0.077801 | 0.037681 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_54_0_load_79 | 100 | 0.40294 | 0.19515 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_54_0_load_73 | 104 | 0.24631 | 0.11929 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_54_0_load_169 | 106 | 0.3131 | 0.15164 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_54_0_load_77 | 108 | 0.37076 | 0.17957 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_54_0_load_78 | 109 | 0.25667 | 0.12431 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_54_0_load_76 | 110 | 0.37949 | 0.18379 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_54_0_load_146 | 111 | 0.40715 | 0.19719 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_54_0_load_106 | 113 | 1.8886 | 0.91471 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_54_0_load_123 | 114 | 0.11635 | 0.056353 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_54_0_load_166 | 116 | 0.32694 | 0.15834 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_54_0_load_138 | 117 | 0.076985 | 0.037286 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_54_0_load_107 | 120 | 0.34436 | 0.16678 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_54_0_load_66 | 123 | 0.33266 | 0.16111 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_54_0_load_171 | 126 | 0.37622 | 0.18221 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_54_0_load_70 | 127 | 0.088621 | 0.042921 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_54_0_load_159 | 130 | 0.29341 | 0.14211 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_54_0_load_161 | 132 | 0.3534 | 0.17116 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_54_0_load_160 | 135 | 0.3992 | 0.19334 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_54_0_load_86 | 139 | 0.29942 | 0.14502 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_54_0_load_117 | 140 | 0.070183 | 0.033991 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_54_0_load_108 | 141 | 0.38558 | 0.18674 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_54_0_load_118 | 142 | 0.090276 | 0.043723 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_54_0_load_83 | 143 | 0.2077 | 0.10059 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_54_0_load_136 | 147 | 0.25863 | 0.12526 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_54_0_load_135 | 148 | 0.11324 | 0.054845 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_54_0_load_98 | 150 | 0.20581 | 0.099678 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_54_0_load_180 | 152 | 0.076714 | 0.037154 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_54_0_load_140 | 154 | 0.085804 | 0.041557 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_54_0_load_164 | 158 | 0.206 | 0.099772 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_54_0_load_145 | 159 | 0.081446 | 0.039446 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_54_0_load_144 | 160 | 0.082554 | 0.039983 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_54_0_load_168 | 162 | 0.18927 | 0.091669 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_54_0_load_177 | 164 | 0.14308 | 0.069297 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_54_0_load_93 | 165 | 0.21814 | 0.10565 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_54_0_load_179 | 167 | 0.14861 | 0.071973 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_54_0_load_139 | 172 | 2.0174 | 0.97709 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_54_0_load_178 | 173 | 0.24323 | 0.1178 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_54_0_load_130 | 174 | 0.11856 | 0.057421 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_54_0_load_127 | 175 | 0.077756 | 0.037659 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_54_0_load_129 | 176 | 0.10114 | 0.048983 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_54_0_load_176 | 178 | 0.072921 | 0.035317 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_54_0_load_175 | 179 | 0.1358 | 0.06577 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_54_0_line_0 |  | 0 | 1 | 0.02212 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
1 | MV_54_0_line_1 |  | 0 | 2 | 0.0269 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
2 | MV_54_0_line_2 |  | 1 | 3 | 0.31583 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
3 | MV_54_0_line_3 |  | 2 | 4 | 0.74669 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
4 | MV_54_0_line_4 |  | 3 | 10 | 0.016675 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
5 | MV_54_0_line_5 |  | 4 | 13 | 0.05564 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_54_0_line_6 |  | 4 | 11 | 0.29559 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
7 | MV_54_0_line_7 |  | 5 | 6 | 1.3471 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
8 | MV_54_0_line_8 |  | 5 | 7 | 0.039588 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
9 | MV_54_0_line_9 |  | 6 | 10 | 0.33718 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
10 | MV_54_0_line_10 |  | 7 | 25 | 0.6665 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
11 | MV_54_0_line_11 |  | 8 | 9 | 0.024435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_54_0_line_12 |  | 9 | 133 | 0.032083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_54_0_line_13 |  | 11 | 12 | 0.071411 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
14 | MV_54_0_line_14 |  | 12 | 14 | 0.034812 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
15 | MV_54_0_line_15 |  | 14 | 21 | 0.41354 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
16 | MV_54_0_line_16 |  | 15 | 16 | 1.9697 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
17 | MV_54_0_line_17 |  | 15 | 17 | 0.054533 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
18 | MV_54_0_line_18 |  | 16 | 20 | 0.06201 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
19 | MV_54_0_line_19 |  | 17 | 169 | 0.077735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_54_0_line_20 |  | 17 | 170 | 0.063332 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
21 | MV_54_0_line_21 |  | 18 | 19 | 0.033872 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
22 | MV_54_0_line_22 |  | 19 | 115 | 0.33223 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
23 | MV_54_0_line_23 |  | 20 | 21 | 0.21436 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
24 | MV_54_0_line_24 |  | 21 | 22 | 1.4564 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
25 | MV_54_0_line_25 |  | 21 | 23 | 0.026783 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_54_0_line_26 |  | 22 | 24 | 0.1108 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
27 | MV_54_0_line_27 |  | 25 | 26 | 0.04852 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
28 | MV_54_0_line_28 |  | 26 | 27 | 0.19241 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
29 | MV_54_0_line_29 |  | 27 | 28 | 0.058057 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
30 | MV_54_0_line_30 |  | 28 | 29 | 0.1118 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
31 | MV_54_0_line_31 |  | 29 | 30 | 0.20544 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
32 | MV_54_0_line_32 |  | 30 | 31 | 0.009934 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_54_0_line_33 |  | 31 | 32 | 0.099935 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
34 | MV_54_0_line_34 |  | 32 | 33 | 0.096976 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
35 | MV_54_0_line_35 |  | 33 | 38 | 0.004248 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_54_0_line_36 |  | 33 | 35 | 0.25615 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
37 | MV_54_0_line_37 |  | 34 | 35 | 0.092702 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
38 | MV_54_0_line_38 |  | 34 | 36 | 0.11706 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
39 | MV_54_0_line_39 |  | 36 | 37 | 0.22697 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
40 | MV_54_0_line_40 |  | 37 | 39 | 0.013211 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
41 | MV_54_0_line_41 |  | 39 | 40 | 0.038703 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
42 | MV_54_0_line_42 |  | 40 | 62 | 1.3715 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
43 | MV_54_0_line_43 |  | 41 | 42 | 0.0099257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_54_0_line_44 |  | 42 | 43 | 0.12178 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
45 | MV_54_0_line_45 |  | 43 | 44 | 0.030642 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_54_0_line_46 |  | 43 | 45 | 0.05473 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_54_0_line_47 |  | 44 | 46 | 0.01743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_54_0_line_48 |  | 45 | 60 | 0.03566 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_54_0_line_49 |  | 45 | 55 | 0.16114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_54_0_line_50 |  | 45 | 58 | 0.2262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_54_0_line_51 |  | 46 | 47 | 0.21704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_54_0_line_52 |  | 47 | 48 | 0.23313 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_54_0_line_53 |  | 47 | 49 | 0.025147 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_54_0_line_54 |  | 48 | 50 | 0.021103 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_54_0_line_55 |  | 49 | 53 | 0.008486 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_54_0_line_56 |  | 49 | 51 | 0.15443 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_54_0_line_57 |  | 51 | 52 | 0.046242 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_54_0_line_58 |  | 53 | 68 | 0.61141 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_54_0_line_59 |  | 54 | 55 | 0.017208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_54_0_line_60 |  | 54 | 56 | 0.064499 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_54_0_line_61 |  | 56 | 57 | 0.53656 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_54_0_line_62 |  | 57 | 61 | 0.114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_54_0_line_63 |  | 58 | 59 | 0.046074 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
64 | MV_54_0_line_64 |  | 62 | 63 | 0.065027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_54_0_line_65 |  | 62 | 64 | 0.99598 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_54_0_line_66 |  | 64 | 179 | 0.018024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_54_0_line_67 |  | 64 | 177 | 0.35262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_54_0_line_68 |  | 65 | 66 | 0.054042 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_54_0_line_69 |  | 66 | 67 | 0.093348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_54_0_line_70 |  | 67 | 68 | 0.3773 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_54_0_line_71 |  | 67 | 69 | 0.013336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_54_0_line_72 |  | 68 | 70 | 0.72878 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_54_0_line_73 |  | 68 | 71 | 0.39889 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_54_0_line_74 |  | 68 | 72 | 0.007849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_54_0_line_75 |  | 70 | 76 | 0.051979 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_54_0_line_76 |  | 70 | 73 | 0.45571 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_54_0_line_77 |  | 71 | 84 | 0.021394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_54_0_line_78 |  | 73 | 74 | 0.023354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_54_0_line_79 |  | 73 | 75 | 0.22231 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_54_0_line_80 |  | 75 | 77 | 0.075607 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
81 | MV_54_0_line_81 |  | 75 | 78 | 0.019123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_54_0_line_82 |  | 77 | 85 | 0.00661 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
83 | MV_54_0_line_83 |  | 77 | 86 | 0.019333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_54_0_line_84 |  | 79 | 80 | 0.14001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_54_0_line_85 |  | 79 | 81 | 0.020301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_54_0_line_86 |  | 80 | 82 | 0.037185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_54_0_line_87 |  | 80 | 83 | 0.017038 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_54_0_line_88 |  | 82 | 87 | 0.014635 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
89 | MV_54_0_line_89 |  | 82 | 88 | 0.027967 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
90 | MV_54_0_line_90 |  | 85 | 97 | 0.10566 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
91 | MV_54_0_line_91 |  | 86 | 174 | 0.015482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_54_0_line_92 |  | 87 | 112 | 0.01635 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_54_0_line_93 |  | 88 | 175 | 0.029552 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_54_0_line_94 |  | 88 | 114 | 0.023756 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
95 | MV_54_0_line_95 |  | 89 | 90 | 0.008351 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
96 | MV_54_0_line_96 |  | 89 | 91 | 0.049342 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
97 | MV_54_0_line_97 |  | 90 | 92 | 0.35762 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
98 | MV_54_0_line_98 |  | 90 | 93 | 0.39119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_54_0_line_99 |  | 91 | 94 | 0.12373 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_54_0_line_100 |  | 92 | 99 | 0.17162 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_54_0_line_101 |  | 92 | 100 | 0.019855 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
102 | MV_54_0_line_102 |  | 93 | 101 | 0.22337 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_54_0_line_103 |  | 93 | 102 | 0.12933 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_54_0_line_104 |  | 93 | 103 | 0.17106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_54_0_line_105 |  | 93 | 104 | 0.008174 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_54_0_line_106 |  | 94 | 95 | 0.032926 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
107 | MV_54_0_line_107 |  | 95 | 112 | 0.037602 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
108 | MV_54_0_line_108 |  | 96 | 97 | 0.034476 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
109 | MV_54_0_line_109 |  | 96 | 98 | 0.078505 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
110 | MV_54_0_line_110 |  | 97 | 113 | 0.11978 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_54_0_line_111 |  | 98 | 114 | 0.025387 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
112 | MV_54_0_line_112 |  | 99 | 110 | 0.004103 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_54_0_line_113 |  | 100 | 115 | 0.01179 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
114 | MV_54_0_line_114 |  | 101 | 107 | 0.18483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_54_0_line_115 |  | 101 | 108 | 0.018806 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
116 | MV_54_0_line_116 |  | 101 | 105 | 0.24925 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_54_0_line_117 |  | 102 | 109 | 0.015842 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_54_0_line_118 |  | 103 | 111 | 0.001367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_54_0_line_119 |  | 104 | 118 | 0.11224 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_54_0_line_120 |  | 105 | 106 | 0.030753 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_54_0_line_121 |  | 106 | 119 | 0.018743 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_54_0_line_122 |  | 107 | 120 | 0.016666 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
123 | MV_54_0_line_123 |  | 107 | 121 | 0.55429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_54_0_line_124 |  | 111 | 122 | 0.007325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_54_0_line_125 |  | 115 | 128 | 0.41724 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
126 | MV_54_0_line_126 |  | 116 | 117 | 0.10533 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
127 | MV_54_0_line_127 |  | 117 | 118 | 0.035224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_54_0_line_128 |  | 119 | 144 | 0.16485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_54_0_line_129 |  | 121 | 127 | 0.077095 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
130 | MV_54_0_line_130 |  | 122 | 125 | 0.15092 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_54_0_line_131 |  | 122 | 124 | 0.27625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_54_0_line_132 |  | 123 | 124 | 0.022559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_54_0_line_133 |  | 125 | 126 | 0.014243 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_54_0_line_134 |  | 128 | 129 | 0.19663 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
135 | MV_54_0_line_135 |  | 128 | 130 | 0.038984 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
136 | MV_54_0_line_136 |  | 129 | 133 | 0.067504 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
137 | MV_54_0_line_137 |  | 129 | 134 | 0.21741 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
138 | MV_54_0_line_138 |  | 129 | 135 | 0.010681 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
139 | MV_54_0_line_139 |  | 129 | 136 | 0.38942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_54_0_line_140 |  | 129 | 137 | 0.30736 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_54_0_line_141 |  | 129 | 131 | 0.49553 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_54_0_line_142 |  | 131 | 132 | 0.032324 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
143 | MV_54_0_line_143 |  | 133 | 142 | 0.037657 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
144 | MV_54_0_line_144 |  | 134 | 150 | 0.044284 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
145 | MV_54_0_line_145 |  | 136 | 138 | 0.094006 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_54_0_line_146 |  | 136 | 139 | 0.049647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_54_0_line_147 |  | 137 | 141 | 0.050975 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
148 | MV_54_0_line_148 |  | 138 | 140 | 0.0333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_54_0_line_149 |  | 142 | 152 | 0.19737 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
150 | MV_54_0_line_150 |  | 143 | 144 | 0.004577 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_54_0_line_151 |  | 145 | 146 | 0.1586 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
152 | MV_54_0_line_152 |  | 145 | 147 | 0.064286 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
153 | MV_54_0_line_153 |  | 146 | 148 | 0.061315 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_54_0_line_154 |  | 146 | 149 | 0.48906 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
155 | MV_54_0_line_155 |  | 147 | 151 | 0.1503 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
156 | MV_54_0_line_156 |  | 149 | 167 | 0.019956 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
157 | MV_54_0_line_157 |  | 149 | 166 | 0.16027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_54_0_line_158 |  | 151 | 153 | 0.88804 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
159 | MV_54_0_line_159 |  | 152 | 171 | 0.009418 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
160 | MV_54_0_line_160 |  | 153 | 161 | 0.37329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_54_0_line_161 |  | 153 | 162 | 0.1857 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
162 | MV_54_0_line_162 |  | 154 | 155 | 0.023062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_54_0_line_163 |  | 155 | 156 | 0.038829 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_54_0_line_164 |  | 156 | 159 | 0.064425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_54_0_line_165 |  | 156 | 160 | 0.029891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_54_0_line_166 |  | 156 | 157 | 0.10284 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_54_0_line_167 |  | 157 | 158 | 0.012622 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_54_0_line_168 |  | 158 | 163 | 0.039793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_54_0_line_169 |  | 161 | 164 | 0.053835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_54_0_line_170 |  | 162 | 163 | 0.55489 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
171 | MV_54_0_line_171 |  | 165 | 166 | 0.021005 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_54_0_line_172 |  | 167 | 168 | 0.010756 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
173 | MV_54_0_line_173 |  | 168 | 170 | 0.18429 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
174 | MV_54_0_line_174 |  | 169 | 173 | 0.003425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_54_0_line_175 |  | 170 | 172 | 0.0021504 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_54_0_line_176 |  | 170 | 171 | 0.19012 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
177 | MV_54_0_line_177 |  | 174 | 176 | 0.001114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_54_0_line_178 |  | 177 | 178 | 0.023954 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_54_0_trafo_114 | 25 MVA 110/20 kV | 180 | 18 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2726427.8342 | 1221928.2538
1 | 2726448.4439 | 1221936.4424
2 | 2726402.6094 | 1221918.7107
3 | 2726681.1268 | 1222132.6893
4 | 2725901.5622 | 1221845.9274
5 | 2728209.3141 | 1222828.3792
6 | 2726953.3598 | 1222341.2098
7 | 2728244.4481 | 1222842.5251
8 | 2722920.8558 | 1221197.0462
9 | 2722914.5724 | 1221176.8339
10 | 2726694.6069 | 1222125.0144
11 | 2725737.3841 | 1221671.4641
12 | 2725671.9403 | 1221642.4485
13 | 2725848.9577 | 1221827.801
14 | 2725639.8902 | 1221628.639
15 | 2723177.9096 | 1221492.8411
16 | 2725147.5702 | 1221503.4735
17 | 2723123.3986 | 1221491.3282
18 | 2723026.9342 | 1220796.4215
19 | 2722995.4101 | 1220808.8135
20 | 2725209.1493 | 1221510.7736
21 | 2725421.7551 | 1221536.4343
22 | 2725789.9029 | 1222346.623
23 | 2725418.9173 | 1221563.0624
24 | 2725839.9457 | 1222445.4816
25 | 2728684.0671 | 1223343.4828
26 | 2728716.2501 | 1223379.8747
27 | 2728817.8049 | 1223500.5469
28 | 2728808.7496 | 1223557.8864
29 | 2728881.4352 | 1223642.8285
30 | 2729023.0347 | 1223533.3955
31 | 2729032.4155 | 1223530.0516
32 | 2729127.8767 | 1223500.4862
33 | 2729149.5574 | 1223415.2538
34 | 2729391.1511 | 1223503.9542
35 | 2729325.1711 | 1223496.9991
36 | 2729479.6812 | 1223505.987
37 | 2729643.408 | 1223398.0287
38 | 2729145.3803 | 1223414.4181
39 | 2729653.0707 | 1223389.0874
40 | 2729670.2561 | 1223356.613
41 | 2722989.7708 | 1219310.7758
42 | 2722998.9471 | 1219314.5594
43 | 2723106.3128 | 1219372.0331
44 | 2723075.9501 | 1219367.9025
45 | 2723160.0737 | 1219382.2856
46 | 2723058.6393 | 1219365.4763
47 | 2722884.3788 | 1219424.2365
48 | 2722880.0677 | 1219195.0906
49 | 2722890.861 | 1219448.5337
50 | 2722884.7813 | 1219174.5273
51 | 2722736.895 | 1219436.6171
52 | 2722693.3294 | 1219452.1207
53 | 2722893.4191 | 1219456.6261
54 | 2723330.0314 | 1219351.8776
55 | 2723313.5586 | 1219357.0073
56 | 2723393.6534 | 1219352.2286
57 | 2723655.5835 | 1219612.2302
58 | 2723283.4786 | 1219501.6092
59 | 2723268.3218 | 1219545.1186
60 | 2723167.3319 | 1219347.3749
61 | 2723704.6719 | 1219509.3018
62 | 2731041.342 | 1223390.6385
63 | 2731066.5626 | 1223420.7961
64 | 2731689.152 | 1223326.1346
65 | 2723185.5144 | 1219751.9012
66 | 2723232.6596 | 1219778.3192
67 | 2723258.9536 | 1219719.2947
68 | 2723066.7628 | 1219883.8725
69 | 2723267.6721 | 1219709.1894
70 | 2722729.669 | 1220132.7685
71 | 2723080.7893 | 1219644.1855
72 | 2723059.4686 | 1219880.9195
73 | 2722945.232 | 1220169.7538
74 | 2722933.1122 | 1220150.1994
75 | 2722902.3979 | 1220307.3778
76 | 2722699.6705 | 1220175.2171
77 | 2722955.5047 | 1220284.9673
78 | 2722902.2793 | 1220288.2553
79 | 2722804.0893 | 1220414.2451
80 | 2722881.0063 | 1220436.5711
81 | 2722796.6561 | 1220433.14
82 | 2722915.7038 | 1220449.9419
83 | 2722888.9664 | 1220421.5067
84 | 2723060.891 | 1219636.9799
85 | 2722962.1115 | 1220284.4255
86 | 2722966.1741 | 1220275.8804
87 | 2722910.6091 | 1220463.6612
88 | 2722943.2253 | 1220453.9353
89 | 2722742.001 | 1220572.6785
90 | 2722733.9256 | 1220574.8917
91 | 2722790.9003 | 1220566.0812
92 | 2722742.0075 | 1220708.1627
93 | 2722457.8283 | 1220629.2961
94 | 2722898.9686 | 1220544.026
95 | 2722898.4036 | 1220511.1107
96 | 2723001.4582 | 1220366.3132
97 | 2723035.375 | 1220360.5535
98 | 2722938.4883 | 1220413.1944
99 | 2722690.8416 | 1220853.4893
100 | 2722761.9161 | 1220707.7171
101 | 2722321.881 | 1220628.3909
102 | 2722570.1425 | 1220643.4395
103 | 2722482.5466 | 1220464.4752
104 | 2722450.1639 | 1220632.1963
105 | 2722221.0226 | 1220473.2435
106 | 2722241.4982 | 1220450.7683
107 | 2722145.2108 | 1220585.9655
108 | 2722315.0095 | 1220645.8968
109 | 2722569.8314 | 1220659.2789
110 | 2722689.0878 | 1220857.2005
111 | 2722482.817 | 1220463.1353
112 | 2722901.4544 | 1220473.6332
113 | 2723147.9865 | 1220319.7296
114 | 2722948.0058 | 1220433.386
115 | 2722773.7404 | 1220707.7164
116 | 2722548.6535 | 1220831.2001
117 | 2722466.8959 | 1220764.7859
118 | 2722457.2626 | 1220744.2078
119 | 2722257.3198 | 1220460.8898
120 | 2722143.8075 | 1220602.5719
121 | 2721649.7334 | 1220454.2784
122 | 2722484.2248 | 1220455.9475
123 | 2722332.7219 | 1220326.922
124 | 2722337.2292 | 1220304.8195
125 | 2722584.009 | 1220407.9403
126 | 2722598.0662 | 1220410.4761
127 | 2721612.7708 | 1220387.4604
128 | 2722767.0999 | 1221044.3438
129 | 2722858.3759 | 1221218.4294
130 | 2722733.0292 | 1221063.2898
131 | 2722645.8885 | 1221193.1189
132 | 2722632.7615 | 1221163.581
133 | 2722889.948 | 1221178.605
134 | 2722873.5832 | 1221435.3025
135 | 2722856.565 | 1221228.9558
136 | 2722611.1317 | 1221034.3676
137 | 2722837.2102 | 1220978.3708
138 | 2722698.118 | 1221025.4741
139 | 2722568.2105 | 1221009.2088
140 | 2722680.5326 | 1220997.1961
141 | 2722886.0968 | 1220992.8128
142 | 2722906.892 | 1221212.2343
143 | 2722376.3151 | 1220499.4636
144 | 2722374.6036 | 1220503.7095
145 | 2722752.372 | 1221768.5985
146 | 2722787.107 | 1221887.8973
147 | 2722695.6862 | 1221798.9208
148 | 2722749.1938 | 1221844.2148
149 | 2723005.1214 | 1221606.0522
150 | 2722908.1072 | 1221463.0367
151 | 2722586.551 | 1221901.1537
152 | 2723004.8097 | 1221383.604
153 | 2722015.2998 | 1222071.2888
154 | 2721506.5975 | 1221797.7451
155 | 2721515.6923 | 1221776.6534
156 | 2721521.7943 | 1221750.2127
157 | 2721573.9537 | 1221682.6466
158 | 2721583.2422 | 1221674.074
159 | 2721538.7383 | 1221692.2576
160 | 2721499.1744 | 1221769.7523
161 | 2721863.7481 | 1222410.4517
162 | 2722102.5675 | 1221907.371
163 | 2721612.5307 | 1221647.0509
164 | 2721829.5575 | 1222452.0847
165 | 2723072.7318 | 1221656.3776
166 | 2723052.6227 | 1221662.6336
167 | 2722991.2979 | 1221591.622
168 | 2722983.8166 | 1221583.8726
169 | 2723143.9472 | 1221431.2279
170 | 2723085.5481 | 1221465.6144
171 | 2722999.1597 | 1221391.1488
172 | 2723083.3997 | 1221465.5205
173 | 2723143.8157 | 1221434.6501
174 | 2722964.8252 | 1220260.4572
175 | 2722954.3967 | 1220478.9522
176 | 2722964.7282 | 1220259.3475
177 | 2731808.2275 | 1223092.7555
178 | 2731824.2444 | 1223074.9066
179 | 2731698.7296 | 1223341.4035
180 | 2723026.9342 | 1220796.4215

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99507 | -0.18322 | 0.40546 | 0.19637
1 | 0.99507 | -0.18328 | 0 | 0
2 | 0.99508 | -0.18314 | 0 | 0
3 | 0.995 | -0.18408 | 0 | 0
4 | 0.99527 | -0.18064 | 0 | 0
5 | 0.99451 | -0.22204 | 0 | 0
6 | 0.99489 | -0.19233 | 0.1203 | 0.058265
7 | 0.99451 | -0.22213 | 0.05048 | 0.024449
8 | 0.99773 | -0.029484 | 0.10372 | 0.050235
9 | 0.99773 | -0.029514 | 0 | 0
10 | 0.995 | -0.18412 | 0.14112 | 0.068349
11 | 0.99536 | -0.17947 | 0 | 0
12 | 0.99538 | -0.17918 | 0.1699 | 0.082285
13 | 0.99525 | -0.18082 | 0.257 | 0.12447
14 | 0.99539 | -0.17903 | 0 | 0
15 | 0.99705 | -0.059415 | 0.10491 | 0.050809
16 | 0.99565 | -0.17256 | 0.18523 | 0.089711
17 | 0.99707 | -0.059081 | 0 | 0
18 | 1 | 0 | -21.1645 | -8.9185
19 | 0.99977 | -0.013851 | 0 | 0
20 | 0.99561 | -0.17591 | 0 | 0
21 | 0.99553 | -0.17717 | 0 | 0
22 | 0.9955 | -0.17852 | 0 | 0
23 | 0.99552 | -0.17707 | 0.30435 | 0.1474
24 | 0.9955 | -0.17873 | 0.11434 | 0.055377
25 | 0.99433 | -0.23615 | 0.11999 | 0.058114
26 | 0.99432 | -0.23625 | 0 | 0
27 | 0.9943 | -0.23662 | 0 | 0
28 | 0.99429 | -0.23673 | 0.13431 | 0.065047
29 | 0.99427 | -0.23851 | 0 | 0
30 | 0.99425 | -0.23884 | 0 | 0
31 | 0.99425 | -0.23885 | 0.10722 | 0.051929
32 | 0.99423 | -0.24021 | 0 | 0
33 | 0.99422 | -0.24035 | 0 | 0
34 | 0.99419 | -0.24074 | 0.13946 | 0.067546
35 | 0.9942 | -0.24065 | 0 | 0
36 | 0.99418 | -0.24084 | 0 | 0
37 | 0.99417 | -0.24099 | 0 | 0
38 | 0.99422 | -0.24034 | 0.12225 | 0.059209
39 | 0.99417 | -0.241 | 0.12982 | 0.062873
40 | 0.99417 | -0.24101 | 0 | 0
41 | 0.98812 | 0.0084456 | 0.27674 | 0.13403
42 | 0.98812 | 0.0084121 | 0 | 0
43 | 0.98819 | 0.0088323 | 0 | 0
44 | 0.98825 | 0.0092895 | 0.27489 | 0.13314
45 | 0.98814 | 0.0092211 | 0 | 0
46 | 0.98828 | 0.0090493 | 0 | 0
47 | 0.98863 | 0.0060983 | 0 | 0
48 | 0.98852 | 0.0070912 | 0 | 0
49 | 0.98871 | 0.0066975 | 0.33623 | 0.16284
50 | 0.98851 | 0.0071851 | 0.36499 | 0.17677
51 | 0.98864 | 0.0062426 | 0 | 0
52 | 0.98862 | 0.0061069 | 0.23725 | 0.11491
53 | 0.98873 | 0.0064896 | 0 | 0
54 | 0.98806 | 0.0097366 | 0.28277 | 0.13695
55 | 0.98807 | 0.0096847 | 0 | 0
56 | 0.98806 | 0.0097114 | 0 | 0
57 | 0.98802 | 0.0097475 | 0 | 0
58 | 0.98805 | 0.01 | 0 | 0
59 | 0.98802 | 0.0098317 | 0.2954 | 0.14307
60 | 0.98813 | 0.0092621 | 0.095851 | 0.046423
61 | 0.98801 | 0.0098116 | 0.052956 | 0.025648
62 | 0.99407 | -0.24822 | 0 | 0
63 | 0.99406 | -0.24818 | 0.050946 | 0.024674
64 | 0.99381 | -0.24705 | 0 | 0
65 | 0.99015 | -0.0058523 | 0.29914 | 0.14488
66 | 0.99019 | -0.0056529 | 0 | 0
67 | 0.99022 | -0.0059866 | 0 | 0
68 | 0.99047 | -0.0081766 | 0 | 0
69 | 0.99022 | -0.005952 | 0.21386 | 0.10358
70 | 0.99359 | -0.033853 | 0 | 0
71 | 0.99033 | -0.0069711 | 0 | 0
72 | 0.99047 | -0.0081437 | 0.34399 | 0.1666
73 | 0.99573 | -0.051259 | 0 | 0
74 | 0.99573 | -0.051214 | 0.15945 | 0.077226
75 | 0.99682 | -0.060027 | 0 | 0
76 | 0.99356 | -0.034066 | 0.33511 | 0.1623
77 | 0.99699 | -0.058054 | 0 | 0
78 | 0.99682 | -0.059963 | 0.28223 | 0.13669
79 | 0.99742 | -0.037815 | 0 | 0
80 | 0.99745 | -0.038098 | 0 | 0
81 | 0.99741 | -0.037771 | 0.17982 | 0.087089
82 | 0.99746 | -0.038217 | 0 | 0
83 | 0.99744 | -0.038076 | 0.11144 | 0.053972
84 | 0.99032 | -0.0068995 | 0.27534 | 0.13335
85 | 0.997 | -0.058032 | 0.15968 | 0.077335
86 | 0.99699 | -0.058004 | 0 | 0
87 | 0.99748 | -0.03814 | 0.10954 | 0.053053
88 | 0.99743 | -0.038359 | 0 | 0
89 | 0.99792 | -0.02455 | 0.26651 | 0.12908
90 | 0.99793 | -0.024501 | 0 | 0
91 | 0.99779 | -0.031849 | 0 | 0
92 | 0.99859 | -0.021467 | 0 | 0
93 | 0.99626 | -0.010247 | 0 | 0
94 | 0.99763 | -0.032551 | 0 | 0
95 | 0.99759 | -0.032735 | 0.34046 | 0.16489
96 | 0.9972 | -0.048698 | 0 | 0
97 | 0.99716 | -0.048865 | 0.32399 | 0.15692
98 | 0.99737 | -0.038603 | 0.077801 | 0.037681
99 | 0.99851 | -0.020709 | 0 | 0
100 | 0.99863 | -0.02129 | 0.40294 | 0.19515
101 | 0.99589 | -0.0071541 | 0 | 0
102 | 0.99622 | -0.0098596 | 0 | 0
103 | 0.99602 | -0.0080905 | 0 | 0
104 | 0.99626 | -0.010183 | 0.24631 | 0.11929
105 | 0.99572 | -0.0057183 | 0 | 0
106 | 0.9957 | -0.0055346 | 0.3131 | 0.15164
107 | 0.99579 | -0.0063925 | 0 | 0
108 | 0.99588 | -0.0072391 | 0.37076 | 0.17957
109 | 0.99621 | -0.0099092 | 0.25667 | 0.12431
110 | 0.99851 | -0.02069 | 0.37949 | 0.18379
111 | 0.99602 | -0.008073 | 0.40715 | 0.19719
112 | 0.9975 | -0.038052 | 0 | 0
113 | 0.99672 | -0.051616 | 1.8886 | 0.91471
114 | 0.9974 | -0.038478 | 0.11635 | 0.056353
115 | 0.99865 | -0.021182 | 0 | 0
116 | 0.99608 | -0.010995 | 0.32694 | 0.15834
117 | 0.99615 | -0.010575 | 0.076985 | 0.037286
118 | 0.99617 | -0.010745 | 0 | 0
119 | 0.9957 | -0.0054927 | 0 | 0
120 | 0.99578 | -0.0064624 | 0.34436 | 0.16678
121 | 0.99573 | -0.0060986 | 0 | 0
122 | 0.99601 | -0.0080156 | 0 | 0
123 | 0.99589 | -0.0068847 | 0.33266 | 0.16111
124 | 0.9959 | -0.0069748 | 0 | 0
125 | 0.99594 | -0.0073514 | 0 | 0
126 | 0.99593 | -0.007287 | 0.37622 | 0.18221
127 | 0.99572 | -0.0060206 | 0.088621 | 0.042921
128 | 0.99807 | -0.026436 | 0 | 0
129 | 0.99781 | -0.028824 | 0 | 0
130 | 0.99805 | -0.026575 | 0.29341 | 0.14211
131 | 0.99758 | -0.026907 | 0 | 0
132 | 0.99756 | -0.027046 | 0.3534 | 0.17116
133 | 0.99773 | -0.029552 | 0 | 0
134 | 0.99772 | -0.029371 | 0 | 0
135 | 0.9978 | -0.028876 | 0.3992 | 0.19334
136 | 0.99762 | -0.027314 | 0 | 0
137 | 0.99765 | -0.027473 | 0 | 0
138 | 0.99761 | -0.027247 | 0 | 0
139 | 0.9976 | -0.027138 | 0.29942 | 0.14502
140 | 0.99761 | -0.027219 | 0.070183 | 0.033991
141 | 0.99762 | -0.027712 | 0.38558 | 0.18674
142 | 0.99769 | -0.029954 | 0.090276 | 0.043723
143 | 0.99565 | -0.0050899 | 0.2077 | 0.10059
144 | 0.99565 | -0.0051013 | 0 | 0
145 | 0.99694 | -0.060612 | 0 | 0
146 | 0.99697 | -0.060328 | 0 | 0
147 | 0.99692 | -0.061967 | 0.25863 | 0.12526
148 | 0.99696 | -0.060247 | 0.11324 | 0.054845
149 | 0.99705 | -0.059266 | 0 | 0
150 | 0.9977 | -0.029481 | 0.20581 | 0.099678
151 | 0.9969 | -0.062192 | 0 | 0
152 | 0.99731 | -0.056586 | 0.076714 | 0.037154
153 | 0.99679 | -0.063095 | 0 | 0
154 | 0.99656 | -0.069055 | 0.085804 | 0.041557
155 | 0.99656 | -0.069078 | 0 | 0
156 | 0.99657 | -0.069116 | 0 | 0
157 | 0.9966 | -0.069393 | 0 | 0
158 | 0.9966 | -0.069426 | 0.206 | 0.099772
159 | 0.99656 | -0.069056 | 0.081446 | 0.039446
160 | 0.99656 | -0.069087 | 0.082554 | 0.039983
161 | 0.99673 | -0.062588 | 0 | 0
162 | 0.99675 | -0.065375 | 0.18927 | 0.091669
163 | 0.99663 | -0.069626 | 0 | 0
164 | 0.99672 | -0.062498 | 0.14308 | 0.069297
165 | 0.997 | -0.058816 | 0.21814 | 0.10565
166 | 0.99701 | -0.05887 | 0 | 0
167 | 0.99706 | -0.059215 | 0.14861 | 0.071973
168 | 0.99706 | -0.059187 | 0 | 0
169 | 0.99705 | -0.058858 | 0 | 0
170 | 0.9971 | -0.058679 | 0 | 0
171 | 0.9973 | -0.056685 | 0 | 0
172 | 0.9971 | -0.058626 | 2.0174 | 0.97709
173 | 0.99705 | -0.058848 | 0.24323 | 0.1178
174 | 0.99698 | -0.057963 | 0.11856 | 0.057421
175 | 0.99743 | -0.038332 | 0.077756 | 0.037659
176 | 0.99698 | -0.057962 | 0.10114 | 0.048983
177 | 0.99377 | -0.24685 | 0 | 0
178 | 0.99377 | -0.24683 | 0.072921 | 0.035317
179 | 0.9938 | -0.24702 | 0.1358 | 0.06577
180 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 1.3253 | 0.38023 | -1.3253 | -0.38298 | 5.4709e-06 | -0.0027493 | 0.039999 | 0.040021 | 0.040021 | 0.99507 | -0.18322 | 0.99507 | -0.18328 | 3.1365
1 | -1.7308 | -0.5766 | 1.7308 | 0.57326 | 1.1634e-05 | -0.0033406 | 0.052924 | 0.052893 | 0.052924 | 0.99507 | -0.18322 | 0.99508 | -0.18314 | 4.1476
2 | 1.3253 | 0.38298 | -1.3252 | -0.42223 | 7.8791e-05 | -0.039251 | 0.040021 | 0.040353 | 0.040353 | 0.99507 | -0.18328 | 0.995 | -0.18408 | 3.1624
3 | -1.7308 | -0.57326 | 1.7311 | 0.48051 | 0.00031779 | -0.09275 | 0.052893 | 0.052108 | 0.052893 | 0.99508 | -0.18314 | 0.99527 | -0.18064 | 4.1452
4 | 1.3252 | 0.42223 | -1.3252 | -0.4243 | 4.197e-06 | -0.0020722 | 0.040353 | 0.040371 | 0.040371 | 0.995 | -0.18408 | 0.995 | -0.18412 | 3.1639
5 | 0.25701 | 0.12441 | -0.257 | -0.12447 | 6.8001e-06 | -6.1536e-05 | 0.0082818 | 0.0082826 | 0.0082826 | 0.99527 | -0.18064 | 0.99525 | -0.18082 | 3.9441
6 | -1.9881 | -0.60492 | 1.9883 | 0.56821 | 0.00016507 | -0.036705 | 0.060275 | 0.059973 | 0.060275 | 0.99527 | -0.18064 | 0.99536 | -0.17947 | 4.7237
7 | -1.0635 | -0.30142 | 1.0637 | 0.2984 | 0.00024732 | -0.0030198 | 0.032085 | 0.032056 | 0.032085 | 0.99451 | -0.22204 | 0.99489 | -0.19233 | 2.4872
8 | 1.0635 | 0.30142 | -1.0635 | -0.30634 | 6.3043e-06 | -0.0049168 | 0.032085 | 0.032125 | 0.032125 | 0.99451 | -0.22204 | 0.99451 | -0.22213 | 2.5176
9 | -1.184 | -0.35667 | 1.1841 | 0.35595 | 7.7469e-05 | -0.00071446 | 0.03588 | 0.035873 | 0.03588 | 0.99489 | -0.19233 | 0.995 | -0.18412 | 2.7814
10 | 1.013 | 0.28189 | -1.0129 | -0.28341 | 0.00011088 | -0.0015239 | 0.030521 | 0.030536 | 0.030536 | 0.99451 | -0.22213 | 0.99433 | -0.23615 | 2.3671
11 | -0.10372 | -0.050235 | 0.10372 | 0.049654 | 3.6192e-07 | -0.00058067 | 0.0033345 | 0.0033272 | 0.0033345 | 0.99773 | -0.029484 | 0.99773 | -0.029514 | 1.5157
12 | -0.10372 | -0.049654 | 0.10372 | 0.048892 | 4.7279e-07 | -0.0007624 | 0.0033272 | 0.0033177 | 0.0033272 | 0.99773 | -0.029514 | 0.99773 | -0.029552 | 1.5124
13 | -1.9883 | -0.56821 | 1.9883 | 0.55935 | 3.9636e-05 | -0.0088686 | 0.059973 | 0.059902 | 0.059973 | 0.99536 | -0.17947 | 0.99538 | -0.17918 | 4.7
14 | -2.1582 | -0.64163 | 2.1582 | 0.63731 | 2.2921e-05 | -0.0043214 | 0.065299 | 0.065263 | 0.065299 | 0.99538 | -0.17918 | 0.99539 | -0.17903 | 5.1175
15 | -2.1582 | -0.63731 | 2.1585 | 0.58597 | 0.0002704 | -0.051344 | 0.065263 | 0.064856 | 0.065263 | 0.99539 | -0.17903 | 0.99553 | -0.17717 | 5.1147
16 | 2.7651 | 0.74178 | -2.7627 | -0.74068 | 0.0024168 | 0.0010932 | 0.082889 | 0.082929 | 0.082929 | 0.99705 | -0.059415 | 0.99565 | -0.17256 | 6.4286
17 | -2.87 | -0.79259 | 2.8701 | 0.78581 | 6.2574e-05 | -0.0067773 | 0.086206 | 0.086154 | 0.086206 | 0.99705 | -0.059415 | 0.99707 | -0.059081 | 6.756
18 | 2.5775 | 0.65097 | -2.5774 | -0.65097 | 6.5759e-05 | 6.892e-06 | 0.077077 | 0.077078 | 0.077078 | 0.99565 | -0.17256 | 0.99561 | -0.17591 | 5.975
19 | 0.24323 | 0.11588 | -0.24323 | -0.11772 | 6.3331e-06 | -0.0018432 | 0.0078004 | 0.0078236 | 0.0078236 | 0.99707 | -0.059081 | 0.99705 | -0.058858 | 3.5562
20 | -3.1133 | -0.90168 | 3.1134 | 0.89382 | 8.6109e-05 | -0.0078638 | 0.093842 | 0.093778 | 0.093842 | 0.99707 | -0.059081 | 0.9971 | -0.058679 | 7.3544
21 | 21.1505 | 8.908 | -21.1478 | -8.9009 | 0.0026537 | 0.0070425 | 0.6625 | 0.66251 | 0.66251 | 1 | 0 | 0.99977 | -0.013851 | 51.357
22 | 21.1478 | 8.9009 | -21.1253 | -8.9299 | 0.022545 | -0.028988 | 0.66251 | 0.66297 | 0.66297 | 0.99977 | -0.013851 | 0.99865 | -0.021182 | 51.9571
23 | 2.5774 | 0.65097 | -2.5772 | -0.67755 | 0.00019725 | -0.026588 | 0.077078 | 0.077271 | 0.077271 | 0.99561 | -0.17591 | 0.99553 | -0.17717 | 6.0557
24 | 0.11434 | -0.055182 | -0.11434 | -0.055094 | 2.93e-06 | -0.11028 | 0.0036815 | 0.0036805 | 0.0036815 | 0.99553 | -0.17717 | 0.9955 | -0.17852 | 0.43724
25 | 0.30436 | 0.14677 | -0.30435 | -0.1474 | 3.4354e-06 | -0.00063274 | 0.009798 | 0.009806 | 0.009806 | 0.99553 | -0.17717 | 0.99552 | -0.17707 | 4.4573
26 | 0.11434 | 0.055094 | -0.11434 | -0.055377 | 5.3544e-07 | -0.00028348 | 0.0036805 | 0.003684 | 0.003684 | 0.9955 | -0.17852 | 0.9955 | -0.17873 | 0.44927
27 | 0.89289 | 0.2253 | -0.89289 | -0.23133 | 5.3667e-06 | -0.0060252 | 0.026735 | 0.026778 | 0.026778 | 0.99433 | -0.23615 | 0.99432 | -0.23625 | 2.0986
28 | 0.89289 | 0.23133 | -0.89287 | -0.25522 | 2.146e-05 | -0.023893 | 0.026778 | 0.026961 | 0.026961 | 0.99432 | -0.23625 | 0.9943 | -0.23662 | 2.1129
29 | 0.89287 | 0.25522 | -0.89286 | -0.26243 | 6.5341e-06 | -0.007209 | 0.026961 | 0.027019 | 0.027019 | 0.9943 | -0.23662 | 0.99429 | -0.23673 | 2.1175
30 | 0.75855 | 0.19738 | -0.75854 | -0.19766 | 1.0335e-05 | -0.00027775 | 0.022757 | 0.022759 | 0.022759 | 0.99429 | -0.23673 | 0.99427 | -0.23851 | 1.7643
31 | 0.75854 | 0.19766 | -0.75853 | -0.22317 | 1.6579e-05 | -0.025511 | 0.022759 | 0.022957 | 0.022957 | 0.99427 | -0.23851 | 0.99425 | -0.23884 | 1.7991
32 | 0.75853 | 0.22317 | -0.75853 | -0.2244 | 8.0915e-07 | -0.0012336 | 0.022957 | 0.022967 | 0.022967 | 0.99425 | -0.23884 | 0.99425 | -0.23885 | 1.7999
33 | 0.65131 | 0.17247 | -0.6513 | -0.17273 | 6.8271e-06 | -0.00025475 | 0.019562 | 0.019564 | 0.019564 | 0.99425 | -0.23885 | 0.99423 | -0.24021 | 1.5166
34 | 0.6513 | 0.17273 | -0.65129 | -0.18477 | 5.7616e-06 | -0.012043 | 0.019564 | 0.019657 | 0.019657 | 0.99423 | -0.24021 | 0.99422 | -0.24035 | 1.5405
35 | 0.12225 | 0.059109 | -0.12225 | -0.059209 | 8.818e-08 | -0.00010023 | 0.0039428 | 0.003944 | 0.003944 | 0.99422 | -0.24035 | 0.99422 | -0.24034 | 1.7927
36 | 0.52904 | 0.12566 | -0.52903 | -0.15747 | 1.0007e-05 | -0.031811 | 0.015788 | 0.016027 | 0.016027 | 0.99422 | -0.24035 | 0.9942 | -0.24065 | 1.256
37 | -0.52903 | -0.16899 | 0.52903 | 0.15747 | 3.7012e-06 | -0.011512 | 0.016126 | 0.016027 | 0.016126 | 0.99419 | -0.24074 | 0.9942 | -0.24065 | 1.2638
38 | 0.38956 | 0.10144 | -0.38956 | -0.11598 | 2.4943e-06 | -0.014538 | 0.011689 | 0.011802 | 0.011802 | 0.99419 | -0.24074 | 0.99418 | -0.24084 | 0.92493
39 | 0.38956 | 0.11598 | -0.38956 | -0.14417 | 4.9871e-06 | -0.028189 | 0.011802 | 0.012061 | 0.012061 | 0.99418 | -0.24084 | 0.99417 | -0.24099 | 0.94523
40 | 0.38956 | 0.14417 | -0.38956 | -0.14581 | 2.9733e-07 | -0.0016407 | 0.012061 | 0.012078 | 0.012078 | 0.99417 | -0.24099 | 0.99417 | -0.241 | 0.94654
41 | 0.25974 | 0.082935 | -0.25974 | -0.087742 | 3.7683e-07 | -0.0048068 | 0.0079171 | 0.0079607 | 0.0079607 | 0.99417 | -0.241 | 0.99417 | -0.24101 | 0.62388
42 | 0.25974 | 0.087742 | -0.25972 | -0.091447 | 1.5583e-05 | -0.0037053 | 0.0079607 | 0.0079962 | 0.0079962 | 0.99417 | -0.24101 | 0.99407 | -0.24822 | 0.61986
43 | -0.27674 | -0.13403 | 0.27674 | 0.1338 | 1.0689e-06 | -0.00023107 | 0.008983 | 0.0089801 | 0.008983 | 0.98812 | 0.0084456 | 0.98812 | 0.0084121 | 4.0832
44 | -0.27674 | -0.1338 | 0.27675 | 0.13367 | 1.7494e-05 | -0.000131 | 0.0089801 | 0.0089783 | 0.0089801 | 0.98812 | 0.0084121 | 0.98819 | 0.0088323 | 4.2762
45 | -1.0038 | -0.45753 | 1.0039 | 0.45753 | 5.6701e-05 | -2.0819e-07 | 0.032227 | 0.032227 | 0.032227 | 0.98819 | 0.0088323 | 0.98825 | 0.0092895 | 15.3462
46 | 0.72708 | 0.32387 | -0.72704 | -0.32513 | 3.9528e-05 | -0.0012643 | 0.023252 | 0.023267 | 0.023267 | 0.98819 | 0.0088323 | 0.98814 | 0.0092211 | 10.5759
47 | -1.2788 | -0.59067 | 1.2788 | 0.59028 | 3.9391e-05 | -0.00039476 | 0.041147 | 0.041142 | 0.041147 | 0.98825 | 0.0092895 | 0.98828 | 0.0090493 | 18.7031
48 | 0.095851 | 0.045591 | -0.095851 | -0.046423 | 4.5929e-07 | -0.0008312 | 0.0031008 | 0.0031113 | 0.0031113 | 0.98814 | 0.0092211 | 0.98813 | 0.0092621 | 1.4142
49 | 0.33576 | 0.14179 | -0.33573 | -0.14553 | 2.4487e-05 | -0.0037491 | 0.010648 | 0.010691 | 0.010691 | 0.98814 | 0.0092211 | 0.98807 | 0.0096847 | 4.8594
50 | 0.29544 | 0.13776 | -0.29541 | -0.14302 | 2.7575e-05 | -0.0052647 | 0.009523 | 0.0095891 | 0.0095891 | 0.98814 | 0.0092211 | 0.98805 | 0.01 | 4.3587
51 | -1.2788 | -0.59028 | 1.2793 | 0.58536 | 0.0004897 | -0.0049177 | 0.041142 | 0.04108 | 0.041142 | 0.98828 | 0.0090493 | 0.98863 | 0.0060983 | 18.7008
52 | 0.36504 | 0.17086 | -0.365 | -0.17628 | 4.3355e-05 | -0.0054269 | 0.011769 | 0.011837 | 0.011837 | 0.98863 | 0.0060983 | 0.98852 | 0.0070912 | 5.3804
53 | -1.6444 | -0.75622 | 1.6445 | 0.75626 | 0.00012514 | 4.9037e-05 | 0.052849 | 0.052848 | 0.052849 | 0.98863 | 0.0060983 | 0.98871 | 0.0066975 | 25.166
54 | 0.365 | 0.17628 | -0.36499 | -0.17677 | 3.9495e-06 | -0.00049118 | 0.011837 | 0.011843 | 0.011843 | 0.98852 | 0.0070912 | 0.98851 | 0.0071851 | 5.3833
55 | -2.218 | -1.0338 | 2.218 | 1.0336 | 5.7829e-05 | -0.00018091 | 0.071448 | 0.071445 | 0.071448 | 0.98871 | 0.0066975 | 0.98873 | 0.0064896 | 32.4763
56 | 0.23727 | 0.11469 | -0.23726 | -0.11486 | 1.6295e-05 | -0.00017 | 0.0076945 | 0.0076968 | 0.0076968 | 0.98871 | 0.0066975 | 0.98864 | 0.0062426 | 3.6651
57 | 0.23726 | 0.11486 | -0.23725 | -0.11491 | 4.8812e-06 | -5.0898e-05 | 0.0076968 | 0.0076975 | 0.0076975 | 0.98864 | 0.0062426 | 0.98862 | 0.0061069 | 3.6655
58 | -2.218 | -1.0336 | 2.2222 | 1.0206 | 0.0041562 | -0.013063 | 0.071445 | 0.07127 | 0.071445 | 0.98873 | 0.0064896 | 0.99047 | -0.0081766 | 32.4751
59 | -0.33573 | -0.14593 | 0.33573 | 0.14553 | 2.6267e-06 | -0.00040033 | 0.010695 | 0.010691 | 0.010695 | 0.98806 | 0.0097366 | 0.98807 | 0.0096847 | 4.8616
60 | 0.052958 | 0.0089817 | -0.052958 | -0.010485 | 2.131e-07 | -0.0015034 | 0.0015693 | 0.0015773 | 0.0015773 | 0.98806 | 0.0097366 | 0.98806 | 0.0097114 | 0.71695
61 | 0.052958 | 0.010485 | -0.052956 | -0.022991 | 1.8861e-06 | -0.012506 | 0.0015773 | 0.0016868 | 0.0016868 | 0.98806 | 0.0097114 | 0.98802 | 0.0097475 | 0.76672
62 | 0.052956 | 0.022991 | -0.052956 | -0.025648 | 4.4116e-07 | -0.0026568 | 0.0016868 | 0.0017192 | 0.0017192 | 0.98802 | 0.0097475 | 0.98801 | 0.0098116 | 0.78144
63 | 0.29541 | 0.14302 | -0.2954 | -0.14307 | 7.5488e-06 | -4.8967e-05 | 0.0095891 | 0.0095898 | 0.0095898 | 0.98805 | 0.01 | 0.98802 | 0.0098317 | 4.5666
64 | 0.050946 | 0.02314 | -0.050946 | -0.024674 | 2.3186e-07 | -0.0015341 | 0.0016249 | 0.0016439 | 0.0016439 | 0.99407 | -0.24822 | 0.99406 | -0.24818 | 0.74721
65 | 0.20878 | 0.068307 | -0.20872 | -0.091783 | 5.6062e-05 | -0.023476 | 0.0063791 | 0.0066231 | 0.0066231 | 0.99407 | -0.24822 | 0.99381 | -0.24705 | 3.0105
66 | 0.1358 | 0.065345 | -0.1358 | -0.06577 | 4.6165e-07 | -0.00042489 | 0.0043775 | 0.0043828 | 0.0043828 | 0.99381 | -0.24705 | 0.9938 | -0.24702 | 1.9922
67 | 0.072924 | 0.026439 | -0.072922 | -0.034753 | 2.484e-06 | -0.0083141 | 0.0022532 | 0.0023465 | 0.0023465 | 0.99381 | -0.24705 | 0.99377 | -0.24685 | 1.0666
68 | -0.29914 | -0.14488 | 0.29915 | 0.14482 | 9.0408e-06 | -5.7591e-05 | 0.0096903 | 0.0096895 | 0.0096903 | 0.99015 | -0.0058523 | 0.99019 | -0.0056529 | 4.6144
69 | -0.29915 | -0.14482 | 0.29916 | 0.14264 | 1.1667e-05 | -0.0021819 | 0.0096895 | 0.0096619 | 0.0096895 | 0.99019 | -0.0056529 | 0.99022 | -0.0059866 | 4.4043
70 | -0.51302 | -0.2459 | 0.51315 | 0.23711 | 0.00013763 | -0.0087945 | 0.016585 | 0.016475 | 0.016585 | 0.99022 | -0.0059866 | 0.99047 | -0.0081766 | 7.5387
71 | 0.21386 | 0.10326 | -0.21386 | -0.10358 | 8.5383e-07 | -0.00031196 | 0.0069232 | 0.0069272 | 0.0069272 | 0.99022 | -0.0059866 | 0.99022 | -0.005952 | 3.1487
72 | -3.3547 | -1.5476 | 3.366 | 1.5338 | 0.011259 | -0.013785 | 0.10768 | 0.10747 | 0.10768 | 0.99047 | -0.0081766 | 0.99359 | -0.033853 | 48.9441
73 | 0.27538 | 0.12352 | -0.27534 | -0.13285 | 4.1738e-05 | -0.0093296 | 0.0087965 | 0.0089115 | 0.0089115 | 0.99047 | -0.0081766 | 0.99033 | -0.0069711 | 4.0507
74 | 0.34399 | 0.16642 | -0.34399 | -0.1666 | 1.3e-06 | -0.00018346 | 0.011137 | 0.01114 | 0.01114 | 0.99047 | -0.0081766 | 0.99047 | -0.0081437 | 5.0635
75 | 0.33512 | 0.16225 | -0.33511 | -0.1623 | 1.0838e-05 | -5.4469e-05 | 0.010818 | 0.010818 | 0.010818 | 0.99359 | -0.033853 | 0.99356 | -0.034066 | 5.1517
76 | -3.7011 | -1.6961 | 3.7096 | 1.6878 | 0.0085025 | -0.0082426 | 0.11828 | 0.11815 | 0.11828 | 0.99359 | -0.033853 | 0.99573 | -0.051259 | 53.7656
77 | 0.27534 | 0.13285 | -0.27534 | -0.13335 | 2.2698e-06 | -0.0005003 | 0.0089115 | 0.0089178 | 0.0089178 | 0.99033 | -0.0069711 | 0.99032 | -0.0068995 | 4.0535
78 | 0.15945 | 0.076674 | -0.15945 | -0.077226 | 8.2142e-07 | -0.00055261 | 0.0051294 | 0.0051364 | 0.0051364 | 0.99573 | -0.051259 | 0.99573 | -0.051214 | 2.3347
79 | -3.8691 | -1.7645 | 3.8736 | 1.7606 | 0.0045085 | -0.0039312 | 0.12328 | 0.12322 | 0.12328 | 0.99573 | -0.051259 | 0.99682 | -0.060027 | 56.0377
80 | -4.1558 | -1.8968 | 4.1564 | 1.8947 | 0.00063897 | -0.0021134 | 0.13229 | 0.13226 | 0.13229 | 0.99682 | -0.060027 | 0.99699 | -0.058054 | 36.545
81 | 0.28223 | 0.13624 | -0.28223 | -0.13669 | 2.104e-06 | -0.00045306 | 0.0090756 | 0.0090813 | 0.0090813 | 0.99682 | -0.060027 | 0.99682 | -0.059963 | 4.1279
82 | -4.3761 | -2.0002 | 4.3762 | 1.9994 | 1.982e-05 | -0.00081449 | 0.13932 | 0.13931 | 0.13932 | 0.99699 | -0.058054 | 0.997 | -0.058032 | 10.9183
83 | 0.2197 | 0.10555 | -0.2197 | -0.10601 | 1.2865e-06 | -0.00045844 | 0.0070574 | 0.0070631 | 0.0070631 | 0.99699 | -0.058054 | 0.99699 | -0.058004 | 3.2105
84 | -0.17982 | -0.086607 | 0.17982 | 0.083283 | 6.1922e-06 | -0.0033238 | 0.0057765 | 0.0057354 | 0.0057765 | 0.99742 | -0.037815 | 0.99745 | -0.038098 | 2.6257
85 | 0.17982 | 0.086607 | -0.17982 | -0.087089 | 9.0529e-07 | -0.00048194 | 0.0057765 | 0.0057826 | 0.0057826 | 0.99742 | -0.037815 | 0.99741 | -0.037771 | 2.6285
86 | -0.29126 | -0.13685 | 0.29127 | 0.13597 | 4.3011e-06 | -0.00088203 | 0.0093137 | 0.0093028 | 0.0093137 | 0.99745 | -0.038098 | 0.99746 | -0.038217 | 4.2335
87 | 0.11144 | 0.053568 | -0.11144 | -0.053972 | 2.9168e-07 | -0.00040464 | 0.0035785 | 0.0035836 | 0.0035836 | 0.99745 | -0.038098 | 0.99744 | -0.038076 | 1.6289
88 | -7.3143 | -3.4045 | 7.3144 | 3.4028 | 0.00012326 | -0.0017604 | 0.23349 | 0.23347 | 0.23349 | 0.99746 | -0.038217 | 0.99748 | -0.03814 | 18.2987
89 | 7.023 | 3.2686 | -7.0228 | -3.2719 | 0.00021721 | -0.0033742 | 0.22419 | 0.22423 | 0.22423 | 0.99746 | -0.038217 | 0.99743 | -0.038359 | 17.573
90 | -4.5358 | -2.0768 | 4.5362 | 2.0775 | 0.00039347 | 0.00076769 | 0.14444 | 0.14444 | 0.14444 | 0.997 | -0.058032 | 0.99716 | -0.048865 | 11.1972
91 | 0.2197 | 0.10601 | -0.2197 | -0.10638 | 1.0318e-06 | -0.00036712 | 0.0070631 | 0.0070678 | 0.0070678 | 0.99699 | -0.058004 | 0.99698 | -0.057963 | 3.2126
92 | -7.424 | -3.4558 | 7.4241 | 3.4538 | 0.00014186 | -0.0019644 | 0.23699 | 0.23697 | 0.23699 | 0.99748 | -0.03814 | 0.9975 | -0.038052 | 18.5729
93 | 0.077757 | 0.036957 | -0.077756 | -0.037659 | 2.458e-07 | -0.00070189 | 0.0024917 | 0.0025005 | 0.0025005 | 0.99743 | -0.038359 | 0.99743 | -0.038332 | 1.1366
94 | 6.9451 | 3.235 | -6.9449 | -3.2378 | 0.00018049 | -0.0028682 | 0.22174 | 0.22178 | 0.22178 | 0.99743 | -0.038359 | 0.9974 | -0.038478 | 17.3805
95 | -8.0335 | -3.7313 | 8.0336 | 3.7303 | 8.4707e-05 | -0.00099737 | 0.25623 | 0.25622 | 0.25623 | 0.99792 | -0.02455 | 0.99793 | -0.024501 | 20.0811
96 | 7.767 | 3.6022 | -7.7664 | -3.6009 | 0.00054026 | 0.001317 | 0.24767 | 0.24767 | 0.24767 | 0.99792 | -0.02455 | 0.99779 | -0.031849 | 19.1993
97 | -11.3882 | -5.289 | 11.3955 | 5.2484 | 0.0072787 | -0.040685 | 0.36323 | 0.36268 | 0.36323 | 0.99793 | -0.024501 | 0.99859 | -0.021467 | 28.466
98 | 3.3546 | 1.5588 | -3.3486 | -1.5663 | 0.005986 | -0.0075103 | 0.107 | 0.10712 | 0.10712 | 0.99793 | -0.024501 | 0.99626 | -0.010247 | 48.6902
99 | 7.7664 | 3.6009 | -7.7653 | -3.6157 | 0.0011735 | -0.014816 | 0.24767 | 0.24786 | 0.24786 | 0.99779 | -0.031849 | 0.99763 | -0.032551 | 19.4247
100 | 0.37952 | 0.17962 | -0.37949 | -0.1837 | 3.3897e-05 | -0.0040758 | 0.012138 | 0.012189 | 0.012189 | 0.99859 | -0.021467 | 0.99851 | -0.020709 | 5.5405
101 | -11.775 | -5.428 | 11.7754 | 5.4257 | 0.00043093 | -0.0022455 | 0.37482 | 0.37479 | 0.37482 | 0.99859 | -0.021467 | 0.99863 | -0.02129 | 29.3746
102 | 1.3252 | 0.60597 | -1.3247 | -0.61111 | 0.00053246 | -0.0051336 | 0.042224 | 0.042288 | 0.042288 | 0.99626 | -0.010247 | 0.99589 | -0.0071541 | 19.2218
103 | 0.25669 | 0.12123 | -0.25667 | -0.12429 | 1.1735e-05 | -0.0030611 | 0.0082255 | 0.0082638 | 0.0082638 | 0.99626 | -0.010247 | 0.99622 | -0.0098596 | 3.7563
104 | 1.1164 | 0.52538 | -1.1161 | -0.52935 | 0.0002923 | -0.0039661 | 0.035752 | 0.035802 | 0.035802 | 0.99626 | -0.010247 | 0.99602 | -0.0080905 | 16.2736
105 | 0.6503 | 0.31367 | -0.65029 | -0.31387 | 4.7765e-06 | -0.00019229 | 0.02092 | 0.020923 | 0.020923 | 0.99626 | -0.010247 | 0.99626 | -0.010183 | 9.5104
106 | 7.7653 | 3.6157 | -7.765 | -3.6196 | 0.00031258 | -0.0039419 | 0.24786 | 0.24791 | 0.24791 | 0.99763 | -0.032551 | 0.99759 | -0.032735 | 19.4287
107 | 7.4245 | 3.4548 | -7.4241 | -3.4538 | 0.00037689 | 0.00091004 | 0.23696 | 0.23697 | 0.23697 | 0.99759 | -0.032735 | 0.9975 | -0.038052 | 18.3694
108 | 6.7499 | 3.1453 | -6.7497 | -3.1495 | 0.0002476 | -0.0041685 | 0.21557 | 0.21563 | 0.21563 | 0.9972 | -0.048698 | 0.99716 | -0.048865 | 16.8987
109 | -6.7499 | -3.1453 | 6.7506 | 3.1469 | 0.00065121 | 0.0015353 | 0.21557 | 0.21557 | 0.21557 | 0.9972 | -0.048698 | 0.99737 | -0.038603 | 16.7112
110 | 1.8894 | 0.91506 | -1.8886 | -0.91471 | 0.00078832 | 0.00035166 | 0.060776 | 0.060778 | 0.060778 | 0.99716 | -0.048865 | 0.99672 | -0.051616 | 28.9417
111 | -6.8284 | -3.1846 | 6.8285 | 3.1815 | 0.00018649 | -0.0030685 | 0.21807 | 0.21803 | 0.21807 | 0.99737 | -0.038603 | 0.9974 | -0.038478 | 17.0904
112 | 0.37949 | 0.1837 | -0.37949 | -0.18379 | 8.1388e-07 | -9.743e-05 | 0.012189 | 0.01219 | 0.01219 | 0.99851 | -0.020709 | 0.99851 | -0.02069 | 5.541
113 | -12.1784 | -5.6209 | 12.1786 | 5.6196 | 0.00027383 | -0.0013234 | 0.38773 | 0.38771 | 0.38773 | 0.99863 | -0.02129 | 0.99865 | -0.021182 | 30.3863
114 | 0.43304 | 0.19038 | -0.43299 | -0.19474 | 4.6565e-05 | -0.0043625 | 0.013712 | 0.013763 | 0.013763 | 0.99589 | -0.0071541 | 0.99579 | -0.0063925 | 6.2561
115 | 0.37076 | 0.17955 | -0.37076 | -0.17957 | 4.7778e-06 | -1.9274e-05 | 0.011941 | 0.011941 | 0.011941 | 0.99589 | -0.0071541 | 0.99588 | -0.0072391 | 5.6863
116 | 0.52091 | 0.24118 | -0.52082 | -0.24706 | 9.2529e-05 | -0.0058739 | 0.016639 | 0.016712 | 0.016712 | 0.99589 | -0.0071541 | 0.99572 | -0.0057183 | 7.5963
117 | 0.25667 | 0.12429 | -0.25667 | -0.12431 | 1.9276e-06 | -1.7563e-05 | 0.0082638 | 0.008264 | 0.008264 | 0.99622 | -0.0098596 | 0.99621 | -0.0099092 | 3.9353
118 | 1.1161 | 0.52935 | -1.1161 | -0.52938 | 2.3392e-06 | -3.1685e-05 | 0.035802 | 0.035802 | 0.035802 | 0.99602 | -0.0080905 | 0.99602 | -0.008073 | 16.2738
119 | 0.40399 | 0.19457 | -0.40395 | -0.19468 | 3.3762e-05 | -0.00011183 | 0.012993 | 0.012994 | 0.012994 | 0.99626 | -0.010183 | 0.99617 | -0.010745 | 6.1879
120 | 0.52082 | 0.24706 | -0.5208 | -0.24778 | 1.1473e-05 | -0.00072458 | 0.016712 | 0.016721 | 0.016721 | 0.99572 | -0.0057183 | 0.9957 | -0.0055346 | 7.6005
121 | 0.20771 | 0.096142 | -0.20771 | -0.096585 | 1.1027e-06 | -0.00044334 | 0.0066357 | 0.0066411 | 0.0066411 | 0.9957 | -0.0055346 | 0.9957 | -0.0054927 | 3.0187
122 | 0.34437 | 0.16676 | -0.34436 | -0.16678 | 3.6533e-06 | -1.744e-05 | 0.011092 | 0.011092 | 0.011092 | 0.99579 | -0.0063925 | 0.99578 | -0.0064624 | 5.282
123 | 0.088627 | 0.027976 | -0.088622 | -0.041096 | 5.6265e-06 | -0.013121 | 0.0026942 | 0.0028321 | 0.0028321 | 0.99579 | -0.0063925 | 0.99573 | -0.0060986 | 1.2873
124 | 0.70896 | 0.33219 | -0.70896 | -0.33236 | 5.0357e-06 | -0.00017201 | 0.022692 | 0.022694 | 0.022694 | 0.99602 | -0.008073 | 0.99601 | -0.0080156 | 10.3153
125 | 8.9466 | 3.3104 | -8.9417 | -3.3599 | 0.0049111 | -0.049495 | 0.27575 | 0.27628 | 0.27628 | 0.99865 | -0.021182 | 0.99807 | -0.026436 | 21.6519
126 | -0.32694 | -0.15834 | 0.32696 | 0.15823 | 2.0797e-05 | -0.00011175 | 0.010528 | 0.010526 | 0.010528 | 0.99608 | -0.010995 | 0.99615 | -0.010575 | 5.0132
127 | -0.40394 | -0.19552 | 0.40395 | 0.19468 | 7.9468e-06 | -0.00083221 | 0.013005 | 0.012994 | 0.013005 | 0.99615 | -0.010575 | 0.99617 | -0.010745 | 5.9114
128 | 0.20771 | 0.096585 | -0.2077 | -0.10048 | 9.7767e-06 | -0.0038991 | 0.0066411 | 0.0066896 | 0.0066896 | 0.9957 | -0.0054927 | 0.99565 | -0.0051013 | 3.0407
129 | 0.088622 | 0.041096 | -0.088621 | -0.042921 | 8.3206e-07 | -0.0018248 | 0.0028321 | 0.0028547 | 0.0028547 | 0.99573 | -0.0060986 | 0.99572 | -0.0060206 | 1.2976
130 | 0.37626 | 0.17831 | -0.37623 | -0.18188 | 2.9449e-05 | -0.0035656 | 0.012068 | 0.012112 | 0.012112 | 0.99601 | -0.0080156 | 0.99594 | -0.0073514 | 5.5056
131 | 0.3327 | 0.15405 | -0.33266 | -0.16058 | 4.1958e-05 | -0.00653 | 0.010626 | 0.010707 | 0.010707 | 0.99601 | -0.0080156 | 0.9959 | -0.0069748 | 4.867
132 | -0.33266 | -0.16111 | 0.33266 | 0.16058 | 3.4549e-06 | -0.00053318 | 0.010714 | 0.010707 | 0.010714 | 0.99589 | -0.0068847 | 0.9959 | -0.0069748 | 4.87
133 | 0.37623 | 0.18188 | -0.37622 | -0.18221 | 2.7906e-06 | -0.00033648 | 0.012112 | 0.012117 | 0.012117 | 0.99594 | -0.0073514 | 0.99593 | -0.007287 | 5.5076
134 | 8.6483 | 3.2178 | -8.6461 | -3.2412 | 0.002166 | -0.023388 | 0.26689 | 0.26714 | 0.26714 | 0.99807 | -0.026436 | 0.99781 | -0.028824 | 20.9357
135 | 0.29342 | 0.14206 | -0.29341 | -0.14211 | 6.1757e-06 | -4.2491e-05 | 0.009429 | 0.0094296 | 0.0094296 | 0.99807 | -0.026436 | 0.99805 | -0.026575 | 4.4903
136 | 6.9323 | 2.4441 | -6.9318 | -2.4523 | 0.00047183 | -0.0081793 | 0.21266 | 0.21274 | 0.21274 | 0.99781 | -0.028824 | 0.99773 | -0.029552 | 16.6723
137 | 0.20583 | 0.09938 | -0.20581 | -0.099627 | 1.6946e-05 | -0.00024777 | 0.0066126 | 0.0066159 | 0.0066159 | 0.99781 | -0.028824 | 0.99772 | -0.029371 | 3.1504
138 | 0.39921 | 0.19333 | -0.3992 | -0.19334 | 3.1339e-06 | -1.0732e-05 | 0.012833 | 0.012833 | 0.012833 | 0.99781 | -0.028824 | 0.9978 | -0.028876 | 6.1108
139 | 0.36968 | 0.16557 | -0.36961 | -0.1748 | 7.2073e-05 | -0.0092341 | 0.011719 | 0.011831 | 0.011831 | 0.99781 | -0.028824 | 0.99762 | -0.027314 | 5.3777
140 | 0.38565 | 0.17941 | -0.38559 | -0.18669 | 6.2589e-05 | -0.0072866 | 0.012306 | 0.012396 | 0.012396 | 0.99781 | -0.028824 | 0.99765 | -0.027473 | 5.6346
141 | 0.35349 | 0.15937 | -0.3534 | -0.17112 | 8.4311e-05 | -0.011752 | 0.011218 | 0.011362 | 0.011362 | 0.99781 | -0.028824 | 0.99758 | -0.026907 | 5.1648
142 | 0.3534 | 0.17112 | -0.3534 | -0.17116 | 7.4356e-06 | -3.3743e-05 | 0.011362 | 0.011363 | 0.011363 | 0.99758 | -0.026907 | 0.99756 | -0.027046 | 5.4109
143 | 6.8281 | 2.4034 | -6.8278 | -2.408 | 0.00025526 | -0.0045667 | 0.20944 | 0.20948 | 0.20948 | 0.99773 | -0.029552 | 0.99769 | -0.029954 | 16.4172
144 | 0.20581 | 0.099627 | -0.20581 | -0.099678 | 3.4538e-06 | -5.0461e-05 | 0.0066159 | 0.0066165 | 0.0066165 | 0.99772 | -0.029371 | 0.9977 | -0.029481 | 3.1507
145 | 0.070184 | 0.030966 | -0.070184 | -0.0332 | 6.2577e-07 | -0.0022336 | 0.0022198 | 0.0022466 | 0.0022466 | 0.99762 | -0.027314 | 0.99761 | -0.027247 | 1.0212
146 | 0.29943 | 0.14384 | -0.29942 | -0.14502 | 6.1331e-06 | -0.0011779 | 0.0096121 | 0.009627 | 0.009627 | 0.99762 | -0.027314 | 0.9976 | -0.027138 | 4.3759
147 | 0.38559 | 0.18669 | -0.38558 | -0.18674 | 1.3957e-05 | -5.1825e-05 | 0.012396 | 0.012397 | 0.012397 | 0.99765 | -0.027473 | 0.99762 | -0.027712 | 5.9033
148 | 0.070184 | 0.0332 | -0.070183 | -0.033991 | 2.2537e-07 | -0.00079122 | 0.0022466 | 0.0022565 | 0.0022565 | 0.99761 | -0.027247 | 0.99761 | -0.027219 | 1.0257
149 | 6.7375 | 2.3643 | -6.736 | -2.3608 | 0.0015038 | 0.0035009 | 0.2066 | 0.2066 | 0.2066 | 0.99769 | -0.029954 | 0.99731 | -0.056586 | 16.0159
150 | -0.2077 | -0.10059 | 0.2077 | 0.10048 | 2.7348e-07 | -0.00010825 | 0.006691 | 0.0066896 | 0.006691 | 0.99565 | -0.0050899 | 0.99565 | -0.0051013 | 3.0414
151 | -1.047 | -0.35789 | 1.047 | 0.33809 | 2.501e-05 | -0.019795 | 0.032039 | 0.031858 | 0.032039 | 0.99694 | -0.060612 | 0.99697 | -0.060328 | 2.5109
152 | 1.047 | 0.35789 | -1.047 | -0.35803 | 1.178e-05 | -0.00014496 | 0.032039 | 0.032041 | 0.032041 | 0.99694 | -0.060612 | 0.99692 | -0.061967 | 2.4838
153 | 0.11324 | 0.053391 | -0.11324 | -0.054845 | 1.0811e-06 | -0.0014548 | 0.0036251 | 0.0036433 | 0.0036433 | 0.99697 | -0.060328 | 0.99696 | -0.060247 | 1.656
154 | -1.1603 | -0.39148 | 1.1604 | 0.33044 | 9.3535e-05 | -0.061037 | 0.035457 | 0.034931 | 0.035457 | 0.99697 | -0.060328 | 0.99705 | -0.059266 | 2.7787
155 | 0.78835 | 0.23277 | -0.78833 | -0.25153 | 1.3242e-05 | -0.018763 | 0.023802 | 0.023962 | 0.023962 | 0.99692 | -0.061967 | 0.9969 | -0.062192 | 1.8779
156 | -1.3785 | -0.43179 | 1.3785 | 0.4293 | 5.3905e-06 | -0.00249 | 0.041824 | 0.041802 | 0.041824 | 0.99705 | -0.059266 | 0.99706 | -0.059215 | 3.2777
157 | 0.21815 | 0.10135 | -0.21814 | -0.10515 | 1.0448e-05 | -0.0038009 | 0.0069644 | 0.0070115 | 0.0070115 | 0.99705 | -0.059266 | 0.99701 | -0.05887 | 3.1871
158 | 0.78833 | 0.25153 | -0.78825 | -0.36238 | 8.234e-05 | -0.11085 | 0.023962 | 0.025125 | 0.025125 | 0.9969 | -0.062192 | 0.99679 | -0.063095 | 1.969
159 | 6.6593 | 2.3236 | -6.6592 | -2.3247 | 6.0649e-05 | -0.001143 | 0.20415 | 0.20416 | 0.20416 | 0.99731 | -0.056586 | 0.9973 | -0.056685 | 16.0004
160 | 0.14309 | 0.059169 | -0.14308 | -0.068021 | 1.0249e-05 | -0.008852 | 0.0044843 | 0.0045885 | 0.0045885 | 0.99679 | -0.063095 | 0.99673 | -0.062588 | 2.0857
161 | 0.64516 | 0.30321 | -0.64514 | -0.30368 | 1.4132e-05 | -0.00047208 | 0.020645 | 0.020651 | 0.020651 | 0.99679 | -0.063095 | 0.99675 | -0.065375 | 1.6008
162 | -0.085804 | -0.041557 | 0.085804 | 0.04101 | 2.3422e-07 | -0.00054677 | 0.0027617 | 0.0027548 | 0.0027617 | 0.99656 | -0.069055 | 0.99656 | -0.069078 | 1.2553
163 | -0.085804 | -0.04101 | 0.085804 | 0.040089 | 3.9175e-07 | -0.0009206 | 0.0027548 | 0.0027434 | 0.0027548 | 0.99656 | -0.069078 | 0.99657 | -0.069116 | 1.2522
164 | 0.081446 | 0.037918 | -0.081446 | -0.039446 | 5.8671e-07 | -0.0015275 | 0.0026024 | 0.0026214 | 0.0026214 | 0.99657 | -0.069116 | 0.99656 | -0.069056 | 1.1915
165 | 0.082554 | 0.039274 | -0.082554 | -0.039983 | 2.8078e-07 | -0.0007087 | 0.0026482 | 0.0026571 | 0.0026571 | 0.99657 | -0.069116 | 0.99656 | -0.069087 | 1.2078
166 | -0.2498 | -0.11728 | 0.24981 | 0.11485 | 8.7405e-06 | -0.0024361 | 0.0079939 | 0.0079641 | 0.0079939 | 0.99657 | -0.069116 | 0.9966 | -0.069393 | 3.6336
167 | -0.24981 | -0.11485 | 0.24981 | 0.11455 | 1.0683e-06 | -0.000299 | 0.0079641 | 0.0079605 | 0.0079641 | 0.9966 | -0.069393 | 0.9966 | -0.069426 | 3.6201
168 | -0.45582 | -0.21432 | 0.45583 | 0.21338 | 1.1299e-05 | -0.00094033 | 0.01459 | 0.014578 | 0.01459 | 0.9966 | -0.069426 | 0.99663 | -0.069626 | 6.6317
169 | 0.14308 | 0.068021 | -0.14308 | -0.069297 | 1.5184e-06 | -0.0012765 | 0.0045885 | 0.0046045 | 0.0046045 | 0.99673 | -0.062588 | 0.99672 | -0.062498 | 2.0929
170 | 0.45587 | 0.21201 | -0.45583 | -0.21338 | 4.1979e-05 | -0.0013662 | 0.014561 | 0.014578 | 0.014578 | 0.99675 | -0.065375 | 0.99663 | -0.069626 | 1.7778
171 | -0.21814 | -0.10565 | 0.21814 | 0.10515 | 1.3798e-06 | -0.00049811 | 0.0070178 | 0.0070115 | 0.0070178 | 0.997 | -0.058816 | 0.99701 | -0.05887 | 3.1899
172 | -1.5271 | -0.50128 | 1.5271 | 0.49994 | 3.5977e-06 | -0.0013417 | 0.046535 | 0.046523 | 0.046535 | 0.99706 | -0.059215 | 0.99706 | -0.059187 | 3.647
173 | -1.5271 | -0.49994 | 1.5272 | 0.47695 | 6.1354e-05 | -0.022989 | 0.046523 | 0.04632 | 0.046523 | 0.99706 | -0.059187 | 0.9971 | -0.058679 | 3.646
174 | 0.24323 | 0.11772 | -0.24323 | -0.1178 | 2.7991e-07 | -8.1211e-05 | 0.0078236 | 0.0078246 | 0.0078246 | 0.99705 | -0.058858 | 0.99705 | -0.058848 | 3.5566
175 | 2.0174 | 0.97704 | -2.0174 | -0.97709 | 1.2091e-05 | -4.746e-05 | 0.064897 | 0.064898 | 0.064898 | 0.9971 | -0.058679 | 0.9971 | -0.058626 | 29.4989
176 | -6.658 | -2.3478 | 6.6592 | 2.3247 | 0.0012257 | -0.023067 | 0.20439 | 0.20416 | 0.20439 | 0.9971 | -0.058679 | 0.9973 | -0.056685 | 16.0182
177 | 0.10114 | 0.048957 | -0.10114 | -0.048983 | 1.5809e-08 | -2.6433e-05 | 0.0032535 | 0.0032538 | 0.0032538 | 0.99698 | -0.057963 | 0.99698 | -0.057962 | 1.479
178 | 0.072922 | 0.034753 | -0.072921 | -0.035317 | 1.7661e-07 | -0.00056478 | 0.0023465 | 0.0023536 | 0.0023536 | 0.99377 | -0.24685 | 0.99377 | -0.24683 | 1.0698

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.3646 | 9.0154

## res_load
| p_mw | q_mvar
0 | 0.40546 | 0.19637
1 | 0.1203 | 0.058265
2 | 0.05048 | 0.024449
3 | 0.10372 | 0.050235
4 | 0.14112 | 0.068349
5 | 0.1699 | 0.082285
6 | 0.257 | 0.12447
7 | 0.10491 | 0.050809
8 | 0.18523 | 0.089711
9 | 0.20016 | 0.096944
10 | 0.30435 | 0.1474
11 | 0.11434 | 0.055377
12 | 0.11999 | 0.058114
13 | 0.13431 | 0.065047
14 | 0.10722 | 0.051929
15 | 0.13946 | 0.067546
16 | 0.12225 | 0.059209
17 | 0.12982 | 0.062873
18 | 0.27674 | 0.13403
19 | 0.27489 | 0.13314
20 | 0.33623 | 0.16284
21 | 0.36499 | 0.17677
22 | 0.23725 | 0.11491
23 | 0.28277 | 0.13695
24 | 0.2954 | 0.14307
25 | 0.095851 | 0.046423
26 | 0.052956 | 0.025648
27 | 0.050946 | 0.024674
28 | 0.29914 | 0.14488
29 | 0.21386 | 0.10358
30 | 0.34399 | 0.1666
31 | 0.15945 | 0.077226
32 | 0.33511 | 0.1623
33 | 0.28223 | 0.13669
34 | 0.17982 | 0.087089
35 | 0.11144 | 0.053972
36 | 0.27534 | 0.13335
37 | 0.15968 | 0.077335
38 | 0.10954 | 0.053053
39 | 0.26651 | 0.12908
40 | 0.34046 | 0.16489
41 | 0.32399 | 0.15692
42 | 0.077801 | 0.037681
43 | 0.40294 | 0.19515
44 | 0.24631 | 0.11929
45 | 0.3131 | 0.15164
46 | 0.37076 | 0.17957
47 | 0.25667 | 0.12431
48 | 0.37949 | 0.18379
49 | 0.40715 | 0.19719
50 | 1.8886 | 0.91471
51 | 0.11635 | 0.056353
52 | 0.32694 | 0.15834
53 | 0.076985 | 0.037286
54 | 0.34436 | 0.16678
55 | 0.33266 | 0.16111
56 | 0.37622 | 0.18221
57 | 0.088621 | 0.042921
58 | 0.29341 | 0.14211
59 | 0.3534 | 0.17116
60 | 0.3992 | 0.19334
61 | 0.29942 | 0.14502
62 | 0.070183 | 0.033991
63 | 0.38558 | 0.18674
64 | 0.090276 | 0.043723
65 | 0.2077 | 0.10059
66 | 0.25863 | 0.12526
67 | 0.11324 | 0.054845
68 | 0.20581 | 0.099678
69 | 0.076714 | 0.037154
70 | 0.085804 | 0.041557
71 | 0.206 | 0.099772
72 | 0.081446 | 0.039446
73 | 0.082554 | 0.039983
74 | 0.18927 | 0.091669
75 | 0.14308 | 0.069297
76 | 0.21814 | 0.10565
77 | 0.14861 | 0.071973
78 | 2.0174 | 0.97709
79 | 0.24323 | 0.1178
80 | 0.11856 | 0.057421
81 | 0.077756 | 0.037659
82 | 0.10114 | 0.048983
83 | 0.072921 | 0.035317
84 | 0.1358 | 0.06577

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1