## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_551_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_551_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_551_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_551_0_node_8 | 20 | n |  | TRUE
4 | bus_MV_551_0_node_66 | 20 | n |  | TRUE
5 | bus_MV_551_0_node_67 | 20 | n |  | TRUE
6 | bus_MV_551_0_node_4 | 20 | n |  | TRUE
7 | bus_MV_551_0_node_23 | 20 | n |  | TRUE
8 | bus_MV_551_0_node_64 | 20 | n |  | TRUE
9 | bus_MV_551_0_node_3 | 20 | n |  | TRUE
10 | bus_MV_551_0_node_6 | 20 | n |  | TRUE
11 | bus_MV_551_0_node_9 | 20 | n |  | TRUE
12 | bus_MV_551_0_node_105 | 20 | n |  | TRUE
13 | bus_MV_551_0_node_68 | 20 | n |  | TRUE
14 | bus_MV_551_0_node_19 | 20 | n |  | TRUE
15 | bus_MV_551_0_node_24 | 20 | n |  | TRUE
16 | bus_MV_551_0_node_101 | 20 | n |  | TRUE
17 | bus_MV_551_0_node_22 | 20 | n |  | TRUE
18 | bus_MV_551_0_node_102 | 20 | n |  | TRUE
19 | bus_MV_551_0_node_104 | 20 | n |  | TRUE
20 | bus_MV_551_0_node_107 | 20 | n |  | TRUE
21 | bus_MV_551_0_node_21 | 20 | n |  | TRUE
22 | bus_MV_551_0_node_10 | 20 | n |  | TRUE
23 | bus_MV_551_0_node_12 | 20 | n |  | TRUE
24 | bus_MV_551_0_node_11 | 20 | n |  | TRUE
25 | bus_MV_551_0_node_15 | 20 | n |  | TRUE
26 | bus_MV_551_0_node_13 | 20 | n |  | TRUE
27 | bus_MV_551_0_node_106 | 20 | n |  | TRUE
28 | bus_MV_551_0_node_37 | 20 | n |  | TRUE
29 | bus_MV_551_0_node_38 | 20 | n |  | TRUE
30 | bus_MV_551_0_node_16 | 20 | n |  | TRUE
31 | bus_MV_551_0_node_103 | 20 | n |  | TRUE
32 | bus_MV_551_0_node_17 | 20 | n |  | TRUE
33 | bus_MV_551_0_node_18 | 20 | n |  | TRUE
34 | bus_MV_551_0_node_63 | 20 | n |  | TRUE
35 | bus_MV_551_0_node_20 | 20 | n |  | TRUE
36 | bus_MV_551_0_node_27 | 20 | n |  | TRUE
37 | bus_MV_551_0_node_96 | 20 | n |  | TRUE
38 | bus_MV_551_0_node_26 | 20 | n |  | TRUE
39 | bus_MV_551_0_node_25 | 20 | n |  | TRUE
40 | bus_MV_551_0_node_28 | 20 | n |  | TRUE
41 | bus_MV_551_0_node_29 | 20 | n |  | TRUE
42 | bus_MV_551_0_node_81 | 20 | n |  | TRUE
43 | bus_MV_551_0_node_30 | 20 | n |  | TRUE
44 | bus_MV_551_0_node_82 | 20 | n |  | TRUE
45 | bus_MV_551_0_node_31 | 20 | n |  | TRUE
46 | bus_MV_551_0_node_32 | 20 | n |  | TRUE
47 | bus_MV_551_0_node_33 | 20 | n |  | TRUE
48 | bus_MV_551_0_node_34 | 20 | n |  | TRUE
49 | bus_MV_551_0_node_35 | 20 | n |  | TRUE
50 | bus_MV_551_0_node_36 | 20 | n |  | TRUE
51 | bus_MV_551_0_node_40 | 20 | n |  | TRUE
52 | bus_MV_551_0_node_41 | 20 | n |  | TRUE
53 | bus_MV_551_0_node_42 | 20 | n |  | TRUE
54 | bus_MV_551_0_node_98 | 20 | n |  | TRUE
55 | bus_MV_551_0_node_39 | 20 | n |  | TRUE
56 | bus_MV_551_0_node_70 | 20 | n |  | TRUE
57 | bus_MV_551_0_node_85 | 20 | n |  | TRUE
58 | bus_MV_551_0_node_50 | 20 | n |  | TRUE
59 | bus_MV_551_0_node_69 | 20 | n |  | TRUE
60 | bus_MV_551_0_node_45 | 20 | n |  | TRUE
61 | bus_MV_551_0_node_71 | 20 | n |  | TRUE
62 | bus_MV_551_0_node_86 | 20 | n |  | TRUE
63 | bus_MV_551_0_node_62 | 20 | n |  | TRUE
64 | bus_MV_551_0_node_46 | 20 | n |  | TRUE
65 | bus_MV_551_0_node_43 | 20 | n |  | TRUE
66 | bus_MV_551_0_node_49 | 20 | n |  | TRUE
67 | bus_MV_551_0_node_47 | 20 | n |  | TRUE
68 | bus_MV_551_0_node_91 | 20 | n |  | TRUE
69 | bus_MV_551_0_node_48 | 20 | n |  | TRUE
70 | bus_MV_551_0_node_94 | 20 | n |  | TRUE
71 | bus_MV_551_0_node_93 | 20 | n |  | TRUE
72 | bus_MV_551_0_node_51 | 20 | n |  | TRUE
73 | bus_MV_551_0_node_90 | 20 | n |  | TRUE
74 | bus_MV_551_0_node_99 | 20 | n |  | TRUE
75 | bus_MV_551_0_node_77 | 20 | n |  | TRUE
76 | bus_MV_551_0_node_52 | 20 | n |  | TRUE
77 | bus_MV_551_0_node_53 | 20 | n |  | TRUE
78 | bus_MV_551_0_node_54 | 20 | n |  | TRUE
79 | bus_MV_551_0_node_55 | 20 | n |  | TRUE
80 | bus_MV_551_0_node_56 | 20 | n |  | TRUE
81 | bus_MV_551_0_node_57 | 20 | n |  | TRUE
82 | bus_MV_551_0_node_58 | 20 | n |  | TRUE
83 | bus_MV_551_0_node_61 | 20 | n |  | TRUE
84 | bus_MV_551_0_node_60 | 20 | n |  | TRUE
85 | bus_MV_551_0_node_74 | 20 | n |  | TRUE
86 | bus_MV_551_0_node_59 | 20 | n |  | TRUE
87 | bus_MV_551_0_node_89 | 20 | n |  | TRUE
88 | bus_MV_551_0_node_72 | 20 | n |  | TRUE
89 | bus_MV_551_0_node_92 | 20 | n |  | TRUE
90 | bus_MV_551_0_node_65 | 20 | n |  | TRUE
91 | bus_MV_551_0_node_97 | 20 | n |  | TRUE
92 | bus_MV_551_0_node_73 | 20 | n |  | TRUE
93 | bus_MV_551_0_node_75 | 20 | n |  | TRUE
94 | bus_MV_551_0_node_76 | 20 | n |  | TRUE
95 | bus_MV_551_0_node_95 | 20 | n |  | TRUE
96 | bus_MV_551_0_node_100 | 20 | n |  | TRUE
97 | bus_MV_551_0_node_84 | 20 | n |  | TRUE
98 | bus_MV_551_0_node_80 | 20 | n |  | TRUE
99 | bus_MV_551_0_node_78 | 20 | n |  | TRUE
100 | bus_MV_551_0_node_79 | 20 | n |  | TRUE
101 | bus_MV_551_0_node_83 | 20 | n |  | TRUE
102 | bus_MV_551_0_node_87 | 20 | n |  | TRUE
103 | bus_MV_551_0_node_88 | 20 | n |  | TRUE
104 | bus_HV_551_0_node_80 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_551_0_load_0 | 0 | 0.21688 | 0.10504 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_551_0_load_66 | 4 | 0.091655 | 0.04439 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_551_0_load_23 | 7 | 0.17362 | 0.084089 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_551_0_load_9 | 11 | 0.17026 | 0.082463 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_551_0_load_105 | 12 | 0.19582 | 0.094838 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_551_0_load_68 | 13 | 0.13511 | 0.065438 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_551_0_load_19 | 14 | 0.33004 | 0.15984 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_551_0_load_24 | 15 | 0.1689 | 0.081804 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_551_0_load_101 | 16 | 0.3665 | 0.1775 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_551_0_load_107 | 20 | 0.24007 | 0.11627 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_551_0_load_10 | 22 | 0.22532 | 0.10913 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_551_0_load_106 | 27 | 0.40873 | 0.19796 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_551_0_load_37 | 28 | 0.12567 | 0.060867 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_551_0_load_16 | 30 | 0.20441 | 0.099002 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_551_0_load_103 | 31 | 0.36655 | 0.17753 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_551_0_load_63 | 34 | 0.084587 | 0.040967 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_551_0_load_20 | 35 | 0.14003 | 0.067819 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_551_0_load_96 | 37 | 0.11829 | 0.057291 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_551_0_load_25 | 39 | 0.056703 | 0.027463 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_551_0_load_81 | 42 | 0.20115 | 0.097423 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_551_0_load_30 | 43 | 0.14172 | 0.068638 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_551_0_load_31 | 45 | 0.41504 | 0.20101 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_551_0_load_34 | 48 | 0.29521 | 0.14298 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_551_0_load_40 | 51 | 0.30184 | 0.14619 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_551_0_load_98 | 54 | 0.15271 | 0.07396 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_551_0_load_85 | 57 | 0.15572 | 0.075418 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_551_0_load_69 | 59 | 0.10424 | 0.050484 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_551_0_load_71 | 61 | 0.072326 | 0.035029 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_551_0_load_86 | 62 | 0.079468 | 0.038488 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_551_0_load_62 | 63 | 0.2394 | 0.11595 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_551_0_load_43 | 65 | 0.12695 | 0.061485 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_551_0_load_91 | 68 | 0.14609 | 0.070755 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_551_0_load_93 | 71 | 1.0212 | 0.49458 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_551_0_load_51 | 72 | 0.078767 | 0.038149 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_551_0_load_99 | 74 | 3.9619 | 1.9188 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_551_0_load_77 | 75 | 0.26613 | 0.12889 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_551_0_load_52 | 76 | 0.2894 | 0.14016 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_551_0_load_53 | 77 | 0.23454 | 0.11359 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_551_0_load_60 | 84 | 0.12324 | 0.05969 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_551_0_load_74 | 85 | 0.16517 | 0.079994 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_551_0_load_59 | 86 | 0.34033 | 0.16483 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_551_0_load_89 | 87 | 0.55876 | 0.27062 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_551_0_load_72 | 88 | 0.18773 | 0.09092 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_551_0_load_92 | 89 | 1.223 | 0.59231 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_551_0_load_97 | 91 | 0.38911 | 0.18845 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_551_0_load_95 | 95 | 0.18553 | 0.089854 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_551_0_load_100 | 96 | 0.33341 | 0.16148 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_551_0_load_79 | 100 | 0.089931 | 0.043556 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_551_0_load_83 | 101 | 0.15759 | 0.076325 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_551_0_load_87 | 102 | 0.11532 | 0.055853 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_551_0_load_88 | 103 | 0.076213 | 0.036912 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 98 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_551_0_line_0 |  | 0 | 1 | 0.007029 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_551_0_line_1 |  | 1 | 2 | 0.085724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_551_0_line_2 |  | 1 | 3 | 0.334 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_551_0_line_3 |  | 2 | 9 | 0.23641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_551_0_line_4 |  | 2 | 10 | 0.21395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_551_0_line_5 |  | 2 | 11 | 0.10997 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_551_0_line_6 |  | 3 | 15 | 0.02237 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_551_0_line_7 |  | 3 | 16 | 0.12553 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
8 | MV_551_0_line_8 |  | 4 | 5 | 0.0956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_551_0_line_9 |  | 4 | 6 | 0.049155 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_551_0_line_10 |  | 4 | 7 | 0.21979 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_551_0_line_11 |  | 4 | 8 | 0.56293 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_551_0_line_12 |  | 5 | 17 | 0.063012 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_551_0_line_13 |  | 6 | 13 | 0.033714 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_551_0_line_14 |  | 8 | 90 | 0.035074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_551_0_line_15 |  | 8 | 34 | 0.02325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_551_0_line_16 |  | 9 | 12 | 0.069387 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
17 | MV_551_0_line_17 |  | 10 | 14 | 0.004496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_551_0_line_18 |  | 15 | 17 | 0.24696 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_551_0_line_19 |  | 16 | 18 | 0.006601 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_551_0_line_20 |  | 17 | 20 | 0.080995 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_551_0_line_21 |  | 17 | 21 | 1.4404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_551_0_line_22 |  | 18 | 19 | 0.17684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_551_0_line_23 |  | 19 | 31 | 0.038112 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_551_0_line_24 |  | 21 | 35 | 0.099823 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_551_0_line_25 |  | 22 | 23 | 0.025488 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_551_0_line_26 |  | 22 | 24 | 0.14816 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_551_0_line_27 |  | 23 | 25 | 0.24817 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_551_0_line_28 |  | 24 | 26 | 0.18535 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_551_0_line_29 |  | 25 | 30 | 0.019891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_551_0_line_30 |  | 26 | 27 | 0.023367 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_551_0_line_31 |  | 27 | 28 | 0.38338 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
32 | MV_551_0_line_32 |  | 28 | 29 | 0.006613 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
33 | MV_551_0_line_33 |  | 29 | 55 | 0.24656 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
34 | MV_551_0_line_34 |  | 30 | 32 | 0.020208 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_551_0_line_35 |  | 32 | 33 | 0.14972 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_551_0_line_36 |  | 33 | 34 | 0.024396 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_551_0_line_37 |  | 36 | 37 | 0.035709 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_551_0_line_38 |  | 36 | 38 | 0.16157 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_551_0_line_39 |  | 38 | 40 | 0.71887 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_551_0_line_40 |  | 38 | 41 | 0.66466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_551_0_line_41 |  | 38 | 39 | 0.012975 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_551_0_line_42 |  | 40 | 42 | 0.029295 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_551_0_line_43 |  | 41 | 43 | 0.038907 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_551_0_line_44 |  | 42 | 44 | 0.0071156 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_551_0_line_45 |  | 44 | 101 | 0.11418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_551_0_line_46 |  | 45 | 46 | 0.03767 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_551_0_line_47 |  | 46 | 47 | 0.54336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_551_0_line_48 |  | 47 | 48 | 0.072591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_551_0_line_49 |  | 48 | 49 | 0.11302 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
50 | MV_551_0_line_50 |  | 49 | 50 | 0.85281 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_551_0_line_51 |  | 50 | 51 | 0.09676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_551_0_line_52 |  | 51 | 52 | 0.19592 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_551_0_line_53 |  | 52 | 53 | 0.28025 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_551_0_line_54 |  | 52 | 54 | 0.28639 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_551_0_line_55 |  | 53 | 63 | 0.03627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_551_0_line_56 |  | 55 | 56 | 0.13031 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
57 | MV_551_0_line_57 |  | 55 | 57 | 0.054102 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_551_0_line_58 |  | 56 | 61 | 0.068594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_551_0_line_59 |  | 56 | 58 | 0.13416 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
60 | MV_551_0_line_60 |  | 57 | 62 | 0.027198 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_551_0_line_61 |  | 58 | 59 | 0.032812 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_551_0_line_62 |  | 58 | 60 | 0.079036 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
63 | MV_551_0_line_63 |  | 60 | 66 | 0.1864 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
64 | MV_551_0_line_64 |  | 60 | 65 | 0.013623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_551_0_line_65 |  | 62 | 102 | 0.027159 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_551_0_line_66 |  | 63 | 64 | 0.004173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_551_0_line_67 |  | 64 | 67 | 0.24688 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_551_0_line_68 |  | 66 | 72 | 0.042841 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_551_0_line_69 |  | 66 | 69 | 0.091589 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
70 | MV_551_0_line_70 |  | 67 | 68 | 0.074209 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_551_0_line_71 |  | 68 | 73 | 0.037863 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_551_0_line_72 |  | 69 | 70 | 0.12257 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
73 | MV_551_0_line_73 |  | 69 | 71 | 0.096175 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_551_0_line_74 |  | 70 | 74 | 0.051015 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
75 | MV_551_0_line_75 |  | 70 | 75 | 0.097423 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
76 | MV_551_0_line_76 |  | 72 | 76 | 0.029539 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_551_0_line_77 |  | 73 | 89 | 0.037191 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_551_0_line_78 |  | 73 | 83 | 0.01517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_551_0_line_79 |  | 75 | 99 | 0.060487 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
80 | MV_551_0_line_80 |  | 77 | 78 | 0.019553 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_551_0_line_81 |  | 77 | 79 | 0.031234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_551_0_line_82 |  | 78 | 80 | 0.28264 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_551_0_line_83 |  | 79 | 81 | 0.1873 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
84 | MV_551_0_line_84 |  | 79 | 82 | 0.34606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_551_0_line_85 |  | 80 | 83 | 0.13786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_551_0_line_86 |  | 80 | 84 | 0.039377 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_551_0_line_87 |  | 81 | 85 | 0.042237 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
88 | MV_551_0_line_88 |  | 82 | 86 | 0.053517 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_551_0_line_89 |  | 83 | 87 | 0.025943 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_551_0_line_90 |  | 85 | 88 | 0.070007 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
91 | MV_551_0_line_91 |  | 88 | 92 | 0.017449 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
92 | MV_551_0_line_92 |  | 90 | 91 | 0.009419 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_551_0_line_93 |  | 92 | 93 | 0.10134 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
94 | MV_551_0_line_94 |  | 93 | 94 | 0.096384 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
95 | MV_551_0_line_95 |  | 93 | 95 | 0.052859 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_551_0_line_96 |  | 94 | 96 | 0.038158 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
97 | MV_551_0_line_97 |  | 95 | 97 | 0.068643 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_551_0_line_98 |  | 96 | 98 | 0.060672 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
99 | MV_551_0_line_99 |  | 97 | 101 | 0.07415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_551_0_line_100 |  | 98 | 99 | 0.087832 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
101 | MV_551_0_line_101 |  | 99 | 100 | 0.011395 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_551_0_line_102 |  | 102 | 103 | 0.076322 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_551_0_trafo_80 | 25 MVA 110/20 kV | 104 | 98 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2685610.8895 | 1251066.6329
1 | 2685603.9352 | 1251067.7889
2 | 2685566.1841 | 1251003.4064
3 | 2685577.4171 | 1251321.5635
4 | 2685292.3803 | 1251389.9298
5 | 2685350.1865 | 1251466.0733
6 | 2685266.4193 | 1251348.19
7 | 2685402.7212 | 1251199.8409
8 | 2685722.6463 | 1251026.9406
9 | 2685416.8477 | 1250906.0237
10 | 2685677.8014 | 1250905.056
11 | 2685481.638 | 1251073.7282
12 | 2685366.1733 | 1250858.6247
13 | 2685245.7959 | 1251321.4732
14 | 2685673.6521 | 1250903.2947
15 | 2685565.3935 | 1251339.2254
16 | 2685700.8146 | 1251344.6195
17 | 2685385.6555 | 1251508.5829
18 | 2685703.1331 | 1251350.8021
19 | 2685750.0039 | 1251475.8521
20 | 2685336.7844 | 1251573.1721
21 | 2685419.3533 | 1251906.1903
22 | 2685974.7236 | 1251174.792
23 | 2685952.8745 | 1251187.9739
24 | 2686056.6778 | 1251298.2189
25 | 2685901.5919 | 1251067.4285
26 | 2686123.7429 | 1251433.0503
27 | 2686123.8356 | 1251454.1898
28 | 2686232.0025 | 1251821.996
29 | 2686230.5424 | 1251828.4463
30 | 2685882.6778 | 1251061.4406
31 | 2685763.3838 | 1251511.5504
32 | 2685863.5918 | 1251054.8017
33 | 2685768.6363 | 1251039.3931
34 | 2685745.0879 | 1251033.0169
35 | 2685442.1841 | 1251809.0128
36 | 2685431.4395 | 1252204.2561
37 | 2685400.9534 | 1252185.5136
38 | 2685331.2868 | 1252323.403
39 | 2685338.4136 | 1252334.2583
40 | 2685749.3436 | 1252370.0287
41 | 2685249.2411 | 1252068.9746
42 | 2685766.4903 | 1252354.3512
43 | 2685247.0818 | 1252107.8172
44 | 2685767.5825 | 1252347.3199
45 | 2685847.2118 | 1253242.2844
46 | 2685879.0457 | 1253253.9991
47 | 2686156.669 | 1253269.308
48 | 2686213.8506 | 1253314.1405
49 | 2686147.3145 | 1253405.4977
50 | 2686538.2077 | 1252879.0275
51 | 2686466.164 | 1252814.5823
52 | 2686624.3245 | 1252698.9602
53 | 2686536.4354 | 1252468.9459
54 | 2686888.4839 | 1252809.5898
55 | 2686409.8703 | 1251959.3018
56 | 2686439.8888 | 1252047.6954
57 | 2686462.2946 | 1251949.4288
58 | 2686533.8612 | 1252095.592
59 | 2686563.0894 | 1252081.4304
60 | 2686538.684 | 1252164.8149
61 | 2686439.3993 | 1252114.957
62 | 2686488.6171 | 1251942.584
63 | 2686514.7016 | 1252439.862
64 | 2686512.9607 | 1252436.0671
65 | 2686549.9328 | 1252171.8512
66 | 2686382.7007 | 1252184.1648
67 | 2686417.8012 | 1252317.8334
68 | 2686374.8353 | 1252273.0235
69 | 2686296.0987 | 1252177.4535
70 | 2686214.3532 | 1252206.2632
71 | 2686300.6924 | 1252081.4053
72 | 2686380.8051 | 1252141.8162
73 | 2686340.403 | 1252288.772
74 | 2686216.2747 | 1252254.1718
75 | 2686128.6962 | 1252159.8506
76 | 2686409.7893 | 1252147.5121
77 | 2686061.1389 | 1252456.4031
78 | 2686080.3298 | 1252452.3788
79 | 2686030.6423 | 1252463.5434
80 | 2686281.434 | 1252383.5738
81 | 2685918.074 | 1252387.1301
82 | 2686194.4758 | 1252562.2436
83 | 2686326.5743 | 1252295.0975
84 | 2686318.5446 | 1252370.104
85 | 2685912.9785 | 1252345.2016
86 | 2686231.7534 | 1252523.7457
87 | 2686315.4459 | 1252271.6629
88 | 2685907.4677 | 1252275.4764
89 | 2686324.5592 | 1252255.1248
90 | 2685707.0794 | 1251004.5542
91 | 2685714.6201 | 1250998.8812
92 | 2685906.8899 | 1252258.037
93 | 2685915.7004 | 1252184.5202
94 | 2685946.9325 | 1252111.7181
95 | 2685863.8226 | 1252174.3833
96 | 2685981.5019 | 1252096.5859
97 | 2685796.4534 | 1252161.2194
98 | 2686042.1734 | 1252096.9224
99 | 2686129.9708 | 1252099.3774
100 | 2686141.3607 | 1252099.7229
101 | 2685785.0848 | 1252234.4926
102 | 2686514.9019 | 1251935.749
103 | 2686588.1394 | 1251914.2698
104 | 2686042.1734 | 1252096.9224

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98691 | -0.094437 | 0.21688 | 0.10504
1 | 0.98691 | -0.094456 | 0 | 0
2 | 0.98683 | -0.093789 | 0 | 0
3 | 0.9873 | -0.097833 | 0 | 0
4 | 0.98867 | -0.095739 | 0.091655 | 0.04439
5 | 0.9884 | -0.093561 | 0 | 0
6 | 0.98865 | -0.095825 | 0 | 0
7 | 0.98859 | -0.096213 | 0.17362 | 0.084089
8 | 0.9915 | -0.07449 | 0 | 0
9 | 0.98678 | -0.093264 | 0 | 0
10 | 0.98674 | -0.092958 | 0 | 0
11 | 0.9868 | -0.094022 | 0.17026 | 0.082463
12 | 0.98675 | -0.093433 | 0.19582 | 0.094838
13 | 0.98865 | -0.09577 | 0.13511 | 0.065438
14 | 0.98674 | -0.09294 | 0.33004 | 0.15984
15 | 0.98735 | -0.098246 | 0.1689 | 0.081804
16 | 0.98712 | -0.099031 | 0.3665 | 0.1775
17 | 0.98822 | -0.092117 | 0 | 0
18 | 0.98712 | -0.099004 | 0 | 0
19 | 0.98704 | -0.098242 | 0 | 0
20 | 0.98818 | -0.092357 | 0.24007 | 0.11627
21 | 0.98797 | -0.091234 | 0 | 0
22 | 0.99358 | -0.091922 | 0.22532 | 0.10913
23 | 0.99347 | -0.091036 | 0 | 0
24 | 0.99458 | -0.084535 | 0 | 0
25 | 0.99243 | -0.082345 | 0 | 0
26 | 0.99541 | -0.091447 | 0 | 0
27 | 0.99552 | -0.092314 | 0.40873 | 0.19796
28 | 0.99729 | -0.046984 | 0.12567 | 0.060867
29 | 0.9973 | -0.046821 | 0 | 0
30 | 0.99235 | -0.081644 | 0.20441 | 0.099002
31 | 0.98702 | -0.098071 | 0.36655 | 0.17753
32 | 0.99227 | -0.080981 | 0 | 0
33 | 0.99168 | -0.076045 | 0 | 0
34 | 0.99159 | -0.075237 | 0.084587 | 0.040967
35 | 0.98794 | -0.091408 | 0.14003 | 0.067819
36 | 0.99897 | -0.010891 | 0 | 0
37 | 0.99897 | -0.010841 | 0.11829 | 0.057291
38 | 0.999 | -0.011091 | 0 | 0
39 | 0.99899 | -0.011083 | 0.056703 | 0.027463
40 | 0.99928 | -0.012427 | 0 | 0
41 | 0.99888 | -0.010338 | 0 | 0
42 | 0.99929 | -0.012465 | 0.20115 | 0.097423
43 | 0.99887 | -0.010273 | 0.14172 | 0.068638
44 | 0.99929 | -0.012491 | 0 | 0
45 | 0.99385 | 0.011823 | 0.41504 | 0.20101
46 | 0.99387 | 0.011634 | 0 | 0
47 | 0.99416 | 0.0091594 | 0 | 0
48 | 0.9942 | 0.0088629 | 0.29521 | 0.14298
49 | 0.99435 | 0.0099952 | 0 | 0
50 | 0.99512 | 0.0040773 | 0 | 0
51 | 0.99521 | 0.0034763 | 0.30184 | 0.14619
52 | 0.99559 | 0.00654 | 0 | 0
53 | 0.996 | 0.003353 | 0 | 0
54 | 0.9955 | 0.0060026 | 0.15271 | 0.07396
55 | 0.99763 | -0.045323 | 0 | 0
56 | 0.99782 | -0.044439 | 0 | 0
57 | 0.9976 | -0.045052 | 0.15572 | 0.075418
58 | 0.99802 | -0.043498 | 0 | 0
59 | 0.99801 | -0.043457 | 0.10424 | 0.050484
60 | 0.99814 | -0.042925 | 0 | 0
61 | 0.99781 | -0.044383 | 0.072326 | 0.035029
62 | 0.99759 | -0.044966 | 0.079468 | 0.038488
63 | 0.99605 | 0.0029495 | 0.2394 | 0.11595
64 | 0.99606 | 0.0028912 | 0 | 0
65 | 0.99814 | -0.042905 | 0.12695 | 0.061485
66 | 0.99843 | -0.041524 | 0 | 0
67 | 0.9965 | -0.00051174 | 0 | 0
68 | 0.99663 | -0.0015159 | 0.14609 | 0.070755
69 | 0.99858 | -0.040783 | 0 | 0
70 | 0.99883 | -0.039629 | 0 | 0
71 | 0.99846 | -0.039611 | 1.0212 | 0.49458
72 | 0.99841 | -0.041338 | 0.078767 | 0.038149
73 | 0.99671 | -0.0020915 | 0 | 0
74 | 0.99872 | -0.040762 | 3.9619 | 1.9188
75 | 0.99949 | -0.0021382 | 0.26613 | 0.12889
76 | 0.9984 | -0.041236 | 0.2894 | 0.14016
77 | 0.99867 | -0.018861 | 0.23454 | 0.11359
78 | 0.99859 | -0.018135 | 0 | 0
79 | 0.99882 | -0.020107 | 0 | 0
80 | 0.99734 | -0.0075597 | 0 | 0
81 | 0.99923 | -0.015508 | 0 | 0
82 | 0.99867 | -0.018814 | 0 | 0
83 | 0.99676 | -0.0025441 | 0 | 0
84 | 0.99734 | -0.0075025 | 0.12324 | 0.05969
85 | 0.99928 | -0.015255 | 0.16517 | 0.079994
86 | 0.99864 | -0.018598 | 0.34033 | 0.16483
87 | 0.99674 | -0.00237 | 0.55876 | 0.27062
88 | 0.99938 | -0.014818 | 0.18773 | 0.09092
89 | 0.99665 | -0.0015448 | 1.223 | 0.59231
90 | 0.99148 | -0.074325 | 0 | 0
91 | 0.99147 | -0.074281 | 0.38911 | 0.18845
92 | 0.9994 | -0.014705 | 0 | 0
93 | 0.99955 | -0.01404 | 0 | 0
94 | 0.99971 | -0.013236 | 0 | 0
95 | 0.99949 | -0.013652 | 0.18553 | 0.089854
96 | 0.99978 | -0.012916 | 0.33341 | 0.16148
97 | 0.99943 | -0.013295 | 0 | 0
98 | 1 | 0 | -16.1244 | -7.5028
99 | 0.9997 | -0.0012723 | 0 | 0
100 | 0.9997 | -0.0012601 | 0.089931 | 0.043556
101 | 0.99937 | -0.0129 | 0.15759 | 0.076325
102 | 0.99758 | -0.044904 | 0.11532 | 0.055853
103 | 0.99757 | -0.044975 | 0.076213 | 0.036912
104 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.21688 | -0.10504 | 0.21688 | 0.10488 | 4.6607e-07 | -0.00016332 | 0.0070486 | 0.0070465 | 0.0070486 | 0.98691 | -0.094437 | 0.98691 | -0.094456 | 3.2039
1 | 0.69623 | 0.3244 | -0.69617 | -0.32638 | 5.783e-05 | -0.0019762 | 0.022467 | 0.022492 | 0.022492 | 0.98691 | -0.094456 | 0.98683 | -0.093789 | 10.2236
2 | -0.91311 | -0.42928 | 0.9135 | 0.42162 | 0.00038712 | -0.0076555 | 0.029513 | 0.029417 | 0.029513 | 0.98691 | -0.094456 | 0.9873 | -0.097833 | 13.4151
3 | 0.19583 | 0.089267 | -0.19582 | -0.09476 | 1.2644e-05 | -0.0054928 | 0.0062957 | 0.0063641 | 0.0063641 | 0.98683 | -0.093789 | 0.98678 | -0.093264 | 2.8928
4 | 0.33007 | 0.15477 | -0.33004 | -0.15974 | 3.2673e-05 | -0.0049646 | 0.010664 | 0.010727 | 0.010727 | 0.98683 | -0.093789 | 0.98674 | -0.092958 | 4.8758
5 | 0.17027 | 0.082339 | -0.17026 | -0.082463 | 5.9993e-06 | -0.00012409 | 0.0055327 | 0.0055343 | 0.0055343 | 0.98683 | -0.093789 | 0.9868 | -0.094022 | 2.6354
6 | -1.6467 | -0.77145 | 1.6468 | 0.77095 | 8.4415e-05 | -0.00049562 | 0.05317 | 0.053163 | 0.05317 | 0.9873 | -0.097833 | 0.98735 | -0.098246 | 24.168
7 | 0.73322 | 0.34982 | -0.73309 | -0.34989 | 0.00012621 | -6.7003e-05 | 0.023753 | 0.023755 | 0.023755 | 0.9873 | -0.097833 | 0.98712 | -0.099031 | 11.312
8 | 2.1984 | 1.0003 | -2.1978 | -1.0024 | 0.000635 | -0.0020422 | 0.070523 | 0.07055 | 0.07055 | 0.98867 | -0.095739 | 0.9884 | -0.093561 | 32.0683
9 | 0.13512 | 0.064596 | -0.13511 | -0.064652 | 1.6749e-06 | -5.6309e-05 | 0.0043728 | 0.0043736 | 0.0043736 | 0.98867 | -0.095739 | 0.98865 | -0.095825 | 2.0826
10 | 0.17363 | 0.08384 | -0.17362 | -0.084089 | 1.2419e-05 | -0.00024868 | 0.0056299 | 0.0056332 | 0.0056332 | 0.98867 | -0.095739 | 0.98859 | -0.096213 | 2.6825
11 | -2.5988 | -1.1932 | 2.6058 | 1.1969 | 0.0069918 | 0.0037207 | 0.083497 | 0.083489 | 0.083497 | 0.98867 | -0.095739 | 0.9915 | -0.07449 | 39.7604
12 | 2.1978 | 1.0024 | -2.1974 | -1.0037 | 0.00041881 | -0.0013453 | 0.07055 | 0.070568 | 0.070568 | 0.9884 | -0.093561 | 0.98822 | -0.092117 | 32.0764
13 | 0.13511 | 0.064652 | -0.13511 | -0.065438 | 8.6288e-07 | -0.00078654 | 0.0043736 | 0.0043835 | 0.0043835 | 0.98865 | -0.095825 | 0.98865 | -0.09577 | 1.9925
14 | 0.38912 | 0.18741 | -0.38911 | -0.18823 | 7.4101e-06 | -0.00082104 | 0.012575 | 0.012585 | 0.012585 | 0.9915 | -0.07449 | 0.99148 | -0.074325 | 5.7205
15 | -2.9949 | -1.3843 | 2.9952 | 1.3838 | 0.0002864 | -0.0004608 | 0.096062 | 0.096055 | 0.096062 | 0.9915 | -0.07449 | 0.99159 | -0.075237 | 43.6644
16 | 0.19582 | 0.09476 | -0.19582 | -0.094838 | 5.0079e-06 | -7.7519e-05 | 0.0063641 | 0.0063651 | 0.0063651 | 0.98678 | -0.093264 | 0.98675 | -0.093433 | 3.031
17 | 0.33004 | 0.15974 | -0.33004 | -0.15984 | 6.9071e-07 | -0.00010431 | 0.010727 | 0.010728 | 0.010728 | 0.98674 | -0.092958 | 0.98674 | -0.09294 | 4.8764
18 | -1.8157 | -0.85276 | 1.8172 | 0.85342 | 0.0015134 | 0.0006603 | 0.05865 | 0.058646 | 0.05865 | 0.98735 | -0.098246 | 0.98822 | -0.092117 | 27.9284
19 | 0.36659 | 0.17239 | -0.36659 | -0.17254 | 1.237e-06 | -0.00015321 | 0.011847 | 0.011849 | 0.011849 | 0.98712 | -0.099031 | 0.98712 | -0.099004 | 5.3858
20 | 0.24008 | 0.11618 | -0.24007 | -0.11627 | 8.7609e-06 | -8.8937e-05 | 0.007791 | 0.0077922 | 0.0077922 | 0.98822 | -0.092117 | 0.98818 | -0.092357 | 3.7106
21 | 0.14007 | 0.034139 | -0.14003 | -0.067705 | 3.6448e-05 | -0.033566 | 0.0042114 | 0.0045448 | 0.0045448 | 0.98822 | -0.092117 | 0.98797 | -0.091234 | 2.0658
22 | 0.36659 | 0.17254 | -0.36656 | -0.17664 | 3.3288e-05 | -0.0041039 | 0.011849 | 0.0119 | 0.0119 | 0.98712 | -0.099004 | 0.98704 | -0.098242 | 5.4093
23 | 0.36656 | 0.17664 | -0.36655 | -0.17753 | 7.2124e-06 | -0.00088437 | 0.0119 | 0.011912 | 0.011912 | 0.98704 | -0.098242 | 0.98702 | -0.098071 | 5.4144
24 | 0.14003 | 0.067705 | -0.14003 | -0.067819 | 3.6748e-06 | -0.00011401 | 0.0045448 | 0.0045462 | 0.0045462 | 0.98797 | -0.091234 | 0.98794 | -0.091408 | 2.1649
25 | 3.2911 | 1.5144 | -3.2907 | -1.5149 | 0.00037701 | -0.00048887 | 0.10526 | 0.10526 | 0.10526 | 0.99358 | -0.091922 | 0.99347 | -0.091036 | 47.8474
26 | -3.5164 | -1.6235 | 3.5198 | 1.6254 | 0.0033426 | 0.0019189 | 0.11253 | 0.11253 | 0.11253 | 0.99358 | -0.091922 | 0.99458 | -0.084535 | 53.5854
27 | 3.2907 | 1.5149 | -3.287 | -1.5196 | 0.0036735 | -0.0047523 | 0.10526 | 0.10534 | 0.10534 | 0.99347 | -0.091036 | 0.99243 | -0.082345 | 47.8797
28 | -3.5198 | -1.6254 | 3.5229 | 1.622 | 0.0031317 | -0.0034522 | 0.11253 | 0.11247 | 0.11253 | 0.99458 | -0.084535 | 0.99541 | -0.091447 | 51.1487
29 | 3.287 | 1.5196 | -3.2867 | -1.52 | 0.00029466 | -0.00038033 | 0.10534 | 0.10534 | 0.10534 | 0.99243 | -0.082345 | 0.99235 | -0.081644 | 47.8823
30 | -3.5229 | -1.622 | 3.5233 | 1.6215 | 0.00039461 | -0.00043581 | 0.11247 | 0.11247 | 0.11247 | 0.99541 | -0.091447 | 0.99552 | -0.092314 | 51.1246
31 | -3.932 | -1.8195 | 3.9376 | 1.8254 | 0.0055548 | 0.0058752 | 0.12563 | 0.12563 | 0.12563 | 0.99552 | -0.092314 | 0.99729 | -0.046984 | 35.8954
32 | -4.0632 | -1.8862 | 4.0633 | 1.886 | 5.3705e-05 | -0.00018661 | 0.12967 | 0.12967 | 0.12967 | 0.99729 | -0.046984 | 0.9973 | -0.046821 | 35.8203
33 | -4.0633 | -1.886 | 4.0646 | 1.8714 | 0.0012791 | -0.014693 | 0.12967 | 0.12948 | 0.12967 | 0.9973 | -0.046821 | 0.99763 | -0.045323 | 20.3239
34 | 3.0823 | 1.421 | -3.0821 | -1.4214 | 0.00026301 | -0.00039707 | 0.098735 | 0.098741 | 0.098741 | 0.99235 | -0.081644 | 0.99227 | -0.080981 | 44.8822
35 | 3.0821 | 1.4214 | -3.0801 | -1.4243 | 0.0019496 | -0.0029393 | 0.098741 | 0.098784 | 0.098784 | 0.99227 | -0.080981 | 0.99168 | -0.076045 | 44.9017
36 | 3.0801 | 1.4243 | -3.0798 | -1.4248 | 0.00031784 | -0.0004785 | 0.098784 | 0.098791 | 0.098791 | 0.99168 | -0.076045 | 0.99159 | -0.075237 | 44.9049
37 | 0.11829 | 0.056441 | -0.11829 | -0.057291 | 6.8577e-07 | -0.00085063 | 0.0037875 | 0.0037981 | 0.0037981 | 0.99897 | -0.010891 | 0.99897 | -0.010841 | 1.7264
38 | -0.11829 | -0.056441 | 0.1183 | 0.052592 | 3.0557e-06 | -0.003849 | 0.0037875 | 0.0037409 | 0.0037875 | 0.99897 | -0.010891 | 0.999 | -0.011091 | 1.7216
39 | -0.31674 | -0.13163 | 0.31683 | 0.11452 | 9.2529e-05 | -0.017107 | 0.0099115 | 0.0097322 | 0.0099115 | 0.999 | -0.011091 | 0.99928 | -0.012427 | 4.5052
40 | 0.14174 | 0.051881 | -0.14172 | -0.067711 | 1.7535e-05 | -0.015831 | 0.0043615 | 0.0045392 | 0.0045392 | 0.999 | -0.011091 | 0.99888 | -0.010338 | 2.0633
41 | 0.056703 | 0.027154 | -0.056703 | -0.027463 | 5.7286e-08 | -0.00030915 | 0.0018167 | 0.0018206 | 0.0018206 | 0.999 | -0.011091 | 0.99899 | -0.011083 | 0.82754
42 | -0.31683 | -0.11452 | 0.31683 | 0.11382 | 3.7016e-06 | -0.00069735 | 0.0097322 | 0.0097254 | 0.0097322 | 0.99928 | -0.012427 | 0.99929 | -0.012465 | 4.4237
43 | 0.14172 | 0.067711 | -0.14172 | -0.068638 | 1.0729e-06 | -0.00092654 | 0.0045392 | 0.0045508 | 0.0045508 | 0.99888 | -0.010338 | 0.99887 | -0.010273 | 2.0685
44 | -0.51799 | -0.21124 | 0.51799 | 0.21108 | 2.4804e-06 | -0.00016892 | 0.01616 | 0.016158 | 0.01616 | 0.99929 | -0.012465 | 0.99929 | -0.012491 | 7.3455
45 | -0.51799 | -0.21108 | 0.51803 | 0.20837 | 3.9724e-05 | -0.0027107 | 0.016158 | 0.016129 | 0.016158 | 0.99929 | -0.012491 | 0.99937 | -0.0129 | 7.3447
46 | -0.41504 | -0.20101 | 0.41505 | 0.20013 | 9.0155e-06 | -0.00088573 | 0.013395 | 0.013384 | 0.013395 | 0.99385 | 0.011823 | 0.99387 | 0.011634 | 6.0886
47 | -0.41505 | -0.20013 | 0.41518 | 0.18735 | 0.00012839 | -0.01278 | 0.013384 | 0.013226 | 0.013384 | 0.99387 | 0.011634 | 0.99416 | 0.0091594 | 6.0835
48 | -0.41518 | -0.18735 | 0.4152 | 0.18564 | 1.6926e-05 | -0.001708 | 0.013226 | 0.013206 | 0.013226 | 0.99416 | 0.0091594 | 0.9942 | 0.0088629 | 6.0119
49 | -0.71041 | -0.32862 | 0.71051 | 0.32855 | 0.000104 | -6.8236e-05 | 0.022727 | 0.022726 | 0.022727 | 0.9942 | 0.0088629 | 0.99435 | 0.0099952 | 10.8226
50 | -0.71051 | -0.32855 | 0.71109 | 0.30857 | 0.00058174 | -0.019975 | 0.022726 | 0.022487 | 0.022726 | 0.99435 | 0.0099952 | 0.99512 | 0.0040773 | 10.3299
51 | -0.71109 | -0.30857 | 0.71116 | 0.3063 | 6.524e-05 | -0.0022686 | 0.022487 | 0.02246 | 0.022487 | 0.99512 | 0.0040773 | 0.99521 | 0.0034763 | 10.2212
52 | -1.013 | -0.45249 | 1.0134 | 0.45249 | 0.00036149 | -5.3136e-06 | 0.032182 | 0.032179 | 0.032182 | 0.99521 | 0.0034763 | 0.99559 | 0.00654 | 15.3247
53 | -1.1661 | -0.52612 | 1.1666 | 0.51964 | 0.00051368 | -0.0064827 | 0.037093 | 0.037015 | 0.037093 | 0.99559 | 0.00654 | 0.996 | 0.003353 | 16.8606
54 | 0.15272 | 0.073629 | -0.15271 | -0.07396 | 1.2342e-05 | -0.00033112 | 0.004916 | 0.0049203 | 0.0049203 | 0.99559 | 0.00654 | 0.9955 | 0.0060026 | 2.343
55 | -1.1666 | -0.51964 | 1.1667 | 0.5188 | 6.6322e-05 | -0.00083944 | 0.037015 | 0.037005 | 0.037015 | 0.996 | 0.003353 | 0.99605 | 0.0029495 | 16.8248
56 | -4.4913 | -2.0754 | 4.4921 | 2.0677 | 0.00082473 | -0.007686 | 0.14317 | 0.14307 | 0.14317 | 0.99763 | -0.045323 | 0.99782 | -0.044439 | 22.4397
57 | 0.42674 | 0.20401 | -0.42673 | -0.20529 | 1.3546e-05 | -0.0012816 | 0.013687 | 0.013703 | 0.013703 | 0.99763 | -0.045323 | 0.9976 | -0.045052 | 6.2285
58 | 0.072326 | 0.033399 | -0.072326 | -0.035029 | 4.9066e-07 | -0.0016305 | 0.0023048 | 0.0023249 | 0.0023249 | 0.99782 | -0.044439 | 0.99781 | -0.044383 | 1.0568
59 | -4.5645 | -2.1011 | 4.5653 | 2.0932 | 0.00087549 | -0.0079018 | 0.14537 | 0.14527 | 0.14537 | 0.99782 | -0.044439 | 0.99802 | -0.043498 | 22.7854
60 | 0.27101 | 0.12987 | -0.27101 | -0.13052 | 2.7484e-06 | -0.00064545 | 0.0086961 | 0.0087042 | 0.0087042 | 0.9976 | -0.045052 | 0.99759 | -0.044966 | 3.9565
61 | 0.10424 | 0.049703 | -0.10424 | -0.050484 | 4.9016e-07 | -0.00078017 | 0.0033402 | 0.00335 | 0.00335 | 0.99802 | -0.043498 | 0.99801 | -0.043457 | 1.5227
62 | -4.6696 | -2.1429 | 4.6701 | 2.1382 | 0.00053914 | -0.0046433 | 0.14861 | 0.14855 | 0.14861 | 0.99802 | -0.043498 | 0.99814 | -0.042925 | 23.293
63 | -4.7971 | -2.1994 | 4.7984 | 2.1885 | 0.0013404 | -0.010917 | 0.15262 | 0.15248 | 0.15262 | 0.99814 | -0.042925 | 0.99843 | -0.041524 | 23.9224
64 | 0.12695 | 0.061161 | -0.12695 | -0.061485 | 3.0237e-07 | -0.00032396 | 0.0040755 | 0.0040796 | 0.0040796 | 0.99814 | -0.042925 | 0.99814 | -0.042905 | 1.8543
65 | 0.19154 | 0.09203 | -0.19154 | -0.092675 | 1.3728e-06 | -0.00064491 | 0.0061492 | 0.0061573 | 0.0061573 | 0.99759 | -0.044966 | 0.99758 | -0.044904 | 2.7988
66 | -1.4061 | -0.63474 | 1.4061 | 0.63465 | 1.1136e-05 | -9.5547e-05 | 0.04471 | 0.044709 | 0.04471 | 0.99605 | 0.0029495 | 0.99606 | 0.0028912 | 20.3228
67 | -1.4061 | -0.63465 | 1.4067 | 0.62899 | 0.00065777 | -0.0056556 | 0.044709 | 0.04464 | 0.044709 | 0.99606 | 0.0028912 | 0.9965 | -0.00051174 | 20.3223
68 | 0.36818 | 0.17659 | -0.36817 | -0.17761 | 7.9807e-06 | -0.0010173 | 0.011806 | 0.011819 | 0.011819 | 0.99843 | -0.041524 | 0.99841 | -0.041338 | 5.3723
69 | -5.1666 | -2.3651 | 5.1673 | 2.3598 | 0.00076354 | -0.0053076 | 0.16429 | 0.16422 | 0.16429 | 0.99843 | -0.041524 | 0.99858 | -0.040783 | 25.7506
70 | -1.4067 | -0.62899 | 1.4069 | 0.62729 | 0.00019732 | -0.0017011 | 0.04464 | 0.044619 | 0.04464 | 0.9965 | -0.00051174 | 0.99663 | -0.0015159 | 20.2907
71 | -1.553 | -0.69804 | 1.5531 | 0.69718 | 0.00012292 | -0.00086154 | 0.049318 | 0.049308 | 0.049318 | 0.99663 | -0.0015159 | 0.99671 | -0.0020915 | 22.4175
72 | -6.1887 | -2.8521 | 6.1901 | 2.8452 | 0.001469 | -0.0068541 | 0.19699 | 0.1969 | 0.19699 | 0.99858 | -0.040783 | 0.99883 | -0.039629 | 30.8762
73 | 1.0213 | 0.49233 | -1.0212 | -0.49458 | 0.00013805 | -0.0022485 | 0.032776 | 0.032805 | 0.032805 | 0.99858 | -0.040783 | 0.99846 | -0.039611 | 14.9114
74 | 3.9623 | 1.9174 | -3.9619 | -1.9188 | 0.00039887 | -0.001456 | 0.12722 | 0.12724 | 0.12724 | 0.99883 | -0.039629 | 0.99872 | -0.040762 | 35.1497
75 | -10.1525 | -4.7626 | 10.1561 | 4.7723 | 0.0036534 | 0.0096897 | 0.3241 | 0.3241 | 0.3241 | 0.99883 | -0.039629 | 0.99949 | -0.0021382 | 50.2484
76 | 0.2894 | 0.13946 | -0.2894 | -0.14016 | 3.4055e-06 | -0.000702 | 0.0092886 | 0.0092975 | 0.0092975 | 0.99841 | -0.041338 | 0.9984 | -0.041236 | 4.2261
77 | 1.223 | 0.59145 | -1.223 | -0.59231 | 7.689e-05 | -0.00085927 | 0.039347 | 0.039358 | 0.039358 | 0.99671 | -0.0020915 | 0.99665 | -0.0015448 | 17.8902
78 | -2.7762 | -1.2886 | 2.7763 | 1.2883 | 0.00015913 | -0.00031263 | 0.088646 | 0.088642 | 0.088646 | 0.99671 | -0.0020915 | 0.99676 | -0.0025441 | 40.2937
79 | -10.4222 | -4.9012 | 10.4243 | 4.8986 | 0.0020678 | -0.002633 | 0.33264 | 0.33259 | 0.33264 | 0.99949 | -0.0021382 | 0.9997 | -0.0012723 | 52.1379
80 | 3.4654 | 1.6087 | -3.4651 | -1.6091 | 0.00031838 | -0.00037113 | 0.11044 | 0.11044 | 0.11044 | 0.99867 | -0.018861 | 0.99859 | -0.018135 | 50.2012
81 | -3.6999 | -1.7223 | 3.7005 | 1.7217 | 0.00058024 | -0.00057176 | 0.11797 | 0.11796 | 0.11797 | 0.99867 | -0.018861 | 0.99882 | -0.020107 | 53.6223
82 | 3.4651 | 1.6091 | -3.4604 | -1.6144 | 0.0046059 | -0.0053547 | 0.11044 | 0.11052 | 0.11052 | 0.99859 | -0.018135 | 0.99734 | -0.0075597 | 50.2385
83 | -4.0409 | -1.8771 | 4.0424 | 1.8717 | 0.0014992 | -0.0053234 | 0.12877 | 0.1287 | 0.12877 | 0.99882 | -0.020107 | 0.99923 | -0.015508 | 35.5728
84 | 0.34039 | 0.15533 | -0.34033 | -0.16356 | 5.4524e-05 | -0.0082256 | 0.010814 | 0.010915 | 0.010915 | 0.99882 | -0.020107 | 0.99867 | -0.018814 | 4.9613
85 | 3.3372 | 1.5557 | -3.3351 | -1.5583 | 0.0020912 | -0.002652 | 0.10657 | 0.10661 | 0.10661 | 0.99734 | -0.0075597 | 0.99676 | -0.0025441 | 48.4604
86 | 0.12324 | 0.058755 | -0.12324 | -0.05969 | 8.2341e-07 | -0.00093493 | 0.0039519 | 0.0039636 | 0.0039636 | 0.99734 | -0.0075597 | 0.99734 | -0.0075025 | 1.8016
87 | -4.0424 | -1.8717 | 4.0426 | 1.8692 | 0.00021611 | -0.0025282 | 0.1287 | 0.12866 | 0.1287 | 0.99923 | -0.015508 | 0.99928 | -0.015255 | 20.1717
88 | 0.34033 | 0.16356 | -0.34033 | -0.16483 | 8.5239e-06 | -0.0012718 | 0.010915 | 0.010931 | 0.010931 | 0.99867 | -0.018814 | 0.99864 | -0.018598 | 4.9685
89 | 0.55877 | 0.27001 | -0.55876 | -0.27062 | 1.1192e-05 | -0.00061207 | 0.017973 | 0.017981 | 0.017981 | 0.99676 | -0.0025441 | 0.99674 | -0.00237 | 8.1731
90 | -4.2078 | -1.9492 | 4.2082 | 1.945 | 0.00038807 | -0.0041743 | 0.13396 | 0.13391 | 0.13396 | 0.99928 | -0.015255 | 0.99938 | -0.014818 | 20.9975
91 | -4.3959 | -2.0359 | 4.396 | 2.0349 | 0.00010557 | -0.0010356 | 0.13993 | 0.13992 | 0.13993 | 0.99938 | -0.014818 | 0.9994 | -0.014705 | 21.9334
92 | 0.38911 | 0.18823 | -0.38911 | -0.18845 | 1.992e-06 | -0.00022048 | 0.012585 | 0.012588 | 0.012588 | 0.99148 | -0.074325 | 0.99147 | -0.074281 | 5.7218
93 | -4.396 | -2.0349 | 4.3966 | 2.0289 | 0.00061276 | -0.0060159 | 0.13992 | 0.13984 | 0.13992 | 0.9994 | -0.014705 | 0.99955 | -0.01404 | 21.9313
94 | -5.2579 | -2.3988 | 5.2587 | 2.3932 | 0.00082933 | -0.0055845 | 0.16691 | 0.16684 | 0.16691 | 0.99955 | -0.01404 | 0.99971 | -0.013236 | 26.1611
95 | 0.86128 | 0.36992 | -0.86123 | -0.37116 | 5.1744e-05 | -0.0012455 | 0.027072 | 0.027086 | 0.027086 | 0.99955 | -0.01404 | 0.99949 | -0.013652 | 12.3118
96 | -5.2587 | -2.3932 | 5.259 | 2.391 | 0.00032813 | -0.0022115 | 0.16684 | 0.16681 | 0.16684 | 0.99971 | -0.013236 | 0.99978 | -0.012916 | 26.1498
97 | 0.67571 | 0.28131 | -0.67566 | -0.28294 | 4.0987e-05 | -0.001625 | 0.02114 | 0.021158 | 0.021158 | 0.99949 | -0.013652 | 0.99943 | -0.013295 | 9.6172
98 | -5.5924 | -2.5525 | 5.5931 | 2.5542 | 0.00068243 | 0.0017512 | 0.1775 | 0.1775 | 0.1775 | 0.99978 | -0.012916 | 1 | 0 | 27.5194
99 | 0.67566 | 0.28294 | -0.67562 | -0.28469 | 4.4355e-05 | -0.0017551 | 0.021158 | 0.021178 | 0.021178 | 0.99943 | -0.013295 | 0.99937 | -0.0129 | 9.6262
100 | 10.5173 | 4.9381 | -10.5142 | -4.9419 | 0.0030538 | -0.0037973 | 0.33541 | 0.33548 | 0.33548 | 1 | 0 | 0.9997 | -0.0012723 | 52.5823
101 | 0.089931 | 0.043284 | -0.089931 | -0.043556 | 1.2649e-07 | -0.00027187 | 0.002882 | 0.0028854 | 0.0028854 | 0.9997 | -0.0012723 | 0.9997 | -0.0012601 | 1.3116
102 | 0.076214 | 0.036822 | -0.076213 | -0.036912 | 8.1619e-07 | -9.0162e-05 | 0.0024494 | 0.0024505 | 0.0024505 | 0.99758 | -0.044904 | 0.99757 | -0.044975 | 1.1669

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 16.1244 | 7.5028

## res_load
| p_mw | q_mvar
0 | 0.21688 | 0.10504
1 | 0.091655 | 0.04439
2 | 0.17362 | 0.084089
3 | 0.17026 | 0.082463
4 | 0.19582 | 0.094838
5 | 0.13511 | 0.065438
6 | 0.33004 | 0.15984
7 | 0.1689 | 0.081804
8 | 0.3665 | 0.1775
9 | 0.24007 | 0.11627
10 | 0.22532 | 0.10913
11 | 0.40873 | 0.19796
12 | 0.12567 | 0.060867
13 | 0.20441 | 0.099002
14 | 0.36655 | 0.17753
15 | 0.084587 | 0.040967
16 | 0.14003 | 0.067819
17 | 0.11829 | 0.057291
18 | 0.056703 | 0.027463
19 | 0.20115 | 0.097423
20 | 0.14172 | 0.068638
21 | 0.41504 | 0.20101
22 | 0.29521 | 0.14298
23 | 0.30184 | 0.14619
24 | 0.15271 | 0.07396
25 | 0.15572 | 0.075418
26 | 0.10424 | 0.050484
27 | 0.072326 | 0.035029
28 | 0.079468 | 0.038488
29 | 0.2394 | 0.11595
30 | 0.12695 | 0.061485
31 | 0.14609 | 0.070755
32 | 1.0212 | 0.49458
33 | 0.078767 | 0.038149
34 | 3.9619 | 1.9188
35 | 0.26613 | 0.12889
36 | 0.2894 | 0.14016
37 | 0.23454 | 0.11359
38 | 0.12324 | 0.05969
39 | 0.16517 | 0.079994
40 | 0.34033 | 0.16483
41 | 0.55876 | 0.27062
42 | 0.18773 | 0.09092
43 | 1.223 | 0.59231
44 | 0.38911 | 0.18845
45 | 0.18553 | 0.089854
46 | 0.33341 | 0.16148
47 | 0.089931 | 0.043556
48 | 0.15759 | 0.076325
49 | 0.11532 | 0.055853
50 | 0.076213 | 0.036912

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1