## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_555_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_555_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_555_0_node_5 | 20 | n |  | TRUE
3 | bus_MV_555_0_node_2 | 20 | n |  | TRUE
4 | bus_MV_555_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_555_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_555_0_node_96 | 20 | n |  | TRUE
7 | bus_MV_555_0_node_98 | 20 | n |  | TRUE
8 | bus_MV_555_0_node_70 | 20 | n |  | TRUE
9 | bus_MV_555_0_node_97 | 20 | n |  | TRUE
10 | bus_MV_555_0_node_99 | 20 | n |  | TRUE
11 | bus_MV_555_0_node_168 | 20 | n |  | TRUE
12 | bus_MV_555_0_node_73 | 20 | n |  | TRUE
13 | bus_MV_555_0_node_133 | 20 | n |  | TRUE
14 | bus_MV_555_0_node_64 | 20 | n |  | TRUE
15 | bus_MV_555_0_node_72 | 20 | n |  | TRUE
16 | bus_MV_555_0_node_6 | 20 | n |  | TRUE
17 | bus_MV_555_0_node_76 | 20 | n |  | TRUE
18 | bus_MV_555_0_node_91 | 20 | n |  | TRUE
19 | bus_MV_555_0_node_92 | 20 | n |  | TRUE
20 | bus_MV_555_0_node_7 | 20 | n |  | TRUE
21 | bus_MV_555_0_node_69 | 20 | n |  | TRUE
22 | bus_MV_555_0_node_159 | 20 | n |  | TRUE
23 | bus_MV_555_0_node_77 | 20 | n |  | TRUE
24 | bus_MV_555_0_node_160 | 20 | n |  | TRUE
25 | bus_MV_555_0_node_9 | 20 | n |  | TRUE
26 | bus_MV_555_0_node_10 | 20 | n |  | TRUE
27 | bus_MV_555_0_node_11 | 20 | n |  | TRUE
28 | bus_MV_555_0_node_12 | 20 | n |  | TRUE
29 | bus_MV_555_0_node_35 | 20 | n |  | TRUE
30 | bus_MV_555_0_node_121 | 20 | n |  | TRUE
31 | bus_MV_555_0_node_32 | 20 | n |  | TRUE
32 | bus_MV_555_0_node_13 | 20 | n |  | TRUE
33 | bus_MV_555_0_node_14 | 20 | n |  | TRUE
34 | bus_MV_555_0_node_15 | 20 | n |  | TRUE
35 | bus_MV_555_0_node_126 | 20 | n |  | TRUE
36 | bus_MV_555_0_node_127 | 20 | n |  | TRUE
37 | bus_MV_555_0_node_63 | 20 | n |  | TRUE
38 | bus_MV_555_0_node_161 | 20 | n |  | TRUE
39 | bus_MV_555_0_node_16 | 20 | n |  | TRUE
40 | bus_MV_555_0_node_17 | 20 | n |  | TRUE
41 | bus_MV_555_0_node_18 | 20 | n |  | TRUE
42 | bus_MV_555_0_node_19 | 20 | n |  | TRUE
43 | bus_MV_555_0_node_23 | 20 | n |  | TRUE
44 | bus_MV_555_0_node_42 | 20 | n |  | TRUE
45 | bus_MV_555_0_node_43 | 20 | n |  | TRUE
46 | bus_MV_555_0_node_45 | 20 | n |  | TRUE
47 | bus_MV_555_0_node_124 | 20 | n |  | TRUE
48 | bus_MV_555_0_node_39 | 20 | n |  | TRUE
49 | bus_MV_555_0_node_166 | 20 | n |  | TRUE
50 | bus_MV_555_0_node_20 | 20 | n |  | TRUE
51 | bus_MV_555_0_node_125 | 20 | n |  | TRUE
52 | bus_MV_555_0_node_41 | 20 | n |  | TRUE
53 | bus_MV_555_0_node_21 | 20 | n |  | TRUE
54 | bus_MV_555_0_node_22 | 20 | n |  | TRUE
55 | bus_MV_555_0_node_117 | 20 | n |  | TRUE
56 | bus_MV_555_0_node_95 | 20 | n |  | TRUE
57 | bus_MV_555_0_node_46 | 20 | n |  | TRUE
58 | bus_MV_555_0_node_66 | 20 | n |  | TRUE
59 | bus_MV_555_0_node_67 | 20 | n |  | TRUE
60 | bus_MV_555_0_node_65 | 20 | n |  | TRUE
61 | bus_MV_555_0_node_116 | 20 | n |  | TRUE
62 | bus_MV_555_0_node_80 | 20 | n |  | TRUE
63 | bus_MV_555_0_node_83 | 20 | n |  | TRUE
64 | bus_MV_555_0_node_24 | 20 | n |  | TRUE
65 | bus_MV_555_0_node_25 | 20 | n |  | TRUE
66 | bus_MV_555_0_node_26 | 20 | n |  | TRUE
67 | bus_MV_555_0_node_48 | 20 | n |  | TRUE
68 | bus_MV_555_0_node_55 | 20 | n |  | TRUE
69 | bus_MV_555_0_node_47 | 20 | n |  | TRUE
70 | bus_MV_555_0_node_57 | 20 | n |  | TRUE
71 | bus_MV_555_0_node_27 | 20 | n |  | TRUE
72 | bus_MV_555_0_node_28 | 20 | n |  | TRUE
73 | bus_MV_555_0_node_29 | 20 | n |  | TRUE
74 | bus_MV_555_0_node_30 | 20 | n |  | TRUE
75 | bus_MV_555_0_node_31 | 20 | n |  | TRUE
76 | bus_MV_555_0_node_33 | 20 | n |  | TRUE
77 | bus_MV_555_0_node_40 | 20 | n |  | TRUE
78 | bus_MV_555_0_node_34 | 20 | n |  | TRUE
79 | bus_MV_555_0_node_36 | 20 | n |  | TRUE
80 | bus_MV_555_0_node_37 | 20 | n |  | TRUE
81 | bus_MV_555_0_node_38 | 20 | n |  | TRUE
82 | bus_MV_555_0_node_123 | 20 | n |  | TRUE
83 | bus_MV_555_0_node_49 | 20 | n |  | TRUE
84 | bus_MV_555_0_node_51 | 20 | n |  | TRUE
85 | bus_MV_555_0_node_50 | 20 | n |  | TRUE
86 | bus_MV_555_0_node_54 | 20 | n |  | TRUE
87 | bus_MV_555_0_node_52 | 20 | n |  | TRUE
88 | bus_MV_555_0_node_59 | 20 | n |  | TRUE
89 | bus_MV_555_0_node_60 | 20 | n |  | TRUE
90 | bus_MV_555_0_node_58 | 20 | n |  | TRUE
91 | bus_MV_555_0_node_53 | 20 | n |  | TRUE
92 | bus_MV_555_0_node_128 | 20 | n |  | TRUE
93 | bus_MV_555_0_node_68 | 20 | n |  | TRUE
94 | bus_MV_555_0_node_167 | 20 | n |  | TRUE
95 | bus_MV_555_0_node_61 | 20 | n |  | TRUE
96 | bus_MV_555_0_node_62 | 20 | n |  | TRUE
97 | bus_MV_555_0_node_131 | 20 | n |  | TRUE
98 | bus_MV_555_0_node_169 | 20 | n |  | TRUE
99 | bus_MV_555_0_node_132 | 20 | n |  | TRUE
100 | bus_MV_555_0_node_130 | 20 | n |  | TRUE
101 | bus_MV_555_0_node_122 | 20 | n |  | TRUE
102 | bus_MV_555_0_node_74 | 20 | n |  | TRUE
103 | bus_MV_555_0_node_75 | 20 | n |  | TRUE
104 | bus_MV_555_0_node_79 | 20 | n |  | TRUE
105 | bus_MV_555_0_node_78 | 20 | n |  | TRUE
106 | bus_MV_555_0_node_164 | 20 | n |  | TRUE
107 | bus_MV_555_0_node_93 | 20 | n |  | TRUE
108 | bus_MV_555_0_node_81 | 20 | n |  | TRUE
109 | bus_MV_555_0_node_82 | 20 | n |  | TRUE
110 | bus_MV_555_0_node_165 | 20 | n |  | TRUE
111 | bus_MV_555_0_node_104 | 20 | n |  | TRUE
112 | bus_MV_555_0_node_84 | 20 | n |  | TRUE
113 | bus_MV_555_0_node_85 | 20 | n |  | TRUE
114 | bus_MV_555_0_node_87 | 20 | n |  | TRUE
115 | bus_MV_555_0_node_88 | 20 | n |  | TRUE
116 | bus_MV_555_0_node_155 | 20 | n |  | TRUE
117 | bus_MV_555_0_node_89 | 20 | n |  | TRUE
118 | bus_MV_555_0_node_94 | 20 | n |  | TRUE
119 | bus_MV_555_0_node_162 | 20 | n |  | TRUE
120 | bus_MV_555_0_node_114 | 20 | n |  | TRUE
121 | bus_MV_555_0_node_120 | 20 | n |  | TRUE
122 | bus_MV_555_0_node_156 | 20 | n |  | TRUE
123 | bus_MV_555_0_node_157 | 20 | n |  | TRUE
124 | bus_MV_555_0_node_119 | 20 | n |  | TRUE
125 | bus_MV_555_0_node_158 | 20 | n |  | TRUE
126 | bus_MV_555_0_node_100 | 20 | n |  | TRUE
127 | bus_MV_555_0_node_102 | 20 | n |  | TRUE
128 | bus_MV_555_0_node_101 | 20 | n |  | TRUE
129 | bus_MV_555_0_node_103 | 20 | n |  | TRUE
130 | bus_MV_555_0_node_105 | 20 | n |  | TRUE
131 | bus_MV_555_0_node_106 | 20 | n |  | TRUE
132 | bus_MV_555_0_node_107 | 20 | n |  | TRUE
133 | bus_MV_555_0_node_108 | 20 | n |  | TRUE
134 | bus_MV_555_0_node_137 | 20 | n |  | TRUE
135 | bus_MV_555_0_node_138 | 20 | n |  | TRUE
136 | bus_MV_555_0_node_136 | 20 | n |  | TRUE
137 | bus_MV_555_0_node_142 | 20 | n |  | TRUE
138 | bus_MV_555_0_node_109 | 20 | n |  | TRUE
139 | bus_MV_555_0_node_111 | 20 | n |  | TRUE
140 | bus_MV_555_0_node_112 | 20 | n |  | TRUE
141 | bus_MV_555_0_node_148 | 20 | n |  | TRUE
142 | bus_MV_555_0_node_135 | 20 | n |  | TRUE
143 | bus_MV_555_0_node_110 | 20 | n |  | TRUE
144 | bus_MV_555_0_node_150 | 20 | n |  | TRUE
145 | bus_MV_555_0_node_149 | 20 | n |  | TRUE
146 | bus_MV_555_0_node_134 | 20 | n |  | TRUE
147 | bus_MV_555_0_node_113 | 20 | n |  | TRUE
148 | bus_MV_555_0_node_115 | 20 | n |  | TRUE
149 | bus_MV_555_0_node_153 | 20 | n |  | TRUE
150 | bus_MV_555_0_node_163 | 20 | n |  | TRUE
151 | bus_MV_555_0_node_147 | 20 | n |  | TRUE
152 | bus_MV_555_0_node_154 | 20 | n |  | TRUE
153 | bus_MV_555_0_node_151 | 20 | n |  | TRUE
154 | bus_MV_555_0_node_145 | 20 | n |  | TRUE
155 | bus_MV_555_0_node_144 | 20 | n |  | TRUE
156 | bus_MV_555_0_node_118 | 20 | n |  | TRUE
157 | bus_MV_555_0_node_129 | 20 | n |  | TRUE
158 | bus_MV_555_0_node_143 | 20 | n |  | TRUE
159 | bus_MV_555_0_node_141 | 20 | n |  | TRUE
160 | bus_MV_555_0_node_139 | 20 | n |  | TRUE
161 | bus_MV_555_0_node_140 | 20 | n |  | TRUE
162 | bus_MV_555_0_node_152 | 20 | n |  | TRUE
163 | bus_HV_555_0_node_79 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_555_0_load_0 | 0 | 0.18809 | 0.091098 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_555_0_load_4 | 5 | 0.27819 | 0.13473 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_555_0_load_96 | 6 | 0.41543 | 0.2012 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_555_0_load_70 | 8 | 0.22863 | 0.11073 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_555_0_load_168 | 11 | 0.32849 | 0.15909 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_555_0_load_133 | 13 | 0.1031 | 0.049932 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_555_0_load_91 | 18 | 0.38734 | 0.1876 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_555_0_load_69 | 21 | 0.35522 | 0.17204 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_555_0_load_160 | 24 | 0.26078 | 0.1263 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_555_0_load_9 | 25 | 0.27931 | 0.13528 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_555_0_load_35 | 29 | 0.39387 | 0.19076 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_555_0_load_121 | 30 | 0.068511 | 0.033181 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_555_0_load_13 | 32 | 0.3209 | 0.15542 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_555_0_load_126 | 35 | 0.12519 | 0.060632 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_555_0_load_127 | 36 | 0.1879 | 0.091005 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_555_0_load_161 | 38 | 0.40373 | 0.19553 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_555_0_load_16 | 39 | 0.3063 | 0.14835 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_555_0_load_23 | 43 | 0.18113 | 0.087727 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_555_0_load_43 | 45 | 0.28675 | 0.13888 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_555_0_load_166 | 49 | 0.41499 | 0.20099 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_555_0_load_125 | 51 | 0.35001 | 0.16952 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_555_0_load_117 | 55 | 0.39182 | 0.18977 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_555_0_load_95 | 56 | 0.23684 | 0.11471 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_555_0_load_46 | 57 | 0.32784 | 0.15878 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_555_0_load_65 | 60 | 0.26117 | 0.12649 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_555_0_load_116 | 61 | 0.36353 | 0.17606 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_555_0_load_24 | 64 | 0.23351 | 0.11309 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_555_0_load_55 | 68 | 0.3693 | 0.17886 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_555_0_load_47 | 69 | 0.37191 | 0.18012 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_555_0_load_27 | 71 | 0.36493 | 0.17675 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_555_0_load_30 | 74 | 0.06938 | 0.033602 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_555_0_load_34 | 78 | 0.26745 | 0.12953 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_555_0_load_36 | 79 | 0.25653 | 0.12424 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_555_0_load_37 | 80 | 0.31054 | 0.1504 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_555_0_load_38 | 81 | 0.087742 | 0.042495 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_555_0_load_123 | 82 | 0.078161 | 0.037855 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_555_0_load_49 | 83 | 0.26357 | 0.12766 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_555_0_load_58 | 90 | 0.41036 | 0.19875 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_555_0_load_128 | 92 | 0.198 | 0.095894 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_555_0_load_68 | 93 | 0.26599 | 0.12882 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_555_0_load_167 | 94 | 0.20511 | 0.099339 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_555_0_load_131 | 97 | 0.32778 | 0.15875 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_555_0_load_169 | 98 | 0.10544 | 0.051066 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_555_0_load_132 | 99 | 0.13977 | 0.067696 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_555_0_load_122 | 101 | 0.078676 | 0.038105 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_555_0_load_74 | 102 | 0.17228 | 0.08344 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_555_0_load_78 | 105 | 0.41101 | 0.19906 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_555_0_load_164 | 106 | 0.13819 | 0.066928 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_555_0_load_93 | 107 | 0.08103 | 0.039245 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_555_0_load_81 | 108 | 0.26222 | 0.127 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_555_0_load_165 | 110 | 0.15917 | 0.07709 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_555_0_load_84 | 112 | 0.27982 | 0.13553 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_555_0_load_155 | 116 | 0.1818 | 0.088052 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_555_0_load_94 | 118 | 0.25111 | 0.12162 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_555_0_load_162 | 119 | 0.28648 | 0.13875 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_555_0_load_156 | 122 | 0.22958 | 0.11119 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_555_0_load_158 | 125 | 0.37942 | 0.18376 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_555_0_load_100 | 126 | 0.13042 | 0.063165 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_555_0_load_105 | 130 | 0.062892 | 0.03046 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_555_0_load_107 | 132 | 0.22045 | 0.10677 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_555_0_load_138 | 135 | 0.3878 | 0.18782 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_555_0_load_136 | 136 | 0.28313 | 0.13713 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_555_0_load_109 | 138 | 0.3224 | 0.15614 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_555_0_load_148 | 141 | 0.60285 | 0.29197 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_555_0_load_135 | 142 | 0.13364 | 0.064725 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_555_0_load_110 | 143 | 0.22773 | 0.1103 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_555_0_load_150 | 144 | 0.74617 | 0.36139 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_555_0_load_149 | 145 | 0.2462 | 0.11924 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_555_0_load_134 | 146 | 0.24569 | 0.11899 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_555_0_load_153 | 149 | 0.15856 | 0.076792 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_555_0_load_163 | 150 | 0.22206 | 0.10755 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_555_0_load_147 | 151 | 1.6255 | 0.78727 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_555_0_load_154 | 152 | 0.12183 | 0.059005 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_555_0_load_151 | 153 | 0.081992 | 0.039711 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_555_0_load_144 | 155 | 0.072802 | 0.03526 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_555_0_load_118 | 156 | 0.33406 | 0.16179 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_555_0_load_129 | 157 | 0.078354 | 0.037949 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_555_0_load_139 | 160 | 0.12126 | 0.05873 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_555_0_load_140 | 161 | 1.0035 | 0.48602 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_555_0_load_152 | 162 | 0.18704 | 0.090587 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 104 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_555_0_line_0 |  | 0 | 1 | 0.026154 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
1 | MV_555_0_line_1 |  | 0 | 2 | 0.25605 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
2 | MV_555_0_line_2 |  | 1 | 3 | 0.44391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_555_0_line_3 |  | 1 | 4 | 0.089443 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
4 | MV_555_0_line_4 |  | 2 | 5 | 0.005233 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
5 | MV_555_0_line_5 |  | 3 | 6 | 0.068617 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_555_0_line_6 |  | 3 | 7 | 0.3387 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_555_0_line_7 |  | 4 | 8 | 0.008151 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
8 | MV_555_0_line_8 |  | 5 | 16 | 0.036308 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
9 | MV_555_0_line_9 |  | 6 | 9 | 0.003239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_555_0_line_10 |  | 7 | 11 | 0.005647 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_555_0_line_11 |  | 8 | 15 | 0.28371 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
12 | MV_555_0_line_12 |  | 9 | 10 | 0.23362 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_555_0_line_13 |  | 10 | 119 | 0.07084 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_555_0_line_14 |  | 12 | 13 | 0.014706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_555_0_line_15 |  | 12 | 14 | 0.029561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_555_0_line_16 |  | 14 | 99 | 0.026136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_555_0_line_17 |  | 14 | 96 | 0.08633 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_555_0_line_18 |  | 15 | 38 | 0.068216 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
19 | MV_555_0_line_19 |  | 16 | 17 | 0.22553 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
20 | MV_555_0_line_20 |  | 17 | 22 | 0.27104 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_555_0_line_21 |  | 17 | 23 | 0.25014 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
22 | MV_555_0_line_22 |  | 17 | 24 | 0.088919 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_555_0_line_23 |  | 18 | 19 | 0.036107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_555_0_line_24 |  | 18 | 20 | 0.23261 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_555_0_line_25 |  | 19 | 107 | 0.041143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_555_0_line_26 |  | 20 | 21 | 0.036697 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_555_0_line_27 |  | 22 | 106 | 0.027347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_555_0_line_28 |  | 23 | 104 | 0.070092 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
29 | MV_555_0_line_29 |  | 23 | 105 | 0.061409 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_555_0_line_30 |  | 23 | 103 | 0.13843 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_555_0_line_31 |  | 25 | 26 | 0.074847 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
32 | MV_555_0_line_32 |  | 26 | 27 | 0.040707 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_555_0_line_33 |  | 27 | 28 | 0.051612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_555_0_line_34 |  | 27 | 29 | 0.00435 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_555_0_line_35 |  | 28 | 30 | 0.085077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_555_0_line_36 |  | 30 | 31 | 0.069423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_555_0_line_37 |  | 31 | 72 | 0.16939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_555_0_line_38 |  | 32 | 33 | 0.045372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_555_0_line_39 |  | 33 | 34 | 0.22297 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_555_0_line_40 |  | 34 | 38 | 0.028392 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
41 | MV_555_0_line_41 |  | 34 | 35 | 0.2023 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
42 | MV_555_0_line_42 |  | 35 | 36 | 0.34708 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
43 | MV_555_0_line_43 |  | 35 | 37 | 0.049086 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_555_0_line_44 |  | 36 | 91 | 0.14552 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_555_0_line_45 |  | 37 | 96 | 0.18908 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_555_0_line_46 |  | 39 | 40 | 0.071745 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
47 | MV_555_0_line_47 |  | 39 | 41 | 0.080048 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
48 | MV_555_0_line_48 |  | 40 | 42 | 0.55731 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
49 | MV_555_0_line_49 |  | 41 | 43 | 0.065958 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
50 | MV_555_0_line_50 |  | 42 | 49 | 0.013884 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
51 | MV_555_0_line_51 |  | 43 | 46 | 0.070743 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
52 | MV_555_0_line_52 |  | 44 | 45 | 0.095151 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_555_0_line_53 |  | 44 | 46 | 0.27684 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
54 | MV_555_0_line_54 |  | 44 | 47 | 0.13245 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_555_0_line_55 |  | 44 | 48 | 0.33675 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_555_0_line_56 |  | 47 | 51 | 0.067353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_555_0_line_57 |  | 47 | 82 | 0.081017 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_555_0_line_58 |  | 48 | 77 | 0.29727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_555_0_line_59 |  | 48 | 80 | 0.063959 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_555_0_line_60 |  | 49 | 58 | 0.3426 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
61 | MV_555_0_line_61 |  | 50 | 51 | 0.044388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_555_0_line_62 |  | 50 | 52 | 0.24129 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_555_0_line_63 |  | 52 | 57 | 0.083467 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_555_0_line_64 |  | 53 | 54 | 0.14002 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
65 | MV_555_0_line_65 |  | 53 | 55 | 0.053332 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
66 | MV_555_0_line_66 |  | 54 | 56 | 0.064203 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
67 | MV_555_0_line_67 |  | 55 | 61 | 0.13033 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
68 | MV_555_0_line_68 |  | 56 | 63 | 0.10548 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
69 | MV_555_0_line_69 |  | 58 | 59 | 0.35014 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
70 | MV_555_0_line_70 |  | 58 | 60 | 0.010442 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_555_0_line_71 |  | 59 | 101 | 0.0061071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_555_0_line_72 |  | 59 | 94 | 0.16733 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
73 | MV_555_0_line_73 |  | 60 | 64 | 0.25574 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
74 | MV_555_0_line_74 |  | 61 | 62 | 0.040598 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
75 | MV_555_0_line_75 |  | 62 | 104 | 0.13273 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
76 | MV_555_0_line_76 |  | 63 | 109 | 0.0912 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_555_0_line_77 |  | 64 | 65 | 0.043355 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_555_0_line_78 |  | 65 | 66 | 0.2754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_555_0_line_79 |  | 66 | 67 | 0.079205 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_555_0_line_80 |  | 66 | 68 | 0.13212 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_555_0_line_81 |  | 67 | 69 | 0.069177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_555_0_line_82 |  | 68 | 70 | 0.2368 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_555_0_line_83 |  | 70 | 93 | 0.001815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_555_0_line_84 |  | 71 | 72 | 0.090128 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_555_0_line_85 |  | 71 | 73 | 0.10555 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_555_0_line_86 |  | 72 | 74 | 0.096058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_555_0_line_87 |  | 72 | 75 | 0.13693 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_555_0_line_88 |  | 73 | 76 | 0.076226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_555_0_line_89 |  | 74 | 77 | 0.043455 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_555_0_line_90 |  | 75 | 78 | 0.020807 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_555_0_line_91 |  | 76 | 79 | 0.067096 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_555_0_line_92 |  | 80 | 81 | 0.023481 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_555_0_line_93 |  | 83 | 84 | 0.083489 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
94 | MV_555_0_line_94 |  | 83 | 85 | 0.18016 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
95 | MV_555_0_line_95 |  | 84 | 86 | 0.11144 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
96 | MV_555_0_line_96 |  | 85 | 87 | 0.16934 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
97 | MV_555_0_line_97 |  | 86 | 90 | 0.023029 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
98 | MV_555_0_line_98 |  | 87 | 91 | 0.11051 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
99 | MV_555_0_line_99 |  | 88 | 89 | 0.24818 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
100 | MV_555_0_line_100 |  | 88 | 90 | 0.13377 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
101 | MV_555_0_line_101 |  | 89 | 94 | 0.033291 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
102 | MV_555_0_line_102 |  | 91 | 92 | 0.12444 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
103 | MV_555_0_line_103 |  | 95 | 96 | 0.25239 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_555_0_line_104 |  | 95 | 97 | 0.0582 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_555_0_line_105 |  | 96 | 98 | 0.046784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_555_0_line_106 |  | 97 | 100 | 0.018406 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_555_0_line_107 |  | 100 | 157 | 0.024295 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_555_0_line_108 |  | 102 | 103 | 0.034795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_555_0_line_109 |  | 104 | 107 | 0.026107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_555_0_line_110 |  | 108 | 109 | 0.026183 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
111 | MV_555_0_line_111 |  | 108 | 110 | 0.23141 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
112 | MV_555_0_line_112 |  | 110 | 111 | 0.02678 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
113 | MV_555_0_line_113 |  | 111 | 127 | 0.10298 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
114 | MV_555_0_line_114 |  | 112 | 113 | 0.012849 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_555_0_line_115 |  | 113 | 114 | 0.16919 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_555_0_line_116 |  | 114 | 115 | 0.38245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_555_0_line_117 |  | 114 | 116 | 0.075867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_555_0_line_118 |  | 115 | 117 | 0.28407 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_555_0_line_119 |  | 115 | 118 | 0.070222 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_555_0_line_120 |  | 116 | 120 | 0.2269 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
121 | MV_555_0_line_121 |  | 117 | 119 | 0.00809 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_555_0_line_122 |  | 120 | 149 | 0.036325 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
123 | MV_555_0_line_123 |  | 121 | 122 | 0.073392 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
124 | MV_555_0_line_124 |  | 121 | 123 | 0.21696 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
125 | MV_555_0_line_125 |  | 121 | 124 | 0.31692 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_555_0_line_126 |  | 122 | 129 | 0.028484 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
127 | MV_555_0_line_127 |  | 123 | 125 | 0.048378 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
128 | MV_555_0_line_128 |  | 124 | 156 | 0.048911 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_555_0_line_129 |  | 125 | 147 | 0.093348 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
130 | MV_555_0_line_130 |  | 126 | 127 | 0.016707 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
131 | MV_555_0_line_131 |  | 126 | 128 | 0.062904 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
132 | MV_555_0_line_132 |  | 128 | 129 | 0.057163 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
133 | MV_555_0_line_133 |  | 130 | 131 | 0.014185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_555_0_line_134 |  | 131 | 132 | 0.027617 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_555_0_line_135 |  | 131 | 133 | 0.087536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_555_0_line_136 |  | 133 | 134 | 0.036161 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
137 | MV_555_0_line_137 |  | 133 | 135 | 0.15059 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
138 | MV_555_0_line_138 |  | 134 | 136 | 0.048639 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
139 | MV_555_0_line_139 |  | 135 | 137 | 0.0756 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
140 | MV_555_0_line_140 |  | 136 | 141 | 0.10777 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
141 | MV_555_0_line_141 |  | 136 | 142 | 0.0058875 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_555_0_line_142 |  | 137 | 158 | 0.033289 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
143 | MV_555_0_line_143 |  | 137 | 159 | 0.014336 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_555_0_line_144 |  | 138 | 139 | 0.073579 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_555_0_line_145 |  | 139 | 140 | 0.068534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_555_0_line_146 |  | 140 | 145 | 0.094485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_555_0_line_147 |  | 140 | 141 | 0.074928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_555_0_line_148 |  | 141 | 151 | 0.076799 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_555_0_line_149 |  | 142 | 146 | 0.0045167 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_555_0_line_150 |  | 143 | 144 | 0.05492 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
151 | MV_555_0_line_151 |  | 144 | 145 | 0.064646 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_555_0_line_152 |  | 147 | 148 | 0.20101 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
153 | MV_555_0_line_153 |  | 148 | 150 | 0.02226 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
154 | MV_555_0_line_154 |  | 149 | 152 | 0.051635 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_555_0_line_155 |  | 149 | 153 | 0.10015 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
156 | MV_555_0_line_156 |  | 150 | 154 | 0.095943 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
157 | MV_555_0_line_157 |  | 153 | 162 | 0.096214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_555_0_line_158 |  | 154 | 155 | 0.10863 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
159 | MV_555_0_line_159 |  | 155 | 158 | 0.0062067 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
160 | MV_555_0_line_160 |  | 159 | 161 | 0.047906 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_555_0_line_161 |  | 160 | 161 | 0.084142 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_555_0_trafo_79 | 25 MVA 110/20 kV | 163 | 104 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2613736.8387 | 1266431.3876
1 | 2613735.6044 | 1266405.2665
2 | 2613702.0762 | 1266685.0622
3 | 2614042.4628 | 1266323.8276
4 | 2613736.5988 | 1266320.4208
5 | 2613706.6243 | 1266687.6745
6 | 2614103.5312 | 1266355.1164
7 | 2614255.9878 | 1266060.9087
8 | 2613736.1885 | 1266312.2808
9 | 2614106.4185 | 1266356.6021
10 | 2614299.6397 | 1266375.3552
11 | 2614255.6701 | 1266055.2707
12 | 2613479.9412 | 1266361.9171
13 | 2613471.7155 | 1266374.118
14 | 2613482.2737 | 1266335.8931
15 | 2613685.6039 | 1266033.1139
16 | 2613738.1756 | 1266705.8045
17 | 2613963.4478 | 1266695.1115
18 | 2613753.0424 | 1266939.6691
19 | 2613772.3692 | 1266970.2019
20 | 2613559.3896 | 1266810.8003
21 | 2613526.5888 | 1266827.256
22 | 2614131.9607 | 1266871.7782
23 | 2613887.0195 | 1266907.7253
24 | 2614019.3754 | 1266625.9839
25 | 2612172.5558 | 1266956.4422
26 | 2612216.4739 | 1266895.8344
27 | 2612239.5011 | 1266873.3661
28 | 2612238.4875 | 1266831.9796
29 | 2612240.7517 | 1266869.1991
30 | 2612307.1635 | 1266781.7624
31 | 2612363.2029 | 1266740.7852
32 | 2613674.7837 | 1265877.1359
33 | 2613688.0996 | 1265920.519
34 | 2613588.79 | 1266029.2111
35 | 2613400.5873 | 1266103.4056
36 | 2613141.9501 | 1265871.9494
37 | 2613403.1698 | 1266152.3416
38 | 2613617.2211 | 1266030.8217
39 | 2612946.8703 | 1267275.7584
40 | 2613014.5583 | 1267300.1123
41 | 2612869.9886 | 1267252.6863
42 | 2613238.3973 | 1267047.1968
43 | 2612806.5551 | 1267233.9583
44 | 2612549.8622 | 1267011.4991
45 | 2612540.7499 | 1267106.2128
46 | 2612738.4266 | 1267214.1868
47 | 2612682.2734 | 1267014.5825
48 | 2612350.8562 | 1266976.7244
49 | 2613225.2426 | 1267042.642
50 | 2612790.5192 | 1267043.546
51 | 2612747.6024 | 1267031.7344
52 | 2612826.2468 | 1266804.9118
53 | 2613566.6441 | 1267130.963
54 | 2613502.9136 | 1267226.5402
55 | 2613608.5326 | 1267097.8245
56 | 2613566.709 | 1267217.7906
57 | 2612905.7926 | 1266779.0327
58 | 2613168.7185 | 1266704.7358
59 | 2613204.3554 | 1266541.7122
60 | 2613165.3982 | 1266694.8326
61 | 2613714.5833 | 1267022.06
62 | 2613748.4172 | 1266999.6226
63 | 2613577.9399 | 1267322.6675
64 | 2613013.2275 | 1266489.2871
65 | 2612986.4807 | 1266455.1047
66 | 2612787.196 | 1266433.813
67 | 2612723.0416 | 1266480.2632
68 | 2612698.2376 | 1266335.8984
69 | 2612745.9517 | 1266545.5468
70 | 2612463.353 | 1266365.9219
71 | 2612574.25 | 1266716.6558
72 | 2612488.0852 | 1266743.9153
73 | 2612675.015 | 1266684.2807
74 | 2612514.245 | 1266836.3431
75 | 2612505.7956 | 1266637.5561
76 | 2612651.9021 | 1266611.6252
77 | 2612526.0792 | 1266878.1557
78 | 2612522.7283 | 1266625.3944
79 | 2612628.8886 | 1266548.5989
80 | 2612303.3377 | 1266944.9975
81 | 2612297.0966 | 1266967.6341
82 | 2612674.7497 | 1267095.249
83 | 2612882.0584 | 1266078.4593
84 | 2612964.3196 | 1266068.6314
85 | 2612768.0178 | 1265938.9826
86 | 2612994.1329 | 1266161.0276
87 | 2612897.078 | 1265866.8779
88 | 2613035.8477 | 1266311.5016
89 | 2613156.4118 | 1266347.7928
90 | 2612995.822 | 1266183.8583
91 | 2613000.4583 | 1265905.9416
92 | 2613011.5309 | 1265781.9903
93 | 2612461.9203 | 1266367.0419
94 | 2613157.535 | 1266381.0629
95 | 2613361.9435 | 1266333.5417
96 | 2613422.9298 | 1266299.4999
97 | 2613386.167 | 1266384.3873
98 | 2613429.8768 | 1266343.3907
99 | 2613459.8536 | 1266323.221
100 | 2613381.5172 | 1266366.5755
101 | 2613198.7523 | 1266544.1416
102 | 2613997.3135 | 1266893.2742
103 | 2613983.1769 | 1266861.4631
104 | 2613828.3007 | 1266932.8725
105 | 2613915.5861 | 1266962.0858
106 | 2614141.8377 | 1266896.5635
107 | 2613806.4733 | 1266947.1879
108 | 2613694.7463 | 1267310.2938
109 | 2613668.6443 | 1267313.1801
110 | 2613915.0472 | 1267381.1335
111 | 2613941.788 | 1267378.6056
112 | 2614310.9172 | 1266868.1155
113 | 2614323.0467 | 1266863.7751
114 | 2614392.8716 | 1266776.4273
115 | 2614252.3289 | 1266562.3053
116 | 2614458.5012 | 1266768.1588
117 | 2614330.1406 | 1266448.0684
118 | 2614192.6742 | 1266598.9213
119 | 2614328.029 | 1266440.2578
120 | 2614678.8167 | 1266822.4376
121 | 2614208.8046 | 1267303.4305
122 | 2614210.089 | 1267376.8072
123 | 2614394.2925 | 1267267.241
124 | 2614005.181 | 1267141.333
125 | 2614393.0701 | 1267218.8819
126 | 2614061.4891 | 1267380.089
127 | 2614044.7355 | 1267379.738
128 | 2614124.3779 | 1267378.7151
129 | 2614181.524 | 1267377.3059
130 | 2614887.5896 | 1267425.0686
131 | 2614894.3699 | 1267437.5388
132 | 2614869.9589 | 1267450.4538
133 | 2614883.336 | 1267392.4907
134 | 2614914.1904 | 1267373.5215
135 | 2614742.3035 | 1267442.1187
136 | 2614900.5505 | 1267329.2006
137 | 2614666.7208 | 1267443.0757
138 | 2614791.0063 | 1267129.8757
139 | 2614761.1713 | 1267174.366
140 | 2614829.7764 | 1267178.6734
141 | 2614823.9718 | 1267253.3758
142 | 2614906.4352 | 1267329.0193
143 | 2614959.7666 | 1267140.9414
144 | 2614988.6539 | 1267187.6502
145 | 2614924.1109 | 1267184.0034
146 | 2614910.9498 | 1267328.8802
147 | 2614477.9779 | 1267180.0946
148 | 2614493.7923 | 1267352.4762
149 | 2614714.3271 | 1266830.0864
150 | 2614493.6852 | 1267374.736
151 | 2614763.5136 | 1267272.6598
152 | 2614710.8572 | 1266881.6027
153 | 2614814.4731 | 1266829.6861
154 | 2614533.2798 | 1267462.1274
155 | 2614641.8448 | 1267458.3241
156 | 2614051.8316 | 1267126.1994
157 | 2613397.0041 | 1266347.8565
158 | 2614648.0478 | 1267458.1068
159 | 2614667.5359 | 1267457.3878
160 | 2614642.2841 | 1267557.1113
161 | 2614670.2508 | 1267505.2164
162 | 2614910.544 | 1266833.3251
163 | 2613828.3007 | 1266932.8725

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99632 | -0.10959 | 0.18809 | 0.091098
1 | 0.99626 | -0.11075 | 0 | 0
2 | 0.99776 | -0.060992 | 0 | 0
3 | 0.99496 | -0.099575 | 0 | 0
4 | 0.99609 | -0.1139 | 0 | 0
5 | 0.99777 | -0.060757 | 0.27819 | 0.13473
6 | 0.9947 | -0.10142 | 0.41543 | 0.2012
7 | 0.99474 | -0.10094 | 0 | 0
8 | 0.99607 | -0.11418 | 0.22863 | 0.11073
9 | 0.99469 | -0.10137 | 0 | 0
10 | 0.99423 | -0.097445 | 0 | 0
11 | 0.99474 | -0.10092 | 0.32849 | 0.15909
12 | 0.99364 | -0.18307 | 0 | 0
13 | 0.99364 | -0.18305 | 0.1031 | 0.049932
14 | 0.99364 | -0.18311 | 0 | 0
15 | 0.99486 | -0.15518 | 0 | 0
16 | 0.99786 | -0.059087 | 0 | 0
17 | 0.99916 | -0.015358 | 0 | 0
18 | 0.9999 | 0.000928 | 0.38734 | 0.1876
19 | 0.99993 | 0.00061078 | 0 | 0
20 | 0.99974 | -9.0954e-05 | 0 | 0
21 | 0.99972 | 6.406e-05 | 0.35522 | 0.17204
22 | 0.99911 | -0.014976 | 0 | 0
23 | 0.99981 | -0.0034882 | 0 | 0
24 | 0.99911 | -0.015639 | 0.26078 | 0.1263
25 | 0.98417 | -0.37522 | 0.27931 | 0.13528
26 | 0.98421 | -0.37495 | 0 | 0
27 | 0.98423 | -0.37509 | 0 | 0
28 | 0.98427 | -0.37552 | 0 | 0
29 | 0.98423 | -0.37507 | 0.39387 | 0.19076
30 | 0.98435 | -0.37621 | 0.068511 | 0.033181
31 | 0.98441 | -0.37682 | 0 | 0
32 | 0.99458 | -0.15747 | 0.3209 | 0.15542
33 | 0.99459 | -0.15765 | 0 | 0
34 | 0.99469 | -0.15846 | 0 | 0
35 | 0.9939 | -0.18528 | 0.12519 | 0.060632
36 | 0.9927 | -0.2262 | 0.1879 | 0.091005
37 | 0.99385 | -0.18489 | 0 | 0
38 | 0.99474 | -0.15753 | 0.40373 | 0.19553
39 | 0.98763 | -0.35906 | 0.3063 | 0.14835
40 | 0.98774 | -0.35696 | 0 | 0
41 | 0.98751 | -0.36121 | 0 | 0
42 | 0.98864 | -0.34057 | 0 | 0
43 | 0.98741 | -0.36297 | 0.18113 | 0.087727
44 | 0.98643 | -0.39454 | 0 | 0
45 | 0.98638 | -0.39488 | 0.28675 | 0.13888
46 | 0.98731 | -0.36476 | 0 | 0
47 | 0.98624 | -0.39587 | 0 | 0
48 | 0.98552 | -0.38664 | 0 | 0
49 | 0.98865 | -0.34037 | 0.41499 | 0.20099
50 | 0.98616 | -0.39515 | 0 | 0
51 | 0.98618 | -0.39532 | 0.35001 | 0.16952
52 | 0.986 | -0.39618 | 0 | 0
53 | 0.99889 | -0.031413 | 0 | 0
54 | 0.99864 | -0.035968 | 0 | 0
55 | 0.99899 | -0.029675 | 0.39182 | 0.18977
56 | 0.99852 | -0.038053 | 0.23684 | 0.11471
57 | 0.98597 | -0.39585 | 0.32784 | 0.15878
58 | 0.98934 | -0.31663 | 0 | 0
59 | 0.98977 | -0.30877 | 0 | 0
60 | 0.98932 | -0.31644 | 0.26117 | 0.12649
61 | 0.99955 | -0.010815 | 0.36353 | 0.17606
62 | 0.99974 | -0.0047028 | 0 | 0
63 | 0.9981 | -0.052215 | 0 | 0
64 | 0.98871 | -0.32069 | 0.23351 | 0.11309
65 | 0.98865 | -0.32019 | 0 | 0
66 | 0.98829 | -0.31698 | 0 | 0
67 | 0.98826 | -0.31663 | 0 | 0
68 | 0.98819 | -0.31596 | 0.3693 | 0.17886
69 | 0.98822 | -0.31632 | 0.37191 | 0.18012
70 | 0.98806 | -0.31675 | 0 | 0
71 | 0.9845 | -0.37762 | 0.36493 | 0.17675
72 | 0.98458 | -0.37828 | 0 | 0
73 | 0.98447 | -0.37731 | 0 | 0
74 | 0.98478 | -0.38008 | 0.06938 | 0.033602
75 | 0.98453 | -0.37785 | 0 | 0
76 | 0.98444 | -0.37707 | 0 | 0
77 | 0.98487 | -0.38093 | 0 | 0
78 | 0.98452 | -0.37778 | 0.26745 | 0.12953
79 | 0.98441 | -0.37729 | 0.25653 | 0.12424
80 | 0.98549 | -0.38633 | 0.31054 | 0.1504
81 | 0.98549 | -0.38631 | 0.087742 | 0.042495
82 | 0.98623 | -0.39579 | 0.078161 | 0.037855
83 | 0.9913 | -0.26705 | 0.26357 | 0.12766
84 | 0.99118 | -0.26918 | 0 | 0
85 | 0.99189 | -0.24698 | 0 | 0
86 | 0.99103 | -0.27201 | 0 | 0
87 | 0.99213 | -0.24249 | 0 | 0
88 | 0.99061 | -0.28597 | 0 | 0
89 | 0.99029 | -0.29186 | 0 | 0
90 | 0.991 | -0.27259 | 0.41036 | 0.19875
91 | 0.99249 | -0.23017 | 0 | 0
92 | 0.99244 | -0.23048 | 0.198 | 0.095894
93 | 0.98806 | -0.31674 | 0.26599 | 0.12882
94 | 0.99025 | -0.29264 | 0.20511 | 0.099339
95 | 0.99354 | -0.18219 | 0 | 0
96 | 0.99367 | -0.18335 | 0 | 0
97 | 0.99351 | -0.18191 | 0.32778 | 0.15875
98 | 0.99366 | -0.18329 | 0.10544 | 0.051066
99 | 0.99364 | -0.18306 | 0.13977 | 0.067696
100 | 0.99351 | -0.1819 | 0 | 0
101 | 0.98977 | -0.30876 | 0.078676 | 0.038105
102 | 0.99977 | -0.0031539 | 0.17228 | 0.08344
103 | 0.99978 | -0.0032247 | 0 | 0
104 | 1 | 0 | -22.4399 | -10.481
105 | 0.99976 | -0.0037935 | 0.41101 | 0.19906
106 | 0.99911 | -0.014931 | 0.13819 | 0.066928
107 | 0.99997 | 0.00025177 | 0.08103 | 0.039245
108 | 0.99789 | -0.05592 | 0.26222 | 0.127
109 | 0.99794 | -0.055094 | 0 | 0
110 | 0.99699 | -0.086005 | 0.15917 | 0.07709
111 | 0.99695 | -0.086808 | 0 | 0
112 | 0.99299 | -0.090018 | 0.27982 | 0.13553
113 | 0.993 | -0.090062 | 0 | 0
114 | 0.99306 | -0.090611 | 0 | 0
115 | 0.99355 | -0.094943 | 0 | 0
116 | 0.99298 | -0.089961 | 0.1818 | 0.088052
117 | 0.99401 | -0.098848 | 0 | 0
118 | 0.99353 | -0.094733 | 0.25111 | 0.12162
119 | 0.99402 | -0.098957 | 0.28648 | 0.13875
120 | 0.99274 | -0.091563 | 0 | 0
121 | 0.99625 | -0.10288 | 0 | 0
122 | 0.99637 | -0.10079 | 0.22958 | 0.11119
123 | 0.99592 | -0.10875 | 0 | 0
124 | 0.99612 | -0.1017 | 0 | 0
125 | 0.99585 | -0.11005 | 0.37942 | 0.18376
126 | 0.99675 | -0.090392 | 0.13042 | 0.063165
127 | 0.99677 | -0.089892 | 0 | 0
128 | 0.99651 | -0.09827 | 0 | 0
129 | 0.99642 | -0.099951 | 0 | 0
130 | 0.9944 | -0.14547 | 0.062892 | 0.03046
131 | 0.9944 | -0.14548 | 0 | 0
132 | 0.99439 | -0.14541 | 0.22045 | 0.10677
133 | 0.99443 | -0.14577 | 0 | 0
134 | 0.99439 | -0.14639 | 0 | 0
135 | 0.99458 | -0.14301 | 0.3878 | 0.18782
136 | 0.99427 | -0.14762 | 0.28313 | 0.13713
137 | 0.99467 | -0.14151 | 0 | 0
138 | 0.99328 | -0.15079 | 0.3224 | 0.15614
139 | 0.99331 | -0.15108 | 0 | 0
140 | 0.99334 | -0.15133 | 0 | 0
141 | 0.99348 | -0.1527 | 0.60285 | 0.29197
142 | 0.99427 | -0.1476 | 0.13364 | 0.064725
143 | 0.99308 | -0.14935 | 0.22773 | 0.1103
144 | 0.99311 | -0.14919 | 0.74617 | 0.36139
145 | 0.99319 | -0.14995 | 0.2462 | 0.11924
146 | 0.99427 | -0.14758 | 0.24569 | 0.11899
147 | 0.99554 | -0.12024 | 0 | 0
148 | 0.99525 | -0.12536 | 0 | 0
149 | 0.9927 | -0.091819 | 0.15856 | 0.076792
150 | 0.99518 | -0.12779 | 0.22206 | 0.10755
151 | 0.99332 | -0.15119 | 1.6255 | 0.78727
152 | 0.9927 | -0.091745 | 0.12183 | 0.059005
153 | 0.99265 | -0.09217 | 0.081992 | 0.039711
154 | 0.99488 | -0.13789 | 0 | 0
155 | 0.99472 | -0.14056 | 0.072802 | 0.03526
156 | 0.9961 | -0.10151 | 0.33406 | 0.16179
157 | 0.9935 | -0.18187 | 0.078354 | 0.037949
158 | 0.99472 | -0.14071 | 0 | 0
159 | 0.99465 | -0.14132 | 0 | 0
160 | 0.99457 | -0.14056 | 0.12126 | 0.05873
161 | 0.99458 | -0.14068 | 1.0035 | 0.48602
162 | 0.99263 | -0.091958 | 0.18704 | 0.090587
163 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 11.0726 | 5.1243 | -11.072 | -5.1257 | 0.00059816 | -0.0014343 | 0.35351 | 0.35353 | 0.35353 | 0.99632 | -0.10959 | 0.99626 | -0.11075 | 41.9873
1 | -11.2607 | -5.2154 | 11.2725 | 5.2318 | 0.011798 | 0.016422 | 0.35956 | 0.35956 | 0.35956 | 0.99632 | -0.10959 | 0.99776 | -0.060992 | 43.8492
2 | 2.2988 | 1.0682 | -2.2956 | -1.0778 | 0.0032028 | -0.0095558 | 0.073451 | 0.07358 | 0.07358 | 0.99626 | -0.11075 | 0.99496 | -0.099575 | 33.4453
3 | 8.7732 | 4.0575 | -8.7719 | -4.0631 | 0.0012844 | -0.0056024 | 0.28008 | 0.28016 | 0.28016 | 0.99626 | -0.11075 | 0.99609 | -0.1139 | 33.2737
4 | -11.2725 | -5.2318 | 11.2726 | 5.2315 | 0.0001238 | -0.00028438 | 0.35956 | 0.35955 | 0.35956 | 0.99776 | -0.060992 | 0.99777 | -0.060757 | 42.7025
5 | 1.9671 | 0.91916 | -1.9666 | -0.91893 | 0.00048517 | 0.00022282 | 0.062995 | 0.062996 | 0.062996 | 0.99496 | -0.099575 | 0.9947 | -0.10142 | 29.9982
6 | 0.32855 | 0.1586 | -0.32849 | -0.15896 | 6.7648e-05 | -0.00035782 | 0.010585 | 0.01059 | 0.01059 | 0.99496 | -0.099575 | 0.99474 | -0.10094 | 5.043
7 | 8.7719 | 4.0631 | -8.7718 | -4.0636 | 0.00011708 | -0.0005104 | 0.28016 | 0.28017 | 0.28017 | 0.99609 | -0.1139 | 0.99607 | -0.11418 | 33.2746
8 | -11.5508 | -5.3662 | 11.5517 | 5.3643 | 0.00090213 | -0.0019338 | 0.36849 | 0.36846 | 0.36849 | 0.99777 | -0.060757 | 0.99786 | -0.059087 | 43.7639
9 | 1.5511 | 0.71773 | -1.5511 | -0.7178 | 1.0639e-05 | -7.3361e-05 | 0.049602 | 0.049603 | 0.049603 | 0.9947 | -0.10142 | 0.99469 | -0.10137 | 22.5467
10 | 0.32849 | 0.15896 | -0.32849 | -0.15909 | 8.4563e-07 | -0.00013316 | 0.01059 | 0.010592 | 0.010592 | 0.99474 | -0.10094 | 0.99474 | -0.10092 | 4.8145
11 | 8.5431 | 3.9529 | -8.5356 | -3.9427 | 0.0075258 | 0.010168 | 0.27281 | 0.27282 | 0.27282 | 0.99607 | -0.11418 | 0.99486 | -0.15518 | 33.2707
12 | 1.5511 | 0.7178 | -1.5504 | -0.72309 | 0.00076842 | -0.0052885 | 0.049603 | 0.04967 | 0.04967 | 0.99469 | -0.10137 | 0.99423 | -0.097445 | 22.5774
13 | 1.5504 | 0.72309 | -1.5501 | -0.72298 | 0.0003114 | 0.00011147 | 0.04967 | 0.049671 | 0.049671 | 0.99423 | -0.097445 | 0.99402 | -0.098957 | 23.653
14 | 0.1031 | 0.049585 | -0.1031 | -0.049932 | 2.1715e-07 | -0.0003466 | 0.0033236 | 0.003328 | 0.003328 | 0.99364 | -0.18307 | 0.99364 | -0.18305 | 1.5127
15 | -0.1031 | -0.049585 | 0.1031 | 0.048888 | 4.3478e-07 | -0.00069673 | 0.0033236 | 0.0033149 | 0.0033236 | 0.99364 | -0.18307 | 0.99364 | -0.18311 | 1.5107
16 | 0.13977 | 0.06708 | -0.13977 | -0.067696 | 7.091e-07 | -0.00061591 | 0.0045042 | 0.004512 | 0.004512 | 0.99364 | -0.18311 | 0.99364 | -0.18306 | 2.0509
17 | -0.24287 | -0.11597 | 0.24288 | 0.11393 | 7.0233e-06 | -0.0020331 | 0.007819 | 0.0077937 | 0.007819 | 0.99364 | -0.18311 | 0.99367 | -0.18335 | 3.5541
18 | 8.5356 | 3.9427 | -8.5347 | -3.947 | 0.00092937 | -0.0043047 | 0.27282 | 0.27288 | 0.27288 | 0.99486 | -0.15518 | 0.99474 | -0.15753 | 32.4089
19 | -11.5517 | -5.3643 | 11.5626 | 5.3795 | 0.010912 | 0.015216 | 0.36846 | 0.36845 | 0.36846 | 0.99786 | -0.059087 | 0.99916 | -0.015358 | 44.934
20 | 0.1382 | 0.059818 | -0.13819 | -0.066276 | 6.969e-06 | -0.006458 | 0.0043507 | 0.0044282 | 0.0044282 | 0.99916 | -0.015358 | 0.99911 | -0.014976 | 2.0128
21 | -11.9616 | -5.5655 | 11.9682 | 5.5525 | 0.0066467 | -0.01299 | 0.38117 | 0.38094 | 0.38117 | 0.99916 | -0.015358 | 0.99981 | -0.0034882 | 45.2696
22 | 0.26079 | 0.1262 | -0.26078 | -0.1263 | 1.1102e-05 | -9.9014e-05 | 0.0083705 | 0.0083719 | 0.0083719 | 0.99916 | -0.015358 | 0.99911 | -0.015639 | 3.9866
23 | -0.74262 | -0.35852 | 0.74264 | 0.35767 | 2.7309e-05 | -0.00085385 | 0.023807 | 0.023797 | 0.023807 | 0.9999 | 0.000928 | 0.99993 | 0.00061078 | 10.8216
24 | 0.35528 | 0.17092 | -0.35523 | -0.17117 | 5.3711e-05 | -0.00024395 | 0.011382 | 0.011386 | 0.011386 | 0.9999 | 0.000928 | 0.99974 | -9.0954e-05 | 5.4218
25 | -0.74264 | -0.35767 | 0.74268 | 0.35669 | 3.1087e-05 | -0.00097302 | 0.023797 | 0.023784 | 0.023797 | 0.99993 | 0.00061078 | 0.99997 | 0.00025177 | 10.8167
26 | 0.35523 | 0.17117 | -0.35522 | -0.17204 | 6.3571e-06 | -0.00087383 | 0.011386 | 0.011397 | 0.011397 | 0.99974 | -9.0954e-05 | 0.99972 | 6.406e-05 | 5.1804
27 | 0.13819 | 0.066276 | -0.13819 | -0.066928 | 7.1721e-07 | -0.00065156 | 0.0044282 | 0.0044364 | 0.0044364 | 0.99911 | -0.014976 | 0.99911 | -0.014931 | 2.0165
28 | -12.5516 | -5.8309 | 12.5536 | 5.8274 | 0.0020478 | -0.0034743 | 0.3996 | 0.39953 | 0.3996 | 0.99981 | -0.0034882 | 1 | 0 | 47.4581
29 | 0.41103 | 0.199 | -0.41101 | -0.19906 | 1.9023e-05 | -6.1364e-05 | 0.013185 | 0.013186 | 0.013186 | 0.99981 | -0.0034882 | 0.99976 | -0.0037935 | 6.2792
30 | 0.17229 | 0.079307 | -0.17228 | -0.08261 | 5.5828e-06 | -0.0033021 | 0.0054762 | 0.0055168 | 0.0055168 | 0.99981 | -0.0034882 | 0.99978 | -0.0032247 | 2.5076
31 | -0.27931 | -0.13528 | 0.27932 | 0.1352 | 1.1049e-05 | -7.963e-05 | 0.009103 | 0.0091019 | 0.009103 | 0.98417 | -0.37522 | 0.98421 | -0.37495 | 4.3348
32 | -0.27932 | -0.1352 | 0.27933 | 0.13426 | 4.4961e-06 | -0.00094016 | 0.0091019 | 0.0090899 | 0.0091019 | 0.98421 | -0.37495 | 0.98423 | -0.37509 | 4.1372
33 | -0.6732 | -0.32492 | 0.67323 | 0.32373 | 3.3097e-05 | -0.001184 | 0.021924 | 0.021909 | 0.021924 | 0.98423 | -0.37509 | 0.98427 | -0.37552 | 9.9656
34 | 0.39387 | 0.19066 | -0.39387 | -0.19076 | 9.5669e-07 | -0.00010033 | 0.012835 | 0.012836 | 0.012836 | 0.98423 | -0.37509 | 0.98423 | -0.37507 | 5.8345
35 | -0.67323 | -0.32373 | 0.67329 | 0.32178 | 5.4457e-05 | -0.0019519 | 0.021909 | 0.021884 | 0.021909 | 0.98427 | -0.37552 | 0.98435 | -0.37621 | 9.9587
36 | -0.7418 | -0.35496 | 0.74185 | 0.35337 | 5.3858e-05 | -0.0015902 | 0.024117 | 0.024096 | 0.024117 | 0.98435 | -0.37621 | 0.98441 | -0.37682 | 10.9621
37 | -0.74185 | -0.35337 | 0.74198 | 0.34949 | 0.00013103 | -0.003881 | 0.024096 | 0.024047 | 0.024096 | 0.98441 | -0.37682 | 0.98458 | -0.37828 | 10.9529
38 | -0.3209 | -0.15542 | 0.32091 | 0.15435 | 6.4789e-06 | -0.0010697 | 0.010349 | 0.010336 | 0.010349 | 0.99458 | -0.15747 | 0.99459 | -0.15765 | 4.7041
39 | -0.32091 | -0.15435 | 0.32094 | 0.14909 | 3.1596e-05 | -0.0052575 | 0.010336 | 0.01027 | 0.010336 | 0.99459 | -0.15765 | 0.99469 | -0.15846 | 4.698
40 | -8.1306 | -3.7533 | 8.131 | 3.7515 | 0.00035091 | -0.0018242 | 0.25989 | 0.25987 | 0.25989 | 0.99469 | -0.15846 | 0.99474 | -0.15753 | 30.8662
41 | 7.8097 | 3.6042 | -7.8052 | -3.5982 | 0.0044927 | 0.0059869 | 0.24962 | 0.24963 | 0.24963 | 0.99469 | -0.15846 | 0.9939 | -0.18528 | 30.4426
42 | 6.9253 | 3.1909 | -6.9192 | -3.183 | 0.0060675 | 0.0078981 | 0.22147 | 0.22148 | 0.22148 | 0.9939 | -0.18528 | 0.9927 | -0.2262 | 27.0095
43 | 0.75471 | 0.34673 | -0.75467 | -0.34788 | 3.8155e-05 | -0.0011463 | 0.024123 | 0.024137 | 0.024137 | 0.9939 | -0.18528 | 0.99385 | -0.18489 | 10.9714
44 | 6.7313 | 3.092 | -6.7301 | -3.1018 | 0.0012364 | -0.009819 | 0.21541 | 0.21554 | 0.21554 | 0.9927 | -0.2262 | 0.99249 | -0.23017 | 25.5987
45 | 0.75467 | 0.34788 | -0.75452 | -0.35229 | 0.00014739 | -0.0044147 | 0.024137 | 0.024192 | 0.024192 | 0.99385 | -0.18489 | 0.99367 | -0.18335 | 10.9962
46 | -3.6358 | -1.7073 | 3.6362 | 1.705 | 0.00036185 | -0.0023415 | 0.11741 | 0.11737 | 0.11741 | 0.98763 | -0.35906 | 0.98774 | -0.35696 | 27.8875
47 | 3.3295 | 1.559 | -3.3292 | -1.5616 | 0.00033843 | -0.0026717 | 0.10746 | 0.1075 | 0.1075 | 0.98763 | -0.35906 | 0.98751 | -0.36121 | 25.5336
48 | -3.6362 | -1.705 | 3.639 | 1.6868 | 0.0028039 | -0.018216 | 0.11737 | 0.11712 | 0.11737 | 0.98774 | -0.35696 | 0.98864 | -0.34057 | 27.8796
49 | 3.3292 | 1.5616 | -3.3289 | -1.5638 | 0.00027904 | -0.0022008 | 0.1075 | 0.10753 | 0.10753 | 0.98751 | -0.36121 | 0.98741 | -0.36297 | 25.5409
50 | -3.639 | -1.6868 | 3.639 | 1.6858 | 3.4846e-05 | -0.0010048 | 0.11712 | 0.1171 | 0.11712 | 0.98864 | -0.34057 | 0.98865 | -0.34037 | 13.9093
51 | 3.1478 | 1.4761 | -3.1475 | -1.4785 | 0.00026759 | -0.002389 | 0.10164 | 0.10168 | 0.10168 | 0.98741 | -0.36297 | 0.98731 | -0.36476 | 24.1511
52 | 0.28676 | 0.13878 | -0.28675 | -0.13888 | 1.4737e-05 | -0.00010129 | 0.009323 | 0.0093244 | 0.0093244 | 0.98643 | -0.39454 | 0.98638 | -0.39488 | 4.4402
53 | -3.1455 | -1.4759 | 3.1475 | 1.4785 | 0.0020401 | 0.0026047 | 0.10168 | 0.10168 | 0.10168 | 0.98643 | -0.39454 | 0.98731 | -0.36476 | 24.8002
54 | 0.75626 | 0.35944 | -0.75612 | -0.35951 | 0.00014171 | -6.5064e-05 | 0.024504 | 0.024506 | 0.024506 | 0.98643 | -0.39454 | 0.98624 | -0.39587 | 11.6696
55 | 2.1025 | 0.97769 | -2.1004 | -0.98489 | 0.0020729 | -0.0072015 | 0.067855 | 0.067952 | 0.067952 | 0.98643 | -0.39454 | 0.98552 | -0.38664 | 30.8871
56 | 0.67796 | 0.32353 | -0.67791 | -0.32508 | 4.351e-05 | -0.0015512 | 0.021988 | 0.022008 | 0.022008 | 0.98624 | -0.39587 | 0.98618 | -0.39532 | 10.0034
57 | 0.078162 | 0.035974 | -0.078161 | -0.037855 | 6.9238e-07 | -0.0018813 | 0.0025185 | 0.002542 | 0.002542 | 0.98624 | -0.39587 | 0.98623 | -0.39579 | 1.1555
58 | 1.7021 | 0.79402 | -1.7009 | -0.80055 | 0.001203 | -0.0065322 | 0.055015 | 0.055101 | 0.055101 | 0.98552 | -0.38664 | 0.98487 | -0.38093 | 25.0458
59 | 0.3983 | 0.19087 | -0.39828 | -0.19235 | 1.4312e-05 | -0.0014789 | 0.012937 | 0.012956 | 0.012956 | 0.98552 | -0.38664 | 0.98549 | -0.38633 | 5.8891
60 | -4.054 | -1.8867 | 4.0561 | 1.8889 | 0.0020814 | 0.002146 | 0.13057 | 0.13055 | 0.13057 | 0.98865 | -0.34037 | 0.98934 | -0.31663 | 15.9226
61 | -0.3279 | -0.1566 | 0.32791 | 0.15557 | 6.6965e-06 | -0.0010287 | 0.010637 | 0.010624 | 0.010637 | 0.98616 | -0.39515 | 0.98618 | -0.39532 | 4.835
62 | 0.3279 | 0.1566 | -0.32785 | -0.15685 | 4.8658e-05 | -0.00024962 | 0.010637 | 0.01064 | 0.01064 | 0.98616 | -0.39515 | 0.986 | -0.39618 | 5.0669
63 | 0.32785 | 0.15685 | -0.32784 | -0.15878 | 1.2645e-05 | -0.0019337 | 0.01064 | 0.010665 | 0.010665 | 0.986 | -0.39618 | 0.98597 | -0.39585 | 4.8478
64 | 8.2857 | 3.8873 | -8.284 | -3.8963 | 0.0017935 | -0.0090254 | 0.2645 | 0.26463 | 0.26463 | 0.99889 | -0.031413 | 0.99864 | -0.035968 | 31.4285
65 | -8.2857 | -3.8873 | 8.2864 | 3.8838 | 0.00068265 | -0.0034394 | 0.2645 | 0.26445 | 0.2645 | 0.99889 | -0.031413 | 0.99899 | -0.029675 | 31.4129
66 | 8.284 | 3.8963 | -8.2831 | -3.9004 | 0.00082296 | -0.0041359 | 0.26463 | 0.26469 | 0.26469 | 0.99864 | -0.035968 | 0.99852 | -0.038053 | 31.4357
67 | -8.6783 | -4.0736 | 8.6818 | 4.0784 | 0.0035648 | 0.0048242 | 0.27703 | 0.27702 | 0.27703 | 0.99899 | -0.029675 | 0.99955 | -0.010815 | 33.7837
68 | 8.0463 | 3.7857 | -8.0438 | -3.7824 | 0.0024845 | 0.003325 | 0.25708 | 0.25708 | 0.25708 | 0.99852 | -0.038053 | 0.9981 | -0.052215 | 31.3517
69 | -5.5593 | -2.6021 | 5.5614 | 2.5778 | 0.0020517 | -0.024313 | 0.1791 | 0.17878 | 0.1791 | 0.98934 | -0.31663 | 0.98977 | -0.30877 | 21.271
70 | 1.5032 | 0.71321 | -1.5032 | -0.71344 | 3.2858e-05 | -0.00023428 | 0.048548 | 0.048551 | 0.048551 | 0.98934 | -0.31663 | 0.98932 | -0.31644 | 22.0687
71 | 0.078676 | 0.037962 | -0.078676 | -0.038105 | 5.296e-08 | -0.00014283 | 0.0025478 | 0.0025496 | 0.0025496 | 0.98977 | -0.30877 | 0.98977 | -0.30876 | 1.1589
72 | -5.6401 | -2.6157 | 5.642 | 2.6182 | 0.0019608 | 0.0024143 | 0.18133 | 0.18132 | 0.18133 | 0.98977 | -0.30877 | 0.99025 | -0.29264 | 22.113
73 | 1.242 | 0.58695 | -1.2413 | -0.58679 | 0.00073218 | 0.00015998 | 0.040084 | 0.040088 | 0.040088 | 0.98932 | -0.31644 | 0.98871 | -0.32069 | 19.0894
74 | -9.0453 | -4.2545 | 9.0465 | 4.2561 | 0.0012058 | 0.0016408 | 0.28869 | 0.28869 | 0.28869 | 0.99955 | -0.010815 | 0.99974 | -0.0047028 | 35.2057
75 | -9.0465 | -4.2561 | 9.0486 | 4.2478 | 0.0020234 | -0.0082809 | 0.28869 | 0.28856 | 0.28869 | 0.99974 | -0.0047028 | 1 | 0 | 34.2857
76 | 8.0438 | 3.7824 | -8.0427 | -3.7883 | 0.0011034 | -0.0059274 | 0.25708 | 0.25717 | 0.25717 | 0.9981 | -0.052215 | 0.99794 | -0.055094 | 30.5427
77 | 1.0078 | 0.4737 | -1.0077 | -0.47469 | 6.1207e-05 | -0.00099369 | 0.032513 | 0.032525 | 0.032525 | 0.98871 | -0.32069 | 0.98865 | -0.32019 | 14.7843
78 | 1.0077 | 0.47469 | -1.0073 | -0.481 | 0.00038991 | -0.0063091 | 0.032525 | 0.032606 | 0.032606 | 0.98865 | -0.32019 | 0.98829 | -0.31698 | 14.8208
79 | 0.37194 | 0.17667 | -0.37192 | -0.17851 | 1.5326e-05 | -0.0018425 | 0.012027 | 0.012051 | 0.012051 | 0.98829 | -0.31698 | 0.98826 | -0.31663 | 5.4776
80 | 0.63539 | 0.30433 | -0.63532 | -0.30738 | 7.4831e-05 | -0.0030584 | 0.020578 | 0.020617 | 0.020617 | 0.98829 | -0.31698 | 0.98819 | -0.31596 | 9.3716
81 | 0.37192 | 0.17851 | -0.37191 | -0.18012 | 1.3434e-05 | -0.0016091 | 0.012051 | 0.012071 | 0.012071 | 0.98826 | -0.31663 | 0.98822 | -0.31632 | 5.4869
82 | 0.26602 | 0.12852 | -0.26599 | -0.12878 | 3.1439e-05 | -0.00025632 | 0.0086306 | 0.0086341 | 0.0086341 | 0.98819 | -0.31596 | 0.98806 | -0.31675 | 4.1115
83 | 0.26599 | 0.12878 | -0.26599 | -0.12882 | 1.8061e-07 | -4.2253e-05 | 0.0086341 | 0.0086346 | 0.0086346 | 0.98806 | -0.31675 | 0.98806 | -0.31674 | 3.9248
84 | -0.62149 | -0.29671 | 0.62154 | 0.29464 | 4.9e-05 | -0.0020713 | 0.020194 | 0.020167 | 0.020194 | 0.9845 | -0.37762 | 0.98458 | -0.37828 | 9.1789
85 | 0.25655 | 0.11997 | -0.25654 | -0.12241 | 9.7535e-06 | -0.0024397 | 0.0083045 | 0.0083351 | 0.0083351 | 0.9845 | -0.37762 | 0.98447 | -0.37731 | 3.7887
86 | -1.631 | -0.77002 | 1.6313 | 0.7679 | 0.00035842 | -0.0021174 | 0.052881 | 0.052854 | 0.052881 | 0.98458 | -0.37828 | 0.98478 | -0.38008 | 24.037
87 | 0.26746 | 0.12588 | -0.26745 | -0.12905 | 1.3795e-05 | -0.003165 | 0.0086671 | 0.008707 | 0.008707 | 0.98458 | -0.37828 | 0.98453 | -0.37785 | 3.9577
88 | 0.25654 | 0.12241 | -0.25654 | -0.12417 | 7.0887e-06 | -0.0017617 | 0.0083351 | 0.0083575 | 0.0083575 | 0.98447 | -0.37731 | 0.98444 | -0.37707 | 3.7988
89 | -1.7007 | -0.8015 | 1.7009 | 0.80055 | 0.00017617 | -0.00095403 | 0.055113 | 0.055101 | 0.055113 | 0.98478 | -0.38008 | 0.98487 | -0.38093 | 25.0515
90 | 0.26745 | 0.12905 | -0.26745 | -0.12953 | 2.1074e-06 | -0.00048091 | 0.008707 | 0.0087132 | 0.0087132 | 0.98453 | -0.37785 | 0.98452 | -0.37778 | 3.9605
91 | 0.25654 | 0.12417 | -0.25653 | -0.12424 | 8.3509e-06 | -7.2394e-05 | 0.0083575 | 0.0083585 | 0.0083585 | 0.98444 | -0.37707 | 0.98441 | -0.37729 | 3.9802
92 | 0.087742 | 0.041951 | -0.087742 | -0.042495 | 2.5503e-07 | -0.00054441 | 0.0028489 | 0.0028558 | 0.0028558 | 0.98549 | -0.38633 | 0.98549 | -0.38631 | 1.2981
93 | 6.2626 | 2.884 | -6.262 | -2.8897 | 0.00061616 | -0.0057019 | 0.20078 | 0.20086 | 0.20086 | 0.9913 | -0.26705 | 0.99118 | -0.26918 | 23.8549
94 | -6.5262 | -3.0117 | 6.529 | 3.0153 | 0.002813 | 0.0036141 | 0.20931 | 0.2093 | 0.20931 | 0.9913 | -0.26705 | 0.99189 | -0.24698 | 25.5255
95 | 6.262 | 2.8897 | -6.2612 | -2.8973 | 0.00082317 | -0.0076079 | 0.20086 | 0.20096 | 0.20096 | 0.99118 | -0.26918 | 0.99103 | -0.27201 | 23.867
96 | -6.529 | -3.0153 | 6.5303 | 3.0038 | 0.0013566 | -0.011487 | 0.2093 | 0.20915 | 0.2093 | 0.99189 | -0.24698 | 0.99213 | -0.24249 | 24.8579
97 | 6.2612 | 2.8973 | -6.261 | -2.8989 | 0.00017021 | -0.0015718 | 0.20096 | 0.20098 | 0.20098 | 0.99103 | -0.27201 | 0.991 | -0.27259 | 23.8696
98 | -6.5303 | -3.0038 | 6.5321 | 3.006 | 0.0017229 | 0.0022127 | 0.20915 | 0.20914 | 0.20915 | 0.99213 | -0.24249 | 0.99249 | -0.23017 | 25.5059
99 | 5.8489 | 2.6981 | -5.8473 | -2.7152 | 0.0016021 | -0.01713 | 0.18771 | 0.18793 | 0.18793 | 0.99061 | -0.28597 | 0.99029 | -0.29186 | 22.3199
100 | -5.8489 | -2.6981 | 5.8506 | 2.7002 | 0.0016798 | 0.002092 | 0.18771 | 0.1877 | 0.18771 | 0.99061 | -0.28597 | 0.991 | -0.27259 | 22.891
101 | 5.8473 | 2.7152 | -5.8471 | -2.7175 | 0.00021521 | -0.0022967 | 0.18793 | 0.18796 | 0.18796 | 0.99029 | -0.29186 | 0.99025 | -0.29264 | 22.3236
102 | 0.19801 | 0.095753 | -0.198 | -0.095894 | 9.0767e-06 | -0.00014065 | 0.0063973 | 0.0063991 | 0.0063991 | 0.99249 | -0.23017 | 0.99244 | -0.23048 | 3.0472
103 | -0.40615 | -0.19433 | 0.40621 | 0.18839 | 5.7337e-05 | -0.0059323 | 0.013082 | 0.013008 | 0.013082 | 0.99354 | -0.18219 | 0.99367 | -0.18335 | 5.9463
104 | 0.40615 | 0.19433 | -0.40614 | -0.19569 | 1.3314e-05 | -0.0013677 | 0.013082 | 0.013099 | 0.013099 | 0.99354 | -0.18219 | 0.99351 | -0.18191 | 5.9542
105 | 0.10544 | 0.049963 | -0.10544 | -0.051066 | 7.2053e-07 | -0.0011027 | 0.0033897 | 0.0034035 | 0.0034035 | 0.99367 | -0.18335 | 0.99366 | -0.18329 | 1.547
106 | 0.078354 | 0.036942 | -0.078354 | -0.037376 | 1.56e-07 | -0.00043373 | 0.002517 | 0.0025224 | 0.0025224 | 0.99351 | -0.18191 | 0.99351 | -0.1819 | 1.1466
107 | 0.078354 | 0.037376 | -0.078354 | -0.037949 | 2.0696e-07 | -0.0005725 | 0.0025224 | 0.0025296 | 0.0025296 | 0.99351 | -0.1819 | 0.9935 | -0.18187 | 1.1498
108 | -0.17228 | -0.08344 | 0.17228 | 0.08261 | 1.4164e-06 | -0.00082997 | 0.0055272 | 0.0055168 | 0.0055272 | 0.99977 | -0.0031539 | 0.99978 | -0.0032247 | 2.5124
109 | 0.82373 | 0.39532 | -0.82371 | -0.39594 | 2.4254e-05 | -0.00061613 | 0.026376 | 0.026383 | 0.026383 | 1 | 0 | 0.99997 | 0.00025177 | 11.9925
110 | -8.0424 | -3.79 | 8.0427 | 3.7883 | 0.00031692 | -0.0017012 | 0.25719 | 0.25717 | 0.25719 | 0.99789 | -0.05592 | 0.99794 | -0.055094 | 30.5456
111 | 7.7802 | 3.663 | -7.7751 | -3.6562 | 0.0051041 | 0.0067937 | 0.24877 | 0.24877 | 0.24877 | 0.99789 | -0.05592 | 0.99699 | -0.086005 | 30.3382
112 | 7.6159 | 3.5791 | -7.6156 | -3.5809 | 0.00029097 | -0.0017666 | 0.24365 | 0.24368 | 0.24368 | 0.99699 | -0.086005 | 0.99695 | -0.086808 | 28.9404
113 | 7.6156 | 3.5809 | -7.6145 | -3.5877 | 0.0011195 | -0.0067913 | 0.24368 | 0.24377 | 0.24377 | 0.99695 | -0.086808 | 0.99677 | -0.089892 | 28.9518
114 | -0.27982 | -0.13553 | 0.27983 | 0.13522 | 1.4008e-06 | -0.00030208 | 0.0090387 | 0.0090349 | 0.0090387 | 0.99299 | -0.090018 | 0.993 | -0.090062 | 4.1085
115 | -0.27983 | -0.13522 | 0.27984 | 0.13125 | 1.8335e-05 | -0.0039779 | 0.0090349 | 0.0089851 | 0.0090349 | 0.993 | -0.090062 | 0.99306 | -0.090611 | 4.1068
116 | -1.0113 | -0.47982 | 1.0118 | 0.47097 | 0.00053871 | -0.0088496 | 0.032539 | 0.032427 | 0.032539 | 0.99306 | -0.090611 | 0.99355 | -0.094943 | 14.7903
117 | 0.73144 | 0.34857 | -0.73139 | -0.35034 | 5.6242e-05 | -0.0017695 | 0.023554 | 0.023576 | 0.023576 | 0.99306 | -0.090611 | 0.99298 | -0.089961 | 10.7164
118 | -1.2629 | -0.59093 | 1.2636 | 0.58442 | 0.00062117 | -0.0065141 | 0.040513 | 0.040431 | 0.040513 | 0.99355 | -0.094943 | 0.99401 | -0.098848 | 18.4149
119 | 0.25111 | 0.11996 | -0.25111 | -0.12162 | 6.1451e-06 | -0.0016532 | 0.0080859 | 0.0081068 | 0.0081068 | 0.99355 | -0.094943 | 0.99353 | -0.094733 | 3.6849
120 | 0.54958 | 0.26229 | -0.54946 | -0.26248 | 0.00012673 | -0.00018765 | 0.017703 | 0.017707 | 0.017707 | 0.99298 | -0.089961 | 0.99274 | -0.091563 | 8.4318
121 | -1.2636 | -0.58442 | 1.2636 | 0.58423 | 1.7653e-05 | -0.00018562 | 0.040431 | 0.040428 | 0.040431 | 0.99401 | -0.098848 | 0.99402 | -0.098957 | 18.3776
122 | 0.54946 | 0.26248 | -0.54944 | -0.26251 | 2.0292e-05 | -3.0025e-05 | 0.017707 | 0.017707 | 0.017707 | 0.99274 | -0.091563 | 0.9927 | -0.091819 | 8.4321
123 | -7.2514 | -3.4233 | 7.2521 | 3.4184 | 0.00072489 | -0.0049007 | 0.23235 | 0.23229 | 0.23235 | 0.99625 | -0.10288 | 0.99637 | -0.10079 | 27.5955
124 | 6.9173 | 3.2702 | -6.9153 | -3.2848 | 0.0019533 | -0.014654 | 0.22171 | 0.22191 | 0.22191 | 0.99625 | -0.10288 | 0.99592 | -0.10875 | 26.355
125 | 0.33411 | 0.15314 | -0.33406 | -0.16063 | 4.8399e-05 | -0.0074948 | 0.01065 | 0.010742 | 0.010742 | 0.99625 | -0.10288 | 0.99612 | -0.1017 | 4.8828
126 | -7.4817 | -3.5296 | 7.482 | 3.5277 | 0.0002994 | -0.0018858 | 0.23968 | 0.23965 | 0.23968 | 0.99637 | -0.10079 | 0.99642 | -0.099951 | 28.465
127 | 6.9153 | 3.2848 | -6.9149 | -3.2881 | 0.00043605 | -0.0032656 | 0.22191 | 0.22195 | 0.22195 | 0.99592 | -0.10875 | 0.99585 | -0.11005 | 26.3605
128 | 0.33406 | 0.16063 | -0.33406 | -0.16179 | 7.5452e-06 | -0.0011565 | 0.010742 | 0.010757 | 0.010757 | 0.99612 | -0.1017 | 0.9961 | -0.10151 | 4.8895
129 | 6.5355 | 3.1043 | -6.534 | -3.1025 | 0.0014635 | 0.0018793 | 0.20973 | 0.20974 | 0.20974 | 0.99585 | -0.11005 | 0.99554 | -0.12024 | 25.5778
130 | -7.6143 | -3.5888 | 7.6145 | 3.5877 | 0.0001817 | -0.0011014 | 0.24379 | 0.24377 | 0.24379 | 0.99675 | -0.090392 | 0.99677 | -0.089892 | 28.9537
131 | 7.4839 | 3.5256 | -7.4826 | -3.5239 | 0.001287 | 0.0017015 | 0.23959 | 0.2396 | 0.2396 | 0.99675 | -0.090392 | 0.99651 | -0.09827 | 29.219
132 | 7.4826 | 3.5239 | -7.482 | -3.5277 | 0.00060065 | -0.0037852 | 0.2396 | 0.23965 | 0.23965 | 0.99651 | -0.09827 | 0.99642 | -0.099951 | 28.4619
133 | -0.062892 | -0.03046 | 0.062892 | 0.030125 | 7.7768e-08 | -0.00033487 | 0.0020286 | 0.0020244 | 0.0020286 | 0.9944 | -0.14547 | 0.9944 | -0.14548 | 0.9221
134 | 0.22045 | 0.10612 | -0.22045 | -0.10677 | 1.8621e-06 | -0.00065146 | 0.0071027 | 0.0071109 | 0.0071109 | 0.9944 | -0.14548 | 0.99439 | -0.14541 | 3.2322
135 | -0.28335 | -0.13624 | 0.28336 | 0.13418 | 9.7073e-06 | -0.0020638 | 0.0091271 | 0.0091012 | 0.0091271 | 0.9944 | -0.14548 | 0.99443 | -0.14577 | 4.1487
136 | 4.4376 | 2.1342 | -4.4375 | -2.1368 | 0.00013525 | -0.0026079 | 0.14294 | 0.14298 | 0.14298 | 0.99443 | -0.14577 | 0.99439 | -0.14639 | 16.9808
137 | -4.721 | -2.2683 | 4.7216 | 2.2576 | 0.00063647 | -0.010795 | 0.15204 | 0.1519 | 0.15204 | 0.99443 | -0.14577 | 0.99458 | -0.14301 | 18.0576
138 | 4.4375 | 2.1368 | -4.437 | -2.1381 | 0.00048032 | -0.0013007 | 0.14298 | 0.143 | 0.143 | 0.99439 | -0.14639 | 0.99427 | -0.14762 | 39.5025
139 | -5.1094 | -2.4454 | 5.1098 | 2.44 | 0.0003738 | -0.0053711 | 0.16441 | 0.16434 | 0.16441 | 0.99458 | -0.14301 | 0.99467 | -0.14151 | 19.5259
140 | 3.7745 | 1.8175 | -3.7717 | -1.8158 | 0.0028406 | 0.0016522 | 0.12163 | 0.12163 | 0.12163 | 0.99427 | -0.14762 | 0.99348 | -0.1527 | 57.9204
141 | 0.37933 | 0.18347 | -0.37933 | -0.18361 | 1.1766e-06 | -0.00013862 | 0.012234 | 0.012236 | 0.012236 | 0.99427 | -0.14762 | 0.99427 | -0.1476 | 5.5617
142 | -6.2347 | -2.9813 | 6.2349 | 2.979 | 0.00024502 | -0.0022916 | 0.20057 | 0.20054 | 0.20057 | 0.99467 | -0.14151 | 0.99472 | -0.14071 | 23.8203
143 | 1.1249 | 0.54132 | -1.1249 | -0.54166 | 2.5124e-05 | -0.00033119 | 0.03623 | 0.036234 | 0.036234 | 0.99467 | -0.14151 | 0.99465 | -0.14132 | 16.4701
144 | -0.3224 | -0.15614 | 0.32241 | 0.15441 | 1.0624e-05 | -0.0017301 | 0.010411 | 0.010389 | 0.010411 | 0.99328 | -0.15079 | 0.99331 | -0.15108 | 4.7322
145 | -0.32241 | -0.15441 | 0.32242 | 0.1528 | 9.8558e-06 | -0.0016116 | 0.010389 | 0.010369 | 0.010389 | 0.99331 | -0.15108 | 0.99334 | -0.15133 | 4.7223
146 | 1.2204 | 0.5872 | -1.2202 | -0.58937 | 0.00019553 | -0.0021676 | 0.039358 | 0.039386 | 0.039386 | 0.99334 | -0.15133 | 0.99319 | -0.14995 | 17.9027
147 | -1.5428 | -0.74 | 1.5431 | 0.73831 | 0.00024723 | -0.0016921 | 0.049727 | 0.049704 | 0.049727 | 0.99334 | -0.15133 | 0.99348 | -0.1527 | 22.603
148 | 1.6258 | 0.78554 | -1.6255 | -0.78727 | 0.00028234 | -0.0017258 | 0.052465 | 0.052488 | 0.052488 | 0.99348 | -0.1527 | 0.99332 | -0.15119 | 23.8583
149 | 0.24569 | 0.11889 | -0.24569 | -0.11899 | 3.7872e-07 | -0.0001065 | 0.0079245 | 0.0079259 | 0.0079259 | 0.99427 | -0.1476 | 0.99427 | -0.14758 | 3.6027
150 | -0.22773 | -0.1103 | 0.22774 | 0.11023 | 5.2933e-06 | -6.1346e-05 | 0.0073554 | 0.0073546 | 0.0073554 | 0.99308 | -0.14935 | 0.99311 | -0.14919 | 3.5026
151 | -0.97391 | -0.47162 | 0.974 | 0.47013 | 8.5333e-05 | -0.0014971 | 0.031454 | 0.031435 | 0.031454 | 0.99311 | -0.14919 | 0.99319 | -0.14995 | 14.2974
152 | 6.534 | 3.1025 | -6.5324 | -3.1162 | 0.0016196 | -0.01373 | 0.20974 | 0.20993 | 0.20993 | 0.99554 | -0.12024 | 0.99525 | -0.12536 | 24.932
153 | 6.5324 | 3.1162 | -6.532 | -3.1157 | 0.00034963 | 0.00044912 | 0.20993 | 0.20993 | 0.20993 | 0.99525 | -0.12536 | 0.99518 | -0.12779 | 25.601
154 | 0.12183 | 0.05779 | -0.12183 | -0.059005 | 1.064e-06 | -0.0012146 | 0.0039212 | 0.0039364 | 0.0039364 | 0.9927 | -0.091819 | 0.9927 | -0.091745 | 1.7893
155 | 0.26905 | 0.12793 | -0.26904 | -0.12804 | 1.3394e-05 | -0.00010942 | 0.0086632 | 0.0086647 | 0.0086647 | 0.9927 | -0.091819 | 0.99265 | -0.09217 | 4.1261
156 | 6.31 | 3.0082 | -6.3086 | -3.0064 | 0.0014059 | 0.0017896 | 0.20277 | 0.20277 | 0.20277 | 0.99518 | -0.12779 | 0.99488 | -0.13789 | 24.7286
157 | 0.18704 | 0.088325 | -0.18704 | -0.090587 | 4.6697e-06 | -0.0022621 | 0.0060154 | 0.0060438 | 0.0060438 | 0.99265 | -0.09217 | 0.99263 | -0.091958 | 2.7472
158 | 6.3086 | 3.0064 | -6.3077 | -3.0139 | 0.00081781 | -0.007463 | 0.20277 | 0.20288 | 0.20288 | 0.99488 | -0.13789 | 0.99472 | -0.14056 | 24.0946
159 | 6.2349 | 2.9786 | -6.2349 | -2.979 | 4.5676e-05 | -0.00042729 | 0.20053 | 0.20054 | 0.20054 | 0.99472 | -0.14056 | 0.99472 | -0.14071 | 23.8165
160 | 1.1249 | 0.54166 | -1.1248 | -0.54276 | 8.3999e-05 | -0.0011066 | 0.036234 | 0.036248 | 0.036248 | 0.99465 | -0.14132 | 0.99458 | -0.14068 | 16.4765
161 | -0.12126 | -0.05873 | 0.12126 | 0.056744 | 1.707e-06 | -0.0019867 | 0.0039108 | 0.003886 | 0.0039108 | 0.99457 | -0.14056 | 0.99458 | -0.14068 | 1.7776

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 22.4399 | 10.481

## res_load
| p_mw | q_mvar
0 | 0.18809 | 0.091098
1 | 0.27819 | 0.13473
2 | 0.41543 | 0.2012
3 | 0.22863 | 0.11073
4 | 0.32849 | 0.15909
5 | 0.1031 | 0.049932
6 | 0.38734 | 0.1876
7 | 0.35522 | 0.17204
8 | 0.26078 | 0.1263
9 | 0.27931 | 0.13528
10 | 0.39387 | 0.19076
11 | 0.068511 | 0.033181
12 | 0.3209 | 0.15542
13 | 0.12519 | 0.060632
14 | 0.1879 | 0.091005
15 | 0.40373 | 0.19553
16 | 0.3063 | 0.14835
17 | 0.18113 | 0.087727
18 | 0.28675 | 0.13888
19 | 0.41499 | 0.20099
20 | 0.35001 | 0.16952
21 | 0.39182 | 0.18977
22 | 0.23684 | 0.11471
23 | 0.32784 | 0.15878
24 | 0.26117 | 0.12649
25 | 0.36353 | 0.17606
26 | 0.23351 | 0.11309
27 | 0.3693 | 0.17886
28 | 0.37191 | 0.18012
29 | 0.36493 | 0.17675
30 | 0.06938 | 0.033602
31 | 0.26745 | 0.12953
32 | 0.25653 | 0.12424
33 | 0.31054 | 0.1504
34 | 0.087742 | 0.042495
35 | 0.078161 | 0.037855
36 | 0.26357 | 0.12766
37 | 0.41036 | 0.19875
38 | 0.198 | 0.095894
39 | 0.26599 | 0.12882
40 | 0.20511 | 0.099339
41 | 0.32778 | 0.15875
42 | 0.10544 | 0.051066
43 | 0.13977 | 0.067696
44 | 0.078676 | 0.038105
45 | 0.17228 | 0.08344
46 | 0.41101 | 0.19906
47 | 0.13819 | 0.066928
48 | 0.08103 | 0.039245
49 | 0.26222 | 0.127
50 | 0.15917 | 0.07709
51 | 0.27982 | 0.13553
52 | 0.1818 | 0.088052
53 | 0.25111 | 0.12162
54 | 0.28648 | 0.13875
55 | 0.22958 | 0.11119
56 | 0.37942 | 0.18376
57 | 0.13042 | 0.063165
58 | 0.062892 | 0.03046
59 | 0.22045 | 0.10677
60 | 0.3878 | 0.18782
61 | 0.28313 | 0.13713
62 | 0.3224 | 0.15614
63 | 0.60285 | 0.29197
64 | 0.13364 | 0.064725
65 | 0.22773 | 0.1103
66 | 0.74617 | 0.36139
67 | 0.2462 | 0.11924
68 | 0.24569 | 0.11899
69 | 0.15856 | 0.076792
70 | 0.22206 | 0.10755
71 | 1.6255 | 0.78727
72 | 0.12183 | 0.059005
73 | 0.081992 | 0.039711
74 | 0.072802 | 0.03526
75 | 0.33406 | 0.16179
76 | 0.078354 | 0.037949
77 | 0.12126 | 0.05873
78 | 1.0035 | 0.48602
79 | 0.18704 | 0.090587

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1