## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_584_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_584_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_584_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_584_0_node_6 | 20 | n |  | TRUE
4 | bus_MV_584_0_node_7 | 20 | n |  | TRUE
5 | bus_MV_584_0_node_120 | 20 | n |  | TRUE
6 | bus_MV_584_0_node_91 | 20 | n |  | TRUE
7 | bus_MV_584_0_node_8 | 20 | n |  | TRUE
8 | bus_MV_584_0_node_110 | 20 | n |  | TRUE
9 | bus_MV_584_0_node_16 | 20 | n |  | TRUE
10 | bus_MV_584_0_node_9 | 20 | n |  | TRUE
11 | bus_MV_584_0_node_12 | 20 | n |  | TRUE
12 | bus_MV_584_0_node_33 | 20 | n |  | TRUE
13 | bus_MV_584_0_node_10 | 20 | n |  | TRUE
14 | bus_MV_584_0_node_75 | 20 | n |  | TRUE
15 | bus_MV_584_0_node_112 | 20 | n |  | TRUE
16 | bus_MV_584_0_node_11 | 20 | n |  | TRUE
17 | bus_MV_584_0_node_106 | 20 | n |  | TRUE
18 | bus_MV_584_0_node_36 | 20 | n |  | TRUE
19 | bus_MV_584_0_node_31 | 20 | n |  | TRUE
20 | bus_MV_584_0_node_5 | 20 | n |  | TRUE
21 | bus_MV_584_0_node_51 | 20 | n |  | TRUE
22 | bus_MV_584_0_node_64 | 20 | n |  | TRUE
23 | bus_MV_584_0_node_65 | 20 | n |  | TRUE
24 | bus_MV_584_0_node_79 | 20 | n |  | TRUE
25 | bus_MV_584_0_node_61 | 20 | n |  | TRUE
26 | bus_MV_584_0_node_80 | 20 | n |  | TRUE
27 | bus_MV_584_0_node_78 | 20 | n |  | TRUE
28 | bus_MV_584_0_node_81 | 20 | n |  | TRUE
29 | bus_MV_584_0_node_95 | 20 | n |  | TRUE
30 | bus_MV_584_0_node_92 | 20 | n |  | TRUE
31 | bus_MV_584_0_node_93 | 20 | n |  | TRUE
32 | bus_MV_584_0_node_94 | 20 | n |  | TRUE
33 | bus_MV_584_0_node_96 | 20 | n |  | TRUE
34 | bus_MV_584_0_node_97 | 20 | n |  | TRUE
35 | bus_MV_584_0_node_100 | 20 | n |  | TRUE
36 | bus_MV_584_0_node_4 | 20 | n |  | TRUE
37 | bus_MV_584_0_node_119 | 20 | n |  | TRUE
38 | bus_MV_584_0_node_114 | 20 | n |  | TRUE
39 | bus_MV_584_0_node_18 | 20 | n |  | TRUE
40 | bus_MV_584_0_node_30 | 20 | n |  | TRUE
41 | bus_MV_584_0_node_39 | 20 | n |  | TRUE
42 | bus_MV_584_0_node_37 | 20 | n |  | TRUE
43 | bus_MV_584_0_node_17 | 20 | n |  | TRUE
44 | bus_MV_584_0_node_38 | 20 | n |  | TRUE
45 | bus_MV_584_0_node_83 | 20 | n |  | TRUE
46 | bus_MV_584_0_node_27 | 20 | n |  | TRUE
47 | bus_MV_584_0_node_56 | 20 | n |  | TRUE
48 | bus_MV_584_0_node_107 | 20 | n |  | TRUE
49 | bus_MV_584_0_node_32 | 20 | n |  | TRUE
50 | bus_MV_584_0_node_118 | 20 | n |  | TRUE
51 | bus_MV_584_0_node_113 | 20 | n |  | TRUE
52 | bus_MV_584_0_node_19 | 20 | n |  | TRUE
53 | bus_MV_584_0_node_34 | 20 | n |  | TRUE
54 | bus_MV_584_0_node_74 | 20 | n |  | TRUE
55 | bus_MV_584_0_node_23 | 20 | n |  | TRUE
56 | bus_MV_584_0_node_13 | 20 | n |  | TRUE
57 | bus_MV_584_0_node_15 | 20 | n |  | TRUE
58 | bus_MV_584_0_node_22 | 20 | n |  | TRUE
59 | bus_MV_584_0_node_14 | 20 | n |  | TRUE
60 | bus_MV_584_0_node_45 | 20 | n |  | TRUE
61 | bus_MV_584_0_node_20 | 20 | n |  | TRUE
62 | bus_MV_584_0_node_21 | 20 | n |  | TRUE
63 | bus_MV_584_0_node_102 | 20 | n |  | TRUE
64 | bus_MV_584_0_node_108 | 20 | n |  | TRUE
65 | bus_MV_584_0_node_41 | 20 | n |  | TRUE
66 | bus_MV_584_0_node_24 | 20 | n |  | TRUE
67 | bus_MV_584_0_node_101 | 20 | n |  | TRUE
68 | bus_MV_584_0_node_111 | 20 | n |  | TRUE
69 | bus_MV_584_0_node_109 | 20 | n |  | TRUE
70 | bus_MV_584_0_node_35 | 20 | n |  | TRUE
71 | bus_MV_584_0_node_67 | 20 | n |  | TRUE
72 | bus_MV_584_0_node_59 | 20 | n |  | TRUE
73 | bus_MV_584_0_node_60 | 20 | n |  | TRUE
74 | bus_MV_584_0_node_62 | 20 | n |  | TRUE
75 | bus_MV_584_0_node_77 | 20 | n |  | TRUE
76 | bus_MV_584_0_node_63 | 20 | n |  | TRUE
77 | bus_MV_584_0_node_71 | 20 | n |  | TRUE
78 | bus_MV_584_0_node_73 | 20 | n |  | TRUE
79 | bus_MV_584_0_node_69 | 20 | n |  | TRUE
80 | bus_MV_584_0_node_72 | 20 | n |  | TRUE
81 | bus_MV_584_0_node_98 | 20 | n |  | TRUE
82 | bus_MV_584_0_node_70 | 20 | n |  | TRUE
83 | bus_MV_584_0_node_104 | 20 | n |  | TRUE
84 | bus_MV_584_0_node_40 | 20 | n |  | TRUE
85 | bus_MV_584_0_node_82 | 20 | n |  | TRUE
86 | bus_MV_584_0_node_49 | 20 | n |  | TRUE
87 | bus_MV_584_0_node_26 | 20 | n |  | TRUE
88 | bus_MV_584_0_node_28 | 20 | n |  | TRUE
89 | bus_MV_584_0_node_84 | 20 | n |  | TRUE
90 | bus_MV_584_0_node_85 | 20 | n |  | TRUE
91 | bus_MV_584_0_node_76 | 20 | n |  | TRUE
92 | bus_MV_584_0_node_57 | 20 | n |  | TRUE
93 | bus_MV_584_0_node_58 | 20 | n |  | TRUE
94 | bus_MV_584_0_node_42 | 20 | n |  | TRUE
95 | bus_MV_584_0_node_44 | 20 | n |  | TRUE
96 | bus_MV_584_0_node_43 | 20 | n |  | TRUE
97 | bus_MV_584_0_node_99 | 20 | n |  | TRUE
98 | bus_MV_584_0_node_50 | 20 | n |  | TRUE
99 | bus_MV_584_0_node_105 | 20 | n |  | TRUE
100 | bus_MV_584_0_node_117 | 20 | n |  | TRUE
101 | bus_MV_584_0_node_103 | 20 | n |  | TRUE
102 | bus_MV_584_0_node_46 | 20 | n |  | TRUE
103 | bus_MV_584_0_node_47 | 20 | n |  | TRUE
104 | bus_MV_584_0_node_48 | 20 | n |  | TRUE
105 | bus_MV_584_0_node_55 | 20 | n |  | TRUE
106 | bus_MV_584_0_node_90 | 20 | n |  | TRUE
107 | bus_MV_584_0_node_89 | 20 | n |  | TRUE
108 | bus_MV_584_0_node_115 | 20 | n |  | TRUE
109 | bus_MV_584_0_node_116 | 20 | n |  | TRUE
110 | bus_MV_584_0_node_86 | 20 | n |  | TRUE
111 | bus_MV_584_0_node_87 | 20 | n |  | TRUE
112 | bus_HV_584_0_node_7 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_584_0_load_0 | 0 | 0.36494 | 0.17675 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_584_0_load_2 | 1 | 0.093746 | 0.045403 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_584_0_load_120 | 5 | 0.27981 | 0.13552 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_584_0_load_91 | 6 | 0.10117 | 0.048997 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_584_0_load_110 | 8 | 0.29598 | 0.14335 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_584_0_load_33 | 12 | 0.16134 | 0.078142 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_584_0_load_75 | 14 | 0.20438 | 0.098987 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_584_0_load_106 | 17 | 0.4123 | 0.19969 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_584_0_load_36 | 18 | 0.28229 | 0.13672 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_584_0_load_31 | 19 | 0.21113 | 0.10225 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_584_0_load_51 | 21 | 0.4099 | 0.19852 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_584_0_load_65 | 23 | 0.092097 | 0.044605 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_584_0_load_61 | 25 | 0.2426 | 0.11749 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_584_0_load_80 | 26 | 0.24644 | 0.11936 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_584_0_load_78 | 27 | 0.23492 | 0.11377 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_584_0_load_92 | 30 | 0.46842 | 0.22687 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_584_0_load_96 | 33 | 0.32069 | 0.15532 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_584_0_load_100 | 35 | 0.61828 | 0.29945 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_584_0_load_119 | 37 | 0.11101 | 0.053762 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_584_0_load_114 | 38 | 0.17783 | 0.086126 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_584_0_load_37 | 42 | 0.24809 | 0.12016 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_584_0_load_83 | 45 | 0.31643 | 0.15326 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_584_0_load_56 | 47 | 0.40517 | 0.19623 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_584_0_load_107 | 48 | 0.26945 | 0.1305 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_584_0_load_118 | 50 | 0.27866 | 0.13496 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_584_0_load_113 | 51 | 0.20384 | 0.098725 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_584_0_load_74 | 54 | 0.30192 | 0.14622 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_584_0_load_13 | 56 | 0.24152 | 0.11697 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_584_0_load_45 | 60 | 0.40102 | 0.19422 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_584_0_load_102 | 63 | 0.094252 | 0.045648 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_584_0_load_108 | 64 | 0.36747 | 0.17797 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_584_0_load_101 | 67 | 0.080492 | 0.038984 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_584_0_load_111 | 68 | 0.34677 | 0.16795 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_584_0_load_109 | 69 | 0.35419 | 0.17154 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_584_0_load_67 | 71 | 0.22595 | 0.10943 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_584_0_load_59 | 72 | 0.3957 | 0.19164 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_584_0_load_77 | 75 | 0.15418 | 0.074672 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_584_0_load_73 | 78 | 0.35811 | 0.17344 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_584_0_load_98 | 81 | 0.20088 | 0.09729 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_584_0_load_104 | 83 | 0.15184 | 0.073539 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_584_0_load_40 | 84 | 0.38031 | 0.18419 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_584_0_load_82 | 85 | 0.29491 | 0.14283 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_584_0_load_26 | 87 | 0.31959 | 0.15479 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_584_0_load_84 | 89 | 1.0808 | 0.52345 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_584_0_load_76 | 91 | 0.22281 | 0.10791 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_584_0_load_99 | 97 | 0.069787 | 0.033799 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_584_0_load_50 | 98 | 0.25992 | 0.12588 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_584_0_load_105 | 99 | 0.92087 | 0.446 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_584_0_load_117 | 100 | 0.25659 | 0.12427 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_584_0_load_103 | 101 | 0.08779 | 0.042519 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_584_0_load_46 | 102 | 0.3619 | 0.17528 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_584_0_load_90 | 106 | 0.076204 | 0.036907 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_584_0_load_89 | 107 | 0.72203 | 0.3497 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_584_0_load_115 | 108 | 0.28223 | 0.13669 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_584_0_load_116 | 109 | 0.34608 | 0.16762 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_584_0_load_87 | 111 | 0.1631 | 0.078994 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_584_0_line_0 |  | 0 | 1 | 0.117 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_584_0_line_1 |  | 1 | 2 | 0.0090877 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_584_0_line_2 |  | 2 | 20 | 0.28834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_584_0_line_3 |  | 2 | 21 | 0.31735 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_584_0_line_4 |  | 3 | 4 | 0.25031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_584_0_line_5 |  | 3 | 5 | 0.030167 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_584_0_line_6 |  | 4 | 6 | 0.031699 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
7 | MV_584_0_line_7 |  | 6 | 18 | 0.10371 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
8 | MV_584_0_line_8 |  | 7 | 8 | 0.006759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_584_0_line_9 |  | 7 | 9 | 0.054717 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
10 | MV_584_0_line_10 |  | 9 | 52 | 0.12244 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
11 | MV_584_0_line_11 |  | 9 | 19 | 0.24455 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
12 | MV_584_0_line_12 |  | 9 | 53 | 0.38116 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
13 | MV_584_0_line_13 |  | 10 | 11 | 0.16586 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_584_0_line_14 |  | 10 | 12 | 0.054724 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_584_0_line_15 |  | 11 | 19 | 0.030528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_584_0_line_16 |  | 13 | 14 | 0.024683 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_584_0_line_17 |  | 13 | 15 | 0.32201 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_584_0_line_18 |  | 14 | 54 | 0.33581 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_584_0_line_19 |  | 15 | 51 | 0.047705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_584_0_line_20 |  | 15 | 55 | 0.16169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_584_0_line_21 |  | 16 | 17 | 0.10579 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_584_0_line_22 |  | 16 | 18 | 0.58605 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_584_0_line_23 |  | 18 | 52 | 0.030963 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
24 | MV_584_0_line_24 |  | 20 | 38 | 0.011843 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_584_0_line_25 |  | 20 | 39 | 0.43471 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
26 | MV_584_0_line_26 |  | 20 | 40 | 0.42404 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
27 | MV_584_0_line_27 |  | 20 | 36 | 0.091528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_584_0_line_28 |  | 22 | 23 | 0.034041 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_584_0_line_29 |  | 22 | 24 | 0.19141 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_584_0_line_30 |  | 23 | 25 | 0.051915 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
31 | MV_584_0_line_31 |  | 24 | 26 | 0.049546 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_584_0_line_32 |  | 24 | 27 | 0.12185 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_584_0_line_33 |  | 25 | 72 | 0.04241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_584_0_line_34 |  | 26 | 28 | 0.025035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_584_0_line_35 |  | 28 | 29 | 0.003136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_584_0_line_36 |  | 29 | 35 | 0.014184 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_584_0_line_37 |  | 29 | 31 | 0.14665 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_584_0_line_38 |  | 30 | 31 | 0.020612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_584_0_line_39 |  | 31 | 32 | 0.027909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_584_0_line_40 |  | 32 | 33 | 0.055978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_584_0_line_41 |  | 32 | 34 | 0.14698 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_584_0_line_42 |  | 34 | 83 | 0.029143 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_584_0_line_43 |  | 36 | 37 | 0.007686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_584_0_line_44 |  | 39 | 41 | 0.34286 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_584_0_line_45 |  | 39 | 42 | 0.005349 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_584_0_line_46 |  | 39 | 43 | 0.070742 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
47 | MV_584_0_line_47 |  | 40 | 44 | 0.47044 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_584_0_line_48 |  | 40 | 45 | 0.00378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_584_0_line_49 |  | 40 | 46 | 0.32047 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_584_0_line_50 |  | 41 | 48 | 0.024674 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_584_0_line_51 |  | 43 | 60 | 0.028281 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_584_0_line_52 |  | 43 | 59 | 0.12508 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
53 | MV_584_0_line_53 |  | 44 | 47 | 0.056663 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_584_0_line_54 |  | 46 | 88 | 0.301 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_584_0_line_55 |  | 46 | 87 | 0.004626 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_584_0_line_56 |  | 47 | 92 | 0.063805 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_584_0_line_57 |  | 49 | 50 | 0.12307 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_584_0_line_58 |  | 49 | 51 | 0.36606 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_584_0_line_59 |  | 52 | 59 | 0.19037 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
60 | MV_584_0_line_60 |  | 53 | 70 | 0.3052 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
61 | MV_584_0_line_61 |  | 54 | 82 | 0.041382 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_584_0_line_62 |  | 55 | 68 | 0.06855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_584_0_line_63 |  | 55 | 58 | 0.40618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_584_0_line_64 |  | 56 | 57 | 0.009992 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_584_0_line_65 |  | 57 | 58 | 0.046097 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_584_0_line_66 |  | 58 | 66 | 0.21123 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_584_0_line_67 |  | 58 | 67 | 0.019741 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_584_0_line_68 |  | 58 | 61 | 0.32784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_584_0_line_69 |  | 61 | 62 | 0.078501 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_584_0_line_70 |  | 61 | 63 | 0.024669 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_584_0_line_71 |  | 62 | 64 | 0.018317 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_584_0_line_72 |  | 62 | 65 | 0.079329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_584_0_line_73 |  | 65 | 84 | 0.029774 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_584_0_line_74 |  | 66 | 69 | 0.009108 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_584_0_line_75 |  | 70 | 71 | 0.006828 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
76 | MV_584_0_line_76 |  | 71 | 79 | 0.004749 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_584_0_line_77 |  | 72 | 73 | 0.017719 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_584_0_line_78 |  | 73 | 74 | 0.17328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_584_0_line_79 |  | 74 | 75 | 0.034738 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_584_0_line_80 |  | 76 | 77 | 0.18561 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_584_0_line_81 |  | 76 | 78 | 0.030494 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_584_0_line_82 |  | 77 | 81 | 0.07611 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_584_0_line_83 |  | 77 | 82 | 0.43516 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_584_0_line_84 |  | 79 | 80 | 0.22838 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
85 | MV_584_0_line_85 |  | 80 | 83 | 0.050173 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_584_0_line_86 |  | 80 | 81 | 0.19516 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
87 | MV_584_0_line_87 |  | 85 | 86 | 0.089791 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_584_0_line_88 |  | 86 | 104 | 0.2259 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_584_0_line_89 |  | 88 | 89 | 0.088241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_584_0_line_90 |  | 89 | 90 | 0.066528 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_584_0_line_91 |  | 89 | 91 | 0.12108 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
92 | MV_584_0_line_92 |  | 90 | 110 | 0.25321 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_584_0_line_93 |  | 91 | 111 | 0.1377 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
94 | MV_584_0_line_94 |  | 92 | 93 | 0.356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_584_0_line_95 |  | 93 | 101 | 0.011318 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_584_0_line_96 |  | 94 | 95 | 0.18823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_584_0_line_97 |  | 94 | 96 | 0.17326 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_584_0_line_98 |  | 94 | 97 | 0.019811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_584_0_line_99 |  | 95 | 99 | 0.034999 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_584_0_line_100 |  | 96 | 98 | 0.034105 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_584_0_line_101 |  | 98 | 100 | 0.26856 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_584_0_line_102 |  | 99 | 101 | 0.068958 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
103 | MV_584_0_line_103 |  | 100 | 104 | 0.055611 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_584_0_line_104 |  | 102 | 103 | 0.026989 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_584_0_line_105 |  | 103 | 104 | 0.23344 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_584_0_line_106 |  | 105 | 106 | 0.20862 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_584_0_line_107 |  | 105 | 107 | 0.37971 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
108 | MV_584_0_line_108 |  | 107 | 109 | 0.62029 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_584_0_line_109 |  | 107 | 110 | 0.047418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_584_0_line_110 |  | 107 | 108 | 0.27832 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_584_0_trafo_7 | 25 MVA 110/20 kV | 112 | 4 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2626088.236 | 1229058.2893
1 | 2626039.6504 | 1229164.7286
2 | 2626031.0914 | 1229167.7832
3 | 2626202.1735 | 1228855.2559
4 | 2626300.3834 | 1228948.9337
5 | 2626173.1438 | 1228863.5889
6 | 2626299.2716 | 1228980.613
7 | 2626478.1434 | 1228889.096
8 | 2626471.3694 | 1228889.3549
9 | 2626486.2514 | 1228943.209
10 | 2626332.6455 | 1228620.6898
11 | 2626410.4875 | 1228679.6475
12 | 2626282.7088 | 1228643.3942
13 | 2626627.5269 | 1228609.0819
14 | 2626611.0011 | 1228590.8527
15 | 2626917.5731 | 1228748.958
16 | 2626016.8595 | 1228567.093
17 | 2625963.9899 | 1228475.463
18 | 2626398.0355 | 1229012.2481
19 | 2626412.2843 | 1228710.1182
20 | 2626191.5388 | 1229244.1544
21 | 2625882.8074 | 1228887.2018
22 | 2625740.809 | 1228130.5658
23 | 2625742.9635 | 1228098.9251
24 | 2625764.203 | 1228320.5363
25 | 2625771.4242 | 1228055.5062
26 | 2625789.881 | 1228362.9095
27 | 2625645.9196 | 1228349.8105
28 | 2625802.8554 | 1228384.3196
29 | 2625804.4955 | 1228386.995
30 | 2625882.989 | 1228403.4825
31 | 2625862.3771 | 1228403.4113
32 | 2625872.6854 | 1228378.0074
33 | 2625876.4183 | 1228326.237
34 | 2625966.7839 | 1228302.0488
35 | 2625816.7611 | 1228380.0427
36 | 2626163.557 | 1229309.2485
37 | 2626170.0003 | 1229313.4682
38 | 2626197.763 | 1229234.4537
39 | 2626493.1664 | 1229153.0884
40 | 2626293.4274 | 1229381.6748
41 | 2626480.7762 | 1229343.1256
42 | 2626498.1805 | 1229154.9896
43 | 2626445.4841 | 1229148.3515
44 | 2626570.7059 | 1229544.4919
45 | 2626296.6686 | 1229383.6348
46 | 2626258.2459 | 1229612.3366
47 | 2626626.9739 | 1229551.1693
48 | 2626480.8026 | 1229318.4553
49 | 2626896.089 | 1228347.6085
50 | 2626951.5316 | 1228237.7374
51 | 2626945.6052 | 1228710.3059
52 | 2626429.0392 | 1229011.3961
53 | 2626213.5952 | 1228676.8655
54 | 2626476.2149 | 1228283.2787
55 | 2626813.8016 | 1228872.2199
56 | 2626533.6762 | 1229050.3289
57 | 2626538.0907 | 1229059.2984
58 | 2626562.5903 | 1229088.2139
59 | 2626500.9278 | 1229067.0377
60 | 2626420.0729 | 1229160.913
61 | 2626667.1467 | 1229170.0302
62 | 2626734.2675 | 1229188.2641
63 | 2626658.0895 | 1229154.1055
64 | 2626738.7183 | 1229170.4956
65 | 2626727.2659 | 1229249.4251
66 | 2626620.2389 | 1228993.7698
67 | 2626581.7322 | 1229083.6205
68 | 2626864.6806 | 1228911.0391
69 | 2626628.5477 | 1228997.5536
70 | 2626135.9238 | 1228402.4483
71 | 2626136.075 | 1228395.6227
72 | 2625813.8254 | 1228054.65
73 | 2625813.4677 | 1228036.9349
74 | 2625726.417 | 1227887.5024
75 | 2625707.5318 | 1227858.3145
76 | 2626242.4338 | 1227960.5956
77 | 2626185.5653 | 1228104.2428
78 | 2626212.0298 | 1227958.2493
79 | 2626136.1792 | 1228390.8759
80 | 2626017.8313 | 1228278.6907
81 | 2626109.4861 | 1228106.3966
82 | 2626485.5922 | 1228242.9739
83 | 2625976.9283 | 1228274.7288
84 | 2626717.3648 | 1229276.4526
85 | 2627022.8168 | 1229170.4216
86 | 2627085.0662 | 1229235.1321
87 | 2626261.8006 | 1229615.3096
88 | 2626029.5109 | 1229465.2666
89 | 2625967.1343 | 1229402.8517
90 | 2625919.0596 | 1229356.8754
91 | 2625868.5951 | 1229473.2152
92 | 2626690.5414 | 1229558.4692
93 | 2626874.9612 | 1229582.4904
94 | 2626967.0023 | 1229614.9258
95 | 2626958.2585 | 1229541.7977
96 | 2627090.4225 | 1229639.6784
97 | 2626975.668 | 1229598.1584
98 | 2627124.4881 | 1229642.7575
99 | 2626932.1131 | 1229532.5898
100 | 2627200.543 | 1229385.1931
101 | 2626874.9592 | 1229571.1725
102 | 2627373.4431 | 1229330.374
103 | 2627377.4747 | 1229303.6876
104 | 2627187.2222 | 1229331.1997
105 | 2625303.7319 | 1229403.6259
106 | 2625106.5736 | 1229404.0329
107 | 2625677.0745 | 1229334.3786
108 | 2625591.3443 | 1229069.5862
109 | 2625502.5329 | 1228739.1513
110 | 2625688.5328 | 1229380.3914
111 | 2625779.1111 | 1229577.8712
112 | 2626300.3834 | 1228948.9337

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99695 | -0.057776 | 0.36494 | 0.17675
1 | 0.99703 | -0.057256 | 0.093746 | 0.045403
2 | 0.99703 | -0.057306 | 0 | 0
3 | 0.99991 | 0.00077884 | 0 | 0
4 | 1 | 0 | -16.6698 | -7.7598
5 | 0.9999 | 0.00087915 | 0.27981 | 0.13552
6 | 0.99992 | -0.00037393 | 0.10117 | 0.048997
7 | 0.9991 | -0.033568 | 0 | 0
8 | 0.99909 | -0.033544 | 0.29598 | 0.14335
9 | 0.99913 | -0.033371 | 0 | 0
10 | 0.99891 | -0.034267 | 0 | 0
11 | 0.99895 | -0.034553 | 0 | 0
12 | 0.9989 | -0.034164 | 0.16134 | 0.078142
13 | 0.99207 | -0.09337 | 0 | 0
14 | 0.99215 | -0.094017 | 0.20438 | 0.098987
15 | 0.99061 | -0.10371 | 0 | 0
16 | 0.99888 | -0.035329 | 0 | 0
17 | 0.9988 | -0.035858 | 0.4123 | 0.19969
18 | 0.99935 | -0.032381 | 0.28229 | 0.13672
19 | 0.99895 | -0.034602 | 0.21113 | 0.10225
20 | 0.99735 | -0.060243 | 0 | 0
21 | 0.99678 | -0.058893 | 0.4099 | 0.19852
22 | 0.99544 | -0.080699 | 0 | 0
23 | 0.9954 | -0.08035 | 0.092097 | 0.044605
24 | 0.99577 | -0.078514 | 0 | 0
25 | 0.99532 | -0.08088 | 0.2426 | 0.11749
26 | 0.99584 | -0.079157 | 0.24644 | 0.11936
27 | 0.99571 | -0.078864 | 0.23492 | 0.11377
28 | 0.99588 | -0.079556 | 0 | 0
29 | 0.99589 | -0.079605 | 0 | 0
30 | 0.99625 | -0.082891 | 0.46842 | 0.22687
31 | 0.99626 | -0.083007 | 0 | 0
32 | 0.99635 | -0.083807 | 0 | 0
33 | 0.99632 | -0.083593 | 0.32069 | 0.15532
34 | 0.99687 | -0.088553 | 0 | 0
35 | 0.99588 | -0.0795 | 0.61828 | 0.29945
36 | 0.99734 | -0.060128 | 0 | 0
37 | 0.99734 | -0.060118 | 0.11101 | 0.053762
38 | 0.99735 | -0.060218 | 0.17783 | 0.086126
39 | 0.99876 | -0.035009 | 0 | 0
40 | 0.99593 | -0.075914 | 0 | 0
41 | 0.99864 | -0.034004 | 0 | 0
42 | 0.99875 | -0.034994 | 0.24809 | 0.12016
43 | 0.99885 | -0.034616 | 0 | 0
44 | 0.99433 | -0.061976 | 0 | 0
45 | 0.99592 | -0.0759 | 0.31643 | 0.15326
46 | 0.99461 | -0.064063 | 0 | 0
47 | 0.99404 | -0.063986 | 0.40517 | 0.19623
48 | 0.99863 | -0.033924 | 0.26945 | 0.1305
49 | 0.99038 | -0.1047 | 0 | 0
50 | 0.99031 | -0.10513 | 0.27866 | 0.13496
51 | 0.99058 | -0.10344 | 0.20384 | 0.098725
52 | 0.99927 | -0.032733 | 0 | 0
53 | 0.99828 | -0.081136 | 0 | 0
54 | 0.99381 | -0.082396 | 0.30192 | 0.14622
55 | 0.99022 | -0.10038 | 0 | 0
56 | 0.98941 | -0.093341 | 0.24152 | 0.11697
57 | 0.98942 | -0.09337 | 0 | 0
58 | 0.98943 | -0.093504 | 0 | 0
59 | 0.99902 | -0.033881 | 0 | 0
60 | 0.99883 | -0.034481 | 0.40102 | 0.19422
61 | 0.98908 | -0.090326 | 0 | 0
62 | 0.989 | -0.089628 | 0 | 0
63 | 0.98907 | -0.090298 | 0.094252 | 0.045648
64 | 0.98899 | -0.089546 | 0.36747 | 0.17797
65 | 0.98896 | -0.089267 | 0 | 0
66 | 0.98934 | -0.092626 | 0 | 0
67 | 0.98943 | -0.093485 | 0.080492 | 0.038984
68 | 0.99019 | -0.10009 | 0.34677 | 0.16795
69 | 0.98933 | -0.092587 | 0.35419 | 0.17154
70 | 0.99796 | -0.082546 | 0 | 0
71 | 0.99795 | -0.082577 | 0.22595 | 0.10943
72 | 0.99529 | -0.080614 | 0.3957 | 0.19164
73 | 0.99529 | -0.080587 | 0 | 0
74 | 0.99525 | -0.080297 | 0 | 0
75 | 0.99525 | -0.080233 | 0.15418 | 0.074672
76 | 0.99547 | -0.096803 | 0 | 0
77 | 0.99555 | -0.097579 | 0 | 0
78 | 0.99545 | -0.096937 | 0.35811 | 0.17344
79 | 0.99794 | -0.082598 | 0 | 0
80 | 0.99716 | -0.091191 | 0 | 0
81 | 0.99587 | -0.10027 | 0.20088 | 0.09729
82 | 0.99396 | -0.08373 | 0 | 0
83 | 0.99697 | -0.08949 | 0.15184 | 0.073539
84 | 0.98895 | -0.089129 | 0.38031 | 0.18419
85 | 0.99118 | -0.051584 | 0.29491 | 0.14283
86 | 0.99123 | -0.051258 | 0 | 0
87 | 0.99461 | -0.064045 | 0.31959 | 0.15479
88 | 0.99349 | -0.053925 | 0 | 0
89 | 0.99317 | -0.050922 | 1.0808 | 0.52345
90 | 0.99305 | -0.049832 | 0 | 0
91 | 0.99308 | -0.051497 | 0.22281 | 0.10791
92 | 0.99385 | -0.062379 | 0 | 0
93 | 0.99283 | -0.053288 | 0 | 0
94 | 0.99215 | -0.051887 | 0 | 0
95 | 0.99245 | -0.054487 | 0 | 0
96 | 0.99189 | -0.049587 | 0 | 0
97 | 0.99215 | -0.051871 | 0.069787 | 0.033799
98 | 0.99184 | -0.049129 | 0.25992 | 0.12588
99 | 0.99251 | -0.054965 | 0.92087 | 0.446
100 | 0.99136 | -0.052432 | 0.25659 | 0.12427
101 | 0.9928 | -0.052995 | 0.08779 | 0.042519
102 | 0.99119 | -0.051162 | 0.3619 | 0.17528
103 | 0.99121 | -0.051042 | 0 | 0
104 | 0.99132 | -0.052029 | 0 | 0
105 | 0.99244 | -0.045342 | 0 | 0
106 | 0.99242 | -0.045182 | 0.076204 | 0.036907
107 | 0.9925 | -0.044819 | 0.72203 | 0.3497
108 | 0.99234 | -0.045786 | 0.28223 | 0.13669
109 | 0.99208 | -0.047473 | 0.34608 | 0.16762
110 | 0.99258 | -0.045619 | 0 | 0
111 | 0.99303 | -0.051774 | 0.1631 | 0.078994
112 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.36494 | -0.17675 | 0.36497 | 0.17663 | 2.8735e-05 | -0.00012084 | 0.011741 | 0.01174 | 0.011741 | 0.99695 | -0.057776 | 0.99703 | -0.057256 | 5.5911
1 | -0.45872 | -0.22203 | 0.45872 | 0.22182 | 2.6409e-06 | -0.00021491 | 0.014755 | 0.014753 | 0.014755 | 0.99703 | -0.057256 | 0.99703 | -0.057306 | 6.707
2 | -0.86871 | -0.42002 | 0.86901 | 0.41327 | 0.00029953 | -0.006757 | 0.027938 | 0.027852 | 0.027938 | 0.99703 | -0.057306 | 0.99735 | -0.060243 | 12.6991
3 | 0.41 | 0.19821 | -0.4099 | -0.19852 | 9.8335e-05 | -0.00031493 | 0.013185 | 0.01319 | 0.01319 | 0.99703 | -0.057306 | 0.99678 | -0.058893 | 6.2809
4 | -0.27981 | -0.1348 | 0.27984 | 0.12883 | 2.6645e-05 | -0.0059681 | 0.0089666 | 0.0088931 | 0.0089666 | 0.99991 | 0.00077884 | 1 | 0 | 4.0757
5 | 0.27981 | 0.1348 | -0.27981 | -0.13552 | 3.2412e-06 | -0.00071917 | 0.0089666 | 0.0089757 | 0.0089757 | 0.99991 | 0.00077884 | 0.9999 | 0.00087915 | 4.0798
6 | 16.3759 | 7.6204 | -16.3746 | -7.6237 | 0.0013316 | -0.0032332 | 0.52141 | 0.52146 | 0.52146 | 1 | 0 | 0.99992 | -0.00037393 | 40.8667
7 | 16.2734 | 7.5747 | -16.2685 | -7.5616 | 0.0049713 | 0.013082 | 0.51821 | 0.51822 | 0.51822 | 0.99992 | -0.00037393 | 0.99935 | -0.032381 | 40.1719
8 | 0.29598 | 0.14319 | -0.29598 | -0.14335 | 8.1452e-07 | -0.00016084 | 0.0095001 | 0.0095021 | 0.0095021 | 0.9991 | -0.033568 | 0.99909 | -0.033544 | 4.3191
9 | -0.29598 | -0.14319 | 0.29599 | 0.14313 | 8.7978e-06 | -5.9695e-05 | 0.0095001 | 0.0094992 | 0.0095001 | 0.9991 | -0.033568 | 0.99913 | -0.033371 | 4.5238
10 | -7.2671 | -3.3951 | 7.2681 | 3.3803 | 0.0010152 | -0.01479 | 0.23175 | 0.23156 | 0.23175 | 0.99913 | -0.033371 | 0.99927 | -0.032733 | 18.1622
11 | 0.37254 | 0.17416 | -0.37248 | -0.17441 | 6.1531e-05 | -0.00025284 | 0.011882 | 0.011885 | 0.011885 | 0.99913 | -0.033371 | 0.99895 | -0.034602 | 5.6597
12 | 6.5985 | 3.0778 | -6.5955 | -3.0708 | 0.0030112 | 0.0070462 | 0.21037 | 0.21038 | 0.21038 | 0.99913 | -0.033371 | 0.99828 | -0.081136 | 16.3087
13 | -0.16135 | -0.076839 | 0.16135 | 0.072889 | 5.8503e-06 | -0.0039498 | 0.0051645 | 0.0051164 | 0.0051645 | 0.99891 | -0.034267 | 0.99895 | -0.034553 | 2.3475
14 | 0.16135 | 0.076839 | -0.16134 | -0.078142 | 1.9547e-06 | -0.0013032 | 0.0051645 | 0.0051808 | 0.0051808 | 0.99891 | -0.034267 | 0.9989 | -0.034164 | 2.3549
15 | -0.16135 | -0.072889 | 0.16135 | 0.072162 | 1.0651e-06 | -0.00072704 | 0.0051164 | 0.0051078 | 0.0051164 | 0.99895 | -0.034553 | 0.99895 | -0.034602 | 2.3256
16 | -2.3534 | -1.1029 | 2.3536 | 1.1023 | 0.00018844 | -0.00052417 | 0.075626 | 0.075619 | 0.075626 | 0.99207 | -0.09337 | 0.99215 | -0.094017 | 34.3755
17 | 2.3534 | 1.1029 | -2.3501 | -1.1012 | 0.0032815 | 0.0016777 | 0.075626 | 0.075631 | 0.075631 | 0.99207 | -0.09337 | 0.99061 | -0.10371 | 36.0147
18 | -2.558 | -1.2013 | 2.562 | 1.2035 | 0.004045 | 0.0021384 | 0.082226 | 0.082221 | 0.082226 | 0.99215 | -0.094017 | 0.99381 | -0.082396 | 39.1552
19 | 0.48259 | 0.23204 | -0.48257 | -0.23316 | 1.5521e-05 | -0.0011131 | 0.015604 | 0.015619 | 0.015619 | 0.99061 | -0.10371 | 0.99058 | -0.10344 | 7.0993
20 | 1.8675 | 0.86915 | -1.8668 | -0.87271 | 0.00077839 | -0.0035559 | 0.060027 | 0.060074 | 0.060074 | 0.99061 | -0.10371 | 0.99022 | -0.10038 | 27.3064
21 | 0.41234 | 0.19958 | -0.4123 | -0.19969 | 3.304e-05 | -0.0001053 | 0.013239 | 0.013241 | 0.013241 | 0.99888 | -0.035329 | 0.9988 | -0.035858 | 6.305
22 | -0.41234 | -0.19958 | 0.41252 | 0.199 | 0.00018289 | -0.00058384 | 0.013239 | 0.01323 | 0.013239 | 0.99888 | -0.035329 | 0.99935 | -0.032381 | 6.3043
23 | 15.5737 | 7.2259 | -15.5725 | -7.2291 | 0.0011767 | -0.003223 | 0.49593 | 0.49598 | 0.49598 | 0.99935 | -0.032381 | 0.99927 | -0.032733 | 38.8697
24 | 0.17783 | 0.085845 | -0.17783 | -0.086126 | 5.1679e-07 | -0.00028112 | 0.0057154 | 0.005719 | 0.005719 | 0.99735 | -0.060243 | 0.99735 | -0.060218 | 2.5995
25 | -7.3729 | -3.468 | 7.3817 | 3.4596 | 0.008841 | -0.0084257 | 0.23583 | 0.23563 | 0.23583 | 0.99735 | -0.060243 | 0.99876 | -0.035009 | 56.0166
26 | 6.215 | 2.9175 | -6.2069 | -2.9261 | 0.0080954 | -0.0085666 | 0.19872 | 0.1989 | 0.1989 | 0.99735 | -0.060243 | 0.99593 | -0.075914 | 54.9448
27 | 0.11101 | 0.051407 | -0.11101 | -0.05358 | 1.5435e-06 | -0.0021733 | 0.0035408 | 0.0035677 | 0.0035677 | 0.99735 | -0.060243 | 0.99734 | -0.060128 | 1.6217
28 | 0.88469 | 0.42126 | -0.88465 | -0.42206 | 3.6708e-05 | -0.00079444 | 0.028416 | 0.028426 | 0.028426 | 0.99544 | -0.080699 | 0.9954 | -0.08035 | 12.9209
29 | -0.88469 | -0.42126 | 0.88496 | 0.42121 | 0.00027534 | -5.4032e-05 | 0.028416 | 0.028413 | 0.028416 | 0.99544 | -0.080699 | 0.99577 | -0.078514 | 13.5314
30 | 0.79255 | 0.37745 | -0.79249 | -0.37748 | 5.9952e-05 | -2.3851e-05 | 0.025458 | 0.025459 | 0.025459 | 0.9954 | -0.08035 | 0.99532 | -0.08088 | 12.1234
31 | -1.1199 | -0.53485 | 1.12 | 0.5337 | 8.5586e-05 | -0.0011477 | 0.035979 | 0.035964 | 0.035979 | 0.99577 | -0.078514 | 0.99584 | -0.079157 | 16.3539
32 | 0.23493 | 0.11364 | -0.23492 | -0.11377 | 1.243e-05 | -0.00013645 | 0.0075656 | 0.0075674 | 0.0075674 | 0.99577 | -0.078514 | 0.99571 | -0.078864 | 3.6035
33 | 0.5499 | 0.25998 | -0.54988 | -0.26098 | 1.7633e-05 | -0.00099787 | 0.017641 | 0.017654 | 0.017654 | 0.99532 | -0.08088 | 0.99529 | -0.080614 | 8.0245
34 | -1.3664 | -0.65306 | 1.3665 | 0.65248 | 6.4403e-05 | -0.00057368 | 0.043901 | 0.043894 | 0.043901 | 0.99584 | -0.079157 | 0.99588 | -0.079556 | 19.9552
35 | -1.3665 | -0.65248 | 1.3665 | 0.65241 | 8.066e-06 | -7.1868e-05 | 0.043894 | 0.043893 | 0.043894 | 0.99588 | -0.079556 | 0.99589 | -0.079605 | 19.9518
36 | 0.61829 | 0.29911 | -0.61828 | -0.29945 | 7.5073e-06 | -0.00033365 | 0.019909 | 0.019913 | 0.019913 | 0.99589 | -0.079605 | 0.99588 | -0.0795 | 9.0516
37 | -1.9848 | -0.95152 | 1.9856 | 0.94829 | 0.00079642 | -0.0032378 | 0.063802 | 0.063759 | 0.063802 | 0.99589 | -0.079605 | 0.99626 | -0.083007 | 29.001
38 | -0.46842 | -0.22687 | 0.46843 | 0.22638 | 6.256e-06 | -0.0004866 | 0.015081 | 0.015075 | 0.015081 | 0.99625 | -0.082891 | 0.99626 | -0.083007 | 6.8551
39 | -2.454 | -1.1747 | 2.4542 | 1.1741 | 0.00023153 | -0.00059276 | 0.078834 | 0.078825 | 0.078834 | 0.99626 | -0.083007 | 0.99635 | -0.083807 | 35.8334
40 | 0.3207 | 0.15399 | -0.32069 | -0.15532 | 7.9524e-06 | -0.0013244 | 0.010307 | 0.010324 | 0.010324 | 0.99635 | -0.083807 | 0.99632 | -0.083593 | 4.6928
41 | -2.7749 | -1.3281 | 2.7765 | 1.325 | 0.0015581 | -0.0030233 | 0.089133 | 0.089089 | 0.089133 | 0.99635 | -0.083807 | 0.99687 | -0.088553 | 40.5149
42 | -2.7765 | -1.325 | 2.7768 | 1.3244 | 0.00030876 | -0.00059994 | 0.089089 | 0.089081 | 0.089089 | 0.99687 | -0.088553 | 0.99697 | -0.08949 | 40.4951
43 | 0.11101 | 0.05358 | -0.11101 | -0.053762 | 1.3069e-07 | -0.0001825 | 0.0035677 | 0.00357 | 0.00357 | 0.99734 | -0.060128 | 0.99734 | -0.060118 | 1.6227
44 | 0.26948 | 0.12176 | -0.26945 | -0.12991 | 3.3824e-05 | -0.0081547 | 0.0085471 | 0.008647 | 0.008647 | 0.99876 | -0.035009 | 0.99864 | -0.034004 | 3.9304
45 | 0.24809 | 0.12003 | -0.24809 | -0.12016 | 4.5321e-07 | -0.00012726 | 0.0079659 | 0.0079675 | 0.0079675 | 0.99876 | -0.035009 | 0.99875 | -0.034994 | 3.6216
46 | -7.8993 | -3.7014 | 7.9 | 3.6929 | 0.00069454 | -0.0084773 | 0.25214 | 0.25203 | 0.25214 | 0.99876 | -0.035009 | 0.99885 | -0.034616 | 19.76
47 | 2.6673 | 1.2459 | -2.6627 | -1.2557 | 0.0045804 | -0.0097644 | 0.085331 | 0.085468 | 0.085468 | 0.99593 | -0.075914 | 0.99433 | -0.061976 | 38.8493
48 | 0.31643 | 0.15317 | -0.31643 | -0.15326 | 5.2403e-07 | -8.9362e-05 | 0.01019 | 0.010191 | 0.010191 | 0.99593 | -0.075914 | 0.99592 | -0.0759 | 4.6323
49 | 3.2232 | 1.527 | -3.2186 | -1.5332 | 0.0045766 | -0.0062218 | 0.10338 | 0.10347 | 0.10347 | 0.99593 | -0.075914 | 0.99461 | -0.064063 | 47.0339
50 | 0.26945 | 0.12991 | -0.26945 | -0.1305 | 2.465e-06 | -0.00058678 | 0.008647 | 0.0086544 | 0.0086544 | 0.99864 | -0.034004 | 0.99863 | -0.033924 | 3.9338
51 | 0.40102 | 0.19355 | -0.40102 | -0.19422 | 6.257e-06 | -0.00067182 | 0.012869 | 0.012878 | 0.012878 | 0.99885 | -0.034616 | 0.99883 | -0.034481 | 5.8535
52 | -8.301 | -3.8864 | 8.3023 | 3.8715 | 0.0013551 | -0.014922 | 0.2649 | 0.26471 | 0.2649 | 0.99885 | -0.034616 | 0.99902 | -0.033881 | 20.76
53 | 2.6627 | 1.2557 | -2.662 | -1.2553 | 0.00073748 | 0.00039507 | 0.085468 | 0.085469 | 0.085469 | 0.99433 | -0.061976 | 0.99404 | -0.063986 | 40.6997
54 | 2.899 | 1.3785 | -2.8955 | -1.3846 | 0.0034915 | -0.0060659 | 0.09317 | 0.093258 | 0.093258 | 0.99461 | -0.064063 | 0.99349 | -0.053925 | 42.3902
55 | 0.31959 | 0.15468 | -0.31959 | -0.15479 | 6.5593e-07 | -0.00010907 | 0.010305 | 0.010307 | 0.010307 | 0.99461 | -0.064063 | 0.99461 | -0.064045 | 4.6848
56 | 2.2568 | 1.0591 | -2.2563 | -1.0604 | 0.00044656 | -0.0013726 | 0.072396 | 0.072415 | 0.072415 | 0.99404 | -0.063986 | 0.99385 | -0.062379 | 32.9159
57 | 0.27868 | 0.13483 | -0.27866 | -0.13496 | 1.7858e-05 | -0.00013291 | 0.0090236 | 0.0090254 | 0.0090254 | 0.99038 | -0.1047 | 0.99031 | -0.10513 | 4.2978
58 | -0.27868 | -0.13483 | 0.27873 | 0.13443 | 5.3074e-05 | -0.00039548 | 0.0090236 | 0.0090181 | 0.0090236 | 0.99038 | -0.1047 | 0.99058 | -0.10344 | 4.2969
59 | 8.3044 | 3.8488 | -8.3023 | -3.8715 | 0.0020586 | -0.022722 | 0.26442 | 0.26471 | 0.26471 | 0.99927 | -0.032733 | 0.99902 | -0.033881 | 20.745
60 | 6.5955 | 3.0708 | -6.5934 | -3.1078 | 0.0020916 | -0.03703 | 0.21038 | 0.21085 | 0.21085 | 0.99828 | -0.081136 | 0.99796 | -0.082546 | 16.5244
61 | -2.8639 | -1.3497 | 2.8644 | 1.3489 | 0.00046717 | -0.00083742 | 0.091965 | 0.091953 | 0.091965 | 0.99381 | -0.082396 | 0.99396 | -0.08373 | 41.8022
62 | 0.34678 | 0.16635 | -0.34677 | -0.16795 | 1.1526e-05 | -0.0016014 | 0.011212 | 0.011233 | 0.011233 | 0.99022 | -0.10038 | 0.99019 | -0.10009 | 5.1058
63 | 1.52 | 0.70636 | -1.5187 | -0.71548 | 0.0012977 | -0.0091166 | 0.048862 | 0.04898 | 0.04898 | 0.99022 | -0.10038 | 0.98943 | -0.093504 | 22.2636
64 | -0.24152 | -0.11697 | 0.24152 | 0.11674 | 8.1741e-07 | -0.0002333 | 0.0078295 | 0.0078266 | 0.0078295 | 0.98941 | -0.093341 | 0.98942 | -0.09337 | 3.5589
65 | -0.24152 | -0.11674 | 0.24152 | 0.11566 | 3.763e-06 | -0.0010763 | 0.0078266 | 0.0078129 | 0.0078266 | 0.98942 | -0.09337 | 0.98943 | -0.093504 | 3.5575
66 | 0.35423 | 0.1664 | -0.35419 | -0.17133 | 3.6966e-05 | -0.0049259 | 0.011418 | 0.01148 | 0.01148 | 0.98943 | -0.093504 | 0.98934 | -0.092626 | 5.2184
67 | 0.080492 | 0.038523 | -0.080492 | -0.038984 | 1.7903e-07 | -0.00046137 | 0.0026035 | 0.0026094 | 0.0026094 | 0.98943 | -0.093504 | 0.98943 | -0.093485 | 1.1861
68 | 0.84244 | 0.39489 | -0.84212 | -0.40245 | 0.00032363 | -0.0075643 | 0.027145 | 0.027241 | 0.027241 | 0.98943 | -0.093504 | 0.98908 | -0.090326 | 12.3822
69 | 0.74786 | 0.35738 | -0.7478 | -0.3592 | 6.1391e-05 | -0.0018152 | 0.024192 | 0.024215 | 0.024215 | 0.98908 | -0.090326 | 0.989 | -0.089628 | 11.0067
70 | 0.094252 | 0.045072 | -0.094252 | -0.045648 | 3.0694e-07 | -0.00057611 | 0.0030492 | 0.0030565 | 0.0030565 | 0.98908 | -0.090326 | 0.98907 | -0.090298 | 1.3893
71 | 0.36747 | 0.17755 | -0.36747 | -0.17797 | 3.4715e-06 | -0.00042674 | 0.011912 | 0.011918 | 0.011918 | 0.989 | -0.089628 | 0.98899 | -0.089546 | 5.4171
72 | 0.38033 | 0.18165 | -0.38032 | -0.1835 | 1.6059e-05 | -0.0018478 | 0.012303 | 0.012326 | 0.012326 | 0.989 | -0.089628 | 0.98896 | -0.089267 | 5.6027
73 | 0.38032 | 0.1835 | -0.38031 | -0.18419 | 6.0432e-06 | -0.00069348 | 0.012326 | 0.012335 | 0.012335 | 0.98896 | -0.089267 | 0.98895 | -0.089129 | 5.6067
74 | 0.35419 | 0.17133 | -0.35419 | -0.17154 | 1.603e-06 | -0.00021237 | 0.01148 | 0.011483 | 0.011483 | 0.98934 | -0.092626 | 0.98933 | -0.092587 | 5.2196
75 | 6.5934 | 3.1078 | -6.5934 | -3.1086 | 4.6902e-05 | -0.00082811 | 0.21085 | 0.21086 | 0.21086 | 0.99796 | -0.082546 | 0.99795 | -0.082577 | 16.5252
76 | 6.3674 | 2.9992 | -6.3674 | -2.9998 | 3.0416e-05 | -0.0005772 | 0.2036 | 0.20361 | 0.20361 | 0.99795 | -0.082577 | 0.99794 | -0.082598 | 15.9567
77 | 0.15419 | 0.069335 | -0.15419 | -0.069754 | 5.6931e-07 | -0.00041891 | 0.0049034 | 0.0049084 | 0.0049084 | 0.99529 | -0.080614 | 0.99529 | -0.080587 | 2.2311
78 | 0.15419 | 0.069754 | -0.15418 | -0.073851 | 5.6295e-06 | -0.0040965 | 0.0049084 | 0.0049585 | 0.0049585 | 0.99529 | -0.080587 | 0.99525 | -0.080297 | 2.2539
79 | 0.15418 | 0.073851 | -0.15418 | -0.074672 | 1.1426e-06 | -0.00082121 | 0.0049585 | 0.0049689 | 0.0049689 | 0.99525 | -0.080297 | 0.99525 | -0.080233 | 2.2586
80 | -0.35811 | -0.17341 | 0.35815 | 0.16903 | 3.2831e-05 | -0.0043821 | 0.011538 | 0.011483 | 0.011538 | 0.99547 | -0.096803 | 0.99555 | -0.097579 | 5.2447
81 | 0.35811 | 0.17341 | -0.35811 | -0.17344 | 7.2337e-06 | -3.1544e-05 | 0.011538 | 0.011539 | 0.011539 | 0.99547 | -0.096803 | 0.99545 | -0.096937 | 5.4947
82 | -3.2275 | -1.5091 | 3.2285 | 1.5076 | 0.0010842 | -0.00148 | 0.10331 | 0.10329 | 0.10331 | 0.99555 | -0.097579 | 0.99587 | -0.10027 | 46.9588
83 | 2.8693 | 1.34 | -2.8644 | -1.3489 | 0.0049053 | -0.0088263 | 0.091826 | 0.091953 | 0.091953 | 0.99555 | -0.097579 | 0.99396 | -0.08373 | 41.7967
84 | 6.3674 | 2.9998 | -6.3628 | -3.0042 | 0.0045751 | -0.0044718 | 0.20361 | 0.2037 | 0.2037 | 0.99794 | -0.082598 | 0.99716 | -0.091191 | 56.2716
85 | 2.9292 | 1.397 | -2.9286 | -1.398 | 0.00059132 | -0.0010155 | 0.093951 | 0.093966 | 0.093966 | 0.99716 | -0.091191 | 0.99697 | -0.08949 | 42.7116
86 | 3.4336 | 1.6073 | -3.4294 | -1.6049 | 0.0041886 | 0.0023922 | 0.10975 | 0.10976 | 0.10976 | 0.99716 | -0.091191 | 0.99587 | -0.10027 | 52.265
87 | -0.29491 | -0.14283 | 0.29493 | 0.14274 | 1.4569e-05 | -9.6191e-05 | 0.0095435 | 0.0095422 | 0.0095435 | 0.99118 | -0.051584 | 0.99123 | -0.051258 | 4.5445
88 | -0.29493 | -0.14274 | 0.29496 | 0.13745 | 2.7268e-05 | -0.0052918 | 0.0095422 | 0.009476 | 0.0095422 | 0.99123 | -0.051258 | 0.99132 | -0.052029 | 4.3374
89 | 2.8955 | 1.3846 | -2.8945 | -1.3864 | 0.0010248 | -0.0017749 | 0.093258 | 0.093284 | 0.093284 | 0.99349 | -0.053925 | 0.99317 | -0.050922 | 42.402
90 | 1.4278 | 0.67628 | -1.4276 | -0.67779 | 0.00018736 | -0.001511 | 0.04592 | 0.045939 | 0.045939 | 0.99317 | -0.050922 | 0.99305 | -0.049832 | 20.8815
91 | 0.38595 | 0.18662 | -0.38592 | -0.18675 | 3.3501e-05 | -0.00012158 | 0.012461 | 0.012463 | 0.012463 | 0.99317 | -0.050922 | 0.99308 | -0.051497 | 5.9345
92 | 1.4276 | 0.67779 | -1.4269 | -0.68354 | 0.00071454 | -0.0057471 | 0.045939 | 0.046014 | 0.046014 | 0.99305 | -0.049832 | 0.99258 | -0.045619 | 20.9154
93 | 0.16311 | 0.078836 | -0.1631 | -0.078994 | 6.8063e-06 | -0.00015784 | 0.0052662 | 0.0052682 | 0.0052682 | 0.99308 | -0.051497 | 0.99303 | -0.051774 | 2.5087
94 | 2.2563 | 1.0604 | -2.2538 | -1.0681 | 0.0024958 | -0.0076467 | 0.072415 | 0.072519 | 0.072519 | 0.99385 | -0.062379 | 0.99283 | -0.053288 | 32.9632
95 | 2.2538 | 1.0681 | -2.2538 | -1.0683 | 7.9464e-05 | -0.00024279 | 0.072519 | 0.072522 | 0.072522 | 0.99283 | -0.053288 | 0.9928 | -0.052995 | 32.9647
96 | -1.244 | -0.58461 | 1.2444 | 0.58031 | 0.00040138 | -0.0043062 | 0.039994 | 0.039939 | 0.039994 | 0.99215 | -0.051887 | 0.99245 | -0.054487 | 18.1791
97 | 1.1743 | 0.55128 | -1.1739 | -0.55525 | 0.00032995 | -0.0039731 | 0.037744 | 0.037794 | 0.037794 | 0.99215 | -0.051887 | 0.99189 | -0.049587 | 17.1792
98 | 0.069787 | 0.033334 | -0.069787 | -0.033799 | 1.3427e-07 | -0.00046557 | 0.0022503 | 0.0022561 | 0.0022561 | 0.99215 | -0.051887 | 0.99215 | -0.051871 | 1.0255
99 | -1.2444 | -0.58031 | 1.2445 | 0.57951 | 7.4512e-05 | -0.000801 | 0.039939 | 0.039929 | 0.039939 | 0.99245 | -0.054487 | 0.99251 | -0.054965 | 18.1543
100 | 1.1739 | 0.55525 | -1.1739 | -0.55603 | 6.5053e-05 | -0.0007818 | 0.037794 | 0.037804 | 0.037804 | 0.99189 | -0.049587 | 0.99184 | -0.049129 | 17.1837
101 | 0.91394 | 0.43015 | -0.91353 | -0.43021 | 0.00041362 | -5.6166e-05 | 0.029399 | 0.029403 | 0.029403 | 0.99184 | -0.049129 | 0.99136 | -0.052432 | 14.0015
102 | -2.1654 | -1.0255 | 2.166 | 1.0258 | 0.00059665 | 0.0002926 | 0.069687 | 0.069686 | 0.069687 | 0.99251 | -0.054965 | 0.9928 | -0.052995 | 33.1843
103 | 0.65694 | 0.30594 | -0.65691 | -0.30723 | 3.3084e-05 | -0.0012951 | 0.021102 | 0.021118 | 0.021118 | 0.99136 | -0.052432 | 0.99132 | -0.052029 | 9.5992
104 | -0.3619 | -0.17528 | 0.36191 | 0.17525 | 6.595e-06 | -2.7524e-05 | 0.011711 | 0.011711 | 0.011711 | 0.99119 | -0.051162 | 0.99121 | -0.051042 | 5.5768
105 | -0.36191 | -0.17525 | 0.36195 | 0.16979 | 4.2487e-05 | -0.005464 | 0.011711 | 0.011642 | 0.011711 | 0.99121 | -0.051042 | 0.99132 | -0.052029 | 5.3231
106 | 0.076206 | 0.032002 | -0.076204 | -0.036907 | 1.6482e-06 | -0.0049055 | 0.0024041 | 0.0024629 | 0.0024629 | 0.99244 | -0.045342 | 0.99242 | -0.045182 | 1.1195
107 | -0.076206 | -0.032002 | 0.07621 | 0.031558 | 3.9021e-06 | -0.00044406 | 0.0024041 | 0.0023991 | 0.0024041 | 0.99244 | -0.045342 | 0.9925 | -0.044819 | 1.1448
108 | 0.34622 | 0.16697 | -0.34608 | -0.16762 | 0.00013825 | -0.00064253 | 0.01118 | 0.011189 | 0.011189 | 0.9925 | -0.044819 | 0.99208 | -0.047473 | 5.3282
109 | -1.4267 | -0.68462 | 1.4269 | 0.68354 | 0.00013407 | -0.0010756 | 0.046028 | 0.046014 | 0.046028 | 0.9925 | -0.044819 | 0.99258 | -0.045619 | 20.9217
110 | 0.28227 | 0.13639 | -0.28223 | -0.13669 | 4.1247e-05 | -0.00030141 | 0.0091181 | 0.0091223 | 0.0091223 | 0.9925 | -0.044819 | 0.99234 | -0.045786 | 4.3439

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 16.6698 | 7.7598

## res_load
| p_mw | q_mvar
0 | 0.36494 | 0.17675
1 | 0.093746 | 0.045403
2 | 0.27981 | 0.13552
3 | 0.10117 | 0.048997
4 | 0.29598 | 0.14335
5 | 0.16134 | 0.078142
6 | 0.20438 | 0.098987
7 | 0.4123 | 0.19969
8 | 0.28229 | 0.13672
9 | 0.21113 | 0.10225
10 | 0.4099 | 0.19852
11 | 0.092097 | 0.044605
12 | 0.2426 | 0.11749
13 | 0.24644 | 0.11936
14 | 0.23492 | 0.11377
15 | 0.46842 | 0.22687
16 | 0.32069 | 0.15532
17 | 0.61828 | 0.29945
18 | 0.11101 | 0.053762
19 | 0.17783 | 0.086126
20 | 0.24809 | 0.12016
21 | 0.31643 | 0.15326
22 | 0.40517 | 0.19623
23 | 0.26945 | 0.1305
24 | 0.27866 | 0.13496
25 | 0.20384 | 0.098725
26 | 0.30192 | 0.14622
27 | 0.24152 | 0.11697
28 | 0.40102 | 0.19422
29 | 0.094252 | 0.045648
30 | 0.36747 | 0.17797
31 | 0.080492 | 0.038984
32 | 0.34677 | 0.16795
33 | 0.35419 | 0.17154
34 | 0.22595 | 0.10943
35 | 0.3957 | 0.19164
36 | 0.15418 | 0.074672
37 | 0.35811 | 0.17344
38 | 0.20088 | 0.09729
39 | 0.15184 | 0.073539
40 | 0.38031 | 0.18419
41 | 0.29491 | 0.14283
42 | 0.31959 | 0.15479
43 | 1.0808 | 0.52345
44 | 0.22281 | 0.10791
45 | 0.069787 | 0.033799
46 | 0.25992 | 0.12588
47 | 0.92087 | 0.446
48 | 0.25659 | 0.12427
49 | 0.08779 | 0.042519
50 | 0.3619 | 0.17528
51 | 0.076204 | 0.036907
52 | 0.72203 | 0.3497
53 | 0.28223 | 0.13669
54 | 0.34608 | 0.16762
55 | 0.1631 | 0.078994

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1