## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_585_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_585_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_585_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_585_0_node_20 | 20 | n |  | TRUE
4 | bus_MV_585_0_node_2 | 20 | n |  | TRUE
5 | bus_MV_585_0_node_177 | 20 | n |  | TRUE
6 | bus_MV_585_0_node_6 | 20 | n |  | TRUE
7 | bus_MV_585_0_node_5 | 20 | n |  | TRUE
8 | bus_MV_585_0_node_14 | 20 | n |  | TRUE
9 | bus_MV_585_0_node_145 | 20 | n |  | TRUE
10 | bus_MV_585_0_node_4 | 20 | n |  | TRUE
11 | bus_MV_585_0_node_27 | 20 | n |  | TRUE
12 | bus_MV_585_0_node_148 | 20 | n |  | TRUE
13 | bus_MV_585_0_node_165 | 20 | n |  | TRUE
14 | bus_MV_585_0_node_7 | 20 | n |  | TRUE
15 | bus_MV_585_0_node_9 | 20 | n |  | TRUE
16 | bus_MV_585_0_node_8 | 20 | n |  | TRUE
17 | bus_MV_585_0_node_13 | 20 | n |  | TRUE
18 | bus_MV_585_0_node_161 | 20 | n |  | TRUE
19 | bus_MV_585_0_node_26 | 20 | n |  | TRUE
20 | bus_MV_585_0_node_12 | 20 | n |  | TRUE
21 | bus_MV_585_0_node_162 | 20 | n |  | TRUE
22 | bus_MV_585_0_node_10 | 20 | n |  | TRUE
23 | bus_MV_585_0_node_163 | 20 | n |  | TRUE
24 | bus_MV_585_0_node_129 | 20 | n |  | TRUE
25 | bus_MV_585_0_node_128 | 20 | n |  | TRUE
26 | bus_MV_585_0_node_49 | 20 | n |  | TRUE
27 | bus_MV_585_0_node_16 | 20 | n |  | TRUE
28 | bus_MV_585_0_node_181 | 20 | n |  | TRUE
29 | bus_MV_585_0_node_15 | 20 | n |  | TRUE
30 | bus_MV_585_0_node_83 | 20 | n |  | TRUE
31 | bus_MV_585_0_node_146 | 20 | n |  | TRUE
32 | bus_MV_585_0_node_21 | 20 | n |  | TRUE
33 | bus_MV_585_0_node_29 | 20 | n |  | TRUE
34 | bus_MV_585_0_node_17 | 20 | n |  | TRUE
35 | bus_MV_585_0_node_18 | 20 | n |  | TRUE
36 | bus_MV_585_0_node_19 | 20 | n |  | TRUE
37 | bus_MV_585_0_node_192 | 20 | n |  | TRUE
38 | bus_MV_585_0_node_188 | 20 | n |  | TRUE
39 | bus_MV_585_0_node_170 | 20 | n |  | TRUE
40 | bus_MV_585_0_node_48 | 20 | n |  | TRUE
41 | bus_MV_585_0_node_136 | 20 | n |  | TRUE
42 | bus_MV_585_0_node_54 | 20 | n |  | TRUE
43 | bus_MV_585_0_node_142 | 20 | n |  | TRUE
44 | bus_MV_585_0_node_178 | 20 | n |  | TRUE
45 | bus_MV_585_0_node_36 | 20 | n |  | TRUE
46 | bus_MV_585_0_node_173 | 20 | n |  | TRUE
47 | bus_MV_585_0_node_53 | 20 | n |  | TRUE
48 | bus_MV_585_0_node_85 | 20 | n |  | TRUE
49 | bus_MV_585_0_node_82 | 20 | n |  | TRUE
50 | bus_MV_585_0_node_28 | 20 | n |  | TRUE
51 | bus_MV_585_0_node_46 | 20 | n |  | TRUE
52 | bus_MV_585_0_node_101 | 20 | n |  | TRUE
53 | bus_MV_585_0_node_134 | 20 | n |  | TRUE
54 | bus_MV_585_0_node_133 | 20 | n |  | TRUE
55 | bus_MV_585_0_node_23 | 20 | n |  | TRUE
56 | bus_MV_585_0_node_24 | 20 | n |  | TRUE
57 | bus_MV_585_0_node_71 | 20 | n |  | TRUE
58 | bus_MV_585_0_node_25 | 20 | n |  | TRUE
59 | bus_MV_585_0_node_52 | 20 | n |  | TRUE
60 | bus_MV_585_0_node_105 | 20 | n |  | TRUE
61 | bus_MV_585_0_node_70 | 20 | n |  | TRUE
62 | bus_MV_585_0_node_72 | 20 | n |  | TRUE
63 | bus_MV_585_0_node_127 | 20 | n |  | TRUE
64 | bus_MV_585_0_node_171 | 20 | n |  | TRUE
65 | bus_MV_585_0_node_184 | 20 | n |  | TRUE
66 | bus_MV_585_0_node_166 | 20 | n |  | TRUE
67 | bus_MV_585_0_node_167 | 20 | n |  | TRUE
68 | bus_MV_585_0_node_30 | 20 | n |  | TRUE
69 | bus_MV_585_0_node_31 | 20 | n |  | TRUE
70 | bus_MV_585_0_node_33 | 20 | n |  | TRUE
71 | bus_MV_585_0_node_121 | 20 | n |  | TRUE
72 | bus_MV_585_0_node_116 | 20 | n |  | TRUE
73 | bus_MV_585_0_node_42 | 20 | n |  | TRUE
74 | bus_MV_585_0_node_169 | 20 | n |  | TRUE
75 | bus_MV_585_0_node_120 | 20 | n |  | TRUE
76 | bus_MV_585_0_node_117 | 20 | n |  | TRUE
77 | bus_MV_585_0_node_43 | 20 | n |  | TRUE
78 | bus_MV_585_0_node_34 | 20 | n |  | TRUE
79 | bus_MV_585_0_node_37 | 20 | n |  | TRUE
80 | bus_MV_585_0_node_38 | 20 | n |  | TRUE
81 | bus_MV_585_0_node_131 | 20 | n |  | TRUE
82 | bus_MV_585_0_node_40 | 20 | n |  | TRUE
83 | bus_MV_585_0_node_41 | 20 | n |  | TRUE
84 | bus_MV_585_0_node_39 | 20 | n |  | TRUE
85 | bus_MV_585_0_node_130 | 20 | n |  | TRUE
86 | bus_MV_585_0_node_50 | 20 | n |  | TRUE
87 | bus_MV_585_0_node_108 | 20 | n |  | TRUE
88 | bus_MV_585_0_node_44 | 20 | n |  | TRUE
89 | bus_MV_585_0_node_187 | 20 | n |  | TRUE
90 | bus_MV_585_0_node_96 | 20 | n |  | TRUE
91 | bus_MV_585_0_node_97 | 20 | n |  | TRUE
92 | bus_MV_585_0_node_45 | 20 | n |  | TRUE
93 | bus_MV_585_0_node_111 | 20 | n |  | TRUE
94 | bus_MV_585_0_node_112 | 20 | n |  | TRUE
95 | bus_MV_585_0_node_95 | 20 | n |  | TRUE
96 | bus_MV_585_0_node_98 | 20 | n |  | TRUE
97 | bus_MV_585_0_node_94 | 20 | n |  | TRUE
98 | bus_MV_585_0_node_182 | 20 | n |  | TRUE
99 | bus_MV_585_0_node_180 | 20 | n |  | TRUE
100 | bus_MV_585_0_node_99 | 20 | n |  | TRUE
101 | bus_MV_585_0_node_100 | 20 | n |  | TRUE
102 | bus_MV_585_0_node_113 | 20 | n |  | TRUE
103 | bus_MV_585_0_node_114 | 20 | n |  | TRUE
104 | bus_MV_585_0_node_119 | 20 | n |  | TRUE
105 | bus_MV_585_0_node_106 | 20 | n |  | TRUE
106 | bus_MV_585_0_node_107 | 20 | n |  | TRUE
107 | bus_MV_585_0_node_168 | 20 | n |  | TRUE
108 | bus_MV_585_0_node_55 | 20 | n |  | TRUE
109 | bus_MV_585_0_node_56 | 20 | n |  | TRUE
110 | bus_MV_585_0_node_132 | 20 | n |  | TRUE
111 | bus_MV_585_0_node_57 | 20 | n |  | TRUE
112 | bus_MV_585_0_node_58 | 20 | n |  | TRUE
113 | bus_MV_585_0_node_59 | 20 | n |  | TRUE
114 | bus_MV_585_0_node_60 | 20 | n |  | TRUE
115 | bus_MV_585_0_node_191 | 20 | n |  | TRUE
116 | bus_MV_585_0_node_62 | 20 | n |  | TRUE
117 | bus_MV_585_0_node_189 | 20 | n |  | TRUE
118 | bus_MV_585_0_node_61 | 20 | n |  | TRUE
119 | bus_MV_585_0_node_64 | 20 | n |  | TRUE
120 | bus_MV_585_0_node_135 | 20 | n |  | TRUE
121 | bus_MV_585_0_node_185 | 20 | n |  | TRUE
122 | bus_MV_585_0_node_63 | 20 | n |  | TRUE
123 | bus_MV_585_0_node_84 | 20 | n |  | TRUE
124 | bus_MV_585_0_node_152 | 20 | n |  | TRUE
125 | bus_MV_585_0_node_65 | 20 | n |  | TRUE
126 | bus_MV_585_0_node_69 | 20 | n |  | TRUE
127 | bus_MV_585_0_node_66 | 20 | n |  | TRUE
128 | bus_MV_585_0_node_67 | 20 | n |  | TRUE
129 | bus_MV_585_0_node_68 | 20 | n |  | TRUE
130 | bus_MV_585_0_node_73 | 20 | n |  | TRUE
131 | bus_MV_585_0_node_74 | 20 | n |  | TRUE
132 | bus_MV_585_0_node_183 | 20 | n |  | TRUE
133 | bus_MV_585_0_node_78 | 20 | n |  | TRUE
134 | bus_MV_585_0_node_81 | 20 | n |  | TRUE
135 | bus_MV_585_0_node_76 | 20 | n |  | TRUE
136 | bus_MV_585_0_node_147 | 20 | n |  | TRUE
137 | bus_MV_585_0_node_176 | 20 | n |  | TRUE
138 | bus_MV_585_0_node_75 | 20 | n |  | TRUE
139 | bus_MV_585_0_node_77 | 20 | n |  | TRUE
140 | bus_MV_585_0_node_79 | 20 | n |  | TRUE
141 | bus_MV_585_0_node_80 | 20 | n |  | TRUE
142 | bus_MV_585_0_node_144 | 20 | n |  | TRUE
143 | bus_MV_585_0_node_143 | 20 | n |  | TRUE
144 | bus_MV_585_0_node_153 | 20 | n |  | TRUE
145 | bus_MV_585_0_node_91 | 20 | n |  | TRUE
146 | bus_MV_585_0_node_174 | 20 | n |  | TRUE
147 | bus_MV_585_0_node_175 | 20 | n |  | TRUE
148 | bus_MV_585_0_node_149 | 20 | n |  | TRUE
149 | bus_MV_585_0_node_154 | 20 | n |  | TRUE
150 | bus_MV_585_0_node_164 | 20 | n |  | TRUE
151 | bus_MV_585_0_node_86 | 20 | n |  | TRUE
152 | bus_MV_585_0_node_87 | 20 | n |  | TRUE
153 | bus_MV_585_0_node_88 | 20 | n |  | TRUE
154 | bus_MV_585_0_node_89 | 20 | n |  | TRUE
155 | bus_MV_585_0_node_150 | 20 | n |  | TRUE
156 | bus_MV_585_0_node_93 | 20 | n |  | TRUE
157 | bus_MV_585_0_node_155 | 20 | n |  | TRUE
158 | bus_MV_585_0_node_90 | 20 | n |  | TRUE
159 | bus_MV_585_0_node_92 | 20 | n |  | TRUE
160 | bus_MV_585_0_node_156 | 20 | n |  | TRUE
161 | bus_MV_585_0_node_109 | 20 | n |  | TRUE
162 | bus_MV_585_0_node_110 | 20 | n |  | TRUE
163 | bus_MV_585_0_node_151 | 20 | n |  | TRUE
164 | bus_MV_585_0_node_103 | 20 | n |  | TRUE
165 | bus_MV_585_0_node_186 | 20 | n |  | TRUE
166 | bus_MV_585_0_node_126 | 20 | n |  | TRUE
167 | bus_MV_585_0_node_125 | 20 | n |  | TRUE
168 | bus_MV_585_0_node_102 | 20 | n |  | TRUE
169 | bus_MV_585_0_node_115 | 20 | n |  | TRUE
170 | bus_MV_585_0_node_179 | 20 | n |  | TRUE
171 | bus_MV_585_0_node_118 | 20 | n |  | TRUE
172 | bus_MV_585_0_node_122 | 20 | n |  | TRUE
173 | bus_MV_585_0_node_190 | 20 | n |  | TRUE
174 | bus_MV_585_0_node_141 | 20 | n |  | TRUE
175 | bus_MV_585_0_node_137 | 20 | n |  | TRUE
176 | bus_MV_585_0_node_138 | 20 | n |  | TRUE
177 | bus_MV_585_0_node_139 | 20 | n |  | TRUE
178 | bus_MV_585_0_node_140 | 20 | n |  | TRUE
179 | bus_MV_585_0_node_172 | 20 | n |  | TRUE
180 | bus_MV_585_0_node_159 | 20 | n |  | TRUE
181 | bus_MV_585_0_node_157 | 20 | n |  | TRUE
182 | bus_MV_585_0_node_158 | 20 | n |  | TRUE
183 | bus_MV_585_0_node_160 | 20 | n |  | TRUE
184 | bus_HV_585_0_node_181 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_585_0_load_0 | 0 | 0.34771 | 0.16841 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_585_0_load_177 | 5 | 0.3682 | 0.17833 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_585_0_load_145 | 9 | 0.086941 | 0.042107 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_585_0_load_27 | 11 | 0.31231 | 0.15126 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_585_0_load_148 | 12 | 0.074206 | 0.035939 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_585_0_load_165 | 13 | 0.13541 | 0.065584 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_585_0_load_161 | 18 | 0.091419 | 0.044276 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_585_0_load_26 | 19 | 0.38389 | 0.18593 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_585_0_load_162 | 21 | 0.10178 | 0.049295 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_585_0_load_163 | 23 | 0.078262 | 0.037904 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_585_0_load_128 | 25 | 0.079404 | 0.038457 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_585_0_load_49 | 26 | 0.3988 | 0.19315 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_585_0_load_181 | 28 | 0.26978 | 0.13066 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_585_0_load_146 | 31 | 0.13727 | 0.066482 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_585_0_load_29 | 33 | 0.079758 | 0.038629 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_585_0_load_192 | 37 | 0.38152 | 0.18478 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_585_0_load_188 | 38 | 0.31409 | 0.15212 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_585_0_load_170 | 39 | 0.38325 | 0.18562 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_585_0_load_48 | 40 | 0.077145 | 0.037363 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_585_0_load_136 | 41 | 0.13229 | 0.064069 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_585_0_load_54 | 42 | 0.33002 | 0.15984 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_585_0_load_142 | 43 | 0.095545 | 0.046274 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_585_0_load_178 | 44 | 0.18602 | 0.090092 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_585_0_load_173 | 46 | 0.40985 | 0.1985 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_585_0_load_85 | 48 | 0.11122 | 0.053867 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_585_0_load_82 | 49 | 0.31057 | 0.15042 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_585_0_load_28 | 50 | 0.27961 | 0.13542 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_585_0_load_46 | 51 | 0.2502 | 0.12118 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_585_0_load_134 | 53 | 0.085073 | 0.041203 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_585_0_load_133 | 54 | 0.55931 | 0.27089 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_585_0_load_23 | 55 | 0.35439 | 0.17164 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_585_0_load_105 | 60 | 0.34125 | 0.16527 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_585_0_load_127 | 63 | 0.48922 | 0.23694 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_585_0_load_171 | 64 | 0.31489 | 0.15251 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_585_0_load_184 | 65 | 0.6215 | 0.30101 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_585_0_load_166 | 66 | 0.070766 | 0.034274 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_585_0_load_30 | 68 | 0.38526 | 0.18659 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_585_0_load_121 | 71 | 0.32589 | 0.15784 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_585_0_load_42 | 73 | 0.22939 | 0.1111 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_585_0_load_169 | 74 | 0.21079 | 0.10209 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_585_0_load_120 | 75 | 0.12687 | 0.061444 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_585_0_load_34 | 78 | 0.34595 | 0.16755 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_585_0_load_131 | 81 | 0.071149 | 0.034459 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_585_0_load_39 | 84 | 0.39804 | 0.19278 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_585_0_load_130 | 85 | 0.068369 | 0.033112 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_585_0_load_50 | 86 | 0.28997 | 0.14044 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_585_0_load_187 | 89 | 0.39105 | 0.1894 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_585_0_load_111 | 93 | 0.24644 | 0.11936 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_585_0_load_94 | 97 | 0.32485 | 0.15733 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_585_0_load_182 | 98 | 0.38578 | 0.18684 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_585_0_load_180 | 99 | 0.33754 | 0.16348 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_585_0_load_100 | 101 | 0.36034 | 0.17452 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_585_0_load_119 | 104 | 0.32784 | 0.15878 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_585_0_load_168 | 107 | 0.19764 | 0.095721 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_585_0_load_55 | 108 | 0.086286 | 0.04179 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_585_0_load_56 | 109 | 0.19152 | 0.092755 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_585_0_load_132 | 110 | 0.11008 | 0.053315 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_585_0_load_57 | 111 | 0.22109 | 0.10708 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_585_0_load_191 | 115 | 0.26556 | 0.12862 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_585_0_load_189 | 117 | 0.28933 | 0.14013 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_585_0_load_64 | 119 | 0.22294 | 0.10797 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_585_0_load_135 | 120 | 0.15724 | 0.076156 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_585_0_load_185 | 121 | 0.3969 | 0.19223 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_585_0_load_69 | 126 | 0.29754 | 0.14411 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_585_0_load_73 | 130 | 0.28325 | 0.13719 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_585_0_load_74 | 131 | 0.40343 | 0.19539 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_585_0_load_183 | 132 | 0.41226 | 0.19967 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_585_0_load_81 | 134 | 0.22221 | 0.10762 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_585_0_load_147 | 136 | 0.099195 | 0.048042 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_585_0_load_75 | 138 | 0.35431 | 0.1716 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_585_0_load_77 | 139 | 0.076733 | 0.037163 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_585_0_load_143 | 143 | 0.16427 | 0.079558 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_585_0_load_175 | 147 | 0.25344 | 0.12275 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_585_0_load_149 | 148 | 0.070077 | 0.03394 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_585_0_load_154 | 149 | 0.16977 | 0.082221 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_585_0_load_164 | 150 | 0.07407 | 0.035874 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_585_0_load_86 | 151 | 0.29924 | 0.14493 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_585_0_load_150 | 155 | 0.068728 | 0.033287 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_585_0_load_155 | 157 | 0.14523 | 0.070337 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_585_0_load_156 | 160 | 0.40363 | 0.19549 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_585_0_load_109 | 161 | 0.39182 | 0.18977 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_585_0_load_110 | 162 | 0.39199 | 0.18985 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_585_0_load_186 | 165 | 0.19964 | 0.096692 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_585_0_load_125 | 167 | 0.062669 | 0.030352 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_585_0_load_102 | 168 | 0.089888 | 0.043535 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_585_0_load_179 | 170 | 0.23299 | 0.11284 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_585_0_load_122 | 172 | 0.22302 | 0.10801 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_585_0_load_190 | 173 | 0.16649 | 0.080632 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_585_0_load_137 | 175 | 0.096631 | 0.046801 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_585_0_load_172 | 179 | 0.18763 | 0.090874 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_585_0_load_157 | 181 | 0.15625 | 0.075676 | 0 | 0 |  | 1 | TRUE | wye
91 | MV_585_0_load_160 | 183 | 0.40652 | 0.19689 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_585_0_line_0 |  | 0 | 1 | 0.01581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_585_0_line_1 |  | 1 | 2 | 0.37623 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
2 | MV_585_0_line_2 |  | 1 | 3 | 0.21909 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
3 | MV_585_0_line_3 |  | 2 | 7 | 0.17609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_585_0_line_4 |  | 2 | 8 | 0.23416 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
5 | MV_585_0_line_5 |  | 2 | 9 | 0.028524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_585_0_line_6 |  | 3 | 40 | 0.037697 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_585_0_line_7 |  | 3 | 22 | 0.10185 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
8 | MV_585_0_line_8 |  | 3 | 35 | 0.20521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_585_0_line_9 |  | 4 | 5 | 0.007034 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_585_0_line_10 |  | 4 | 6 | 0.055391 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_585_0_line_11 |  | 6 | 13 | 0.034131 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_585_0_line_12 |  | 6 | 7 | 0.15124 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_585_0_line_13 |  | 7 | 12 | 0.039961 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_585_0_line_14 |  | 7 | 10 | 0.32127 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_585_0_line_15 |  | 8 | 27 | 0.1924 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
16 | MV_585_0_line_16 |  | 8 | 28 | 0.020557 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
17 | MV_585_0_line_17 |  | 10 | 11 | 0.026764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_585_0_line_18 |  | 13 | 42 | 0.041384 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_585_0_line_19 |  | 13 | 43 | 0.057909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_585_0_line_20 |  | 14 | 15 | 0.085672 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
21 | MV_585_0_line_21 |  | 14 | 16 | 0.13526 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_585_0_line_22 |  | 14 | 17 | 0.18067 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
23 | MV_585_0_line_23 |  | 14 | 18 | 0.033691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_585_0_line_24 |  | 15 | 20 | 0.074157 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
25 | MV_585_0_line_25 |  | 15 | 21 | 0.032544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_585_0_line_26 |  | 16 | 19 | 0.013279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_585_0_line_27 |  | 17 | 26 | 0.017637 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_585_0_line_28 |  | 17 | 22 | 0.11226 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
29 | MV_585_0_line_29 |  | 20 | 24 | 0.23478 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_585_0_line_30 |  | 20 | 25 | 0.020795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_585_0_line_31 |  | 22 | 23 | 0.028303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_585_0_line_32 |  | 24 | 46 | 0.030056 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_585_0_line_33 |  | 25 | 47 | 0.026813 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_585_0_line_34 |  | 27 | 32 | 0.102 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
35 | MV_585_0_line_35 |  | 27 | 33 | 0.046219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_585_0_line_36 |  | 27 | 29 | 0.12347 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
37 | MV_585_0_line_37 |  | 29 | 30 | 0.086082 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
38 | MV_585_0_line_38 |  | 29 | 31 | 0.015225 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_585_0_line_39 |  | 30 | 48 | 0.03483 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_585_0_line_40 |  | 30 | 49 | 0.026029 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
41 | MV_585_0_line_41 |  | 32 | 41 | 0.0009298 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
42 | MV_585_0_line_42 |  | 33 | 50 | 0.039583 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_585_0_line_43 |  | 34 | 35 | 0.46238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_585_0_line_44 |  | 34 | 36 | 0.4681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_585_0_line_45 |  | 34 | 37 | 0.004818 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_585_0_line_46 |  | 35 | 38 | 0.014552 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_585_0_line_47 |  | 36 | 39 | 0.017849 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
48 | MV_585_0_line_48 |  | 40 | 51 | 0.034304 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
49 | MV_585_0_line_49 |  | 41 | 52 | 0.028118 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
50 | MV_585_0_line_50 |  | 42 | 108 | 0.02798 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_585_0_line_51 |  | 43 | 174 | 0.028791 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_585_0_line_52 |  | 44 | 45 | 0.098051 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_585_0_line_53 |  | 45 | 80 | 0.02928 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_585_0_line_54 |  | 45 | 78 | 0.059015 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_585_0_line_55 |  | 47 | 59 | 0.088307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_585_0_line_56 |  | 48 | 112 | 0.28151 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_585_0_line_57 |  | 49 | 113 | 0.17849 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
58 | MV_585_0_line_58 |  | 49 | 122 | 0.029733 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_585_0_line_59 |  | 52 | 91 | 0.2508 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
60 | MV_585_0_line_60 |  | 53 | 54 | 0.04564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_585_0_line_61 |  | 54 | 110 | 0.019847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_585_0_line_62 |  | 54 | 120 | 0.063721 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_585_0_line_63 |  | 55 | 56 | 0.007876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_585_0_line_64 |  | 55 | 57 | 0.16208 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
65 | MV_585_0_line_65 |  | 56 | 58 | 0.022746 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_585_0_line_66 |  | 57 | 62 | 0.2083 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_585_0_line_67 |  | 57 | 64 | 0.015551 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_585_0_line_68 |  | 58 | 66 | 0.010763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_585_0_line_69 |  | 59 | 60 | 0.030175 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_585_0_line_70 |  | 60 | 105 | 0.022107 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_585_0_line_71 |  | 61 | 62 | 0.11427 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_585_0_line_72 |  | 61 | 63 | 0.0027421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_585_0_line_73 |  | 62 | 65 | 0.006929 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_585_0_line_74 |  | 66 | 67 | 0.011452 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_585_0_line_75 |  | 67 | 106 | 0.012066 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_585_0_line_76 |  | 68 | 69 | 0.037872 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_585_0_line_77 |  | 69 | 70 | 0.36219 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_585_0_line_78 |  | 69 | 71 | 0.30446 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_585_0_line_79 |  | 70 | 73 | 0.10911 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
80 | MV_585_0_line_80 |  | 71 | 72 | 0.081998 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_585_0_line_81 |  | 72 | 171 | 0.36984 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_585_0_line_82 |  | 72 | 169 | 0.29245 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_585_0_line_83 |  | 73 | 77 | 0.021478 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
84 | MV_585_0_line_84 |  | 74 | 75 | 0.66474 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_585_0_line_85 |  | 75 | 76 | 0.062331 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_585_0_line_86 |  | 76 | 171 | 0.31514 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_585_0_line_87 |  | 77 | 88 | 0.61343 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
88 | MV_585_0_line_88 |  | 78 | 79 | 0.051391 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_585_0_line_89 |  | 79 | 81 | 0.025345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_585_0_line_90 |  | 80 | 84 | 0.004009 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_585_0_line_91 |  | 82 | 83 | 0.043742 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_585_0_line_92 |  | 82 | 84 | 0.041618 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
93 | MV_585_0_line_93 |  | 83 | 85 | 0.020184 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_585_0_line_94 |  | 83 | 86 | 0.058116 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
95 | MV_585_0_line_95 |  | 85 | 87 | 0.019547 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_585_0_line_96 |  | 87 | 105 | 0.075802 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_585_0_line_97 |  | 88 | 89 | 0.003591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_585_0_line_98 |  | 88 | 90 | 0.98379 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
99 | MV_585_0_line_99 |  | 88 | 91 | 1.0141 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_585_0_line_100 |  | 90 | 98 | 0.05811 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_585_0_line_101 |  | 90 | 96 | 0.46595 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
102 | MV_585_0_line_102 |  | 91 | 99 | 0.006088 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_585_0_line_103 |  | 92 | 93 | 0.03197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_585_0_line_104 |  | 92 | 94 | 0.078933 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
105 | MV_585_0_line_105 |  | 93 | 102 | 0.038727 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_585_0_line_106 |  | 94 | 103 | 0.094343 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_585_0_line_107 |  | 95 | 96 | 0.4063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_585_0_line_108 |  | 95 | 97 | 0.084956 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
109 | MV_585_0_line_109 |  | 96 | 100 | 0.52146 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
110 | MV_585_0_line_110 |  | 96 | 101 | 0.037038 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_585_0_line_111 |  | 100 | 165 | 0.078572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_585_0_line_112 |  | 100 | 166 | 0.76436 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_585_0_line_113 |  | 102 | 169 | 0.34169 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_585_0_line_114 |  | 103 | 104 | 0.013217 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_585_0_line_115 |  | 105 | 106 | 0.032714 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_585_0_line_116 |  | 106 | 107 | 0.007752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
117 | MV_585_0_line_117 |  | 108 | 109 | 0.0011619 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_585_0_line_118 |  | 109 | 110 | 0.0037939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_585_0_line_119 |  | 111 | 112 | 0.021729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_585_0_line_120 |  | 113 | 114 | 0.32245 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
121 | MV_585_0_line_121 |  | 113 | 115 | 0.014823 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
122 | MV_585_0_line_122 |  | 114 | 116 | 0.52668 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
123 | MV_585_0_line_123 |  | 114 | 117 | 0.018592 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
124 | MV_585_0_line_124 |  | 116 | 121 | 0.017362 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
125 | MV_585_0_line_125 |  | 117 | 124 | 0.004549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
126 | MV_585_0_line_126 |  | 118 | 119 | 0.031264 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
127 | MV_585_0_line_127 |  | 118 | 120 | 0.4806 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
128 | MV_585_0_line_128 |  | 120 | 125 | 0.34417 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
129 | MV_585_0_line_129 |  | 121 | 133 | 0.23373 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
130 | MV_585_0_line_130 |  | 122 | 123 | 0.015867 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_585_0_line_131 |  | 123 | 136 | 0.011106 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_585_0_line_132 |  | 124 | 163 | 0.20889 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
133 | MV_585_0_line_133 |  | 125 | 126 | 0.050671 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_585_0_line_134 |  | 127 | 128 | 0.51206 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
135 | MV_585_0_line_135 |  | 127 | 129 | 0.35402 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
136 | MV_585_0_line_136 |  | 127 | 130 | 0.003916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_585_0_line_137 |  | 128 | 131 | 0.034095 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
138 | MV_585_0_line_138 |  | 129 | 132 | 0.044935 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
139 | MV_585_0_line_139 |  | 131 | 133 | 0.46504 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
140 | MV_585_0_line_140 |  | 132 | 137 | 0.005243 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
141 | MV_585_0_line_141 |  | 133 | 134 | 0.035783 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
142 | MV_585_0_line_142 |  | 133 | 135 | 0.49108 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
143 | MV_585_0_line_143 |  | 135 | 140 | 0.10343 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
144 | MV_585_0_line_144 |  | 135 | 138 | 0.015192 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
145 | MV_585_0_line_145 |  | 137 | 146 | 0.66455 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
146 | MV_585_0_line_146 |  | 138 | 139 | 0.023377 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
147 | MV_585_0_line_147 |  | 139 | 141 | 0.026273 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_585_0_line_148 |  | 140 | 142 | 0.012909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
149 | MV_585_0_line_149 |  | 140 | 143 | 0.023764 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
150 | MV_585_0_line_150 |  | 141 | 144 | 0.020939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_585_0_line_151 |  | 141 | 145 | 0.061062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_585_0_line_152 |  | 142 | 148 | 0.01699 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_585_0_line_153 |  | 144 | 149 | 0.026456 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
154 | MV_585_0_line_154 |  | 145 | 150 | 0.021241 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_585_0_line_155 |  | 146 | 147 | 0.027801 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_585_0_line_156 |  | 149 | 180 | 0.02713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
157 | MV_585_0_line_157 |  | 151 | 152 | 0.011623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_585_0_line_158 |  | 152 | 153 | 0.059447 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_585_0_line_159 |  | 152 | 154 | 0.46428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_585_0_line_160 |  | 153 | 155 | 0.05523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_585_0_line_161 |  | 154 | 156 | 0.18572 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_585_0_line_162 |  | 154 | 157 | 0.029411 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_585_0_line_163 |  | 155 | 163 | 0.0050512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_585_0_line_164 |  | 156 | 162 | 0.003725 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_585_0_line_165 |  | 156 | 158 | 0.70021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_585_0_line_166 |  | 158 | 159 | 0.15232 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_585_0_line_167 |  | 158 | 160 | 0.049534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_585_0_line_168 |  | 159 | 161 | 0.10426 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
169 | MV_585_0_line_169 |  | 160 | 164 | 0.51211 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
170 | MV_585_0_line_170 |  | 164 | 168 | 0.025862 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_585_0_line_171 |  | 166 | 167 | 0.031986 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_585_0_line_172 |  | 169 | 170 | 0.004235 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_585_0_line_173 |  | 171 | 172 | 0.071178 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
174 | MV_585_0_line_174 |  | 171 | 173 | 0.27612 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
175 | MV_585_0_line_175 |  | 174 | 177 | 0.035146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_585_0_line_176 |  | 175 | 176 | 0.018496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
177 | MV_585_0_line_177 |  | 175 | 177 | 0.053618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
178 | MV_585_0_line_178 |  | 176 | 178 | 0.19144 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
179 | MV_585_0_line_179 |  | 178 | 179 | 0.039176 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
180 | MV_585_0_line_180 |  | 180 | 181 | 0.030719 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
181 | MV_585_0_line_181 |  | 181 | 182 | 0.028425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
182 | MV_585_0_line_182 |  | 182 | 183 | 0.004497 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_585_0_trafo_181 | 25 MVA 110/20 kV | 184 | 28 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2704700.2119 | 1231723.0264
1 | 2704684.5878 | 1231720.3271
2 | 2704909.5309 | 1231819.2331
3 | 2704549.0361 | 1231792.1293
4 | 2705059.6965 | 1231700.8177
5 | 2705058.121 | 1231707.6728
6 | 2705023.3045 | 1231687.3313
7 | 2704948.411 | 1231758.7292
8 | 2705029.6684 | 1231908.7661
9 | 2704916.7855 | 1231792.5297
10 | 2705153.6071 | 1231776.0568
11 | 2705179.5733 | 1231782.8434
12 | 2704939.9069 | 1231721.7402
13 | 2704990.317 | 1231678.5695
14 | 2704533.016 | 1231625.5446
15 | 2704577.9236 | 1231620.5083
16 | 2704451.5102 | 1231656.7356
17 | 2704551.1217 | 1231723.114
18 | 2704552.0045 | 1231653.375
19 | 2704458.6679 | 1231645.5529
20 | 2704574.6434 | 1231564.1527
21 | 2704595.8428 | 1231647.6742
22 | 2704618.6696 | 1231755.8824
23 | 2704605.196 | 1231731.0823
24 | 2704679.8081 | 1231444.7691
25 | 2704554.6635 | 1231558.3884
26 | 2704537.6701 | 1231711.7208
27 | 2705147.9386 | 1231905.0315
28 | 2705016.7458 | 1231916.9551
29 | 2705239.6068 | 1231868.4481
30 | 2705271.1266 | 1231832.3678
31 | 2705254.6352 | 1231866.0078
32 | 2705105.5225 | 1231963.2588
33 | 2705167.2195 | 1231946.4601
34 | 2704620.4393 | 1232130.2286
35 | 2704638.1724 | 1231887.558
36 | 2704482.9141 | 1232415.9919
37 | 2704621.7931 | 1232125.6045
38 | 2704649.6171 | 1231878.5305
39 | 2704471.9498 | 1232430.0765
40 | 2704556.2158 | 1231818.8645
41 | 2705105.108 | 1231964.0911
42 | 2704997.721 | 1231637.8533
43 | 2704934.3485 | 1231663.7038
44 | 2704323.5444 | 1231604.6053
45 | 2704278.122 | 1231517.7099
46 | 2704702.4958 | 1231464.4834
47 | 2704528.5632 | 1231552.7227
48 | 2705250.0468 | 1231808.4432
49 | 2705297.2316 | 1231832.1632
50 | 2705179.6164 | 1231984.0515
51 | 2704529.9312 | 1231840.9078
52 | 2705092.5727 | 1231989.2606
53 | 2704990.0363 | 1231564.5139
54 | 2704961.1182 | 1231599.8228
55 | 2704424.8014 | 1231421.9123
56 | 2704432.4801 | 1231423.7597
57 | 2704382.8678 | 1231265.3474
58 | 2704454.6645 | 1231429.0644
59 | 2704497.1412 | 1231494.7045
60 | 2704467.8726 | 1231487.3625
61 | 2704450.463 | 1231133.3242
62 | 2704370.8677 | 1231140.7877
63 | 2704452.3897 | 1231133.0707
64 | 2704367.4908 | 1231262.7422
65 | 2704366.5081 | 1231146.1819
66 | 2704451.6664 | 1231439.3258
67 | 2704448.3614 | 1231450.2251
68 | 2704065.0428 | 1232935.9538
69 | 2704103.019 | 1232935.2071
70 | 2704384.9591 | 1232853.3229
71 | 2704339.0996 | 1233127.461
72 | 2704419.2974 | 1233110.3755
73 | 2704485.8905 | 1232894.7719
74 | 2703590.3534 | 1233025.6634
75 | 2704189.278 | 1233314.0485
76 | 2704233.8251 | 1233340.4606
77 | 2704493.3032 | 1232874.6092
78 | 2704220.1724 | 1231505.7849
79 | 2704228.5609 | 1231455.0828
80 | 2704288.0287 | 1231490.1519
81 | 2704246.898 | 1231437.5865
82 | 2704332.4693 | 1231500.5393
83 | 2704368.8743 | 1231512.1425
84 | 2704291.944 | 1231491.0657
85 | 2704377.4461 | 1231497.1999
86 | 2704385.9793 | 1231567.6845
87 | 2704380.0816 | 1231477.8357
88 | 2704601.6973 | 1232643.152
89 | 2704599.7741 | 1232640.1159
90 | 2704925.2284 | 1232365.7999
91 | 2704889.7809 | 1231979.8834
92 | 2704794.118 | 1233078.5365
93 | 2704789.0101 | 1233110.0925
94 | 2704869.9271 | 1233100.5234
95 | 2705153.9137 | 1232409.1399
96 | 2704865.4916 | 1232620.8161
97 | 2705229.3867 | 1232370.1347
98 | 2704898.7855 | 1232314.0831
99 | 2704884.3932 | 1231977.0195
100 | 2705268.107 | 1232928.4869
101 | 2704873.0915 | 1232657.0664
102 | 2704768.154 | 1233140.1921
103 | 2704959.9994 | 1233097.8334
104 | 2704973.2454 | 1233097.3335
105 | 2704446.2491 | 1231482.4789
106 | 2704446.9766 | 1231462.2098
107 | 2704454.6338 | 1231463.5565
108 | 2704978.318 | 1231617.6935
109 | 2704977.5123 | 1231616.8563
110 | 2704974.8813 | 1231614.1228
111 | 2705362.2612 | 1231547.9343
112 | 2705380.8998 | 1231559.1953
113 | 2705417.0874 | 1231699.8985
114 | 2705499.6116 | 1231924.2872
115 | 2705431.4104 | 1231696.0829
116 | 2705631.8126 | 1231552.3982
117 | 2705481.0719 | 1231922.8905
118 | 2705365.9777 | 1231264.0418
119 | 2705396.7274 | 1231257.9266
120 | 2704970.245 | 1231536.759
121 | 2705647.0789 | 1231544.1298
122 | 2705301.6641 | 1231861.5639
123 | 2705291.6691 | 1231868.2253
124 | 2705476.5267 | 1231922.4984
125 | 2705107.8623 | 1231221.2969
126 | 2705149.6756 | 1231200.4092
127 | 2705578.7373 | 1231130.3261
128 | 2705798.8806 | 1231194.265
129 | 2705380.7126 | 1230964.5552
130 | 2705582.6189 | 1231129.7279
131 | 2705814.9419 | 1231224.3624
132 | 2705354.4212 | 1230928.0619
133 | 2705830.388 | 1231689.1438
134 | 2705864.4688 | 1231700.0476
135 | 2705902.3323 | 1232029.0263
136 | 2705302.1801 | 1231871.336
137 | 2705351.1379 | 1230923.9673
138 | 2705917.5646 | 1232029.409
139 | 2705923.4734 | 1232052.0265
140 | 2705852.526 | 1231960.0871
141 | 2705930.1143 | 1232077.4467
142 | 2705859.4835 | 1231949.2139
143 | 2705841.8782 | 1231981.332
144 | 2705935.997 | 1232097.5445
145 | 2705988.8934 | 1232072.1236
146 | 2705654.8306 | 1230709.8499
147 | 2705628.3212 | 1230718.4632
148 | 2705849.8384 | 1231935.8831
149 | 2705910.4193 | 1232104.3044
150 | 2705993.1886 | 1232051.3219
151 | 2705512.3952 | 1232120.1286
152 | 2705523.9484 | 1232121.6793
153 | 2705514.0324 | 1232075.713
154 | 2705884.6581 | 1232186.8865
155 | 2705475.8666 | 1232035.792
156 | 2705988.3731 | 1232236.7056
157 | 2705891.8216 | 1232213.6505
158 | 2706197.857 | 1232571.1087
159 | 2706091.5429 | 1232501.0128
160 | 2706148.6338 | 1232565.5721
161 | 2705989.3063 | 1232521.4491
162 | 2705988.3218 | 1232240.4298
163 | 2705472.376 | 1232032.1409
164 | 2706089.1435 | 1233074.2161
165 | 2705239.4666 | 1233001.1125
166 | 2705389.0307 | 1233561.9208
167 | 2705358.7385 | 1233553.5774
168 | 2706112.2741 | 1233085.9046
169 | 2704586.2918 | 1233194.6195
170 | 2704590.5266 | 1233194.9498
171 | 2704498.0812 | 1233369.2111
172 | 2704544.6042 | 1233423.081
173 | 2704606.5586 | 1233623.1334
174 | 2704906.5224 | 1231656.3129
175 | 2704820.5339 | 1231633.9156
176 | 2704803.5338 | 1231627.3748
177 | 2704872.4519 | 1231647.3051
178 | 2704718.7014 | 1231610.8566
179 | 2704680.5295 | 1231601.5885
180 | 2705883.9597 | 1232108.359
181 | 2705853.5234 | 1232106.2915
182 | 2705826.2913 | 1232102.3833
183 | 2705821.8769 | 1232101.4595
184 | 2705016.7458 | 1231916.9551

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99909 | -0.004272 | 0.34771 | 0.16841
1 | 0.9991 | -0.0043377 | 0 | 0
2 | 0.99953 | -0.0023022 | 0 | 0
3 | 0.99886 | -0.0054183 | 0 | 0
4 | 0.9982 | 0.0096457 | 0 | 0
5 | 0.9982 | 0.0096767 | 0.3682 | 0.17833
6 | 0.99823 | 0.0094037 | 0 | 0
7 | 0.99879 | 0.0043 | 0 | 0
8 | 0.99993 | -0.0004415 | 0 | 0
9 | 0.99953 | -0.0022731 | 0.086941 | 0.042107
10 | 0.99866 | 0.0054119 | 0 | 0
11 | 0.99865 | 0.0055116 | 0.31231 | 0.15126
12 | 0.99878 | 0.0043344 | 0.074206 | 0.035939
13 | 0.99811 | 0.010413 | 0.13541 | 0.065584
14 | 0.99853 | -0.0067898 | 0 | 0
15 | 0.99847 | -0.0070299 | 0 | 0
16 | 0.99847 | -0.0061834 | 0 | 0
17 | 0.99868 | -0.0062054 | 0 | 0
18 | 0.99853 | -0.0067537 | 0.091419 | 0.044276
19 | 0.99846 | -0.0061224 | 0.38389 | 0.18593
20 | 0.9983 | -0.0088448 | 0 | 0
21 | 0.99847 | -0.006991 | 0.10178 | 0.049295
22 | 0.99877 | -0.0058007 | 0 | 0
23 | 0.99877 | -0.0057748 | 0.078262 | 0.037904
24 | 0.99818 | -0.007732 | 0 | 0
25 | 0.9982 | -0.0079168 | 0.079404 | 0.038457
26 | 0.99867 | -0.0061213 | 0.3988 | 0.19315
27 | 0.99957 | -0.0030068 | 0 | 0
28 | 1 | 0 | -22.2051 | -9.594
29 | 0.99944 | -0.0038635 | 0 | 0
30 | 0.99935 | -0.0044454 | 0 | 0
31 | 0.99944 | -0.0038386 | 0.13727 | 0.066482
32 | 0.99949 | -0.0036177 | 0 | 0
33 | 0.99955 | -0.0028097 | 0.079758 | 0.038629
34 | 0.99813 | 0.00065729 | 0 | 0
35 | 0.99858 | -0.0030915 | 0 | 0
36 | 0.9979 | 0.0026448 | 0 | 0
37 | 0.99813 | 0.00067935 | 0.38152 | 0.18478
38 | 0.99857 | -0.0030368 | 0.31409 | 0.15212
39 | 0.99789 | 0.0025618 | 0.38325 | 0.18562
40 | 0.99884 | -0.0052716 | 0.077145 | 0.037363
41 | 0.99949 | -0.0036232 | 0.13229 | 0.064069
42 | 0.99795 | 0.0093649 | 0.33002 | 0.15984
43 | 0.99809 | 0.010643 | 0.095545 | 0.046274
44 | 0.99694 | -0.0015689 | 0.18602 | 0.090092
45 | 0.99698 | -0.0013467 | 0 | 0
46 | 0.99816 | -0.0078814 | 0.40985 | 0.1985
47 | 0.99807 | -0.0067444 | 0 | 0
48 | 0.99933 | -0.0043096 | 0.11122 | 0.053867
49 | 0.99932 | -0.0046147 | 0.31057 | 0.15042
50 | 0.99953 | -0.0029436 | 0.27961 | 0.13542
51 | 0.99883 | -0.0053756 | 0.2502 | 0.12118
52 | 0.99947 | -0.0037878 | 0 | 0
53 | 0.99784 | 0.010367 | 0.085073 | 0.041203
54 | 0.99785 | 0.010322 | 0.55931 | 0.27089
55 | 0.9971 | -0.0012583 | 0.35439 | 0.17164
56 | 0.99712 | -0.0014228 | 0 | 0
57 | 0.99665 | -0.0041856 | 0 | 0
58 | 0.99717 | -0.0018973 | 0 | 0
59 | 0.99765 | -0.0028735 | 0 | 0
60 | 0.99743 | -0.004296 | 0.34125 | 0.16527
61 | 0.99629 | -0.00080707 | 0 | 0
62 | 0.99636 | -0.0014704 | 0 | 0
63 | 0.99629 | -0.0007909 | 0.48922 | 0.23694
64 | 0.99665 | -0.0041268 | 0.31489 | 0.15251
65 | 0.99635 | -0.0014185 | 0.6215 | 0.30101
66 | 0.99719 | -0.0021215 | 0.070766 | 0.034274
67 | 0.99722 | -0.0023697 | 0 | 0
68 | 0.99643 | -0.01843 | 0.38526 | 0.18659
69 | 0.99645 | -0.018605 | 0 | 0
70 | 0.99748 | -0.027348 | 0 | 0
71 | 0.99536 | -0.026569 | 0.32589 | 0.15784
72 | 0.9952 | -0.025256 | 0 | 0
73 | 0.99777 | -0.019972 | 0.22939 | 0.1111
74 | 0.99442 | -0.022671 | 0.21079 | 0.10209
75 | 0.99469 | -0.020937 | 0.12687 | 0.061444
76 | 0.99472 | -0.021185 | 0 | 0
77 | 0.9978 | -0.019647 | 0 | 0
78 | 0.99694 | -0.0010556 | 0.34595 | 0.16755
79 | 0.99694 | -0.0011028 | 0 | 0
80 | 0.997 | -0.0015545 | 0 | 0
81 | 0.99693 | -0.0010816 | 0.071149 | 0.034459
82 | 0.99708 | -0.0010657 | 0 | 0
83 | 0.99714 | -0.0015828 | 0 | 0
84 | 0.997 | -0.0015828 | 0.39804 | 0.19278
85 | 0.99717 | -0.0018907 | 0.068369 | 0.033112
86 | 0.9971 | -0.0017878 | 0.28997 | 0.14044
87 | 0.9972 | -0.0022044 | 0 | 0
88 | 0.99862 | -0.010237 | 0 | 0
89 | 0.99862 | -0.010221 | 0.39105 | 0.1894
90 | 0.99841 | -0.012026 | 0 | 0
91 | 0.99929 | -0.0052233 | 0 | 0
92 | 0.99461 | -0.020134 | 0 | 0
93 | 0.99462 | -0.020255 | 0.24644 | 0.11936
94 | 0.99456 | -0.020468 | 0 | 0
95 | 0.99811 | -0.011519 | 0 | 0
96 | 0.99827 | -0.012976 | 0 | 0
97 | 0.99805 | -0.011854 | 0.32485 | 0.15733
98 | 0.99839 | -0.011759 | 0.38578 | 0.18684
99 | 0.99929 | -0.0051987 | 0.33754 | 0.16348
100 | 0.9982 | -0.014102 | 0 | 0
101 | 0.99825 | -0.013137 | 0.36034 | 0.17452
102 | 0.99465 | -0.020514 | 0 | 0
103 | 0.99452 | -0.020103 | 0 | 0
104 | 0.99451 | -0.02005 | 0.32784 | 0.15878
105 | 0.99734 | -0.0034152 | 0 | 0
106 | 0.99725 | -0.0026309 | 0 | 0
107 | 0.99725 | -0.0026125 | 0.19764 | 0.095721
108 | 0.99789 | 0.0099282 | 0.086286 | 0.04179
109 | 0.99789 | 0.0099504 | 0.19152 | 0.092755
110 | 0.99788 | 0.010014 | 0.11008 | 0.053315
111 | 0.99921 | -0.005022 | 0.22109 | 0.10708
112 | 0.99921 | -0.0050792 | 0 | 0
113 | 0.999 | -0.024684 | 0 | 0
114 | 0.99871 | -0.026607 | 0 | 0
115 | 0.99899 | -0.024732 | 0.26556 | 0.12862
116 | 0.99842 | -0.028715 | 0 | 0
117 | 0.99867 | -0.027769 | 0.28933 | 0.14013
118 | 0.99759 | 0.0094833 | 0 | 0
119 | 0.99758 | 0.0095663 | 0.22294 | 0.10797
120 | 0.99779 | 0.010826 | 0.15724 | 0.076156
121 | 0.99841 | -0.029878 | 0.3969 | 0.19223
122 | 0.99932 | -0.0046521 | 0 | 0
123 | 0.99931 | -0.0046337 | 0 | 0
124 | 0.99866 | -0.027685 | 0 | 0
125 | 0.99759 | 0.0095416 | 0 | 0
126 | 0.99758 | 0.0097209 | 0.29754 | 0.14411
127 | 0.99792 | -0.057105 | 0 | 0
128 | 0.99799 | -0.056348 | 0 | 0
129 | 0.99788 | -0.057428 | 0 | 0
130 | 0.99792 | -0.057092 | 0.28325 | 0.13719
131 | 0.998 | -0.056289 | 0.40343 | 0.19539
132 | 0.99788 | -0.057461 | 0.41226 | 0.19967
133 | 0.99818 | -0.043781 | 0 | 0
134 | 0.99817 | -0.043877 | 0.22221 | 0.10762
135 | 0.99807 | -0.044363 | 0 | 0
136 | 0.99931 | -0.0046206 | 0.099195 | 0.048042
137 | 0.99788 | -0.057463 | 0 | 0
138 | 0.99806 | -0.044375 | 0.35431 | 0.1716
139 | 0.99806 | -0.044454 | 0.076733 | 0.037163
140 | 0.99804 | -0.044088 | 0 | 0
141 | 0.99803 | -0.044209 | 0 | 0
142 | 0.99803 | -0.044078 | 0 | 0
143 | 0.99803 | -0.044042 | 0.16427 | 0.079558
144 | 0.99801 | -0.044029 | 0 | 0
145 | 0.99803 | -0.04416 | 0 | 0
146 | 0.99782 | -0.057871 | 0 | 0
147 | 0.99781 | -0.057787 | 0.25344 | 0.12275
148 | 0.99803 | -0.044064 | 0.070077 | 0.03394
149 | 0.99799 | -0.043801 | 0.16977 | 0.082221
150 | 0.99802 | -0.044141 | 0.07407 | 0.035874
151 | 0.99792 | -0.02158 | 0.29924 | 0.14493
152 | 0.99792 | -0.021622 | 0 | 0
153 | 0.99805 | -0.022699 | 0 | 0
154 | 0.99708 | -0.014674 | 0 | 0
155 | 0.99817 | -0.023696 | 0.068728 | 0.033287
156 | 0.99678 | -0.012116 | 0 | 0
157 | 0.99708 | -0.014623 | 0.14523 | 0.070337
158 | 0.99599 | -0.0052932 | 0 | 0
159 | 0.99592 | -0.0045922 | 0 | 0
160 | 0.99596 | -0.0050042 | 0.40363 | 0.19549
161 | 0.99584 | -0.0050905 | 0.39182 | 0.18977
162 | 0.99678 | -0.012099 | 0.39199 | 0.18985
163 | 0.99818 | -0.023791 | 0 | 0
164 | 0.99587 | -0.0056052 | 0 | 0
165 | 0.99818 | -0.013918 | 0.19964 | 0.096692
166 | 0.99814 | -0.014008 | 0 | 0
167 | 0.99814 | -0.013985 | 0.062669 | 0.030352
168 | 0.99587 | -0.0055777 | 0.089888 | 0.043535
169 | 0.9949 | -0.022703 | 0 | 0
170 | 0.9949 | -0.022691 | 0.23299 | 0.11284
171 | 0.99486 | -0.022351 | 0 | 0
172 | 0.99483 | -0.022545 | 0.22302 | 0.10801
173 | 0.99477 | -0.022916 | 0.16649 | 0.080632
174 | 0.99808 | 0.010726 | 0 | 0
175 | 0.99804 | 0.010989 | 0.096631 | 0.046801
176 | 0.99804 | 0.011024 | 0 | 0
177 | 0.99806 | 0.010828 | 0 | 0
178 | 0.99799 | 0.011416 | 0 | 0
179 | 0.99799 | 0.011503 | 0.18763 | 0.090874
180 | 0.99797 | -0.04362 | 0 | 0
181 | 0.99795 | -0.043415 | 0.15625 | 0.075676
182 | 0.99793 | -0.043277 | 0 | 0
183 | 0.99793 | -0.043255 | 0.40652 | 0.19689
184 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.34771 | -0.16841 | 0.34772 | 0.16803 | 2.629e-06 | -0.00037602 | 0.011163 | 0.011158 | 0.011163 | 0.99909 | -0.004272 | 0.9991 | -0.0043377 | 5.0741
1 | -7.0572 | -3.2651 | 7.0601 | 3.2196 | 0.0029268 | -0.045566 | 0.22467 | 0.2241 | 0.22467 | 0.9991 | -0.0043377 | 0.99953 | -0.0023022 | 17.6076
2 | 6.7094 | 3.0971 | -6.7079 | -3.1237 | 0.0015456 | -0.026605 | 0.21352 | 0.21385 | 0.21385 | 0.9991 | -0.0043377 | 0.99886 | -0.0054183 | 16.7595
3 | 3.3154 | 1.5686 | -3.3128 | -1.572 | 0.002639 | -0.0034144 | 0.10593 | 0.10598 | 0.10598 | 0.99953 | -0.0023022 | 0.99879 | 0.0043 | 48.1728
4 | -10.4624 | -4.8296 | 10.4664 | 4.8024 | 0.0040028 | -0.027156 | 0.33281 | 0.33245 | 0.33281 | 0.99953 | -0.0023022 | 0.99993 | -0.0004415 | 26.082
5 | 0.086941 | 0.041427 | -0.086941 | -0.042107 | 2.955e-07 | -0.00068031 | 0.0027814 | 0.00279 | 0.00279 | 0.99953 | -0.0023022 | 0.99953 | -0.0022731 | 1.2682
6 | 0.32736 | 0.15761 | -0.32735 | -0.1585 | 5.5545e-06 | -0.00089634 | 0.0105 | 0.010511 | 0.010511 | 0.99886 | -0.0054183 | 0.99884 | -0.0052716 | 4.7779
7 | 5.3009 | 2.4709 | -5.3004 | -2.4834 | 0.00044996 | -0.012515 | 0.16902 | 0.16918 | 0.16918 | 0.99886 | -0.0054183 | 0.99877 | -0.0058007 | 13.2586
8 | 1.0796 | 0.49525 | -1.0793 | -0.50004 | 0.0003234 | -0.0047911 | 0.034328 | 0.034388 | 0.034388 | 0.99886 | -0.0054183 | 0.99858 | -0.0030915 | 15.6307
9 | 0.3682 | 0.17816 | -0.3682 | -0.17833 | 1.3142e-06 | -0.00016695 | 0.011829 | 0.011831 | 0.011831 | 0.9982 | 0.0096457 | 0.9982 | 0.0096767 | 5.3778
10 | -0.3682 | -0.17816 | 0.36821 | 0.17684 | 1.0333e-05 | -0.0013147 | 0.011829 | 0.011813 | 0.011829 | 0.9982 | 0.0096457 | 0.99823 | 0.0094037 | 5.3769
11 | 2.5562 | 1.2202 | -2.5559 | -1.221 | 0.00030577 | -0.00072124 | 0.081914 | 0.081924 | 0.081924 | 0.99823 | 0.0094037 | 0.99811 | 0.010413 | 37.238
12 | -2.9244 | -1.3971 | 2.9262 | 1.394 | 0.0017729 | -0.0030745 | 0.093726 | 0.093681 | 0.093726 | 0.99823 | 0.0094037 | 0.99879 | 0.0043 | 42.6027
13 | 0.074206 | 0.034988 | -0.074206 | -0.035939 | 3.0144e-07 | -0.00095172 | 0.0023712 | 0.002383 | 0.002383 | 0.99879 | 0.0043 | 0.99878 | 0.0043344 | 1.0832
14 | 0.31235 | 0.14298 | -0.31231 | -0.15062 | 4.2678e-05 | -0.0076385 | 0.0099288 | 0.010023 | 0.010023 | 0.99879 | 0.0043 | 0.99866 | 0.0054119 | 4.5558
15 | 11.7231 | 4.7828 | -11.7192 | -4.8047 | 0.0039745 | -0.021928 | 0.36553 | 0.36579 | 0.36579 | 0.99993 | -0.0004415 | 0.99957 | -0.0030068 | 28.6669
16 | -22.1896 | -9.5852 | 22.1911 | 9.5835 | 0.0015465 | -0.0017122 | 0.69782 | 0.69779 | 0.69782 | 0.99993 | -0.0004415 | 1 | 0 | 54.6879
17 | 0.31231 | 0.15062 | -0.31231 | -0.15126 | 3.5922e-06 | -0.00063624 | 0.010023 | 0.010031 | 0.010031 | 0.99866 | 0.0054119 | 0.99865 | 0.0055116 | 4.5595
18 | 2.0407 | 0.98152 | -2.0403 | -0.98137 | 0.00031626 | 0.00014889 | 0.065492 | 0.065493 | 0.065493 | 0.99811 | 0.010413 | 0.99795 | 0.0093649 | 31.1869
19 | 0.37984 | 0.17386 | -0.37983 | -0.17524 | 1.1301e-05 | -0.001374 | 0.012082 | 0.012099 | 0.012099 | 0.99811 | 0.010413 | 0.99809 | 0.010643 | 5.4994
20 | 4.3469 | 2.0636 | -4.3466 | -2.0742 | 0.00025639 | -0.010589 | 0.13911 | 0.13924 | 0.13924 | 0.99853 | -0.0067898 | 0.99847 | -0.0070299 | 10.9125
21 | 0.38392 | 0.1824 | -0.38389 | -0.18561 | 2.7353e-05 | -0.0032116 | 0.012288 | 0.012328 | 0.012328 | 0.99853 | -0.0067898 | 0.99847 | -0.0061834 | 5.6037
22 | -4.8222 | -2.2895 | 4.8229 | 2.2672 | 0.00066357 | -0.022266 | 0.15432 | 0.15405 | 0.15432 | 0.99853 | -0.0067898 | 0.99868 | -0.0062054 | 12.0944
23 | 0.09142 | 0.043474 | -0.091419 | -0.044276 | 3.8654e-07 | -0.00080194 | 0.0029266 | 0.0029366 | 0.0029366 | 0.99853 | -0.0067898 | 0.99853 | -0.0067537 | 1.3348
24 | 4.2449 | 2.0257 | -4.2442 | -2.0277 | 0.00066248 | -0.0020544 | 0.13598 | 0.13602 | 0.13602 | 0.99847 | -0.0070299 | 0.9983 | -0.0088448 | 37.5733
25 | 0.10178 | 0.048521 | -0.10178 | -0.049295 | 4.6308e-07 | -0.0007745 | 0.00326 | 0.0032697 | 0.0032697 | 0.99847 | -0.0070299 | 0.99847 | -0.006991 | 1.4862
26 | 0.38389 | 0.18561 | -0.38389 | -0.18593 | 2.6952e-06 | -0.00031528 | 0.012328 | 0.012332 | 0.012332 | 0.99847 | -0.0061834 | 0.99846 | -0.0061224 | 5.6055
27 | 0.3988 | 0.19273 | -0.3988 | -0.19315 | 3.8613e-06 | -0.00041885 | 0.012803 | 0.012809 | 0.012809 | 0.99868 | -0.0062054 | 0.99867 | -0.0061213 | 5.8221
28 | -5.2217 | -2.4599 | 5.2222 | 2.4461 | 0.00048234 | -0.0138 | 0.16685 | 0.16667 | 0.16685 | 0.99868 | -0.0062054 | 0.99877 | -0.0058007 | 13.0759
29 | 0.40992 | 0.1929 | -0.40986 | -0.19847 | 5.4074e-05 | -0.0055699 | 0.0131 | 0.01317 | 0.01317 | 0.9983 | -0.0088448 | 0.99818 | -0.007732 | 5.9863
30 | 3.8343 | 1.8348 | -3.8339 | -1.8352 | 0.00041944 | -0.00037035 | 0.12292 | 0.12292 | 0.12292 | 0.9983 | -0.0088448 | 0.9982 | -0.0079168 | 55.8734
31 | 0.078262 | 0.03723 | -0.078262 | -0.037904 | 2.3788e-07 | -0.00067404 | 0.0025049 | 0.0025133 | 0.0025133 | 0.99877 | -0.0058007 | 0.99877 | -0.0057748 | 1.1424
32 | 0.40986 | 0.19847 | -0.40985 | -0.1985 | 9.2885e-06 | -2.9932e-05 | 0.01317 | 0.01317 | 0.01317 | 0.99818 | -0.007732 | 0.99816 | -0.0078814 | 6.2716
33 | 3.7545 | 1.7967 | -3.7539 | -1.7972 | 0.00051867 | -0.00048396 | 0.12037 | 0.12038 | 0.12038 | 0.9982 | -0.0079168 | 0.99807 | -0.0067444 | 54.7173
34 | 4.6815 | 1.8186 | -4.6812 | -1.8312 | 0.00033183 | -0.012618 | 0.14504 | 0.14518 | 0.14518 | 0.99957 | -0.0030068 | 0.99949 | -0.0036177 | 11.3777
35 | 0.35939 | 0.17291 | -0.35938 | -0.17401 | 8.1953e-06 | -0.0011001 | 0.011518 | 0.011532 | 0.011532 | 0.99957 | -0.0030068 | 0.99955 | -0.0028097 | 5.2417
36 | 6.6783 | 2.8132 | -6.6774 | -2.8282 | 0.00083619 | -0.015029 | 0.20928 | 0.20946 | 0.20946 | 0.99957 | -0.0030068 | 0.99944 | -0.0038635 | 16.415
37 | 6.5402 | 2.7621 | -6.5396 | -2.7726 | 0.00055958 | -0.010489 | 0.20506 | 0.20518 | 0.20518 | 0.99944 | -0.0038635 | 0.99935 | -0.0044454 | 16.0801
38 | 0.13727 | 0.066119 | -0.13727 | -0.066482 | 3.9405e-07 | -0.00036299 | 0.0044008 | 0.0044053 | 0.0044053 | 0.99944 | -0.0038635 | 0.99944 | -0.0038386 | 2.0024
39 | 0.33234 | 0.15928 | -0.33234 | -0.16011 | 5.2748e-06 | -0.00082894 | 0.010646 | 0.010656 | 0.010656 | 0.99935 | -0.0044454 | 0.99933 | -0.0043096 | 4.8437
40 | 6.2073 | 2.6133 | -6.2071 | -2.6165 | 0.00015224 | -0.0031808 | 0.19455 | 0.19458 | 0.19458 | 0.99935 | -0.0044454 | 0.99932 | -0.0046147 | 15.2496
41 | 4.6812 | 1.8312 | -4.6812 | -1.8314 | 3.0279e-06 | -0.00011502 | 0.14518 | 0.14518 | 0.14518 | 0.99949 | -0.0036177 | 0.99949 | -0.0036232 | 11.3778
42 | 0.27962 | 0.13538 | -0.27961 | -0.13542 | 5.6777e-06 | -4.3654e-05 | 0.0089723 | 0.0089729 | 0.0089729 | 0.99955 | -0.0028097 | 0.99953 | -0.0029436 | 4.2728
43 | -0.76487 | -0.35916 | 0.76524 | 0.34826 | 0.00036664 | -0.010895 | 0.024439 | 0.024305 | 0.024439 | 0.99813 | 0.00065729 | 0.99858 | -0.0030915 | 11.1085
44 | 0.38335 | 0.17449 | -0.38325 | -0.1856 | 9.3763e-05 | -0.011104 | 0.012182 | 0.012318 | 0.012318 | 0.99813 | 0.00065729 | 0.9979 | 0.0026448 | 5.5993
45 | 0.38153 | 0.18467 | -0.38152 | -0.18478 | 9.667e-07 | -0.00011432 | 0.012259 | 0.01226 | 0.01226 | 0.99813 | 0.00065729 | 0.99813 | 0.00067935 | 5.5729
46 | 0.31409 | 0.15177 | -0.31409 | -0.15212 | 1.9764e-06 | -0.00034587 | 0.010084 | 0.010089 | 0.010089 | 0.99858 | -0.0030915 | 0.99857 | -0.0030368 | 4.5858
47 | 0.38325 | 0.1856 | -0.38325 | -0.18562 | 4.8258e-06 | -1.8196e-05 | 0.012318 | 0.012319 | 0.012319 | 0.9979 | 0.0026448 | 0.99789 | 0.0025618 | 5.866
48 | 0.25021 | 0.12114 | -0.2502 | -0.12118 | 3.9454e-06 | -3.8386e-05 | 0.0080341 | 0.0080347 | 0.0080347 | 0.99884 | -0.0052716 | 0.99883 | -0.0053756 | 3.826
49 | 4.5489 | 1.7673 | -4.5488 | -1.7708 | 8.6328e-05 | -0.0034812 | 0.14095 | 0.14099 | 0.14099 | 0.99949 | -0.0036232 | 0.99947 | -0.0037878 | 11.049
50 | 1.7103 | 0.82153 | -1.7102 | -0.82216 | 0.00011254 | -0.0006319 | 0.054885 | 0.054894 | 0.054894 | 0.99795 | 0.0093649 | 0.99789 | 0.0099282 | 24.9517
51 | 0.28429 | 0.12896 | -0.28428 | -0.12965 | 3.1362e-06 | -0.00068385 | 0.0090289 | 0.0090371 | 0.0090371 | 0.99809 | 0.010643 | 0.99808 | 0.010726 | 4.1078
52 | -0.18602 | -0.090092 | 0.18602 | 0.089979 | 6.2557e-06 | -0.00011242 | 0.0059848 | 0.0059833 | 0.0059848 | 0.99694 | -0.0015689 | 0.99698 | -0.0013467 | 2.8499
53 | -0.60313 | -0.28993 | 0.60315 | 0.28924 | 1.467e-05 | -0.00069053 | 0.019377 | 0.019368 | 0.019377 | 0.99698 | -0.0013467 | 0.997 | -0.0015545 | 8.8076
54 | 0.41711 | 0.19995 | -0.4171 | -0.20135 | 1.4151e-05 | -0.0013963 | 0.013393 | 0.013411 | 0.013411 | 0.99698 | -0.0013467 | 0.99694 | -0.0010556 | 6.0959
55 | 3.7539 | 1.7972 | -3.7522 | -1.7988 | 0.0017087 | -0.0015926 | 0.12038 | 0.1204 | 0.1204 | 0.99807 | -0.0067444 | 0.99765 | -0.0028735 | 54.7292
56 | 0.22111 | 0.10624 | -0.22109 | -0.10656 | 2.5201e-05 | -0.00031979 | 0.0070863 | 0.0070905 | 0.0070905 | 0.99933 | -0.0043096 | 0.99921 | -0.0050792 | 3.3764
57 | 5.7974 | 2.4187 | -5.7963 | -2.4164 | 0.0010491 | 0.0023286 | 0.18146 | 0.18146 | 0.18146 | 0.99932 | -0.0046147 | 0.999 | -0.024684 | 14.067
58 | 0.099196 | 0.047364 | -0.099196 | -0.047399 | 5.3422e-07 | -3.5112e-05 | 0.0031754 | 0.0031758 | 0.0031758 | 0.99932 | -0.0046147 | 0.99932 | -0.0046521 | 1.5123
59 | 4.5488 | 1.7708 | -4.548 | -1.8018 | 0.00077203 | -0.031044 | 0.14099 | 0.14132 | 0.14132 | 0.99947 | -0.0037878 | 0.99929 | -0.0052233 | 11.0751
60 | -0.085073 | -0.041203 | 0.085073 | 0.040118 | 4.5337e-07 | -0.0010849 | 0.0027346 | 0.0027211 | 0.0027346 | 0.99784 | 0.010367 | 0.99785 | 0.010322 | 1.243
61 | -1.3223 | -0.63488 | 1.3223 | 0.63442 | 4.7702e-05 | -0.0004577 | 0.042433 | 0.042428 | 0.042433 | 0.99785 | 0.010322 | 0.99788 | 0.010014 | 19.2879
62 | 0.67787 | 0.32387 | -0.67783 | -0.32537 | 4.0218e-05 | -0.0015028 | 0.021734 | 0.021753 | 0.021753 | 0.99785 | 0.010322 | 0.99779 | 0.010826 | 9.8877
63 | -1.781 | -0.85415 | 1.781 | 0.85398 | 3.4383e-05 | -0.00017676 | 0.057186 | 0.057184 | 0.057186 | 0.9971 | -0.0012583 | 0.99712 | -0.0014228 | 25.9936
64 | 1.4266 | 0.68252 | -1.426 | -0.68233 | 0.00060543 | 0.00018693 | 0.045786 | 0.045788 | 0.045788 | 0.9971 | -0.0012583 | 0.99665 | -0.0041856 | 21.804
65 | -1.781 | -0.85398 | 1.7811 | 0.85347 | 9.9283e-05 | -0.00051054 | 0.057184 | 0.057177 | 0.057184 | 0.99712 | -0.0014228 | 0.99717 | -0.0018973 | 25.9925
66 | 1.1111 | 0.53019 | -1.1108 | -0.53502 | 0.00035422 | -0.0048337 | 0.035659 | 0.035721 | 0.035721 | 0.99665 | -0.0041856 | 0.99636 | -0.0014704 | 16.2368
67 | 0.31489 | 0.15214 | -0.31489 | -0.15251 | 2.1311e-06 | -0.00036818 | 0.010129 | 0.010134 | 0.010134 | 0.99665 | -0.0041856 | 0.99665 | -0.0041268 | 4.6064
68 | -1.7811 | -0.85347 | 1.7812 | 0.85322 | 4.6972e-05 | -0.0002416 | 0.057177 | 0.057174 | 0.057177 | 0.99717 | -0.0018973 | 0.99719 | -0.0021215 | 25.9894
69 | 3.7522 | 1.7988 | -3.7514 | -1.7984 | 0.00077942 | 0.00045236 | 0.1204 | 0.1204 | 0.1204 | 0.99765 | -0.0028735 | 0.99743 | -0.004296 | 57.3356
70 | 3.4102 | 1.6331 | -3.4098 | -1.6335 | 0.00035344 | -0.00042023 | 0.10943 | 0.10944 | 0.10944 | 0.99743 | -0.004296 | 0.99734 | -0.0034152 | 49.7444
71 | -0.48922 | -0.23688 | 0.48926 | 0.23418 | 3.7757e-05 | -0.002697 | 0.01575 | 0.015716 | 0.01575 | 0.99629 | -0.00080707 | 0.99636 | -0.0014704 | 7.1589
72 | 0.48922 | 0.23688 | -0.48922 | -0.23694 | 9.0806e-07 | -6.4717e-05 | 0.01575 | 0.01575 | 0.01575 | 0.99629 | -0.00080707 | 0.99629 | -0.0007909 | 7.1593
73 | 0.62151 | 0.30084 | -0.6215 | -0.30101 | 3.7025e-06 | -0.00016314 | 0.020006 | 0.020008 | 0.020008 | 0.99636 | -0.0014704 | 0.99635 | -0.0014185 | 9.0944
74 | -1.8519 | -0.8875 | 1.852 | 0.88724 | 5.4028e-05 | -0.00025587 | 0.05945 | 0.059446 | 0.05945 | 0.99719 | -0.0021215 | 0.99722 | -0.0023697 | 27.0226
75 | -1.852 | -0.88724 | 1.8521 | 0.88697 | 5.6921e-05 | -0.00026961 | 0.059446 | 0.059443 | 0.059446 | 0.99722 | -0.0023697 | 0.99725 | -0.0026309 | 27.0211
76 | -0.38526 | -0.18659 | 0.38526 | 0.18569 | 7.7686e-06 | -0.0008955 | 0.012401 | 0.01239 | 0.012401 | 0.99643 | -0.01843 | 0.99645 | -0.018605 | 5.637
77 | -2.2486 | -1.0477 | 2.2511 | 1.0399 | 0.0024937 | -0.0078555 | 0.071868 | 0.071763 | 0.071868 | 0.99645 | -0.018605 | 0.99748 | -0.027348 | 32.6673
78 | 1.8634 | 0.86202 | -1.8615 | -0.86118 | 0.0019192 | 0.00084166 | 0.059479 | 0.059484 | 0.059484 | 0.99645 | -0.018605 | 0.99536 | -0.026569 | 28.3256
79 | -2.2511 | -1.0399 | 2.2517 | 1.0403 | 0.00051583 | 0.00045354 | 0.071763 | 0.071762 | 0.071763 | 0.99748 | -0.027348 | 0.99777 | -0.019972 | 20.5038
80 | 1.5356 | 0.70334 | -1.5353 | -0.7052 | 0.00026278 | -0.0018614 | 0.048984 | 0.049007 | 0.049007 | 0.99536 | -0.026569 | 0.9952 | -0.025256 | 22.2761
81 | 0.72756 | 0.33347 | -0.72729 | -0.34213 | 0.00026732 | -0.0086635 | 0.023215 | 0.023322 | 0.023322 | 0.9952 | -0.025256 | 0.99486 | -0.022351 | 10.601
82 | 0.80774 | 0.37173 | -0.80748 | -0.37857 | 0.00026057 | -0.0068364 | 0.025792 | 0.025877 | 0.025877 | 0.9952 | -0.025256 | 0.9949 | -0.022703 | 11.7621
83 | -2.481 | -1.1514 | 2.4811 | 1.1507 | 6.4957e-05 | -0.00068636 | 0.079135 | 0.079126 | 0.079135 | 0.99777 | -0.019972 | 0.9978 | -0.019647 | 21.8604
84 | -0.21079 | -0.10209 | 0.21084 | 0.10134 | 5.4668e-05 | -0.00075071 | 0.0067989 | 0.006789 | 0.0067989 | 0.99442 | -0.022671 | 0.99469 | -0.020937 | 3.2376
85 | -0.33771 | -0.16278 | 0.33772 | 0.16131 | 9.8333e-06 | -0.0014696 | 0.01088 | 0.010861 | 0.01088 | 0.99469 | -0.020937 | 0.99472 | -0.021185 | 4.9454
86 | -0.33772 | -0.16131 | 0.33777 | 0.15388 | 4.9211e-05 | -0.0074314 | 0.010861 | 0.01077 | 0.010861 | 0.99472 | -0.021185 | 0.99486 | -0.022351 | 4.937
87 | -2.4811 | -1.1507 | 2.483 | 1.1311 | 0.0018491 | -0.019625 | 0.079126 | 0.078873 | 0.079126 | 0.9978 | -0.019647 | 0.99862 | -0.010237 | 21.8579
88 | 0.07115 | 0.033797 | -0.071149 | -0.033858 | 4.765e-07 | -6.0678e-05 | 0.0022808 | 0.0022816 | 0.0022816 | 0.99694 | -0.0010556 | 0.99694 | -0.0011028 | 1.0865
89 | 0.071149 | 0.033858 | -0.071149 | -0.034459 | 1.7672e-07 | -0.00060139 | 0.0022816 | 0.0022891 | 0.0022891 | 0.99694 | -0.0011028 | 0.99693 | -0.0010816 | 1.0405
90 | -0.60315 | -0.28924 | 0.60315 | 0.28915 | 2.0075e-06 | -9.455e-05 | 0.019368 | 0.019367 | 0.019368 | 0.997 | -0.0015545 | 0.997 | -0.0015828 | 8.8037
91 | -1.0013 | -0.48192 | 1.0013 | 0.4809 | 6.0415e-05 | -0.0010204 | 0.032172 | 0.032159 | 0.032172 | 0.99708 | -0.0010657 | 0.99714 | -0.0015828 | 14.6235
92 | 1.0013 | 0.48192 | -1.0012 | -0.48192 | 7.6749e-05 | -1.3172e-06 | 0.032172 | 0.032172 | 0.032172 | 0.99708 | -0.0010657 | 0.997 | -0.0015828 | 15.3201
93 | -1.2913 | -0.62128 | 1.2913 | 0.62081 | 4.6368e-05 | -0.00046542 | 0.041485 | 0.041479 | 0.041485 | 0.99714 | -0.0015828 | 0.99717 | -0.0018907 | 18.857
94 | 0.28997 | 0.14037 | -0.28997 | -0.14044 | 9.0082e-06 | -6.3338e-05 | 0.0093268 | 0.0093277 | 0.0093277 | 0.99714 | -0.0015828 | 0.9971 | -0.0017878 | 4.4417
95 | -1.3597 | -0.65392 | 1.3598 | 0.65347 | 4.9779e-05 | -0.00044932 | 0.043679 | 0.043673 | 0.043679 | 0.99717 | -0.0018907 | 0.9972 | -0.0022044 | 19.8539
96 | -1.3598 | -0.65347 | 1.36 | 0.65173 | 0.00019291 | -0.0017428 | 0.043673 | 0.04365 | 0.043673 | 0.9972 | -0.0022044 | 0.99734 | -0.0034152 | 19.8512
97 | 0.39105 | 0.18931 | -0.39105 | -0.1894 | 7.5628e-07 | -8.5278e-05 | 0.012559 | 0.01256 | 0.01256 | 0.99862 | -0.010237 | 0.99862 | -0.010221 | 5.7093
98 | 1.3338 | 0.44373 | -1.3335 | -0.56685 | 0.0002584 | -0.12312 | 0.040634 | 0.041896 | 0.041896 | 0.99862 | -0.010237 | 0.99841 | -0.012026 | 3.2834
99 | -4.2078 | -1.7641 | 4.2105 | 1.6385 | 0.0026968 | -0.12565 | 0.13189 | 0.13052 | 0.13189 | 0.99862 | -0.010237 | 0.99929 | -0.0052233 | 10.3366
100 | 0.38579 | 0.18546 | -0.38578 | -0.18684 | 1.19e-05 | -0.0013795 | 0.012376 | 0.012394 | 0.012394 | 0.99841 | -0.012026 | 0.99839 | -0.011759 | 5.6335
101 | 0.94774 | 0.38139 | -0.94761 | -0.41049 | 0.00012699 | -0.029108 | 0.029538 | 0.029863 | 0.029863 | 0.99841 | -0.012026 | 0.99827 | -0.012976 | 4.6807
102 | 0.33754 | 0.16333 | -0.33754 | -0.16348 | 9.5383e-07 | -0.00014487 | 0.010832 | 0.010834 | 0.010834 | 0.99929 | -0.0052233 | 0.99929 | -0.0051987 | 4.9246
103 | -0.32788 | -0.15616 | 0.32788 | 0.15541 | 4.7376e-06 | -0.00075371 | 0.010541 | 0.010531 | 0.010541 | 0.99461 | -0.020134 | 0.99462 | -0.020255 | 4.7912
104 | 0.32788 | 0.15616 | -0.32786 | -0.15625 | 1.5627e-05 | -8.3424e-05 | 0.010541 | 0.010542 | 0.010542 | 0.99461 | -0.020134 | 0.99456 | -0.020468 | 5.0199
105 | -0.57432 | -0.27477 | 0.57434 | 0.27386 | 1.7642e-05 | -0.00090952 | 0.018478 | 0.018467 | 0.018478 | 0.99462 | -0.020255 | 0.99465 | -0.020514 | 8.3993
106 | 0.32786 | 0.15625 | -0.32785 | -0.15847 | 1.4033e-05 | -0.0022238 | 0.010542 | 0.01057 | 0.01057 | 0.99456 | -0.020468 | 0.99452 | -0.020103 | 4.8044
107 | -0.32487 | -0.15724 | 0.32492 | 0.14759 | 5.8425e-05 | -0.0096485 | 0.010439 | 0.01032 | 0.010439 | 0.99811 | -0.011519 | 0.99827 | -0.012976 | 4.7448
108 | 0.32487 | 0.15724 | -0.32485 | -0.15733 | 1.6496e-05 | -9.07e-05 | 0.010439 | 0.01044 | 0.01044 | 0.99811 | -0.011519 | 0.99805 | -0.011854 | 4.9714
109 | 0.26234 | 0.088419 | -0.26232 | -0.10623 | 1.649e-05 | -0.017814 | 0.0080054 | 0.0081847 | 0.0081847 | 0.99827 | -0.012976 | 0.9982 | -0.014102 | 2.261
110 | 0.36035 | 0.17448 | -0.36034 | -0.17452 | 8.8462e-06 | -3.8522e-05 | 0.011578 | 0.011578 | 0.011578 | 0.99827 | -0.012976 | 0.99825 | -0.013137 | 5.5135
111 | 0.19965 | 0.094824 | -0.19964 | -0.096692 | 4.3011e-06 | -0.0018679 | 0.0063919 | 0.0064152 | 0.0064152 | 0.9982 | -0.014102 | 0.99818 | -0.013918 | 2.916
112 | 0.062673 | 0.011409 | -0.062669 | -0.029591 | 3.7108e-06 | -0.018182 | 0.0018423 | 0.0020044 | 0.0020044 | 0.9982 | -0.014102 | 0.99814 | -0.014008 | 0.91107
113 | -0.57434 | -0.27386 | 0.5745 | 0.26583 | 0.00015472 | -0.0080272 | 0.018467 | 0.018367 | 0.018467 | 0.99465 | -0.020514 | 0.9949 | -0.022703 | 8.3941
114 | 0.32785 | 0.15847 | -0.32784 | -0.15878 | 1.972e-06 | -0.00031153 | 0.01057 | 0.010574 | 0.010574 | 0.99452 | -0.020103 | 0.99451 | -0.02005 | 4.8062
115 | 2.0499 | 0.98179 | -2.0497 | -0.98251 | 0.00018904 | -0.00072078 | 0.065787 | 0.065797 | 0.065797 | 0.99734 | -0.0034152 | 0.99725 | -0.0026309 | 29.9078
116 | 0.19764 | 0.095537 | -0.19764 | -0.095721 | 4.1802e-07 | -0.00018395 | 0.0063544 | 0.0063568 | 0.0063568 | 0.99725 | -0.0026309 | 0.99725 | -0.0026125 | 2.8894
117 | 1.6239 | 0.78037 | -1.6239 | -0.7804 | 4.2139e-06 | -2.6375e-05 | 0.05212 | 0.052121 | 0.052121 | 0.99789 | 0.0099282 | 0.99789 | 0.0099504 | 23.6912
118 | 1.4324 | 0.68765 | -1.4324 | -0.68773 | 1.0701e-05 | -8.7027e-05 | 0.045965 | 0.045966 | 0.045966 | 0.99789 | 0.0099504 | 0.99788 | 0.010014 | 20.8936
119 | -0.22109 | -0.10708 | 0.22109 | 0.10656 | 1.4597e-06 | -0.00051755 | 0.007097 | 0.0070905 | 0.007097 | 0.99921 | -0.005022 | 0.99921 | -0.0050792 | 3.2259
120 | 5.5307 | 2.2878 | -5.5292 | -2.3274 | 0.0014941 | -0.039586 | 0.17295 | 0.1734 | 0.1734 | 0.999 | -0.024684 | 0.99871 | -0.026607 | 13.5895
121 | 0.26556 | 0.1286 | -0.26556 | -0.12862 | 1.92e-06 | -1.6457e-05 | 0.0085263 | 0.0085266 | 0.0085266 | 0.999 | -0.024684 | 0.99899 | -0.024732 | 4.0603
122 | 3.4454 | 1.3659 | -3.4444 | -1.4314 | 0.00094008 | -0.065466 | 0.10713 | 0.10785 | 0.10785 | 0.99871 | -0.026607 | 0.99842 | -0.028715 | 8.4519
123 | 2.0839 | 0.96141 | -2.0838 | -0.96135 | 7.5104e-05 | 6.2601e-05 | 0.066335 | 0.066335 | 0.066335 | 0.99871 | -0.026607 | 0.99867 | -0.027769 | 18.953
124 | 3.4444 | 1.4314 | -3.4444 | -1.4314 | 3.6045e-05 | 4.9081e-05 | 0.10785 | 0.10785 | 0.10785 | 0.99842 | -0.028715 | 0.99841 | -0.029878 | 8.3602
125 | 1.7945 | 0.82122 | -1.7944 | -0.82133 | 1.9762e-05 | -0.00010246 | 0.057045 | 0.057046 | 0.057046 | 0.99867 | -0.027769 | 0.99866 | -0.027685 | 25.93
126 | 0.22294 | 0.10723 | -0.22294 | -0.10797 | 2.1417e-06 | -0.00074222 | 0.0071588 | 0.0071681 | 0.0071681 | 0.99759 | 0.0094833 | 0.99758 | 0.0095663 | 3.2582
127 | -0.22294 | -0.10723 | 0.22298 | 0.10669 | 4.3839e-05 | -0.00054364 | 0.0071588 | 0.0071516 | 0.0071588 | 0.99759 | 0.0094833 | 0.99779 | 0.010826 | 3.4089
128 | 0.2976 | 0.14253 | -0.29755 | -0.1429 | 5.5916e-05 | -0.00037396 | 0.0095466 | 0.0095517 | 0.0095517 | 0.99779 | 0.010826 | 0.99759 | 0.0095416 | 4.5484
129 | 3.0475 | 1.2391 | -3.0471 | -1.2388 | 0.00037751 | 0.00037119 | 0.09512 | 0.095127 | 0.095127 | 0.99841 | -0.029878 | 0.99818 | -0.043781 | 7.3742
130 | 0.099196 | 0.047399 | -0.099195 | -0.047778 | 2.1395e-07 | -0.00037825 | 0.0031758 | 0.0031805 | 0.0031805 | 0.99932 | -0.0046521 | 0.99931 | -0.0046337 | 1.4457
131 | 0.099195 | 0.047778 | -0.099195 | -0.048042 | 1.5015e-07 | -0.00026476 | 0.0031805 | 0.0031839 | 0.0031839 | 0.99931 | -0.0046337 | 0.99931 | -0.0046206 | 1.4472
132 | 1.7944 | 0.82133 | -1.7935 | -0.82603 | 0.00090845 | -0.0047022 | 0.057046 | 0.057106 | 0.057106 | 0.99866 | -0.027685 | 0.99818 | -0.023791 | 25.9573
133 | 0.29755 | 0.1429 | -0.29754 | -0.14411 | 6.1813e-06 | -0.0012021 | 0.0095517 | 0.0095668 | 0.0095668 | 0.99759 | 0.0095416 | 0.99758 | 0.0097209 | 4.3485
134 | -0.94899 | -0.36671 | 0.94906 | 0.30266 | 6.7038e-05 | -0.064047 | 0.029431 | 0.028814 | 0.029431 | 0.99792 | -0.057105 | 0.99799 | -0.056348 | 2.3065
135 | 0.66574 | 0.22962 | -0.66572 | -0.27391 | 2.3187e-05 | -0.044288 | 0.020372 | 0.020825 | 0.020825 | 0.99792 | -0.057105 | 0.99788 | -0.057428 | 1.632
136 | 0.28325 | 0.13709 | -0.28325 | -0.13719 | 4.3325e-07 | -9.2981e-05 | 0.0091031 | 0.0091043 | 0.0091043 | 0.99792 | -0.057105 | 0.99792 | -0.057092 | 4.1383
137 | -0.94906 | -0.30266 | 0.94907 | 0.2984 | 4.3679e-06 | -0.0042649 | 0.028814 | 0.028777 | 0.028814 | 0.99799 | -0.056348 | 0.998 | -0.056289 | 2.2582
138 | 0.66572 | 0.27391 | -0.66571 | -0.27953 | 3.0197e-06 | -0.0056211 | 0.020825 | 0.020887 | 0.020887 | 0.99788 | -0.057428 | 0.99788 | -0.057461 | 1.6369
139 | -1.3525 | -0.49379 | 1.3526 | 0.4929 | 0.00014394 | -0.00089369 | 0.041647 | 0.041635 | 0.041647 | 0.998 | -0.056289 | 0.99818 | -0.043781 | 3.2285
140 | 0.25346 | 0.079863 | -0.25346 | -0.080519 | 4.7923e-08 | -0.00065603 | 0.0076876 | 0.0076934 | 0.0076934 | 0.99788 | -0.057461 | 0.99788 | -0.057463 | 0.60293
141 | 0.22222 | 0.10758 | -0.22221 | -0.10762 | 3.2504e-06 | -4.0526e-05 | 0.00714 | 0.0071406 | 0.0071406 | 0.99818 | -0.043781 | 0.99817 | -0.043877 | 3.4003
142 | 1.4723 | 0.63829 | -1.4721 | -0.69967 | 0.00016595 | -0.061386 | 0.046407 | 0.047143 | 0.047143 | 0.99818 | -0.043781 | 0.99807 | -0.044363 | 3.6946
143 | 0.23435 | 0.10976 | -0.23435 | -0.11222 | 7.7673e-06 | -0.0024576 | 0.007485 | 0.0075154 | 0.0075154 | 0.99807 | -0.044363 | 0.99804 | -0.044088 | 3.4161
144 | 1.2378 | 0.58991 | -1.2378 | -0.59181 | 3.6937e-06 | -0.0018996 | 0.039658 | 0.039682 | 0.039682 | 0.99807 | -0.044363 | 0.99806 | -0.044375 | 3.1099
145 | 0.25346 | 0.080519 | -0.25344 | -0.12209 | 1.2804e-05 | -0.041568 | 0.0076934 | 0.0081387 | 0.0081387 | 0.99788 | -0.057463 | 0.99782 | -0.057871 | 1.2757
146 | 0.88344 | 0.42021 | -0.88343 | -0.42198 | 3.4277e-06 | -0.001776 | 0.028295 | 0.028317 | 0.028317 | 0.99806 | -0.044375 | 0.99806 | -0.044454 | 3.3631
147 | 0.8067 | 0.38482 | -0.80668 | -0.38544 | 2.3448e-05 | -0.0006179 | 0.025852 | 0.025859 | 0.025859 | 0.99806 | -0.044454 | 0.99803 | -0.044209 | 11.7542
148 | 0.070077 | 0.033229 | -0.070077 | -0.033536 | 8.6874e-08 | -0.00030697 | 0.0022433 | 0.0022471 | 0.0022471 | 0.99804 | -0.044088 | 0.99803 | -0.044078 | 1.0214
149 | 0.16427 | 0.078993 | -0.16427 | -0.079558 | 8.83e-07 | -0.0005649 | 0.0052722 | 0.0052793 | 0.0052793 | 0.99804 | -0.044088 | 0.99803 | -0.044042 | 2.3997
150 | 0.73261 | 0.35152 | -0.73259 | -0.35201 | 1.5446e-05 | -0.00049338 | 0.023503 | 0.02351 | 0.02351 | 0.99803 | -0.044209 | 0.99801 | -0.044029 | 10.6861
151 | 0.074071 | 0.033917 | -0.07407 | -0.035369 | 4.5603e-07 | -0.0014521 | 0.0023564 | 0.0023742 | 0.0023742 | 0.99803 | -0.044209 | 0.99803 | -0.04416 | 1.0792
152 | 0.070077 | 0.033536 | -0.070077 | -0.03394 | 1.1479e-07 | -0.00040404 | 0.0022471 | 0.0022522 | 0.0022522 | 0.99803 | -0.044078 | 0.99803 | -0.044064 | 1.0237
153 | 0.73259 | 0.35201 | -0.73257 | -0.35264 | 1.9527e-05 | -0.00062335 | 0.02351 | 0.023517 | 0.023517 | 0.99801 | -0.044029 | 0.99799 | -0.043801 | 10.6897
154 | 0.07407 | 0.035369 | -0.07407 | -0.035874 | 1.6026e-07 | -0.00050509 | 0.0023742 | 0.0023805 | 0.0023805 | 0.99803 | -0.04416 | 0.99802 | -0.044141 | 1.082
155 | 0.25344 | 0.12209 | -0.25344 | -0.12275 | 2.4609e-06 | -0.00066016 | 0.0081387 | 0.008147 | 0.008147 | 0.99782 | -0.057871 | 0.99781 | -0.057787 | 3.7032
156 | 0.56281 | 0.27041 | -0.56279 | -0.27106 | 1.182e-05 | -0.00064165 | 0.018061 | 0.018069 | 0.018069 | 0.99799 | -0.043801 | 0.99797 | -0.04362 | 8.2133
157 | -0.29924 | -0.14493 | 0.29924 | 0.14465 | 1.4349e-06 | -0.00027593 | 0.0096182 | 0.0096147 | 0.0096182 | 0.99792 | -0.02158 | 0.99792 | -0.021622 | 4.3719
158 | -1.7243 | -0.79545 | 1.7246 | 0.7941 | 0.0002394 | -0.0013426 | 0.054932 | 0.054915 | 0.054932 | 0.99792 | -0.021622 | 0.99805 | -0.022699 | 24.9692
159 | 1.4251 | 0.65079 | -1.4238 | -0.66144 | 0.0012767 | -0.010651 | 0.04532 | 0.045453 | 0.045453 | 0.99792 | -0.021622 | 0.99708 | -0.014674 | 20.6605
160 | -1.7246 | -0.7941 | 1.7248 | 0.79286 | 0.00022229 | -0.0012478 | 0.054915 | 0.054899 | 0.054915 | 0.99805 | -0.022699 | 0.99817 | -0.023696 | 24.9615
161 | 1.2786 | 0.59181 | -1.2782 | -0.59609 | 0.00041308 | -0.0042846 | 0.04079 | 0.040844 | 0.040844 | 0.99708 | -0.014674 | 0.99678 | -0.012116 | 18.5655
162 | 0.14523 | 0.069639 | -0.14523 | -0.070337 | 8.5537e-07 | -0.00069788 | 0.0046631 | 0.0046718 | 0.0046718 | 0.99708 | -0.014674 | 0.99708 | -0.014623 | 2.1236
163 | -1.7935 | -0.82614 | 1.7935 | 0.82603 | 2.1991e-05 | -0.00011364 | 0.057107 | 0.057106 | 0.057107 | 0.99817 | -0.023696 | 0.99818 | -0.023791 | 25.9579
164 | 0.39199 | 0.18976 | -0.39199 | -0.18985 | 7.9114e-07 | -8.8132e-05 | 0.012612 | 0.012614 | 0.012614 | 0.99678 | -0.012116 | 0.99678 | -0.012099 | 5.7335
165 | 0.88618 | 0.40633 | -0.88543 | -0.42271 | 0.0007505 | -0.016375 | 0.028234 | 0.028437 | 0.028437 | 0.99678 | -0.012116 | 0.99599 | -0.0052932 | 12.9261
166 | 0.39189 | 0.18607 | -0.39185 | -0.18966 | 3.2262e-05 | -0.0035978 | 0.012574 | 0.012619 | 0.012619 | 0.99599 | -0.0052932 | 0.99592 | -0.0045922 | 5.7358
167 | 0.49354 | 0.23664 | -0.49353 | -0.23781 | 1.6657e-05 | -0.0011682 | 0.015864 | 0.015879 | 0.015879 | 0.99599 | -0.0052932 | 0.99596 | -0.0050042 | 7.2176
168 | 0.39185 | 0.18966 | -0.39182 | -0.18977 | 2.9582e-05 | -0.00010491 | 0.012619 | 0.01262 | 0.01262 | 0.99592 | -0.0045922 | 0.99584 | -0.0050905 | 6.0097
169 | 0.089896 | 0.042321 | -0.089888 | -0.042922 | 7.5872e-06 | -0.00060162 | 0.0028799 | 0.0028874 | 0.0028874 | 0.99596 | -0.0050042 | 0.99587 | -0.0056052 | 1.375
170 | 0.089888 | 0.042922 | -0.089888 | -0.043535 | 2.8861e-07 | -0.00061231 | 0.0028874 | 0.0028951 | 0.0028951 | 0.99587 | -0.0056052 | 0.99587 | -0.0055777 | 1.316
171 | 0.062669 | 0.029591 | -0.062669 | -0.030352 | 1.7236e-07 | -0.00076082 | 0.0020044 | 0.0020139 | 0.0020139 | 0.99814 | -0.014008 | 0.99814 | -0.013985 | 0.91539
172 | 0.23299 | 0.11274 | -0.23299 | -0.11284 | 3.1895e-07 | -9.9991e-05 | 0.0075101 | 0.0075113 | 0.0075113 | 0.9949 | -0.022703 | 0.9949 | -0.022691 | 3.4142
173 | 0.22303 | 0.10793 | -0.22302 | -0.10801 | 6.5561e-06 | -7.9992e-05 | 0.0071895 | 0.0071906 | 0.0071906 | 0.99486 | -0.022351 | 0.99483 | -0.022545 | 3.4241
174 | 0.1665 | 0.080315 | -0.16649 | -0.080632 | 1.4166e-05 | -0.00031735 | 0.005364 | 0.0053681 | 0.0053681 | 0.99486 | -0.022351 | 0.99477 | -0.022916 | 2.5562
175 | 0.28428 | 0.12965 | -0.28428 | -0.13048 | 3.8361e-06 | -0.00083478 | 0.0090371 | 0.0090471 | 0.0090471 | 0.99808 | 0.010726 | 0.99806 | 0.010828 | 4.1123
176 | 0.18764 | 0.084954 | -0.18764 | -0.085393 | 8.772e-07 | -0.00043962 | 0.0059577 | 0.005963 | 0.005963 | 0.99804 | 0.010989 | 0.99804 | 0.011024 | 2.7105
177 | -0.28427 | -0.13175 | 0.28428 | 0.13048 | 5.8689e-06 | -0.0012735 | 0.0090626 | 0.0090471 | 0.0090626 | 0.99804 | 0.010989 | 0.99806 | 0.010828 | 4.1194
178 | 0.18764 | 0.085393 | -0.18763 | -0.089943 | 9.1719e-06 | -0.0045501 | 0.005963 | 0.0060187 | 0.0060187 | 0.99804 | 0.011024 | 0.99799 | 0.011416 | 2.7358
179 | 0.18763 | 0.089943 | -0.18763 | -0.090874 | 1.8983e-06 | -0.00093105 | 0.0060187 | 0.0060304 | 0.0060304 | 0.99799 | 0.011416 | 0.99799 | 0.011503 | 2.7411
180 | 0.56279 | 0.27106 | -0.56278 | -0.27178 | 1.3396e-05 | -0.00072647 | 0.018069 | 0.018078 | 0.018078 | 0.99797 | -0.04362 | 0.99795 | -0.043415 | 8.2175
181 | 0.40653 | 0.19611 | -0.40652 | -0.19678 | 6.473e-06 | -0.00067396 | 0.013056 | 0.013065 | 0.013065 | 0.99795 | -0.043415 | 0.99793 | -0.043277 | 5.9386
182 | 0.40652 | 0.19678 | -0.40652 | -0.19689 | 1.0248e-06 | -0.00010662 | 0.013065 | 0.013066 | 0.013066 | 0.99793 | -0.043277 | 0.99793 | -0.043255 | 5.9392

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 22.4749 | 9.7247

## res_load
| p_mw | q_mvar
0 | 0.34771 | 0.16841
1 | 0.3682 | 0.17833
2 | 0.086941 | 0.042107
3 | 0.31231 | 0.15126
4 | 0.074206 | 0.035939
5 | 0.13541 | 0.065584
6 | 0.091419 | 0.044276
7 | 0.38389 | 0.18593
8 | 0.10178 | 0.049295
9 | 0.078262 | 0.037904
10 | 0.079404 | 0.038457
11 | 0.3988 | 0.19315
12 | 0.26978 | 0.13066
13 | 0.13727 | 0.066482
14 | 0.079758 | 0.038629
15 | 0.38152 | 0.18478
16 | 0.31409 | 0.15212
17 | 0.38325 | 0.18562
18 | 0.077145 | 0.037363
19 | 0.13229 | 0.064069
20 | 0.33002 | 0.15984
21 | 0.095545 | 0.046274
22 | 0.18602 | 0.090092
23 | 0.40985 | 0.1985
24 | 0.11122 | 0.053867
25 | 0.31057 | 0.15042
26 | 0.27961 | 0.13542
27 | 0.2502 | 0.12118
28 | 0.085073 | 0.041203
29 | 0.55931 | 0.27089
30 | 0.35439 | 0.17164
31 | 0.34125 | 0.16527
32 | 0.48922 | 0.23694
33 | 0.31489 | 0.15251
34 | 0.6215 | 0.30101
35 | 0.070766 | 0.034274
36 | 0.38526 | 0.18659
37 | 0.32589 | 0.15784
38 | 0.22939 | 0.1111
39 | 0.21079 | 0.10209
40 | 0.12687 | 0.061444
41 | 0.34595 | 0.16755
42 | 0.071149 | 0.034459
43 | 0.39804 | 0.19278
44 | 0.068369 | 0.033112
45 | 0.28997 | 0.14044
46 | 0.39105 | 0.1894
47 | 0.24644 | 0.11936
48 | 0.32485 | 0.15733
49 | 0.38578 | 0.18684
50 | 0.33754 | 0.16348
51 | 0.36034 | 0.17452
52 | 0.32784 | 0.15878
53 | 0.19764 | 0.095721
54 | 0.086286 | 0.04179
55 | 0.19152 | 0.092755
56 | 0.11008 | 0.053315
57 | 0.22109 | 0.10708
58 | 0.26556 | 0.12862
59 | 0.28933 | 0.14013
60 | 0.22294 | 0.10797
61 | 0.15724 | 0.076156
62 | 0.3969 | 0.19223
63 | 0.29754 | 0.14411
64 | 0.28325 | 0.13719
65 | 0.40343 | 0.19539
66 | 0.41226 | 0.19967
67 | 0.22221 | 0.10762
68 | 0.099195 | 0.048042
69 | 0.35431 | 0.1716
70 | 0.076733 | 0.037163
71 | 0.16427 | 0.079558
72 | 0.25344 | 0.12275
73 | 0.070077 | 0.03394
74 | 0.16977 | 0.082221
75 | 0.07407 | 0.035874
76 | 0.29924 | 0.14493
77 | 0.068728 | 0.033287
78 | 0.14523 | 0.070337
79 | 0.40363 | 0.19549
80 | 0.39182 | 0.18977
81 | 0.39199 | 0.18985
82 | 0.19964 | 0.096692
83 | 0.062669 | 0.030352
84 | 0.089888 | 0.043535
85 | 0.23299 | 0.11284
86 | 0.22302 | 0.10801
87 | 0.16649 | 0.080632
88 | 0.096631 | 0.046801
89 | 0.18763 | 0.090874
90 | 0.15625 | 0.075676
91 | 0.40652 | 0.19689

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1