## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_589_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_589_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_589_0_node_1 | 20 | n |  | TRUE
3 | bus_MV_589_0_node_8 | 20 | n |  | TRUE
4 | bus_MV_589_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_589_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_589_0_node_7 | 20 | n |  | TRUE
7 | bus_MV_589_0_node_5 | 20 | n |  | TRUE
8 | bus_MV_589_0_node_6 | 20 | n |  | TRUE
9 | bus_MV_589_0_node_73 | 20 | n |  | TRUE
10 | bus_MV_589_0_node_74 | 20 | n |  | TRUE
11 | bus_MV_589_0_node_81 | 20 | n |  | TRUE
12 | bus_MV_589_0_node_79 | 20 | n |  | TRUE
13 | bus_MV_589_0_node_31 | 20 | n |  | TRUE
14 | bus_MV_589_0_node_135 | 20 | n |  | TRUE
15 | bus_MV_589_0_node_75 | 20 | n |  | TRUE
16 | bus_MV_589_0_node_80 | 20 | n |  | TRUE
17 | bus_MV_589_0_node_109 | 20 | n |  | TRUE
18 | bus_MV_589_0_node_104 | 20 | n |  | TRUE
19 | bus_MV_589_0_node_101 | 20 | n |  | TRUE
20 | bus_MV_589_0_node_133 | 20 | n |  | TRUE
21 | bus_MV_589_0_node_12 | 20 | n |  | TRUE
22 | bus_MV_589_0_node_166 | 20 | n |  | TRUE
23 | bus_MV_589_0_node_178 | 20 | n |  | TRUE
24 | bus_MV_589_0_node_142 | 20 | n |  | TRUE
25 | bus_MV_589_0_node_10 | 20 | n |  | TRUE
26 | bus_MV_589_0_node_11 | 20 | n |  | TRUE
27 | bus_MV_589_0_node_136 | 20 | n |  | TRUE
28 | bus_MV_589_0_node_137 | 20 | n |  | TRUE
29 | bus_MV_589_0_node_116 | 20 | n |  | TRUE
30 | bus_MV_589_0_node_14 | 20 | n |  | TRUE
31 | bus_MV_589_0_node_15 | 20 | n |  | TRUE
32 | bus_MV_589_0_node_16 | 20 | n |  | TRUE
33 | bus_MV_589_0_node_19 | 20 | n |  | TRUE
34 | bus_MV_589_0_node_121 | 20 | n |  | TRUE
35 | bus_MV_589_0_node_120 | 20 | n |  | TRUE
36 | bus_MV_589_0_node_17 | 20 | n |  | TRUE
37 | bus_MV_589_0_node_20 | 20 | n |  | TRUE
38 | bus_MV_589_0_node_65 | 20 | n |  | TRUE
39 | bus_MV_589_0_node_18 | 20 | n |  | TRUE
40 | bus_MV_589_0_node_30 | 20 | n |  | TRUE
41 | bus_MV_589_0_node_175 | 20 | n |  | TRUE
42 | bus_MV_589_0_node_179 | 20 | n |  | TRUE
43 | bus_MV_589_0_node_149 | 20 | n |  | TRUE
44 | bus_MV_589_0_node_122 | 20 | n |  | TRUE
45 | bus_MV_589_0_node_123 | 20 | n |  | TRUE
46 | bus_MV_589_0_node_128 | 20 | n |  | TRUE
47 | bus_MV_589_0_node_176 | 20 | n |  | TRUE
48 | bus_MV_589_0_node_29 | 20 | n |  | TRUE
49 | bus_MV_589_0_node_21 | 20 | n |  | TRUE
50 | bus_MV_589_0_node_22 | 20 | n |  | TRUE
51 | bus_MV_589_0_node_23 | 20 | n |  | TRUE
52 | bus_MV_589_0_node_24 | 20 | n |  | TRUE
53 | bus_MV_589_0_node_25 | 20 | n |  | TRUE
54 | bus_MV_589_0_node_28 | 20 | n |  | TRUE
55 | bus_MV_589_0_node_82 | 20 | n |  | TRUE
56 | bus_MV_589_0_node_26 | 20 | n |  | TRUE
57 | bus_MV_589_0_node_119 | 20 | n |  | TRUE
58 | bus_MV_589_0_node_124 | 20 | n |  | TRUE
59 | bus_MV_589_0_node_27 | 20 | n |  | TRUE
60 | bus_MV_589_0_node_118 | 20 | n |  | TRUE
61 | bus_MV_589_0_node_171 | 20 | n |  | TRUE
62 | bus_MV_589_0_node_43 | 20 | n |  | TRUE
63 | bus_MV_589_0_node_125 | 20 | n |  | TRUE
64 | bus_MV_589_0_node_72 | 20 | n |  | TRUE
65 | bus_MV_589_0_node_32 | 20 | n |  | TRUE
66 | bus_MV_589_0_node_33 | 20 | n |  | TRUE
67 | bus_MV_589_0_node_34 | 20 | n |  | TRUE
68 | bus_MV_589_0_node_40 | 20 | n |  | TRUE
69 | bus_MV_589_0_node_42 | 20 | n |  | TRUE
70 | bus_MV_589_0_node_35 | 20 | n |  | TRUE
71 | bus_MV_589_0_node_38 | 20 | n |  | TRUE
72 | bus_MV_589_0_node_111 | 20 | n |  | TRUE
73 | bus_MV_589_0_node_36 | 20 | n |  | TRUE
74 | bus_MV_589_0_node_39 | 20 | n |  | TRUE
75 | bus_MV_589_0_node_151 | 20 | n |  | TRUE
76 | bus_MV_589_0_node_37 | 20 | n |  | TRUE
77 | bus_MV_589_0_node_96 | 20 | n |  | TRUE
78 | bus_MV_589_0_node_41 | 20 | n |  | TRUE
79 | bus_MV_589_0_node_98 | 20 | n |  | TRUE
80 | bus_MV_589_0_node_150 | 20 | n |  | TRUE
81 | bus_MV_589_0_node_165 | 20 | n |  | TRUE
82 | bus_MV_589_0_node_97 | 20 | n |  | TRUE
83 | bus_MV_589_0_node_112 | 20 | n |  | TRUE
84 | bus_MV_589_0_node_110 | 20 | n |  | TRUE
85 | bus_MV_589_0_node_99 | 20 | n |  | TRUE
86 | bus_MV_589_0_node_68 | 20 | n |  | TRUE
87 | bus_MV_589_0_node_113 | 20 | n |  | TRUE
88 | bus_MV_589_0_node_44 | 20 | n |  | TRUE
89 | bus_MV_589_0_node_46 | 20 | n |  | TRUE
90 | bus_MV_589_0_node_45 | 20 | n |  | TRUE
91 | bus_MV_589_0_node_174 | 20 | n |  | TRUE
92 | bus_MV_589_0_node_47 | 20 | n |  | TRUE
93 | bus_MV_589_0_node_167 | 20 | n |  | TRUE
94 | bus_MV_589_0_node_48 | 20 | n |  | TRUE
95 | bus_MV_589_0_node_50 | 20 | n |  | TRUE
96 | bus_MV_589_0_node_173 | 20 | n |  | TRUE
97 | bus_MV_589_0_node_51 | 20 | n |  | TRUE
98 | bus_MV_589_0_node_114 | 20 | n |  | TRUE
99 | bus_MV_589_0_node_52 | 20 | n |  | TRUE
100 | bus_MV_589_0_node_56 | 20 | n |  | TRUE
101 | bus_MV_589_0_node_53 | 20 | n |  | TRUE
102 | bus_MV_589_0_node_54 | 20 | n |  | TRUE
103 | bus_MV_589_0_node_55 | 20 | n |  | TRUE
104 | bus_MV_589_0_node_168 | 20 | n |  | TRUE
105 | bus_MV_589_0_node_141 | 20 | n |  | TRUE
106 | bus_MV_589_0_node_140 | 20 | n |  | TRUE
107 | bus_MV_589_0_node_57 | 20 | n |  | TRUE
108 | bus_MV_589_0_node_95 | 20 | n |  | TRUE
109 | bus_MV_589_0_node_58 | 20 | n |  | TRUE
110 | bus_MV_589_0_node_59 | 20 | n |  | TRUE
111 | bus_MV_589_0_node_94 | 20 | n |  | TRUE
112 | bus_MV_589_0_node_60 | 20 | n |  | TRUE
113 | bus_MV_589_0_node_130 | 20 | n |  | TRUE
114 | bus_MV_589_0_node_180 | 20 | n |  | TRUE
115 | bus_MV_589_0_node_62 | 20 | n |  | TRUE
116 | bus_MV_589_0_node_61 | 20 | n |  | TRUE
117 | bus_MV_589_0_node_63 | 20 | n |  | TRUE
118 | bus_MV_589_0_node_131 | 20 | n |  | TRUE
119 | bus_MV_589_0_node_170 | 20 | n |  | TRUE
120 | bus_MV_589_0_node_177 | 20 | n |  | TRUE
121 | bus_MV_589_0_node_64 | 20 | n |  | TRUE
122 | bus_MV_589_0_node_102 | 20 | n |  | TRUE
123 | bus_MV_589_0_node_100 | 20 | n |  | TRUE
124 | bus_MV_589_0_node_132 | 20 | n |  | TRUE
125 | bus_MV_589_0_node_105 | 20 | n |  | TRUE
126 | bus_MV_589_0_node_66 | 20 | n |  | TRUE
127 | bus_MV_589_0_node_67 | 20 | n |  | TRUE
128 | bus_MV_589_0_node_69 | 20 | n |  | TRUE
129 | bus_MV_589_0_node_169 | 20 | n |  | TRUE
130 | bus_MV_589_0_node_70 | 20 | n |  | TRUE
131 | bus_MV_589_0_node_71 | 20 | n |  | TRUE
132 | bus_MV_589_0_node_78 | 20 | n |  | TRUE
133 | bus_MV_589_0_node_76 | 20 | n |  | TRUE
134 | bus_MV_589_0_node_89 | 20 | n |  | TRUE
135 | bus_MV_589_0_node_88 | 20 | n |  | TRUE
136 | bus_MV_589_0_node_77 | 20 | n |  | TRUE
137 | bus_MV_589_0_node_172 | 20 | n |  | TRUE
138 | bus_MV_589_0_node_87 | 20 | n |  | TRUE
139 | bus_MV_589_0_node_90 | 20 | n |  | TRUE
140 | bus_MV_589_0_node_93 | 20 | n |  | TRUE
141 | bus_MV_589_0_node_108 | 20 | n |  | TRUE
142 | bus_MV_589_0_node_181 | 20 | n |  | TRUE
143 | bus_MV_589_0_node_103 | 20 | n |  | TRUE
144 | bus_MV_589_0_node_134 | 20 | n |  | TRUE
145 | bus_MV_589_0_node_83 | 20 | n |  | TRUE
146 | bus_MV_589_0_node_84 | 20 | n |  | TRUE
147 | bus_MV_589_0_node_154 | 20 | n |  | TRUE
148 | bus_MV_589_0_node_85 | 20 | n |  | TRUE
149 | bus_MV_589_0_node_153 | 20 | n |  | TRUE
150 | bus_MV_589_0_node_86 | 20 | n |  | TRUE
151 | bus_MV_589_0_node_91 | 20 | n |  | TRUE
152 | bus_MV_589_0_node_92 | 20 | n |  | TRUE
153 | bus_MV_589_0_node_106 | 20 | n |  | TRUE
154 | bus_MV_589_0_node_107 | 20 | n |  | TRUE
155 | bus_MV_589_0_node_115 | 20 | n |  | TRUE
156 | bus_MV_589_0_node_117 | 20 | n |  | TRUE
157 | bus_MV_589_0_node_139 | 20 | n |  | TRUE
158 | bus_MV_589_0_node_148 | 20 | n |  | TRUE
159 | bus_MV_589_0_node_144 | 20 | n |  | TRUE
160 | bus_MV_589_0_node_143 | 20 | n |  | TRUE
161 | bus_MV_589_0_node_138 | 20 | n |  | TRUE
162 | bus_MV_589_0_node_145 | 20 | n |  | TRUE
163 | bus_MV_589_0_node_126 | 20 | n |  | TRUE
164 | bus_MV_589_0_node_127 | 20 | n |  | TRUE
165 | bus_MV_589_0_node_147 | 20 | n |  | TRUE
166 | bus_MV_589_0_node_146 | 20 | n |  | TRUE
167 | bus_MV_589_0_node_152 | 20 | n |  | TRUE
168 | bus_MV_589_0_node_155 | 20 | n |  | TRUE
169 | bus_MV_589_0_node_156 | 20 | n |  | TRUE
170 | bus_MV_589_0_node_164 | 20 | n |  | TRUE
171 | bus_MV_589_0_node_163 | 20 | n |  | TRUE
172 | bus_MV_589_0_node_162 | 20 | n |  | TRUE
173 | bus_MV_589_0_node_157 | 20 | n |  | TRUE
174 | bus_MV_589_0_node_158 | 20 | n |  | TRUE
175 | bus_MV_589_0_node_159 | 20 | n |  | TRUE
176 | bus_MV_589_0_node_160 | 20 | n |  | TRUE
177 | bus_MV_589_0_node_161 | 20 | n |  | TRUE
178 | bus_HV_589_0_node_133 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_589_0_load_0 | 0 | 0.21316 | 0.10324 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_589_0_load_73 | 9 | 0.22907 | 0.11094 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_589_0_load_74 | 10 | 0.24478 | 0.11855 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_589_0_load_79 | 12 | 0.22911 | 0.11096 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_589_0_load_31 | 13 | 0.24191 | 0.11716 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_589_0_load_135 | 14 | 0.10549 | 0.051091 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_589_0_load_109 | 17 | 0.16864 | 0.081675 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_589_0_load_133 | 20 | 0.081656 | 0.039548 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_589_0_load_12 | 21 | 0.10252 | 0.049651 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_589_0_load_166 | 22 | 0.35749 | 0.17314 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_589_0_load_178 | 23 | 0.40392 | 0.19563 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_589_0_load_10 | 25 | 0.2934 | 0.1421 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_589_0_load_136 | 27 | 0.073415 | 0.035556 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_589_0_load_137 | 28 | 0.30184 | 0.14619 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_589_0_load_14 | 30 | 0.29787 | 0.14426 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_589_0_load_120 | 35 | 0.12767 | 0.061833 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_589_0_load_65 | 38 | 0.23247 | 0.11259 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_589_0_load_175 | 41 | 0.14848 | 0.071914 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_589_0_load_179 | 42 | 0.29829 | 0.14447 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_589_0_load_149 | 43 | 0.069871 | 0.03384 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_589_0_load_123 | 45 | 0.072549 | 0.035137 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_589_0_load_128 | 46 | 0.37607 | 0.18214 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_589_0_load_176 | 47 | 0.18318 | 0.088716 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_589_0_load_29 | 48 | 0.10749 | 0.052057 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_589_0_load_21 | 49 | 0.15462 | 0.074885 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_589_0_load_82 | 55 | 0.40291 | 0.19514 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_589_0_load_119 | 57 | 0.13477 | 0.065273 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_589_0_load_118 | 60 | 0.1123 | 0.054388 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_589_0_load_171 | 61 | 0.18248 | 0.088377 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_589_0_load_125 | 63 | 0.22537 | 0.10915 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_589_0_load_32 | 65 | 0.35102 | 0.17001 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_589_0_load_34 | 67 | 0.075393 | 0.036515 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_589_0_load_111 | 72 | 0.27476 | 0.13307 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_589_0_load_151 | 75 | 0.085724 | 0.041518 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_589_0_load_96 | 77 | 0.070441 | 0.034116 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_589_0_load_98 | 79 | 0.19787 | 0.095831 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_589_0_load_150 | 80 | 0.27032 | 0.13092 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_589_0_load_165 | 81 | 0.368 | 0.17823 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_589_0_load_97 | 82 | 0.072566 | 0.035145 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_589_0_load_112 | 83 | 0.08322 | 0.040305 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_589_0_load_110 | 84 | 0.11067 | 0.0536 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_589_0_load_99 | 85 | 0.096876 | 0.046919 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_589_0_load_44 | 88 | 0.31616 | 0.15313 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_589_0_load_174 | 91 | 0.081444 | 0.039445 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_589_0_load_167 | 93 | 0.10673 | 0.051693 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_589_0_load_50 | 95 | 0.39661 | 0.19209 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_589_0_load_173 | 96 | 0.25631 | 0.12414 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_589_0_load_56 | 100 | 0.29532 | 0.14303 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_589_0_load_53 | 101 | 0.37924 | 0.18368 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_589_0_load_168 | 104 | 0.33285 | 0.1612 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_589_0_load_140 | 106 | 0.10683 | 0.051741 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_589_0_load_57 | 107 | 0.33233 | 0.16096 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_589_0_load_95 | 108 | 0.080916 | 0.039189 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_589_0_load_94 | 111 | 1.2145 | 0.58821 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_589_0_load_130 | 113 | 0.29733 | 0.144 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_589_0_load_180 | 114 | 0.41231 | 0.19969 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_589_0_load_131 | 118 | 0.75296 | 0.36467 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_589_0_load_170 | 119 | 0.15866 | 0.076844 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_589_0_load_177 | 120 | 0.2572 | 0.12457 | 0 | 0 |  | 1 | TRUE | wye
59 | MV_589_0_load_100 | 123 | 0.18866 | 0.091372 | 0 | 0 |  | 1 | TRUE | wye
60 | MV_589_0_load_132 | 124 | 0.72025 | 0.34883 | 0 | 0 |  | 1 | TRUE | wye
61 | MV_589_0_load_105 | 125 | 0.25195 | 0.12203 | 0 | 0 |  | 1 | TRUE | wye
62 | MV_589_0_load_66 | 126 | 0.3872 | 0.18753 | 0 | 0 |  | 1 | TRUE | wye
63 | MV_589_0_load_169 | 129 | 0.31332 | 0.15175 | 0 | 0 |  | 1 | TRUE | wye
64 | MV_589_0_load_70 | 130 | 0.40425 | 0.19579 | 0 | 0 |  | 1 | TRUE | wye
65 | MV_589_0_load_88 | 135 | 0.38708 | 0.18747 | 0 | 0 |  | 1 | TRUE | wye
66 | MV_589_0_load_172 | 137 | 0.30509 | 0.14776 | 0 | 0 |  | 1 | TRUE | wye
67 | MV_589_0_load_87 | 138 | 0.27228 | 0.13187 | 0 | 0 |  | 1 | TRUE | wye
68 | MV_589_0_load_90 | 139 | 0.26105 | 0.12643 | 0 | 0 |  | 1 | TRUE | wye
69 | MV_589_0_load_108 | 141 | 0.17147 | 0.083045 | 0 | 0 |  | 1 | TRUE | wye
70 | MV_589_0_load_181 | 142 | 0.3833 | 0.18564 | 0 | 0 |  | 1 | TRUE | wye
71 | MV_589_0_load_103 | 143 | 0.32303 | 0.15645 | 0 | 0 |  | 1 | TRUE | wye
72 | MV_589_0_load_134 | 144 | 0.12644 | 0.061235 | 0 | 0 |  | 1 | TRUE | wye
73 | MV_589_0_load_83 | 145 | 0.34362 | 0.16642 | 0 | 0 |  | 1 | TRUE | wye
74 | MV_589_0_load_154 | 147 | 0.23998 | 0.11623 | 0 | 0 |  | 1 | TRUE | wye
75 | MV_589_0_load_86 | 150 | 0.19702 | 0.095419 | 0 | 0 |  | 1 | TRUE | wye
76 | MV_589_0_load_91 | 151 | 0.31633 | 0.1532 | 0 | 0 |  | 1 | TRUE | wye
77 | MV_589_0_load_106 | 153 | 0.25566 | 0.12382 | 0 | 0 |  | 1 | TRUE | wye
78 | MV_589_0_load_107 | 154 | 0.49188 | 0.23823 | 0 | 0 |  | 1 | TRUE | wye
79 | MV_589_0_load_148 | 158 | 0.070301 | 0.034048 | 0 | 0 |  | 1 | TRUE | wye
80 | MV_589_0_load_144 | 159 | 0.17757 | 0.086001 | 0 | 0 |  | 1 | TRUE | wye
81 | MV_589_0_load_143 | 160 | 0.071137 | 0.034453 | 0 | 0 |  | 1 | TRUE | wye
82 | MV_589_0_load_138 | 161 | 0.073017 | 0.035364 | 0 | 0 |  | 1 | TRUE | wye
83 | MV_589_0_load_126 | 163 | 0.092604 | 0.04485 | 0 | 0 |  | 1 | TRUE | wye
84 | MV_589_0_load_146 | 166 | 0.13581 | 0.065776 | 0 | 0 |  | 1 | TRUE | wye
85 | MV_589_0_load_152 | 167 | 0.072563 | 0.035144 | 0 | 0 |  | 1 | TRUE | wye
86 | MV_589_0_load_164 | 170 | 0.12324 | 0.059689 | 0 | 0 |  | 1 | TRUE | wye
87 | MV_589_0_load_163 | 171 | 0.10777 | 0.052195 | 0 | 0 |  | 1 | TRUE | wye
88 | MV_589_0_load_157 | 173 | 0.32852 | 0.15911 | 0 | 0 |  | 1 | TRUE | wye
89 | MV_589_0_load_158 | 174 | 0.131 | 0.063445 | 0 | 0 |  | 1 | TRUE | wye
90 | MV_589_0_load_161 | 177 | 0.084294 | 0.040826 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_589_0_line_0 |  | 0 | 1 | 0.040228 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
1 | MV_589_0_line_1 |  | 0 | 2 | 0.108 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
2 | MV_589_0_line_2 |  | 1 | 3 | 0.31222 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
3 | MV_589_0_line_3 |  | 2 | 4 | 0.5515 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
4 | MV_589_0_line_4 |  | 3 | 14 | 0.04426 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
5 | MV_589_0_line_5 |  | 4 | 5 | 0.48162 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
6 | MV_589_0_line_6 |  | 4 | 6 | 0.5758 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_589_0_line_7 |  | 5 | 7 | 0.12864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_589_0_line_8 |  | 5 | 8 | 0.32503 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
9 | MV_589_0_line_9 |  | 5 | 9 | 0.032578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_589_0_line_10 |  | 6 | 13 | 0.14981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_589_0_line_11 |  | 7 | 10 | 0.081333 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_589_0_line_12 |  | 8 | 11 | 0.11924 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
13 | MV_589_0_line_13 |  | 8 | 12 | 0.002884 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_589_0_line_14 |  | 10 | 15 | 0.005418 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_589_0_line_15 |  | 11 | 18 | 0.1117 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_589_0_line_16 |  | 11 | 19 | 0.066441 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
17 | MV_589_0_line_17 |  | 11 | 20 | 0.0073422 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
18 | MV_589_0_line_18 |  | 11 | 16 | 0.057655 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_589_0_line_19 |  | 14 | 21 | 0.1452 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
20 | MV_589_0_line_20 |  | 15 | 132 | 0.35784 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_589_0_line_21 |  | 16 | 17 | 0.012749 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_589_0_line_22 |  | 17 | 141 | 0.010642 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_589_0_line_23 |  | 18 | 142 | 0.024524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_589_0_line_24 |  | 19 | 143 | 0.008409 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_589_0_line_25 |  | 19 | 123 | 0.034497 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
26 | MV_589_0_line_26 |  | 20 | 144 | 0.0027396 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_589_0_line_27 |  | 21 | 25 | 0.06085 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
28 | MV_589_0_line_28 |  | 22 | 23 | 0.20102 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_589_0_line_29 |  | 22 | 24 | 0.094071 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
30 | MV_589_0_line_30 |  | 24 | 103 | 0.23806 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_589_0_line_31 |  | 25 | 26 | 0.22022 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
32 | MV_589_0_line_32 |  | 26 | 27 | 0.11537 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
33 | MV_589_0_line_33 |  | 27 | 28 | 0.016853 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
34 | MV_589_0_line_34 |  | 27 | 29 | 0.023795 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
35 | MV_589_0_line_35 |  | 29 | 155 | 0.059268 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
36 | MV_589_0_line_36 |  | 30 | 31 | 0.062771 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_589_0_line_37 |  | 31 | 32 | 0.52882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_589_0_line_38 |  | 31 | 33 | 0.33852 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_589_0_line_39 |  | 32 | 34 | 0.047403 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_589_0_line_40 |  | 32 | 35 | 0.0095174 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_589_0_line_41 |  | 33 | 37 | 0.32011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_589_0_line_42 |  | 33 | 42 | 0.02692 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_589_0_line_43 |  | 34 | 44 | 0.089904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_589_0_line_44 |  | 34 | 45 | 0.025905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_589_0_line_45 |  | 36 | 37 | 0.49058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_589_0_line_46 |  | 36 | 38 | 0.068382 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_589_0_line_47 |  | 37 | 43 | 0.067311 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_589_0_line_48 |  | 37 | 39 | 0.25194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_589_0_line_49 |  | 39 | 40 | 0.22925 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_589_0_line_50 |  | 39 | 41 | 0.049276 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
51 | MV_589_0_line_51 |  | 40 | 48 | 0.13961 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_589_0_line_52 |  | 44 | 46 | 0.047824 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_589_0_line_53 |  | 44 | 47 | 0.10613 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_589_0_line_54 |  | 45 | 56 | 0.0074542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_589_0_line_55 |  | 46 | 164 | 0.023559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_589_0_line_56 |  | 49 | 50 | 0.005262 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_589_0_line_57 |  | 49 | 51 | 0.055512 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_589_0_line_58 |  | 50 | 52 | 0.20995 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_589_0_line_59 |  | 51 | 53 | 0.20564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_589_0_line_60 |  | 51 | 54 | 0.48936 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_589_0_line_61 |  | 52 | 55 | 0.007578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_589_0_line_62 |  | 53 | 56 | 0.14078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_589_0_line_63 |  | 53 | 57 | 0.01909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_589_0_line_64 |  | 54 | 61 | 0.031122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_589_0_line_65 |  | 55 | 62 | 0.004978 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_589_0_line_66 |  | 56 | 58 | 0.093716 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_589_0_line_67 |  | 56 | 59 | 0.15971 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_589_0_line_68 |  | 58 | 63 | 0.031272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_589_0_line_69 |  | 59 | 60 | 0.027488 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_589_0_line_70 |  | 60 | 64 | 0.041393 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_589_0_line_71 |  | 62 | 71 | 0.15888 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_589_0_line_72 |  | 64 | 131 | 0.077627 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_589_0_line_73 |  | 65 | 66 | 0.004153 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_589_0_line_74 |  | 65 | 67 | 0.0348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_589_0_line_75 |  | 66 | 68 | 0.10831 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_589_0_line_76 |  | 66 | 69 | 0.23011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_589_0_line_77 |  | 68 | 81 | 0.006279 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_589_0_line_78 |  | 69 | 83 | 0.01252 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_589_0_line_79 |  | 69 | 76 | 0.29337 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_589_0_line_80 |  | 70 | 71 | 0.20996 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_589_0_line_81 |  | 70 | 72 | 0.0097257 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_589_0_line_82 |  | 71 | 74 | 0.20615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_589_0_line_83 |  | 71 | 78 | 0.071814 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_589_0_line_84 |  | 71 | 79 | 0.0070001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_589_0_line_85 |  | 71 | 76 | 0.14952 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
86 | MV_589_0_line_86 |  | 72 | 84 | 0.00082716 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_589_0_line_87 |  | 73 | 74 | 0.0087215 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_589_0_line_88 |  | 73 | 75 | 0.039551 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_589_0_line_89 |  | 74 | 80 | 0.051077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_589_0_line_90 |  | 76 | 77 | 0.009101 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_589_0_line_91 |  | 78 | 82 | 0.020691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_589_0_line_92 |  | 79 | 85 | 0.020707 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_589_0_line_93 |  | 82 | 86 | 0.002384 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_589_0_line_94 |  | 83 | 87 | 0.02748 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
95 | MV_589_0_line_95 |  | 86 | 127 | 0.2823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_589_0_line_96 |  | 87 | 98 | 0.0392 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_589_0_line_97 |  | 87 | 155 | 0.26512 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
98 | MV_589_0_line_98 |  | 88 | 89 | 0.025534 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_589_0_line_99 |  | 88 | 90 | 0.049156 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_589_0_line_100 |  | 89 | 91 | 0.068652 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
101 | MV_589_0_line_101 |  | 90 | 92 | 0.080546 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_589_0_line_102 |  | 91 | 96 | 0.034711 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
103 | MV_589_0_line_103 |  | 92 | 93 | 0.002832 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_589_0_line_104 |  | 92 | 94 | 0.098945 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_589_0_line_105 |  | 94 | 95 | 0.02857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_589_0_line_106 |  | 95 | 97 | 0.027058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_589_0_line_107 |  | 96 | 98 | 0.011371 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_589_0_line_108 |  | 97 | 99 | 0.19016 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_589_0_line_109 |  | 99 | 100 | 0.004319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_589_0_line_110 |  | 101 | 102 | 0.039279 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
111 | MV_589_0_line_111 |  | 102 | 103 | 0.35834 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_589_0_line_112 |  | 103 | 104 | 0.045833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_589_0_line_113 |  | 103 | 105 | 0.058421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_589_0_line_114 |  | 105 | 106 | 0.021039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
115 | MV_589_0_line_115 |  | 106 | 157 | 0.014466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
116 | MV_589_0_line_116 |  | 107 | 108 | 0.078294 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
117 | MV_589_0_line_117 |  | 107 | 109 | 0.045318 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
118 | MV_589_0_line_118 |  | 109 | 110 | 0.1152 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_589_0_line_119 |  | 109 | 111 | 0.14156 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
120 | MV_589_0_line_120 |  | 110 | 112 | 0.25856 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
121 | MV_589_0_line_121 |  | 110 | 113 | 0.08428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
122 | MV_589_0_line_122 |  | 112 | 114 | 0.00836 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
123 | MV_589_0_line_123 |  | 112 | 115 | 0.0096414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
124 | MV_589_0_line_124 |  | 112 | 116 | 0.12987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
125 | MV_589_0_line_125 |  | 115 | 119 | 0.046492 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
126 | MV_589_0_line_126 |  | 116 | 117 | 0.18817 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
127 | MV_589_0_line_127 |  | 116 | 118 | 0.0195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
128 | MV_589_0_line_128 |  | 117 | 120 | 0.042709 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
129 | MV_589_0_line_129 |  | 117 | 121 | 0.19176 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
130 | MV_589_0_line_130 |  | 118 | 124 | 0.0051559 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
131 | MV_589_0_line_131 |  | 121 | 122 | 0.021596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
132 | MV_589_0_line_132 |  | 121 | 123 | 0.016958 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
133 | MV_589_0_line_133 |  | 122 | 125 | 0.011921 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
134 | MV_589_0_line_134 |  | 126 | 127 | 0.022759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
135 | MV_589_0_line_135 |  | 127 | 128 | 0.2041 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
136 | MV_589_0_line_136 |  | 128 | 129 | 0.022549 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
137 | MV_589_0_line_137 |  | 130 | 131 | 0.005177 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
138 | MV_589_0_line_138 |  | 132 | 138 | 0.017258 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
139 | MV_589_0_line_139 |  | 132 | 133 | 0.9644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
140 | MV_589_0_line_140 |  | 132 | 136 | 0.42981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
141 | MV_589_0_line_141 |  | 133 | 134 | 0.83681 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
142 | MV_589_0_line_142 |  | 133 | 135 | 0.022927 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
143 | MV_589_0_line_143 |  | 134 | 139 | 0.082139 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
144 | MV_589_0_line_144 |  | 136 | 137 | 0.01308 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
145 | MV_589_0_line_145 |  | 137 | 140 | 0.063942 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
146 | MV_589_0_line_146 |  | 140 | 152 | 0.45719 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
147 | MV_589_0_line_147 |  | 141 | 154 | 0.023663 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
148 | MV_589_0_line_148 |  | 145 | 146 | 0.021943 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
149 | MV_589_0_line_149 |  | 145 | 147 | 1.0366 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
150 | MV_589_0_line_150 |  | 146 | 148 | 0.53289 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
151 | MV_589_0_line_151 |  | 147 | 149 | 0.005491 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
152 | MV_589_0_line_152 |  | 148 | 150 | 0.039194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
153 | MV_589_0_line_153 |  | 148 | 151 | 1.3499 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
154 | MV_589_0_line_154 |  | 149 | 168 | 0.019325 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
155 | MV_589_0_line_155 |  | 149 | 167 | 0.056815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
156 | MV_589_0_line_156 |  | 151 | 152 | 0.11355 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
157 | MV_589_0_line_157 |  | 153 | 154 | 0.0069733 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
158 | MV_589_0_line_158 |  | 155 | 156 | 0.053496 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
159 | MV_589_0_line_159 |  | 155 | 157 | 0.013266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
160 | MV_589_0_line_160 |  | 155 | 158 | 0.010639 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
161 | MV_589_0_line_161 |  | 156 | 159 | 0.012035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
162 | MV_589_0_line_162 |  | 156 | 160 | 0.012415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
163 | MV_589_0_line_163 |  | 157 | 161 | 0.007917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
164 | MV_589_0_line_164 |  | 159 | 162 | 0.0278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
165 | MV_589_0_line_165 |  | 162 | 165 | 0.011372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
166 | MV_589_0_line_166 |  | 163 | 164 | 0.032319 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
167 | MV_589_0_line_167 |  | 165 | 166 | 0.010618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
168 | MV_589_0_line_168 |  | 168 | 169 | 0.16606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
169 | MV_589_0_line_169 |  | 168 | 170 | 0.076864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
170 | MV_589_0_line_170 |  | 169 | 171 | 0.065035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
171 | MV_589_0_line_171 |  | 170 | 172 | 0.059604 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
172 | MV_589_0_line_172 |  | 172 | 176 | 0.43031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
173 | MV_589_0_line_173 |  | 173 | 174 | 0.016033 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
174 | MV_589_0_line_174 |  | 173 | 175 | 0.075755 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
175 | MV_589_0_line_175 |  | 175 | 176 | 0.092606 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
176 | MV_589_0_line_176 |  | 176 | 177 | 0.081088 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_589_0_trafo_133 | 25 MVA 110/20 kV | 178 | 20 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2721061.7223 | 1257537.7554
1 | 2721102.0013 | 1257535.4105
2 | 2720953.7714 | 1257540.9182
3 | 2721356.6744 | 1257574.1709
4 | 2720939.0257 | 1257790.2795
5 | 2720632.1157 | 1257618.4114
6 | 2720772.7392 | 1257387.6438
7 | 2720610.1278 | 1257501.2722
8 | 2720533.2676 | 1257872.9981
9 | 2720663.8819 | 1257611.1819
10 | 2720596.3417 | 1257421.2994
11 | 2720487.7285 | 1257943.7551
12 | 2720535.9374 | 1257874.109
13 | 2720920.6722 | 1257361.4073
14 | 2721347.0122 | 1257617.363
15 | 2720596.2938 | 1257415.8825
16 | 2720495.1234 | 1257986.1315
17 | 2720482.451 | 1257984.7356
18 | 2720453.2752 | 1257854.9875
19 | 2720442.418 | 1257934.8252
20 | 2720490.3286 | 1257936.8887
21 | 2721241.2658 | 1257716.8643
22 | 2721353.8851 | 1257946.4622
23 | 2721539.48 | 1258023.6822
24 | 2721309.1537 | 1258029.2179
25 | 2721181.3433 | 1257706.2794
26 | 2721109.8574 | 1257914.5699
27 | 2721074.7544 | 1258024.475
28 | 2721074.172 | 1258007.6325
29 | 2721070.9409 | 1258047.9462
30 | 2720170.301 | 1258192.7866
31 | 2720213.6852 | 1258238.1517
32 | 2720409.182 | 1258432.2396
33 | 2720105.7357 | 1258344.7868
34 | 2720446.3649 | 1258419.0512
35 | 2720399.7001 | 1258433.0603
36 | 2719776.7927 | 1258728.9901
37 | 2719958.6316 | 1258450.1735
38 | 2719839.626 | 1258703.1505
39 | 2720084.7412 | 1258592.8443
40 | 2720198.1987 | 1258791.5323
41 | 2720118.9585 | 1258557.3854
42 | 2720085.8174 | 1258326.6779
43 | 2719907.2056 | 1258421.3062
44 | 2720453.0305 | 1258508.6875
45 | 2720468.4553 | 1258429.3097
46 | 2720458.3441 | 1258556.2151
47 | 2720406.0648 | 1258603.8597
48 | 2720257.3691 | 1258918.0563
49 | 2720739.17 | 1258337.3341
50 | 2720738.6661 | 1258332.097
51 | 2720683.7153 | 1258342.2964
52 | 2720738.0677 | 1258158.6106
53 | 2720549.2253 | 1258402.4974
54 | 2720594.6382 | 1258601.8416
55 | 2720744.9941 | 1258156.6057
56 | 2720474.0015 | 1258424.3294
57 | 2720546.0694 | 1258420.1594
58 | 2720515.6298 | 1258472.3967
59 | 2720486.6193 | 1258296.9303
60 | 2720510.0343 | 1258299.3289
61 | 2720573.7909 | 1258585.0243
62 | 2720744.4541 | 1258151.657
63 | 2720486.7942 | 1258483.7263
64 | 2720551.2729 | 1258295.7568
65 | 2721016.2589 | 1258394.5985
66 | 2721014.6123 | 1258398.4127
67 | 2721048.0741 | 1258408.6984
68 | 2720933.1447 | 1258399.8489
69 | 2720962.698 | 1258239.5122
70 | 2720945.7459 | 1258110.7529
71 | 2720807.513 | 1258100.1542
72 | 2720955.0708 | 1258109.1288
73 | 2720748.5355 | 1258010.4834
74 | 2720749.8719 | 1258014.1027
75 | 2720787.9007 | 1258006.6591
76 | 2720859.8789 | 1258147.5535
77 | 2720862.1208 | 1258155.94
78 | 2720864.8934 | 1258105.8861
79 | 2720814.3946 | 1258098.8713
80 | 2720800.8398 | 1258010.8059
81 | 2720926.854 | 1258399.5423
82 | 2720866.4502 | 1258088.2554
83 | 2720975.148 | 1258238.1936
84 | 2720955.8963 | 1258109.0766
85 | 2720810.8079 | 1258078.4769
86 | 2720867.5817 | 1258086.1571
87 | 2721002.475 | 1258235.2993
88 | 2721107.1874 | 1258324.1076
89 | 2721104.3572 | 1258298.8053
90 | 2721089.1772 | 1258369.8459
91 | 2721035.8502 | 1258303.2635
92 | 2721144.2879 | 1258359.5979
93 | 2721144.0214 | 1258356.7789
94 | 2721194.6237 | 1258417.1344
95 | 2721220.6895 | 1258428.8302
96 | 2721026.8911 | 1258269.7286
97 | 2721245.3771 | 1258439.905
98 | 2721015.755 | 1258272.1809
99 | 2721349.9053 | 1258351.0134
100 | 2721345.7902 | 1258352.3636
101 | 2721326.5451 | 1258169.642
102 | 2721334.0044 | 1258208.2065
103 | 2721137.0919 | 1258117.049
104 | 2721176.7849 | 1258140.1706
105 | 2721110.2572 | 1258088.764
106 | 2721091.7803 | 1258078.7583
107 | 2720033.1737 | 1257687.797
108 | 2720006.6864 | 1257614.1198
109 | 2720002.1613 | 1257720.8415
110 | 2720040.5882 | 1257793.306
111 | 2719871.4328 | 1257775.1437
112 | 2720214.3872 | 1257737.5955
113 | 2720008.6866 | 1257871.305
114 | 2720222.0014 | 1257741.0976
115 | 2720214.2438 | 1257729.0629
116 | 2720163.8075 | 1257841.6593
117 | 2720258.2005 | 1257891.8311
118 | 2720156.2693 | 1257859.6435
119 | 2720229.6016 | 1257685.181
120 | 2720228.8687 | 1257899.3196
121 | 2720395.0257 | 1257914.788
122 | 2720386.5835 | 1257934.5669
123 | 2720410.6375 | 1257921.4083
124 | 2720154.2761 | 1257864.3985
125 | 2720383.4705 | 1257946.0742
126 | 2720941.9717 | 1257851.282
127 | 2720919.1944 | 1257852.7846
128 | 2720791.0616 | 1257876.9008
129 | 2720777.4312 | 1257858.907
130 | 2720557.7443 | 1258233.9345
131 | 2720562.9352 | 1258233.8179
132 | 2720613.9361 | 1257081.1055
133 | 2720609.5306 | 1256836.5916
134 | 2720304.1581 | 1256614.3853
135 | 2720589.1281 | 1256826.1335
136 | 2720289.1371 | 1257192.0272
137 | 2720284.2093 | 1257179.9054
138 | 2720609.6683 | 1257064.3817
139 | 2720386.1118 | 1256619.9003
140 | 2720259.5982 | 1257120.8651
141 | 2720471.873 | 1257983.5704
142 | 2720429.1477 | 1257850.2146
143 | 2720440.2689 | 1257942.9552
144 | 2720491.2988 | 1257934.3267
145 | 2718891.9699 | 1257138.1015
146 | 2718913.3822 | 1257133.3051
147 | 2719080.5168 | 1258157.4093
148 | 2718809.7664 | 1256656.0008
149 | 2719081.32 | 1258162.8413
150 | 2718770.6013 | 1256659.3735
151 | 2720148.4198 | 1256829.5432
152 | 2720260.5915 | 1256847.1693
153 | 2720449.4255 | 1257972.9134
154 | 2720448.8801 | 1257979.6959
155 | 2721073.7288 | 1258083.4343
156 | 2721038.8374 | 1258064.8155
157 | 2721079.3222 | 1258071.4048
158 | 2721082.8776 | 1258088.8648
159 | 2721027.9445 | 1258065.6165
160 | 2721050.4065 | 1258069.2402
161 | 2721072.6787 | 1258067.0986
162 | 2721000.2777 | 1258063.6595
163 | 2720492.5307 | 1258576.7286
164 | 2720460.347 | 1258579.6875
165 | 2721009.469 | 1258060.4446
166 | 2721009.1377 | 1258071.0578
167 | 2719136.6437 | 1258160.9378
168 | 2719084.1402 | 1258181.9592
169 | 2718931.9546 | 1258201.0382
170 | 2719160.2007 | 1258170.8766
171 | 2718867.4965 | 1258209.6756
172 | 2719219.182 | 1258162.2826
173 | 2719631.5889 | 1257975.5262
174 | 2719642.2414 | 1257965.7082
175 | 2719556.701 | 1257964.2176
176 | 2719541.9116 | 1258055.6319
177 | 2719622.2627 | 1258068.1883
178 | 2720490.3286 | 1257936.8887

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99663 | -0.038448 | 0.21316 | 0.10324
1 | 0.99655 | -0.038793 | 0 | 0
2 | 0.99702 | -0.015556 | 0 | 0
3 | 0.996 | -0.041423 | 0 | 0
4 | 0.99801 | -0.010631 | 0 | 0
5 | 0.9989 | -0.0059785 | 0 | 0
6 | 0.99784 | -0.0093411 | 0 | 0
7 | 0.99834 | -0.0016768 | 0 | 0
8 | 0.99968 | -0.0017282 | 0 | 0
9 | 0.99889 | -0.0058899 | 0.22907 | 0.11094
10 | 0.99798 | 0.0010585 | 0.24478 | 0.11855
11 | 0.99997 | -0.00013012 | 0 | 0
12 | 0.99968 | -0.0017203 | 0.22911 | 0.11096
13 | 0.99779 | -0.0089227 | 0.24191 | 0.11716
14 | 0.99593 | -0.041789 | 0.10549 | 0.051091
15 | 0.99796 | 0.0012252 | 0 | 0
16 | 0.99989 | 0.00061293 | 0 | 0
17 | 0.99988 | 0.00077794 | 0.16864 | 0.081675
18 | 0.99992 | 0.00036851 | 0 | 0
19 | 0.99992 | -0.0003518 | 0 | 0
20 | 1 | 0 | -21.8588 | -9.8986
21 | 0.9954 | -0.07168 | 0.10252 | 0.049651
22 | 0.99343 | -0.13637 | 0.35749 | 0.17314
23 | 0.99327 | -0.13737 | 0.40392 | 0.19563
24 | 0.99356 | -0.13549 | 0 | 0
25 | 0.9953 | -0.072175 | 0.2934 | 0.1421
26 | 0.99454 | -0.1159 | 0 | 0
27 | 0.99414 | -0.13884 | 0.073415 | 0.035556
28 | 0.99413 | -0.1389 | 0.30184 | 0.14619
29 | 0.9941 | -0.13902 | 0 | 0
30 | 0.9888 | -0.11564 | 0.29787 | 0.14426
31 | 0.98884 | -0.11541 | 0 | 0
32 | 0.98962 | -0.12112 | 0 | 0
33 | 0.98847 | -0.11275 | 0 | 0
34 | 0.98969 | -0.12168 | 0 | 0
35 | 0.98962 | -0.12111 | 0.12767 | 0.061833
36 | 0.9881 | -0.11009 | 0 | 0
37 | 0.98824 | -0.11125 | 0 | 0
38 | 0.98808 | -0.1099 | 0.23247 | 0.11259
39 | 0.98816 | -0.11065 | 0 | 0
40 | 0.98813 | -0.11044 | 0 | 0
41 | 0.98815 | -0.11074 | 0.14848 | 0.071914
42 | 0.98846 | -0.11285 | 0.29829 | 0.14447
43 | 0.98824 | -0.1112 | 0.069871 | 0.03384
44 | 0.98962 | -0.12098 | 0 | 0
45 | 0.98976 | -0.12219 | 0.072549 | 0.035137
46 | 0.98958 | -0.12127 | 0.37607 | 0.18214
47 | 0.98958 | -0.12122 | 0.18318 | 0.088716
48 | 0.98811 | -0.11027 | 0.10749 | 0.052057
49 | 0.99125 | -0.13429 | 0.15462 | 0.074885
50 | 0.99127 | -0.13447 | 0 | 0
51 | 0.99103 | -0.13256 | 0 | 0
52 | 0.99213 | -0.14136 | 0 | 0
53 | 0.99027 | -0.12639 | 0 | 0
54 | 0.99092 | -0.13168 | 0 | 0
55 | 0.99216 | -0.14161 | 0.40291 | 0.19514
56 | 0.98978 | -0.12234 | 0 | 0
57 | 0.99027 | -0.12635 | 0.13477 | 0.065273
58 | 0.98975 | -0.1221 | 0 | 0
59 | 0.98967 | -0.12139 | 0 | 0
60 | 0.98965 | -0.12123 | 0.1123 | 0.054388
61 | 0.99091 | -0.13161 | 0.18248 | 0.088377
62 | 0.99218 | -0.1418 | 0 | 0
63 | 0.98974 | -0.12201 | 0.22537 | 0.10915
64 | 0.98963 | -0.12103 | 0 | 0
65 | 0.99339 | -0.13921 | 0.35102 | 0.17001
66 | 0.99339 | -0.13923 | 0 | 0
67 | 0.99338 | -0.13917 | 0.075393 | 0.036515
68 | 0.99334 | -0.13875 | 0 | 0
69 | 0.99362 | -0.14135 | 0 | 0
70 | 0.99282 | -0.14679 | 0 | 0
71 | 0.99292 | -0.14774 | 0 | 0
72 | 0.99281 | -0.14675 | 0.27476 | 0.13307
73 | 0.99282 | -0.1469 | 0 | 0
74 | 0.99283 | -0.14691 | 0 | 0
75 | 0.99282 | -0.14686 | 0.085724 | 0.041518
76 | 0.99336 | -0.14265 | 0 | 0
77 | 0.99336 | -0.14264 | 0.070441 | 0.034116
78 | 0.99285 | -0.14713 | 0 | 0
79 | 0.99292 | -0.14771 | 0.19787 | 0.095831
80 | 0.99281 | -0.14675 | 0.27032 | 0.13092
81 | 0.99334 | -0.13873 | 0.368 | 0.17823
82 | 0.99283 | -0.14695 | 0.072566 | 0.035145
83 | 0.99364 | -0.14128 | 0.08322 | 0.040305
84 | 0.99281 | -0.14675 | 0.11067 | 0.0536
85 | 0.99291 | -0.14769 | 0.096876 | 0.046919
86 | 0.99283 | -0.14693 | 0 | 0
87 | 0.99366 | -0.14114 | 0 | 0
88 | 0.99331 | -0.14151 | 0.31616 | 0.15313
89 | 0.99334 | -0.14183 | 0 | 0
90 | 0.99323 | -0.14203 | 0 | 0
91 | 0.99349 | -0.14083 | 0.081444 | 0.039445
92 | 0.99315 | -0.1413 | 0 | 0
93 | 0.99315 | -0.14129 | 0.10673 | 0.051693
94 | 0.99306 | -0.14051 | 0 | 0
95 | 0.99303 | -0.14028 | 0.39661 | 0.19209
96 | 0.99357 | -0.14029 | 0.25631 | 0.12414
97 | 0.99302 | -0.14019 | 0 | 0
98 | 0.99359 | -0.14048 | 0 | 0
99 | 0.99295 | -0.13954 | 0 | 0
100 | 0.99295 | -0.13953 | 0.29532 | 0.14303
101 | 0.99359 | -0.13628 | 0.37924 | 0.18368
102 | 0.99362 | -0.13609 | 0 | 0
103 | 0.9938 | -0.13764 | 0 | 0
104 | 0.99378 | -0.13746 | 0.33285 | 0.1612
105 | 0.99391 | -0.13862 | 0 | 0
106 | 0.99395 | -0.13898 | 0.10683 | 0.051741
107 | 0.99802 | 0.0063321 | 0.33233 | 0.16096
108 | 0.99801 | 0.006255 | 0.080916 | 0.039189
109 | 0.99806 | 0.0065598 | 0 | 0
110 | 0.9983 | 0.0043196 | 0 | 0
111 | 0.99772 | 0.0044725 | 1.2145 | 0.58821
112 | 0.99893 | -0.0015196 | 0 | 0
113 | 0.99826 | 0.0046151 | 0.29733 | 0.144
114 | 0.99893 | -0.0014783 | 0.41231 | 0.19969
115 | 0.99893 | -0.0015013 | 0 | 0
116 | 0.99934 | -0.0052956 | 0 | 0
117 | 0.99975 | -0.0010304 | 0 | 0
118 | 0.99931 | -0.0049519 | 0.75296 | 0.36467
119 | 0.99891 | -0.0015908 | 0.15866 | 0.076844
120 | 0.99973 | -0.00090029 | 0.2572 | 0.12457
121 | 0.99988 | -0.00050908 | 0 | 0
122 | 0.99987 | -0.00044471 | 0 | 0
123 | 0.99989 | -0.00045876 | 0.18866 | 0.091372
124 | 0.9993 | -0.0049075 | 0.72025 | 0.34883
125 | 0.99987 | -0.00040888 | 0.25195 | 0.12203
126 | 0.99256 | -0.14459 | 0.3872 | 0.18753
127 | 0.99257 | -0.1447 | 0 | 0
128 | 0.99249 | -0.14396 | 0 | 0
129 | 0.99248 | -0.14388 | 0.31332 | 0.15175
130 | 0.98959 | -0.12062 | 0.40425 | 0.19579
131 | 0.98959 | -0.12065 | 0 | 0
132 | 0.99652 | 0.012351 | 0 | 0
133 | 0.99573 | 0.017946 | 0 | 0
134 | 0.99545 | 0.020045 | 0 | 0
135 | 0.99571 | 0.017838 | 0.38708 | 0.18747
136 | 0.99528 | 0.022429 | 0 | 0
137 | 0.99525 | 0.02274 | 0.30509 | 0.14776
138 | 0.99651 | 0.012407 | 0.27228 | 0.13187
139 | 0.99541 | 0.019783 | 0.26105 | 0.12643
140 | 0.99509 | 0.024031 | 0 | 0
141 | 0.99986 | 0.0008944 | 0.17147 | 0.083045
142 | 0.99991 | 0.00048053 | 0.3833 | 0.18564
143 | 0.99992 | -0.00031935 | 0.32303 | 0.15645
144 | 1 | 4.1383e-06 | 0.12644 | 0.061235
145 | 0.98823 | 0.0060758 | 0.34362 | 0.16642
146 | 0.98829 | 0.0065176 | 0 | 0
147 | 0.98604 | -0.010371 | 0.23998 | 0.11623
148 | 0.98926 | -0.0016591 | 0 | 0
149 | 0.98603 | -0.010323 | 0 | 0
150 | 0.98925 | -0.0015659 | 0.19702 | 0.095419
151 | 0.99352 | 0.03033 | 0.31633 | 0.1532
152 | 0.99395 | 0.033457 | 0 | 0
153 | 0.99984 | 0.0011267 | 0.25566 | 0.12382
154 | 0.99984 | 0.0011054 | 0.49188 | 0.23823
155 | 0.994 | -0.13949 | 0 | 0
156 | 0.99398 | -0.13925 | 0 | 0
157 | 0.99398 | -0.13924 | 0 | 0
158 | 0.994 | -0.13948 | 0.070301 | 0.034048
159 | 0.99397 | -0.1392 | 0.17757 | 0.086001
160 | 0.99398 | -0.13923 | 0.071137 | 0.034453
161 | 0.99397 | -0.13923 | 0.073017 | 0.035364
162 | 0.99397 | -0.13916 | 0 | 0
163 | 0.98957 | -0.12121 | 0.092604 | 0.04485
164 | 0.98957 | -0.12124 | 0 | 0
165 | 0.99397 | -0.13914 | 0 | 0
166 | 0.99396 | -0.13912 | 0.13581 | 0.065776
167 | 0.98603 | -0.010275 | 0.072563 | 0.035144
168 | 0.98601 | -0.01017 | 0 | 0
169 | 0.98599 | -0.0099873 | 0 | 0
170 | 0.98595 | -0.009632 | 0.12324 | 0.059689
171 | 0.98598 | -0.0099043 | 0.10777 | 0.052195
172 | 0.98591 | -0.0092988 | 0 | 0
173 | 0.98551 | -0.0058051 | 0.32852 | 0.15911
174 | 0.9855 | -0.0057795 | 0.131 | 0.063445
175 | 0.98555 | -0.0062277 | 0 | 0
176 | 0.98561 | -0.0067324 | 0 | 0
177 | 0.9856 | -0.0066532 | 0.084294 | 0.040826
178 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 10.8585 | 4.9564 | -10.8578 | -4.961 | 0.00074306 | -0.0046024 | 0.34574 | 0.3458 | 0.3458 | 0.99663 | -0.038448 | 0.99655 | -0.038793 | 27.1
1 | -11.0717 | -5.0597 | 11.0741 | 5.0658 | 0.0023966 | 0.006148 | 0.35259 | 0.35259 | 0.35259 | 0.99663 | -0.038448 | 0.99702 | -0.015556 | 27.3329
2 | 10.8578 | 4.961 | -10.852 | -4.9967 | 0.005776 | -0.035691 | 0.3458 | 0.34627 | 0.34627 | 0.99655 | -0.038793 | 0.996 | -0.041423 | 27.1369
3 | -11.0741 | -5.0658 | 11.0846 | 5.0028 | 0.010568 | -0.063009 | 0.35259 | 0.35177 | 0.35259 | 0.99702 | -0.015556 | 0.99801 | -0.010631 | 27.6325
4 | 10.852 | 4.9967 | -10.8512 | -5.0018 | 0.00082005 | -0.0050553 | 0.34627 | 0.34633 | 0.34633 | 0.996 | -0.041423 | 0.99593 | -0.041789 | 27.1421
5 | -11.3266 | -5.1027 | 11.3362 | 5.0478 | 0.0095888 | -0.054936 | 0.35933 | 0.35862 | 0.35933 | 0.99801 | -0.010631 | 0.9989 | -0.0059785 | 28.1609
6 | 0.24197 | 0.099928 | -0.24192 | -0.11361 | 4.4987e-05 | -0.013678 | 0.0075723 | 0.0077322 | 0.0077322 | 0.99801 | -0.010631 | 0.99784 | -0.0093411 | 3.5146
7 | 3.4409 | 1.5423 | -3.4389 | -1.5448 | 0.0020401 | -0.0024578 | 0.10897 | 0.10901 | 0.10901 | 0.9989 | -0.0059785 | 0.99834 | -0.0016768 | 49.5499
8 | -15.0062 | -6.7003 | 15.0175 | 6.6659 | 0.011316 | -0.034414 | 0.47494 | 0.47446 | 0.47494 | 0.9989 | -0.0059785 | 0.99968 | -0.0017282 | 37.2207
9 | 0.22907 | 0.11017 | -0.22907 | -0.11094 | 2.3501e-06 | -0.00077542 | 0.0073459 | 0.0073557 | 0.0073557 | 0.9989 | -0.0059785 | 0.99889 | -0.0058899 | 3.3435
10 | 0.24192 | 0.11361 | -0.24191 | -0.11716 | 1.2025e-05 | -0.0035577 | 0.0077322 | 0.0077765 | 0.0077765 | 0.99784 | -0.0093411 | 0.99779 | -0.0089227 | 3.5348
11 | 3.4389 | 1.5448 | -3.4376 | -1.5463 | 0.0012905 | -0.001552 | 0.10901 | 0.10903 | 0.10903 | 0.99834 | -0.0016768 | 0.99798 | 0.0010585 | 49.5604
12 | -15.2466 | -6.7768 | 15.2509 | 6.7642 | 0.004275 | -0.012572 | 0.4818 | 0.48163 | 0.4818 | 0.99968 | -0.0017282 | 0.99997 | -0.00013012 | 37.7589
13 | 0.22911 | 0.11089 | -0.22911 | -0.11096 | 2.0805e-07 | -6.8753e-05 | 0.0073502 | 0.0073511 | 0.0073511 | 0.99968 | -0.0017282 | 0.99968 | -0.0017203 | 3.3414
14 | 3.1928 | 1.4278 | -3.1928 | -1.4279 | 7.4032e-05 | -0.00010688 | 0.10117 | 0.10117 | 0.10117 | 0.99798 | 0.0010585 | 0.99796 | 0.0012252 | 45.9866
15 | 0.38332 | 0.18239 | -0.3833 | -0.18505 | 2.2456e-05 | -0.0026601 | 0.012255 | 0.012288 | 0.012288 | 0.99997 | -0.00013012 | 0.99992 | 0.00036851 | 5.5854
16 | 4.9959 | 2.3568 | -4.9956 | -2.365 | 0.0002612 | -0.0082013 | 0.15946 | 0.15957 | 0.15957 | 0.99997 | -0.00013012 | 0.99992 | -0.0003518 | 12.5053
17 | -21.7179 | -9.8275 | 21.7184 | 9.8269 | 0.00053719 | -0.00062013 | 0.68816 | 0.68815 | 0.68816 | 0.99997 | -0.00013012 | 1 | 0 | 53.931
18 | 1.0878 | 0.52414 | -1.0877 | -0.52549 | 9.3569e-05 | -0.0013486 | 0.034858 | 0.034875 | 0.034875 | 0.99997 | -0.00013012 | 0.99989 | 0.00061293 | 15.8522
19 | 10.7457 | 4.9507 | -10.7426 | -4.9429 | 0.0030482 | 0.0077988 | 0.34294 | 0.34294 | 0.34294 | 0.99593 | -0.041789 | 0.9954 | -0.07168 | 26.5846
20 | 3.1928 | 1.4279 | -3.1879 | -1.4349 | 0.0048945 | -0.0070449 | 0.10117 | 0.10127 | 0.10127 | 0.99796 | 0.0012252 | 0.99652 | 0.012351 | 46.0324
21 | 1.0877 | 0.52549 | -1.0877 | -0.52579 | 2.0703e-05 | -0.00029819 | 0.034875 | 0.034879 | 0.034879 | 0.99989 | 0.00061293 | 0.99988 | 0.00077794 | 15.854
22 | 0.91903 | 0.44412 | -0.91902 | -0.44437 | 1.2339e-05 | -0.00025036 | 0.029469 | 0.029472 | 0.029472 | 0.99988 | 0.00077794 | 0.99986 | 0.0008944 | 13.3965
23 | 0.3833 | 0.18505 | -0.3833 | -0.18564 | 4.9464e-06 | -0.00058397 | 0.012288 | 0.012295 | 0.012295 | 0.99992 | 0.00036851 | 0.99991 | 0.00048053 | 5.5888
24 | 0.32303 | 0.15625 | -0.32303 | -0.15645 | 1.2051e-06 | -0.00020038 | 0.010359 | 0.010362 | 0.010362 | 0.99992 | -0.0003518 | 0.99992 | -0.00031935 | 4.71
25 | 4.6726 | 2.2087 | -4.6725 | -2.213 | 0.0001187 | -0.0042673 | 0.14921 | 0.14926 | 0.14926 | 0.99992 | -0.0003518 | 0.99989 | -0.00045876 | 11.6977
26 | 0.12644 | 0.06117 | -0.12644 | -0.061235 | 6.014e-08 | -6.5393e-05 | 0.0040546 | 0.0040554 | 0.0040554 | 1 | 0 | 1 | 4.1383e-06 | 1.8434
27 | 10.6401 | 4.8932 | -10.639 | -4.9002 | 0.0010848 | -0.0069649 | 0.33964 | 0.33973 | 0.33973 | 0.9954 | -0.07168 | 0.9953 | -0.072175 | 26.6247
28 | 0.40398 | 0.19543 | -0.40392 | -0.19563 | 6.0921e-05 | -0.00019864 | 0.013041 | 0.013044 | 0.013044 | 0.99343 | -0.13637 | 0.99327 | -0.13737 | 6.2112
29 | -0.76147 | -0.36857 | 0.76157 | 0.36852 | 0.00010128 | -4.7406e-05 | 0.024583 | 0.024582 | 0.024583 | 0.99343 | -0.13637 | 0.99356 | -0.13549 | 11.7062
30 | -0.76157 | -0.36852 | 0.76177 | 0.36297 | 0.00019149 | -0.0055556 | 0.024582 | 0.024511 | 0.024582 | 0.99356 | -0.13549 | 0.9938 | -0.13764 | 11.1735
31 | 10.3456 | 4.7581 | -10.3413 | -4.7472 | 0.004288 | 0.010928 | 0.33028 | 0.33028 | 0.33028 | 0.9953 | -0.072175 | 0.99454 | -0.1159 | 25.6035
32 | 10.3413 | 4.7472 | -10.3391 | -4.7415 | 0.0022466 | 0.005726 | 0.33028 | 0.33029 | 0.33029 | 0.99454 | -0.1159 | 0.99414 | -0.13884 | 25.6038
33 | 0.30185 | 0.14617 | -0.30184 | -0.14619 | 2.8478e-06 | -1.81e-05 | 0.0097386 | 0.0097388 | 0.0097388 | 0.99414 | -0.13884 | 0.99413 | -0.1389 | 4.6375
34 | 9.9638 | 4.5597 | -9.9635 | -4.5625 | 0.00037224 | -0.0027455 | 0.31818 | 0.31822 | 0.31822 | 0.99414 | -0.13884 | 0.9941 | -0.13902 | 24.9388
35 | 9.9635 | 4.5625 | -9.9625 | -4.5693 | 0.00092753 | -0.0068372 | 0.31822 | 0.31831 | 0.31831 | 0.9941 | -0.13902 | 0.994 | -0.13949 | 24.9458
36 | -0.29787 | -0.14426 | 0.29788 | 0.1442 | 1.044e-05 | -6.6731e-05 | 0.0096622 | 0.0096613 | 0.0096622 | 0.9888 | -0.11564 | 0.98884 | -0.11541 | 4.6011
37 | -1.155 | -0.5147 | 1.156 | 0.50263 | 0.00095826 | -0.012071 | 0.036915 | 0.03677 | 0.036915 | 0.98884 | -0.11541 | 0.98962 | -0.12112 | 16.7797
38 | 0.85715 | 0.3705 | -0.85681 | -0.37831 | 0.00033698 | -0.0078003 | 0.027261 | 0.027353 | 0.027353 | 0.98884 | -0.11541 | 0.98847 | -0.11275 | 12.4332
39 | -1.2837 | -0.56424 | 1.2838 | 0.56316 | 0.00010584 | -0.0010771 | 0.040902 | 0.040889 | 0.040902 | 0.98962 | -0.12112 | 0.98969 | -0.12168 | 18.592
40 | 0.12767 | 0.061611 | -0.12767 | -0.061833 | 2.1741e-07 | -0.00022248 | 0.0041352 | 0.004138 | 0.004138 | 0.98962 | -0.12112 | 0.98962 | -0.12111 | 1.8809
41 | 0.55851 | 0.23386 | -0.55838 | -0.24129 | 0.00013427 | -0.0074263 | 0.017683 | 0.017768 | 0.017768 | 0.98847 | -0.11275 | 0.98824 | -0.11125 | 8.0766
42 | 0.2983 | 0.14444 | -0.29829 | -0.14447 | 4.4936e-06 | -2.8585e-05 | 0.0096792 | 0.0096796 | 0.0096796 | 0.98847 | -0.11275 | 0.98846 | -0.11285 | 4.6093
43 | 0.65193 | 0.31215 | -0.65188 | -0.31424 | 5.3416e-05 | -0.0020865 | 0.021083 | 0.02111 | 0.02111 | 0.98969 | -0.12168 | 0.98962 | -0.12098 | 9.5953
44 | -1.9357 | -0.87531 | 1.9358 | 0.87475 | 0.00013277 | -0.00056649 | 0.061965 | 0.061957 | 0.061965 | 0.98969 | -0.12168 | 0.98976 | -0.12219 | 28.1658
45 | -0.23247 | -0.111 | 0.23251 | 0.099569 | 3.6405e-05 | -0.011427 | 0.0075261 | 0.0073883 | 0.0075261 | 0.9881 | -0.11009 | 0.98824 | -0.11125 | 3.421
46 | 0.23247 | 0.111 | -0.23247 | -0.11259 | 5.1847e-06 | -0.0015925 | 0.0075261 | 0.0075463 | 0.0075463 | 0.9881 | -0.11009 | 0.98808 | -0.1099 | 3.4301
47 | 0.069871 | 0.03227 | -0.069871 | -0.03384 | 4.5811e-07 | -0.0015694 | 0.0022482 | 0.0022678 | 0.0022678 | 0.98824 | -0.11125 | 0.98824 | -0.1112 | 1.0308
48 | 0.256 | 0.10945 | -0.25598 | -0.11532 | 2.2433e-05 | -0.0058677 | 0.0081327 | 0.0082017 | 0.0082017 | 0.98824 | -0.11125 | 0.98816 | -0.11065 | 3.7281
49 | 0.10749 | 0.04346 | -0.10749 | -0.048804 | 3.5737e-06 | -0.0053436 | 0.0033871 | 0.0034487 | 0.0034487 | 0.98816 | -0.11065 | 0.98813 | -0.11044 | 1.5676
50 | 0.14849 | 0.071858 | -0.14848 | -0.071914 | 2.0392e-06 | -5.6164e-05 | 0.004819 | 0.0048197 | 0.0048197 | 0.98816 | -0.11065 | 0.98815 | -0.11074 | 2.2951
51 | 0.10749 | 0.048804 | -0.10749 | -0.052057 | 2.2423e-06 | -0.0032538 | 0.0034487 | 0.0034891 | 0.0034891 | 0.98813 | -0.11044 | 0.98811 | -0.11027 | 1.5859
52 | 0.4687 | 0.22564 | -0.46868 | -0.22568 | 1.962e-05 | -4.3621e-05 | 0.015174 | 0.015175 | 0.015175 | 0.98962 | -0.12098 | 0.98958 | -0.12127 | 7.226
53 | 0.18318 | 0.088596 | -0.18318 | -0.088716 | 6.6638e-06 | -0.0001199 | 0.0059357 | 0.0059372 | 0.0059372 | 0.98962 | -0.12098 | 0.98958 | -0.12122 | 2.8273
54 | -2.0084 | -0.90988 | 2.0084 | 0.90972 | 4.1152e-05 | -0.00016215 | 0.064308 | 0.064306 | 0.064308 | 0.98976 | -0.12219 | 0.98978 | -0.12234 | 29.2308
55 | 0.092604 | 0.043544 | -0.092604 | -0.044094 | 2.8091e-07 | -0.00055075 | 0.0029852 | 0.002992 | 0.002992 | 0.98958 | -0.12127 | 0.98957 | -0.12124 | 1.36
56 | -3.2269 | -1.4667 | 3.2269 | 1.4666 | 7.4852e-05 | -0.00010125 | 0.10323 | 0.10322 | 0.10323 | 0.99125 | -0.13429 | 0.99127 | -0.13447 | 46.9209
57 | 3.0722 | 1.3918 | -3.0715 | -1.3929 | 0.00071511 | -0.0010899 | 0.098224 | 0.09824 | 0.09824 | 0.99125 | -0.13429 | 0.99103 | -0.13256 | 44.6545
58 | -3.2269 | -1.4666 | 3.2299 | 1.4626 | 0.0029848 | -0.0040445 | 0.10322 | 0.10317 | 0.10322 | 0.99127 | -0.13447 | 0.99213 | -0.14136 | 46.9202
59 | 2.889 | 1.3167 | -2.8867 | -1.3208 | 0.0023496 | -0.0041216 | 0.092482 | 0.092541 | 0.092541 | 0.99103 | -0.13256 | 0.99027 | -0.12639 | 42.0639
60 | 0.1825 | 0.07618 | -0.18248 | -0.087648 | 2.2182e-05 | -0.011467 | 0.0057606 | 0.0058974 | 0.0058974 | 0.99103 | -0.13256 | 0.99092 | -0.13168 | 2.6806
61 | -3.2299 | -1.4626 | 3.23 | 1.4624 | 0.00010767 | -0.00014616 | 0.10317 | 0.10316 | 0.10317 | 0.99213 | -0.14136 | 0.99216 | -0.14161 | 46.8933
62 | 2.7519 | 1.256 | -2.7504 | -1.2589 | 0.0014621 | -0.0028608 | 0.088182 | 0.088222 | 0.088222 | 0.99027 | -0.12639 | 0.98978 | -0.12234 | 40.1008
63 | 0.13477 | 0.064826 | -0.13477 | -0.065273 | 4.8501e-07 | -0.00044682 | 0.0043596 | 0.0043653 | 0.0043653 | 0.99027 | -0.12639 | 0.99027 | -0.12635 | 1.9842
64 | 0.18248 | 0.087648 | -0.18248 | -0.088377 | 1.4473e-06 | -0.0007292 | 0.0058974 | 0.0059066 | 0.0059066 | 0.99092 | -0.13168 | 0.99091 | -0.13161 | 2.6848
65 | -3.6329 | -1.6575 | 3.633 | 1.6575 | 8.9707e-05 | -9.0392e-05 | 0.11618 | 0.11618 | 0.11618 | 0.99216 | -0.14161 | 0.99218 | -0.1418 | 52.8111
66 | 0.22538 | 0.10623 | -0.22537 | -0.10842 | 6.6318e-06 | -0.00219 | 0.0072669 | 0.0072944 | 0.0072944 | 0.98978 | -0.12234 | 0.98975 | -0.1221 | 3.3156
67 | 0.51665 | 0.24292 | -0.51659 | -0.24664 | 5.928e-05 | -0.0037177 | 0.016651 | 0.016698 | 0.016698 | 0.98978 | -0.12234 | 0.98967 | -0.12139 | 7.5898
68 | 0.22537 | 0.10842 | -0.22537 | -0.10915 | 2.2242e-06 | -0.00073075 | 0.0072944 | 0.0073037 | 0.0073037 | 0.98975 | -0.1221 | 0.98974 | -0.12201 | 3.3199
69 | 0.51659 | 0.24664 | -0.51658 | -0.24728 | 1.0236e-05 | -0.00063978 | 0.016698 | 0.016706 | 0.016706 | 0.98967 | -0.12139 | 0.98965 | -0.12123 | 7.5935
70 | 0.40428 | 0.19289 | -0.40427 | -0.19386 | 9.4429e-06 | -0.00096514 | 0.013066 | 0.013078 | 0.013078 | 0.98965 | -0.12123 | 0.98963 | -0.12103 | 5.9447
71 | -3.633 | -1.6575 | 3.6359 | 1.6546 | 0.0028619 | -0.0028881 | 0.11618 | 0.11614 | 0.11618 | 0.99218 | -0.1418 | 0.99292 | -0.14774 | 52.8105
72 | 0.40427 | 0.19386 | -0.40425 | -0.19567 | 1.7757e-05 | -0.0018098 | 0.013078 | 0.013101 | 0.013101 | 0.98963 | -0.12103 | 0.98959 | -0.12065 | 5.9551
73 | -0.42641 | -0.2057 | 0.42641 | 0.2056 | 1.0493e-06 | -9.7539e-05 | 0.013758 | 0.013757 | 0.013758 | 0.99339 | -0.13921 | 0.99339 | -0.13923 | 6.2535
74 | 0.075393 | 0.035695 | -0.075393 | -0.036515 | 2.7414e-07 | -0.00081984 | 0.002424 | 0.0024343 | 0.0024343 | 0.99339 | -0.13921 | 0.99338 | -0.13917 | 1.1065
75 | 0.36803 | 0.17554 | -0.36801 | -0.17809 | 2.0356e-05 | -0.0025458 | 0.011849 | 0.011881 | 0.011881 | 0.99339 | -0.13923 | 0.99334 | -0.13875 | 5.4005
76 | -0.79444 | -0.38114 | 0.79464 | 0.37578 | 0.00020088 | -0.0053635 | 0.025605 | 0.025538 | 0.025605 | 0.99339 | -0.13923 | 0.99362 | -0.14135 | 11.6388
77 | 0.36801 | 0.17809 | -0.368 | -0.17823 | 1.1835e-06 | -0.00014758 | 0.011881 | 0.011883 | 0.011883 | 0.99334 | -0.13875 | 0.99334 | -0.13873 | 5.4013
78 | -6.3143 | -2.8738 | 6.3143 | 2.8723 | 7.8571e-05 | -0.001509 | 0.20155 | 0.20153 | 0.20155 | 0.99362 | -0.14135 | 0.99364 | -0.14128 | 15.7957
79 | 5.5196 | 2.498 | -5.5182 | -2.5336 | 0.0014078 | -0.035595 | 0.17602 | 0.17646 | 0.17646 | 0.99362 | -0.14135 | 0.99336 | -0.14265 | 13.8289
80 | -0.38543 | -0.18642 | 0.38547 | 0.1815 | 4.3223e-05 | -0.0049289 | 0.012449 | 0.012387 | 0.012449 | 0.99282 | -0.14679 | 0.99292 | -0.14774 | 5.6586
81 | 0.38543 | 0.18642 | -0.38543 | -0.18665 | 2.0127e-06 | -0.00022829 | 0.012449 | 0.012452 | 0.012452 | 0.99282 | -0.14679 | 0.99281 | -0.14675 | 5.66
82 | 0.35609 | 0.16526 | -0.35605 | -0.1701 | 3.6037e-05 | -0.0048414 | 0.011413 | 0.011473 | 0.011473 | 0.99292 | -0.14774 | 0.99283 | -0.14691 | 5.2152
83 | 0.77339 | 0.35977 | -0.77333 | -0.36144 | 5.9009e-05 | -0.0016728 | 0.024799 | 0.02482 | 0.02482 | 0.99292 | -0.14774 | 0.99285 | -0.14713 | 11.2817
84 | 0.29474 | 0.1421 | -0.29474 | -0.14226 | 8.459e-07 | -0.00016453 | 0.009513 | 0.0095151 | 0.0095151 | 0.99292 | -0.14774 | 0.99292 | -0.14771 | 4.3251
85 | -5.4456 | -2.5032 | 5.4478 | 2.4997 | 0.0021919 | -0.0034663 | 0.17425 | 0.17419 | 0.17425 | 0.99292 | -0.14774 | 0.99336 | -0.14265 | 48.1346
86 | 0.11067 | 0.053581 | -0.11067 | -0.0536 | 1.4072e-08 | -1.9462e-05 | 0.0035752 | 0.0035755 | 0.0035755 | 0.99281 | -0.14675 | 0.99281 | -0.14675 | 1.6252
87 | -0.085725 | -0.040587 | 0.085725 | 0.040382 | 8.8479e-08 | -0.00020523 | 0.0027578 | 0.0027552 | 0.0027578 | 0.99282 | -0.1469 | 0.99283 | -0.14691 | 1.2535
88 | 0.085725 | 0.040587 | -0.085724 | -0.041518 | 4.0326e-07 | -0.00093069 | 0.0027578 | 0.0027695 | 0.0027695 | 0.99282 | -0.1469 | 0.99282 | -0.14686 | 1.2589
89 | 0.27033 | 0.12972 | -0.27032 | -0.13092 | 5.1918e-06 | -0.0012005 | 0.0087182 | 0.0087334 | 0.0087334 | 0.99283 | -0.14691 | 0.99281 | -0.14675 | 3.9697
90 | 0.070441 | 0.033902 | -0.070441 | -0.034116 | 6.2773e-08 | -0.0002144 | 0.0022718 | 0.0022745 | 0.0022745 | 0.99336 | -0.14265 | 0.99336 | -0.14264 | 1.0339
91 | 0.77333 | 0.36144 | -0.77331 | -0.36193 | 1.702e-05 | -0.00048191 | 0.02482 | 0.024826 | 0.024826 | 0.99285 | -0.14713 | 0.99283 | -0.14695 | 11.2844
92 | 0.096876 | 0.046432 | -0.096876 | -0.046919 | 2.702e-07 | -0.00048735 | 0.0031233 | 0.0031295 | 0.0031295 | 0.99292 | -0.14771 | 0.99291 | -0.14769 | 1.4225
93 | 0.70075 | 0.32678 | -0.70075 | -0.32684 | 1.6086e-06 | -5.563e-05 | 0.022482 | 0.022482 | 0.022482 | 0.99283 | -0.14695 | 0.99283 | -0.14693 | 10.2192
94 | -6.3976 | -2.9126 | 6.3977 | 2.9093 | 0.00017703 | -0.0033098 | 0.20422 | 0.20418 | 0.20422 | 0.99364 | -0.14128 | 0.99366 | -0.14114 | 16.0047
95 | 0.70075 | 0.32684 | -0.70056 | -0.33342 | 0.00019119 | -0.0065855 | 0.022482 | 0.022565 | 0.022565 | 0.99283 | -0.14693 | 0.99257 | -0.1447 | 10.2566
96 | 1.4533 | 0.69166 | -1.4531 | -0.69256 | 0.00011444 | -0.0008901 | 0.046757 | 0.046769 | 0.046769 | 0.99366 | -0.14114 | 0.99359 | -0.14048 | 21.2586
97 | -7.851 | -3.601 | 7.8536 | 3.5695 | 0.0025751 | -0.031457 | 0.25093 | 0.25053 | 0.25093 | 0.99366 | -0.14114 | 0.994 | -0.13949 | 19.6654
98 | -1.1151 | -0.52979 | 1.1151 | 0.5292 | 4.3869e-05 | -0.00058853 | 0.035878 | 0.03587 | 0.035878 | 0.99331 | -0.14151 | 0.99334 | -0.14183 | 16.3081
99 | 0.7989 | 0.37666 | -0.79884 | -0.37668 | 5.7709e-05 | -2.1749e-05 | 0.025669 | 0.02567 | 0.02567 | 0.99331 | -0.14151 | 0.99323 | -0.14203 | 12.2236
100 | -1.1151 | -0.5292 | 1.1153 | 0.52921 | 0.00015738 | 1.7695e-05 | 0.03587 | 0.035869 | 0.03587 | 0.99334 | -0.14183 | 0.99349 | -0.14083 | 17.0811
101 | 0.79884 | 0.37668 | -0.79877 | -0.37856 | 7.0918e-05 | -0.001876 | 0.02567 | 0.025693 | 0.025693 | 0.99323 | -0.14203 | 0.99315 | -0.1413 | 11.6787
102 | -1.1967 | -0.56866 | 1.1968 | 0.56868 | 9.1661e-05 | 1.651e-05 | 0.038499 | 0.038498 | 0.038499 | 0.99349 | -0.14083 | 0.99357 | -0.14029 | 18.3327
103 | 0.10673 | 0.051626 | -0.10673 | -0.051693 | 4.4965e-08 | -6.668e-05 | 0.0034462 | 0.003447 | 0.003447 | 0.99315 | -0.1413 | 0.99315 | -0.14129 | 1.5668
104 | 0.69204 | 0.32693 | -0.69198 | -0.32924 | 6.5462e-05 | -0.0023105 | 0.022247 | 0.022276 | 0.022276 | 0.99315 | -0.1413 | 0.99306 | -0.14051 | 10.1255
105 | 0.69198 | 0.32924 | -0.69196 | -0.32991 | 1.8933e-05 | -0.00066706 | 0.022276 | 0.022284 | 0.022284 | 0.99306 | -0.14051 | 0.99303 | -0.14028 | 10.1293
106 | 0.29535 | 0.13782 | -0.29534 | -0.13846 | 3.2452e-06 | -0.0006361 | 0.0094745 | 0.0094824 | 0.0094824 | 0.99303 | -0.14028 | 0.99302 | -0.14019 | 4.3102
107 | -1.4531 | -0.69281 | 1.4531 | 0.69256 | 3.3207e-05 | -0.00025817 | 0.046772 | 0.046769 | 0.046772 | 0.99357 | -0.14029 | 0.99359 | -0.14048 | 21.2601
108 | 0.29534 | 0.13846 | -0.29532 | -0.14293 | 2.2961e-05 | -0.0044701 | 0.0094824 | 0.0095383 | 0.0095383 | 0.99302 | -0.14019 | 0.99295 | -0.13954 | 4.3356
109 | 0.29532 | 0.14293 | -0.29532 | -0.14303 | 5.2465e-07 | -0.00010152 | 0.0095383 | 0.0095396 | 0.0095396 | 0.99295 | -0.13954 | 0.99295 | -0.13953 | 4.3362
110 | -0.37924 | -0.18368 | 0.37925 | 0.18364 | 1.0489e-05 | -3.9724e-05 | 0.012243 | 0.012242 | 0.012243 | 0.99359 | -0.13628 | 0.99362 | -0.13609 | 5.8298
111 | -0.37925 | -0.18364 | 0.37933 | 0.17521 | 7.1076e-05 | -0.0084274 | 0.012242 | 0.012137 | 0.012242 | 0.99362 | -0.13609 | 0.9938 | -0.13764 | 5.5646
112 | 0.33285 | 0.16013 | -0.33285 | -0.1612 | 7.0526e-06 | -0.0010787 | 0.010729 | 0.010743 | 0.010743 | 0.9938 | -0.13764 | 0.99378 | -0.13746 | 4.8831
113 | -1.4739 | -0.6983 | 1.4741 | 0.69698 | 0.00017499 | -0.0013259 | 0.047377 | 0.047359 | 0.047377 | 0.9938 | -0.13764 | 0.99391 | -0.13862 | 21.5348
114 | -1.4741 | -0.69698 | 1.4742 | 0.6965 | 6.2989e-05 | -0.00047757 | 0.047359 | 0.047353 | 0.047359 | 0.99391 | -0.13862 | 0.99395 | -0.13898 | 21.527
115 | -1.581 | -0.74824 | 1.5811 | 0.74791 | 4.9836e-05 | -0.00032646 | 0.050801 | 0.050796 | 0.050801 | 0.99395 | -0.13898 | 0.99398 | -0.13924 | 23.0912
116 | 0.080917 | 0.039097 | -0.080916 | -0.039189 | 9.4298e-07 | -9.2506e-05 | 0.0025994 | 0.0026006 | 0.0026006 | 0.99802 | 0.0063321 | 0.99801 | 0.006255 | 1.2384
117 | -0.41325 | -0.20005 | 0.41326 | 0.20001 | 1.4239e-05 | -4.497e-05 | 0.01328 | 0.013279 | 0.01328 | 0.99802 | 0.0063321 | 0.99806 | 0.0065598 | 6.3238
118 | -1.6281 | -0.78829 | 1.6286 | 0.78567 | 0.00042072 | -0.0026157 | 0.052321 | 0.052287 | 0.052321 | 0.99806 | 0.0065598 | 0.9983 | 0.0043196 | 23.7823
119 | 1.2149 | 0.58828 | -1.2145 | -0.58821 | 0.00038446 | 7.2532e-05 | 0.039042 | 0.039044 | 0.039044 | 0.99806 | 0.0065598 | 0.99772 | 0.0044725 | 18.5923
120 | -1.9259 | -0.92767 | 1.9272 | 0.9219 | 0.0013173 | -0.0057656 | 0.061815 | 0.061738 | 0.061815 | 0.9983 | 0.0043196 | 0.99893 | -0.0015196 | 28.0976
121 | 0.29734 | 0.142 | -0.29733 | -0.144 | 1.0242e-05 | -0.0020023 | 0.0095282 | 0.0095533 | 0.0095533 | 0.9983 | 0.0043196 | 0.99826 | 0.0046151 | 4.3424
122 | 0.41231 | 0.19949 | -0.41231 | -0.19969 | 1.9558e-06 | -0.0001986 | 0.013237 | 0.013239 | 0.013239 | 0.99893 | -0.0015196 | 0.99893 | -0.0014783 | 6.0177
123 | 0.15867 | 0.07656 | -0.15866 | -0.07679 | 3.3379e-07 | -0.00022961 | 0.0050911 | 0.0050939 | 0.0050939 | 0.99893 | -0.0015196 | 0.99893 | -0.0015013 | 2.3154
124 | -2.4982 | -1.198 | 2.4993 | 1.1952 | 0.0011109 | -0.0027659 | 0.080065 | 0.080026 | 0.080065 | 0.99893 | -0.0015196 | 0.99934 | -0.0052956 | 36.3932
125 | 0.15866 | 0.07679 | -0.15866 | -0.076844 | 2.1497e-06 | -5.4036e-05 | 0.0050939 | 0.0050946 | 0.0050946 | 0.99893 | -0.0015013 | 0.99891 | -0.0015908 | 2.426
126 | -3.9726 | -1.9081 | 3.974 | 1.9027 | 0.001472 | -0.0053798 | 0.1273 | 0.12722 | 0.1273 | 0.99934 | -0.0052956 | 0.99975 | -0.0010304 | 35.1671
127 | 1.4733 | 0.71294 | -1.4732 | -0.71338 | 5.8197e-05 | -0.00044769 | 0.047279 | 0.047284 | 0.047284 | 0.99934 | -0.0052956 | 0.99931 | -0.0049519 | 21.4929
128 | 0.25721 | 0.12355 | -0.2572 | -0.12457 | 3.8766e-06 | -0.001018 | 0.0082392 | 0.008252 | 0.008252 | 0.99975 | -0.0010304 | 0.99973 | -0.00090029 | 3.7509
129 | -4.2313 | -2.0263 | 4.2318 | 2.0025 | 0.00054246 | -0.023783 | 0.13546 | 0.13516 | 0.13546 | 0.99975 | -0.0010304 | 0.99988 | -0.00050908 | 10.6163
130 | 0.72025 | 0.34871 | -0.72025 | -0.34883 | 3.6784e-06 | -0.00012184 | 0.023117 | 0.023118 | 0.023118 | 0.99931 | -0.0049519 | 0.9993 | -0.0049075 | 10.5082
131 | 0.25196 | 0.12123 | -0.25195 | -0.12174 | 1.8802e-06 | -0.00051494 | 0.0080724 | 0.0080789 | 0.0080789 | 0.99988 | -0.00050908 | 0.99987 | -0.00044471 | 3.6722
132 | -4.4837 | -2.1237 | 4.4838 | 2.1216 | 5.3743e-05 | -0.0021002 | 0.14324 | 0.14321 | 0.14324 | 0.99988 | -0.00050908 | 0.99989 | -0.00045876 | 11.2255
133 | 0.25195 | 0.12174 | -0.25195 | -0.12203 | 1.0392e-06 | -0.00028425 | 0.0080789 | 0.0080825 | 0.0080825 | 0.99987 | -0.00044471 | 0.99987 | -0.00040888 | 3.6738
134 | -0.3872 | -0.18753 | 0.3872 | 0.187 | 4.7543e-06 | -0.00053394 | 0.012512 | 0.012506 | 0.012512 | 0.99256 | -0.14459 | 0.99257 | -0.1447 | 5.6875
135 | 0.31335 | 0.14643 | -0.31332 | -0.15122 | 2.7734e-05 | -0.0047923 | 0.010059 | 0.010119 | 0.010119 | 0.99257 | -0.1447 | 0.99249 | -0.14396 | 4.5996
136 | 0.31332 | 0.15122 | -0.31332 | -0.15175 | 3.0845e-06 | -0.00052941 | 0.010119 | 0.010126 | 0.010126 | 0.99249 | -0.14396 | 0.99248 | -0.14388 | 4.6027
137 | -0.40425 | -0.19579 | 0.40425 | 0.19567 | 1.1864e-06 | -0.00012069 | 0.013103 | 0.013101 | 0.013103 | 0.98959 | -0.12062 | 0.98959 | -0.12065 | 5.9558
138 | 0.27228 | 0.13146 | -0.27228 | -0.13187 | 1.7686e-06 | -0.00040866 | 0.0087588 | 0.008764 | 0.008764 | 0.99652 | 0.012351 | 0.99651 | 0.012407 | 3.9836
139 | 0.64877 | 0.27132 | -0.64823 | -0.29401 | 0.00054112 | -0.022688 | 0.020371 | 0.020636 | 0.020636 | 0.99652 | 0.012351 | 0.99573 | 0.017946 | 9.3798
140 | 2.2668 | 1.0321 | -2.2638 | -1.0414 | 0.0029922 | -0.0092906 | 0.072152 | 0.072275 | 0.072275 | 0.99652 | 0.012351 | 0.99528 | 0.022429 | 32.8524
141 | 0.26114 | 0.10656 | -0.26107 | -0.12634 | 7.6769e-05 | -0.019781 | 0.0081769 | 0.0084107 | 0.0084107 | 0.99573 | 0.017946 | 0.99545 | 0.020045 | 3.823
142 | 0.38709 | 0.18745 | -0.38708 | -0.18747 | 6.3508e-06 | -2.3158e-05 | 0.012469 | 0.012469 | 0.012469 | 0.99573 | 0.017946 | 0.99571 | 0.017838 | 5.9376
143 | 0.26107 | 0.12634 | -0.26105 | -0.12643 | 1.0354e-05 | -9.0679e-05 | 0.0084107 | 0.0084119 | 0.0084119 | 0.99545 | 0.020045 | 0.99541 | 0.019783 | 4.0057
144 | 2.2638 | 1.0414 | -2.2637 | -1.0417 | 9.122e-05 | -0.00028229 | 0.072275 | 0.072279 | 0.072279 | 0.99528 | 0.022429 | 0.99525 | 0.02274 | 32.8541
145 | 1.9586 | 0.89396 | -1.9583 | -0.89537 | 0.000333 | -0.0014132 | 0.062449 | 0.062467 | 0.062467 | 0.99525 | 0.02274 | 0.99509 | 0.024031 | 28.3941
146 | 1.9583 | 0.89537 | -1.9559 | -0.90546 | 0.0023866 | -0.010089 | 0.062467 | 0.062598 | 0.062598 | 0.99509 | 0.024031 | 0.99395 | 0.033457 | 28.4536
147 | 0.74755 | 0.36132 | -0.74753 | -0.36188 | 1.8158e-05 | -0.00055942 | 0.023972 | 0.023979 | 0.023979 | 0.99986 | 0.0008944 | 0.99984 | 0.0011054 | 10.8995
148 | -1.4336 | -0.6668 | 1.4337 | 0.66683 | 8.3394e-05 | 2.6651e-05 | 0.046185 | 0.046185 | 0.046185 | 0.98823 | 0.0060758 | 0.98829 | 0.0065176 | 21.993
149 | 1.09 | 0.50038 | -1.0877 | -0.50017 | 0.0022679 | 0.00021465 | 0.035034 | 0.035049 | 0.035049 | 0.98823 | 0.0060758 | 0.98604 | -0.010371 | 16.69
150 | -1.4337 | -0.66683 | 1.4352 | 0.65484 | 0.0015125 | -0.011991 | 0.046185 | 0.046033 | 0.046185 | 0.98829 | 0.0065176 | 0.98926 | -0.0016591 | 20.9932
151 | 0.84771 | 0.38394 | -0.84771 | -0.38406 | 5.4415e-06 | -0.00012585 | 0.027245 | 0.027246 | 0.027246 | 0.98604 | -0.010371 | 0.98603 | -0.010323 | 12.3846
152 | 0.19702 | 0.094504 | -0.19702 | -0.095419 | 2.1312e-06 | -0.00091517 | 0.0063763 | 0.0063879 | 0.0063879 | 0.98926 | -0.0016591 | 0.98925 | -0.0015659 | 2.9036
153 | -1.6322 | -0.74934 | 1.6388 | 0.7519 | 0.0066034 | 0.0025523 | 0.052408 | 0.052389 | 0.052408 | 0.98926 | -0.0016591 | 0.99352 | 0.03033 | 24.9564
154 | 0.77515 | 0.35024 | -0.77513 | -0.35068 | 1.6002e-05 | -0.00044385 | 0.024902 | 0.024908 | 0.024908 | 0.98603 | -0.010323 | 0.98601 | -0.01017 | 11.3218
155 | 0.072564 | 0.033825 | -0.072563 | -0.035144 | 4.1962e-07 | -0.0013188 | 0.0023439 | 0.0023604 | 0.0023604 | 0.98603 | -0.010323 | 0.98603 | -0.010275 | 1.0729
156 | -1.9551 | -0.9051 | 1.9559 | 0.90546 | 0.00079277 | 0.0003627 | 0.0626 | 0.062598 | 0.0626 | 0.99352 | 0.03033 | 0.99395 | 0.033457 | 29.8093
157 | -0.25566 | -0.12382 | 0.25566 | 0.12365 | 6.2604e-07 | -0.00016626 | 0.0082015 | 0.0081994 | 0.0082015 | 0.99984 | 0.0011267 | 0.99984 | 0.0011054 | 3.7279
158 | 0.38453 | 0.18322 | -0.38452 | -0.18448 | 1.0943e-05 | -0.0012587 | 0.01237 | 0.012386 | 0.012386 | 0.994 | -0.13949 | 0.99398 | -0.13925 | 5.6301
159 | 1.6541 | 0.78279 | -1.6541 | -0.78309 | 5.0027e-05 | -0.00029811 | 0.053146 | 0.05315 | 0.05315 | 0.994 | -0.13949 | 0.99398 | -0.13924 | 24.1592
160 | 0.070301 | 0.033797 | -0.070301 | -0.034048 | 7.2982e-08 | -0.00025096 | 0.0022653 | 0.0022685 | 0.0022685 | 0.994 | -0.13949 | 0.994 | -0.13948 | 1.0311
161 | 0.31338 | 0.15032 | -0.31338 | -0.1506 | 1.6377e-06 | -0.00028342 | 0.010094 | 0.010098 | 0.010098 | 0.99398 | -0.13925 | 0.99397 | -0.1392 | 4.5899
162 | 0.071137 | 0.03416 | -0.071137 | -0.034453 | 8.7195e-08 | -0.00029284 | 0.0022918 | 0.0022955 | 0.0022955 | 0.99398 | -0.13925 | 0.99398 | -0.13923 | 1.0434
163 | 0.073017 | 0.035177 | -0.073017 | -0.035364 | 5.8619e-08 | -0.00018674 | 0.0023539 | 0.0023562 | 0.0023562 | 0.99398 | -0.13924 | 0.99397 | -0.13923 | 1.071
164 | 0.13581 | 0.064602 | -0.13581 | -0.065258 | 7.0936e-07 | -0.00065556 | 0.0043678 | 0.0043761 | 0.0043761 | 0.99397 | -0.1392 | 0.99397 | -0.13916 | 1.9891
165 | 0.13581 | 0.065258 | -0.13581 | -0.065526 | 2.9096e-07 | -0.00026817 | 0.0043761 | 0.0043794 | 0.0043794 | 0.99397 | -0.13916 | 0.99397 | -0.13914 | 1.9907
166 | -0.092604 | -0.04485 | 0.092604 | 0.044094 | 3.8749e-07 | -0.00075553 | 0.0030016 | 0.002992 | 0.0030016 | 0.98957 | -0.12121 | 0.98957 | -0.12124 | 1.3644
167 | 0.13581 | 0.065526 | -0.13581 | -0.065776 | 2.7206e-07 | -0.0002504 | 0.0043794 | 0.0043826 | 0.0043826 | 0.99397 | -0.13914 | 0.99396 | -0.13912 | 1.9921
168 | 0.10777 | 0.046832 | -0.10777 | -0.050686 | 2.6589e-06 | -0.0038539 | 0.0034403 | 0.0034868 | 0.0034868 | 0.98601 | -0.01017 | 0.98599 | -0.0099873 | 1.5849
169 | 0.66736 | 0.30385 | -0.66731 | -0.30562 | 4.734e-05 | -0.0017701 | 0.021468 | 0.02149 | 0.02149 | 0.98601 | -0.01017 | 0.98595 | -0.009632 | 9.768
170 | 0.10777 | 0.050686 | -0.10777 | -0.052195 | 1.0613e-06 | -0.0015092 | 0.0034868 | 0.0035059 | 0.0035059 | 0.98599 | -0.0099873 | 0.98598 | -0.0099043 | 1.5936
171 | 0.54407 | 0.24593 | -0.54404 | -0.24731 | 2.4341e-05 | -0.0013761 | 0.017481 | 0.017498 | 0.017498 | 0.98595 | -0.009632 | 0.98591 | -0.0092988 | 7.9537
172 | 0.54404 | 0.24731 | -0.54386 | -0.25724 | 0.00017712 | -0.009931 | 0.017498 | 0.017621 | 0.017621 | 0.98591 | -0.0092988 | 0.98561 | -0.0067324 | 8.0096
173 | 0.131 | 0.063074 | -0.131 | -0.063445 | 3.8865e-07 | -0.00037167 | 0.0042588 | 0.0042636 | 0.0042636 | 0.98551 | -0.0058051 | 0.9855 | -0.0057795 | 1.938
174 | -0.45952 | -0.22218 | 0.45954 | 0.22043 | 2.2573e-05 | -0.0017501 | 0.014951 | 0.014929 | 0.014951 | 0.98551 | -0.0058051 | 0.98555 | -0.0062277 | 6.7959
175 | -0.45954 | -0.22043 | 0.45957 | 0.21829 | 2.7503e-05 | -0.0021396 | 0.014929 | 0.014902 | 0.014929 | 0.98555 | -0.0062277 | 0.98561 | -0.0067324 | 6.7858
176 | 0.084295 | 0.038945 | -0.084294 | -0.040826 | 8.076e-07 | -0.0018805 | 0.0027197 | 0.0027433 | 0.0027433 | 0.98561 | -0.0067324 | 0.9856 | -0.0066532 | 1.2469

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 21.9405 | 9.9381

## res_load
| p_mw | q_mvar
0 | 0.21316 | 0.10324
1 | 0.22907 | 0.11094
2 | 0.24478 | 0.11855
3 | 0.22911 | 0.11096
4 | 0.24191 | 0.11716
5 | 0.10549 | 0.051091
6 | 0.16864 | 0.081675
7 | 0.081656 | 0.039548
8 | 0.10252 | 0.049651
9 | 0.35749 | 0.17314
10 | 0.40392 | 0.19563
11 | 0.2934 | 0.1421
12 | 0.073415 | 0.035556
13 | 0.30184 | 0.14619
14 | 0.29787 | 0.14426
15 | 0.12767 | 0.061833
16 | 0.23247 | 0.11259
17 | 0.14848 | 0.071914
18 | 0.29829 | 0.14447
19 | 0.069871 | 0.03384
20 | 0.072549 | 0.035137
21 | 0.37607 | 0.18214
22 | 0.18318 | 0.088716
23 | 0.10749 | 0.052057
24 | 0.15462 | 0.074885
25 | 0.40291 | 0.19514
26 | 0.13477 | 0.065273
27 | 0.1123 | 0.054388
28 | 0.18248 | 0.088377
29 | 0.22537 | 0.10915
30 | 0.35102 | 0.17001
31 | 0.075393 | 0.036515
32 | 0.27476 | 0.13307
33 | 0.085724 | 0.041518
34 | 0.070441 | 0.034116
35 | 0.19787 | 0.095831
36 | 0.27032 | 0.13092
37 | 0.368 | 0.17823
38 | 0.072566 | 0.035145
39 | 0.08322 | 0.040305
40 | 0.11067 | 0.0536
41 | 0.096876 | 0.046919
42 | 0.31616 | 0.15313
43 | 0.081444 | 0.039445
44 | 0.10673 | 0.051693
45 | 0.39661 | 0.19209
46 | 0.25631 | 0.12414
47 | 0.29532 | 0.14303
48 | 0.37924 | 0.18368
49 | 0.33285 | 0.1612
50 | 0.10683 | 0.051741
51 | 0.33233 | 0.16096
52 | 0.080916 | 0.039189
53 | 1.2145 | 0.58821
54 | 0.29733 | 0.144
55 | 0.41231 | 0.19969
56 | 0.75296 | 0.36467
57 | 0.15866 | 0.076844
58 | 0.2572 | 0.12457
59 | 0.18866 | 0.091372
60 | 0.72025 | 0.34883
61 | 0.25195 | 0.12203
62 | 0.3872 | 0.18753
63 | 0.31332 | 0.15175
64 | 0.40425 | 0.19579
65 | 0.38708 | 0.18747
66 | 0.30509 | 0.14776
67 | 0.27228 | 0.13187
68 | 0.26105 | 0.12643
69 | 0.17147 | 0.083045
70 | 0.3833 | 0.18564
71 | 0.32303 | 0.15645
72 | 0.12644 | 0.061235
73 | 0.34362 | 0.16642
74 | 0.23998 | 0.11623
75 | 0.19702 | 0.095419
76 | 0.31633 | 0.1532
77 | 0.25566 | 0.12382
78 | 0.49188 | 0.23823
79 | 0.070301 | 0.034048
80 | 0.17757 | 0.086001
81 | 0.071137 | 0.034453
82 | 0.073017 | 0.035364
83 | 0.092604 | 0.04485
84 | 0.13581 | 0.065776
85 | 0.072563 | 0.035144
86 | 0.12324 | 0.059689
87 | 0.10777 | 0.052195
88 | 0.32852 | 0.15911
89 | 0.131 | 0.063445
90 | 0.084294 | 0.040826

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1