## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_58_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_58_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_58_0_node_3 | 20 | n |  | TRUE
3 | bus_MV_58_0_node_1 | 20 | n |  | TRUE
4 | bus_MV_58_0_node_6 | 20 | n |  | TRUE
5 | bus_MV_58_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_58_0_node_5 | 20 | n |  | TRUE
7 | bus_MV_58_0_node_42 | 20 | n |  | TRUE
8 | bus_MV_58_0_node_37 | 20 | n |  | TRUE
9 | bus_MV_58_0_node_40 | 20 | n |  | TRUE
10 | bus_MV_58_0_node_35 | 20 | n |  | TRUE
11 | bus_MV_58_0_node_39 | 20 | n |  | TRUE
12 | bus_MV_58_0_node_17 | 20 | n |  | TRUE
13 | bus_MV_58_0_node_43 | 20 | n |  | TRUE
14 | bus_MV_58_0_node_41 | 20 | n |  | TRUE
15 | bus_MV_58_0_node_52 | 20 | n |  | TRUE
16 | bus_MV_58_0_node_7 | 20 | n |  | TRUE
17 | bus_MV_58_0_node_57 | 20 | n |  | TRUE
18 | bus_MV_58_0_node_59 | 20 | n |  | TRUE
19 | bus_MV_58_0_node_8 | 20 | n |  | TRUE
20 | bus_MV_58_0_node_9 | 20 | n |  | TRUE
21 | bus_MV_58_0_node_10 | 20 | n |  | TRUE
22 | bus_MV_58_0_node_58 | 20 | n |  | TRUE
23 | bus_MV_58_0_node_11 | 20 | n |  | TRUE
24 | bus_MV_58_0_node_13 | 20 | n |  | TRUE
25 | bus_MV_58_0_node_61 | 20 | n |  | TRUE
26 | bus_MV_58_0_node_76 | 20 | n |  | TRUE
27 | bus_MV_58_0_node_66 | 20 | n |  | TRUE
28 | bus_MV_58_0_node_60 | 20 | n |  | TRUE
29 | bus_MV_58_0_node_12 | 20 | n |  | TRUE
30 | bus_MV_58_0_node_14 | 20 | n |  | TRUE
31 | bus_MV_58_0_node_15 | 20 | n |  | TRUE
32 | bus_MV_58_0_node_16 | 20 | n |  | TRUE
33 | bus_MV_58_0_node_34 | 20 | n |  | TRUE
34 | bus_MV_58_0_node_36 | 20 | n |  | TRUE
35 | bus_MV_58_0_node_32 | 20 | n |  | TRUE
36 | bus_MV_58_0_node_18 | 20 | n |  | TRUE
37 | bus_MV_58_0_node_19 | 20 | n |  | TRUE
38 | bus_MV_58_0_node_20 | 20 | n |  | TRUE
39 | bus_MV_58_0_node_77 | 20 | n |  | TRUE
40 | bus_MV_58_0_node_28 | 20 | n |  | TRUE
41 | bus_MV_58_0_node_75 | 20 | n |  | TRUE
42 | bus_MV_58_0_node_21 | 20 | n |  | TRUE
43 | bus_MV_58_0_node_27 | 20 | n |  | TRUE
44 | bus_MV_58_0_node_25 | 20 | n |  | TRUE
45 | bus_MV_58_0_node_22 | 20 | n |  | TRUE
46 | bus_MV_58_0_node_23 | 20 | n |  | TRUE
47 | bus_MV_58_0_node_79 | 20 | n |  | TRUE
48 | bus_MV_58_0_node_78 | 20 | n |  | TRUE
49 | bus_MV_58_0_node_29 | 20 | n |  | TRUE
50 | bus_MV_58_0_node_30 | 20 | n |  | TRUE
51 | bus_MV_58_0_node_31 | 20 | n |  | TRUE
52 | bus_MV_58_0_node_55 | 20 | n |  | TRUE
53 | bus_MV_58_0_node_47 | 20 | n |  | TRUE
54 | bus_MV_58_0_node_54 | 20 | n |  | TRUE
55 | bus_MV_58_0_node_68 | 20 | n |  | TRUE
56 | bus_MV_58_0_node_67 | 20 | n |  | TRUE
57 | bus_MV_58_0_node_33 | 20 | n |  | TRUE
58 | bus_MV_58_0_node_38 | 20 | n |  | TRUE
59 | bus_MV_58_0_node_53 | 20 | n |  | TRUE
60 | bus_MV_58_0_node_49 | 20 | n |  | TRUE
61 | bus_MV_58_0_node_48 | 20 | n |  | TRUE
62 | bus_MV_58_0_node_46 | 20 | n |  | TRUE
63 | bus_MV_58_0_node_50 | 20 | n |  | TRUE
64 | bus_MV_58_0_node_44 | 20 | n |  | TRUE
65 | bus_MV_58_0_node_45 | 20 | n |  | TRUE
66 | bus_MV_58_0_node_51 | 20 | n |  | TRUE
67 | bus_MV_58_0_node_64 | 20 | n |  | TRUE
68 | bus_MV_58_0_node_62 | 20 | n |  | TRUE
69 | bus_MV_58_0_node_63 | 20 | n |  | TRUE
70 | bus_MV_58_0_node_65 | 20 | n |  | TRUE
71 | bus_MV_58_0_node_69 | 20 | n |  | TRUE
72 | bus_MV_58_0_node_70 | 20 | n |  | TRUE
73 | bus_MV_58_0_node_71 | 20 | n |  | TRUE
74 | bus_MV_58_0_node_72 | 20 | n |  | TRUE
75 | bus_MV_58_0_node_73 | 20 | n |  | TRUE
76 | bus_MV_58_0_node_74 | 20 | n |  | TRUE
77 | bus_HV_58_0_node_60 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_58_0_load_0 | 0 | 0.14421 | 0.069846 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_58_0_load_2 | 1 | 0.18025 | 0.087298 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_58_0_load_3 | 2 | 1.0608 | 0.51375 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_58_0_load_1 | 3 | 0.50992 | 0.24697 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_58_0_load_6 | 4 | 0.27987 | 0.13555 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_58_0_load_4 | 5 | 0.11409 | 0.055256 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_58_0_load_5 | 6 | 0.40275 | 0.19506 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_58_0_load_42 | 7 | 0.086096 | 0.041698 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_58_0_load_37 | 8 | 1.9556 | 0.94714 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_58_0_load_35 | 10 | 0.19936 | 0.096552 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_58_0_load_39 | 11 | 0.18148 | 0.087897 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_58_0_load_52 | 15 | 0.30341 | 0.14695 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_58_0_load_7 | 16 | 0.15805 | 0.076545 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_58_0_load_59 | 18 | 0.38845 | 0.18813 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_58_0_load_58 | 22 | 0.22938 | 0.11109 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_58_0_load_11 | 23 | 0.30022 | 0.1454 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_58_0_load_13 | 24 | 0.21517 | 0.10421 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_58_0_load_76 | 26 | 0.18369 | 0.088963 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_58_0_load_66 | 27 | 0.077242 | 0.03741 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_58_0_load_60 | 28 | 0.29459 | 0.14268 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_58_0_load_14 | 30 | 0.103 | 0.049886 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_58_0_load_15 | 31 | 0.31073 | 0.15049 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_58_0_load_16 | 32 | 0.19877 | 0.096267 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_58_0_load_36 | 34 | 0.087902 | 0.042573 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_58_0_load_32 | 35 | 0.17031 | 0.082486 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_58_0_load_18 | 36 | 0.26797 | 0.12978 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_58_0_load_28 | 40 | 0.20552 | 0.09954 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_58_0_load_75 | 41 | 0.41946 | 0.20315 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_58_0_load_27 | 43 | 0.3629 | 0.17576 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_58_0_load_22 | 45 | 0.35252 | 0.17073 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_58_0_load_79 | 47 | 1.9119 | 0.92596 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_58_0_load_78 | 48 | 0.865 | 0.41894 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_58_0_load_29 | 49 | 0.053251 | 0.02579 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_58_0_load_31 | 51 | 0.15564 | 0.075382 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_58_0_load_47 | 53 | 0.36195 | 0.1753 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_58_0_load_54 | 54 | 0.70733 | 0.34258 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_58_0_load_68 | 55 | 0.30211 | 0.14632 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_58_0_load_67 | 56 | 0.30412 | 0.14729 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_58_0_load_33 | 57 | 0.39612 | 0.19185 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_58_0_load_38 | 58 | 0.12696 | 0.06149 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_58_0_load_53 | 59 | 0.27708 | 0.13419 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_58_0_load_49 | 60 | 0.081952 | 0.039691 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_58_0_load_48 | 61 | 0.46336 | 0.22442 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_58_0_load_46 | 62 | 0.12197 | 0.059072 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_58_0_load_50 | 63 | 0.59311 | 0.28726 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_58_0_load_44 | 64 | 0.32335 | 0.15661 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_58_0_load_45 | 65 | 0.43015 | 0.20833 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_58_0_load_51 | 66 | 0.6666 | 0.32285 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_58_0_load_64 | 67 | 0.10452 | 0.050622 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_58_0_load_62 | 68 | 0.30419 | 0.14732 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_58_0_load_63 | 69 | 0.078671 | 0.038102 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_58_0_load_65 | 70 | 0.20222 | 0.097938 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_58_0_load_69 | 71 | 0.35922 | 0.17398 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_58_0_load_70 | 72 | 0.18514 | 0.089666 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_58_0_load_71 | 73 | 0.15973 | 0.077358 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_58_0_load_72 | 74 | 0.091165 | 0.044153 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_58_0_load_73 | 75 | 0.1405 | 0.068048 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_58_0_load_74 | 76 | 0.32539 | 0.15759 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_58_0_line_0 |  | 0 | 1 | 0.046569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_58_0_line_1 |  | 0 | 2 | 0.057345 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
2 | MV_58_0_line_2 |  | 0 | 3 | 0.047291 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
3 | MV_58_0_line_3 |  | 2 | 4 | 0.048023 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
4 | MV_58_0_line_4 |  | 3 | 5 | 0.00071641 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
5 | MV_58_0_line_5 |  | 4 | 7 | 0.010154 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_58_0_line_6 |  | 5 | 6 | 0.011249 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
7 | MV_58_0_line_7 |  | 6 | 11 | 0.093187 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
8 | MV_58_0_line_8 |  | 7 | 13 | 0.017643 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_58_0_line_9 |  | 8 | 9 | 0.039272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_58_0_line_10 |  | 8 | 10 | 0.035062 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_58_0_line_11 |  | 9 | 14 | 0.10562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_58_0_line_12 |  | 9 | 20 | 0.11157 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_58_0_line_13 |  | 10 | 57 | 0.026768 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_58_0_line_14 |  | 11 | 12 | 0.005231 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
15 | MV_58_0_line_15 |  | 12 | 28 | 0.051377 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
16 | MV_58_0_line_16 |  | 12 | 31 | 0.041612 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
17 | MV_58_0_line_17 |  | 13 | 60 | 0.057968 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_58_0_line_18 |  | 13 | 61 | 0.041763 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_58_0_line_19 |  | 14 | 15 | 0.060328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_58_0_line_20 |  | 15 | 59 | 0.0038597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_58_0_line_21 |  | 16 | 17 | 0.16841 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
22 | MV_58_0_line_22 |  | 17 | 18 | 0.29059 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_58_0_line_23 |  | 18 | 20 | 0.036522 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_58_0_line_24 |  | 19 | 20 | 0.1519 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_58_0_line_25 |  | 19 | 21 | 0.28378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_58_0_line_26 |  | 21 | 22 | 0.030562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_58_0_line_27 |  | 23 | 24 | 0.037404 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_58_0_line_28 |  | 23 | 25 | 0.083891 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
29 | MV_58_0_line_29 |  | 25 | 26 | 0.044738 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
30 | MV_58_0_line_30 |  | 25 | 27 | 0.11614 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_58_0_line_31 |  | 25 | 28 | 0.037798 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
32 | MV_58_0_line_32 |  | 26 | 39 | 0.033559 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
33 | MV_58_0_line_33 |  | 27 | 67 | 0.0013224 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_58_0_line_34 |  | 29 | 30 | 0.025878 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_58_0_line_35 |  | 29 | 31 | 0.042151 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
36 | MV_58_0_line_36 |  | 30 | 32 | 0.010208 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
37 | MV_58_0_line_37 |  | 32 | 33 | 0.013657 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
38 | MV_58_0_line_38 |  | 33 | 34 | 0.021691 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_58_0_line_39 |  | 33 | 35 | 0.055886 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
40 | MV_58_0_line_40 |  | 34 | 58 | 0.031389 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_58_0_line_41 |  | 35 | 57 | 0.006582 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_58_0_line_42 |  | 36 | 37 | 0.102 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_58_0_line_43 |  | 37 | 38 | 0.15307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_58_0_line_44 |  | 38 | 42 | 0.10499 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_58_0_line_45 |  | 38 | 43 | 0.0299 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_58_0_line_46 |  | 39 | 40 | 1.311 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
47 | MV_58_0_line_47 |  | 39 | 41 | 0.04348 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
48 | MV_58_0_line_48 |  | 40 | 42 | 0.17361 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_58_0_line_49 |  | 41 | 76 | 0.036797 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
50 | MV_58_0_line_50 |  | 43 | 44 | 0.059962 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_58_0_line_51 |  | 44 | 46 | 0.30382 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_58_0_line_52 |  | 45 | 46 | 0.006426 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_58_0_line_53 |  | 47 | 48 | 0.15503 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_58_0_line_54 |  | 48 | 76 | 0.12833 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
55 | MV_58_0_line_55 |  | 49 | 50 | 0.023346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_58_0_line_56 |  | 50 | 51 | 2.2733 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_58_0_line_57 |  | 51 | 55 | 3.3431 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
58 | MV_58_0_line_58 |  | 52 | 53 | 0.13052 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
59 | MV_58_0_line_59 |  | 52 | 54 | 0.018677 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_58_0_line_60 |  | 53 | 65 | 0.015937 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_58_0_line_61 |  | 55 | 56 | 0.0043394 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_58_0_line_62 |  | 56 | 71 | 0.066548 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_58_0_line_63 |  | 60 | 63 | 0.034246 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_58_0_line_64 |  | 61 | 62 | 0.05789 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_58_0_line_65 |  | 62 | 64 | 0.05002 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_58_0_line_66 |  | 63 | 66 | 0.0018071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_58_0_line_67 |  | 64 | 65 | 0.0063407 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_58_0_line_68 |  | 67 | 68 | 0.031721 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_58_0_line_69 |  | 68 | 69 | 0.020816 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_58_0_line_70 |  | 69 | 70 | 0.018285 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_58_0_line_71 |  | 71 | 72 | 0.00090596 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_58_0_line_72 |  | 72 | 73 | 0.027659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_58_0_line_73 |  | 73 | 74 | 0.016515 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_58_0_line_74 |  | 74 | 75 | 0.004324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_58_0_line_75 |  | 75 | 76 | 0.025182 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_58_0_trafo_60 | 25 MVA 110/20 kV | 77 | 28 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2751976.3143 | 1188098.1791
1 | 2751982.8298 | 1188052.0686
2 | 2752033.0142 | 1188106.7459
3 | 2751929.4838 | 1188091.5983
4 | 2752080.4706 | 1188114.1015
5 | 2751928.7744 | 1188091.4987
6 | 2751917.6344 | 1188089.9339
7 | 2752090.5052 | 1188115.6568
8 | 2751978.0452 | 1188190.5441
9 | 2751980.9878 | 1188228.5506
10 | 2751946.6952 | 1188178.7052
11 | 2751825.3529 | 1188076.9717
12 | 2751820.1728 | 1188076.244
13 | 2752107.9396 | 1188118.3591
14 | 2752085.7891 | 1188240.8993
15 | 2752145.1783 | 1188250.6475
16 | 2752457.1535 | 1188464.2185
17 | 2752342.4901 | 1188340.8746
18 | 2752059.0289 | 1188296.7121
19 | 2752025.5854 | 1188419.8764
20 | 2752023.2787 | 1188295.8805
21 | 2751928.2003 | 1188673.7513
22 | 2751898.6341 | 1188666.4362
23 | 2751713.5208 | 1188145.1066
24 | 2751708.0677 | 1188182.1106
25 | 2751731.9473 | 1188063.2639
26 | 2751687.6841 | 1188056.7599
27 | 2751749.8584 | 1187948.5157
28 | 2751769.3431 | 1188068.7629
29 | 2751809.0828 | 1188159.2658
30 | 2751834.7052 | 1188162.8953
31 | 2751814.9259 | 1188117.5235
32 | 2751844.8123 | 1188164.327
33 | 2751858.3345 | 1188166.2425
34 | 2751855.3006 | 1188187.72
35 | 2751913.6725 | 1188174.0476
36 | 2750207.1169 | 1188619.5766
37 | 2750206.4873 | 1188517.5759
38 | 2750152.6711 | 1188402.4195
39 | 2751654.4813 | 1188051.8811
40 | 2750399.3804 | 1188430.7118
41 | 2751660.7368 | 1188008.8537
42 | 2750244.451 | 1188430.8784
43 | 2750132.0202 | 1188380.7504
44 | 2750093.0574 | 1188335.1247
45 | 2750197.1026 | 1188134.967
46 | 2750191.1824 | 1188132.4275
47 | 2751489.0461 | 1188093.8517
48 | 2751539.8908 | 1187948.8165
49 | 2753533.0417 | 1182644.9643
50 | 2753539.0181 | 1182666.6355
51 | 2752238.4281 | 1184531.1499
52 | 2752267.0525 | 1187944.6011
53 | 2752136.615 | 1187949.2236
54 | 2752279.7656 | 1187958.2836
55 | 2751686.9607 | 1187828.4797
56 | 2751686.3363 | 1187832.774
57 | 2751920.19 | 1188174.9668
58 | 2751850.9102 | 1188218.8003
59 | 2752148.9994 | 1188251.1914
60 | 2752165.3852 | 1188126.1269
61 | 2752115.256 | 1188077.4165
62 | 2752126.3991 | 1188020.7958
63 | 2752199.3222 | 1188130.7159
64 | 2752133.467 | 1187971.2781
65 | 2752134.363 | 1187965.001
66 | 2752201.1131 | 1188130.958
67 | 2751750.0623 | 1187947.2091
68 | 2751754.9544 | 1187915.8678
69 | 2751758.1647 | 1187895.3011
70 | 2751760.9847 | 1187877.2347
71 | 2751676.7618 | 1187898.6297
72 | 2751676.6315 | 1187899.5262
73 | 2751672.6522 | 1187926.8971
74 | 2751670.2761 | 1187943.2402
75 | 2751669.654 | 1187947.5192
76 | 2751666.031 | 1187972.4394
77 | 2751769.3431 | 1188068.7629

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99958 | -0.0093107 | 0.14421 | 0.069846
1 | 0.99957 | -0.0092119 | 0.18025 | 0.087298
2 | 0.99951 | -0.010443 | 1.0608 | 0.51375
3 | 0.99971 | -0.0050286 | 0.50992 | 0.24697
4 | 0.99941 | -0.011559 | 0.27987 | 0.13555
5 | 0.99971 | -0.0050121 | 0.11409 | 0.055256
6 | 0.99973 | -0.0047493 | 0.40275 | 0.19506
7 | 0.99936 | -0.011097 | 0.086096 | 0.041698
8 | 0.99931 | -0.0033004 | 1.9556 | 0.94714
9 | 0.99924 | -0.0027281 | 0 | 0
10 | 0.99946 | -0.0046306 | 0.19936 | 0.096552
11 | 0.99986 | -0.0024267 | 0.18148 | 0.087897
12 | 0.99987 | -0.0022925 | 0 | 0
13 | 0.99927 | -0.010313 | 0 | 0
14 | 0.99916 | -0.0020122 | 0 | 0
15 | 0.99912 | -0.0015956 | 0.30341 | 0.14695
16 | 0.999 | -0.0014559 | 0.15805 | 0.076545
17 | 0.99905 | -0.0011322 | 0 | 0
18 | 0.99911 | -0.0016147 | 0.38845 | 0.18813
19 | 0.99909 | -0.0015089 | 0 | 0
20 | 0.99913 | -0.0018363 | 0 | 0
21 | 0.99901 | -0.00080313 | 0 | 0
22 | 0.999 | -0.0007198 | 0.22938 | 0.11109
23 | 0.99985 | -0.0016835 | 0.30022 | 0.1454
24 | 0.99984 | -0.0015882 | 0.21517 | 0.10421
25 | 0.99993 | -0.0011541 | 0 | 0
26 | 0.99987 | -0.0022996 | 0.18369 | 0.088963
27 | 0.99982 | -0.00011142 | 0.077242 | 0.03741
28 | 1 | 0 | -19.5723 | -9.3618
29 | 0.99978 | -0.0038294 | 0 | 0
30 | 0.99976 | -0.0042881 | 0.103 | 0.049886
31 | 0.99982 | -0.0030812 | 0.31073 | 0.15049
32 | 0.99975 | -0.004465 | 0.19877 | 0.096267
33 | 0.99973 | -0.0046912 | 0 | 0
34 | 0.99973 | -0.0046368 | 0.087902 | 0.042573
35 | 0.99961 | -0.0060046 | 0.17031 | 0.082486
36 | 0.99637 | -0.021211 | 0.26797 | 0.12978
37 | 0.99642 | -0.020878 | 0 | 0
38 | 0.99647 | -0.021353 | 0 | 0
39 | 0.99982 | -0.0031346 | 0 | 0
40 | 0.99682 | -0.024358 | 0.20552 | 0.09954
41 | 0.99977 | -0.0040109 | 0.41946 | 0.20315
42 | 0.9966 | -0.0225 | 0 | 0
43 | 0.99644 | -0.021113 | 0.3629 | 0.17576
44 | 0.99642 | -0.020889 | 0 | 0
45 | 0.99628 | -0.019645 | 0.35252 | 0.17073
46 | 0.99628 | -0.019672 | 0 | 0
47 | 0.99861 | -0.0058428 | 1.9119 | 0.92596
48 | 0.99898 | -0.0093792 | 0.865 | 0.41894
49 | 0.99789 | -0.014834 | 0.053251 | 0.02579
50 | 0.99789 | -0.014849 | 0 | 0
51 | 0.99812 | -0.01301 | 0.15564 | 0.075382
52 | 0.99867 | -0.0074997 | 0 | 0
53 | 0.99885 | -0.0063755 | 0.36195 | 0.1753
54 | 0.99866 | -0.0073415 | 0.70733 | 0.34258
55 | 0.99946 | -0.0030548 | 0.30211 | 0.14632
56 | 0.99946 | -0.0030793 | 0.30412 | 0.14729
57 | 0.99958 | -0.0057085 | 0.39612 | 0.19185
58 | 0.99972 | -0.0045899 | 0.12696 | 0.06149
59 | 0.99912 | -0.0015828 | 0.27708 | 0.13419
60 | 0.99917 | -0.0093867 | 0.081952 | 0.039691
61 | 0.99915 | -0.0091188 | 0.46336 | 0.22442
62 | 0.999 | -0.0077804 | 0.12197 | 0.059072
63 | 0.99912 | -0.0088706 | 0.59311 | 0.28726
64 | 0.99889 | -0.0066927 | 0.32335 | 0.15661
65 | 0.99887 | -0.0065791 | 0.43015 | 0.20833
66 | 0.99912 | -0.0088562 | 0.6666 | 0.32285
67 | 0.99982 | -0.00010065 | 0.10452 | 0.050622
68 | 0.9998 | 0.00011882 | 0.30419 | 0.14732
69 | 0.99979 | 0.00018789 | 0.078671 | 0.038102
70 | 0.99978 | 0.0002319 | 0.20222 | 0.097938
71 | 0.99953 | -0.0036948 | 0.35922 | 0.17398
72 | 0.99953 | -0.003707 | 0.18514 | 0.089666
73 | 0.99958 | -0.0041411 | 0.15973 | 0.077358
74 | 0.99961 | -0.0044312 | 0.091165 | 0.044153
75 | 0.99962 | -0.0045119 | 0.1405 | 0.068048
76 | 0.99967 | -0.0050232 | 0.32539 | 0.15759
77 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.18025 | 0.086187 | -0.18025 | -0.087298 | 2.0748e-06 | -0.0011103 | 0.00577 | 0.0057839 | 0.0057839 | 0.99958 | -0.0093107 | 0.99957 | -0.0092119 | 2.6291
1 | 5.179 | 2.4946 | -5.1787 | -2.4987 | 0.00028932 | -0.0041118 | 0.16601 | 0.16607 | 0.16607 | 0.99958 | -0.0093107 | 0.99951 | -0.010443 | 19.7232
2 | -5.5035 | -2.6506 | 5.504 | 2.6513 | 0.00052453 | 0.00063708 | 0.17641 | 0.17641 | 0.17641 | 0.99958 | -0.0093107 | 0.99971 | -0.0050286 | 21.5137
3 | 4.118 | 1.985 | -4.1176 | -1.9863 | 0.00040439 | -0.0013518 | 0.13203 | 0.13205 | 0.13205 | 0.99951 | -0.010443 | 0.99941 | -0.011559 | 36.4778
4 | -6.0139 | -2.8983 | 6.0139 | 2.8982 | 4.8727e-06 | -5.0232e-05 | 0.19277 | 0.19277 | 0.19277 | 0.99971 | -0.0050286 | 0.99971 | -0.0050121 | 22.8945
5 | 3.8377 | 1.8508 | -3.8375 | -1.851 | 0.00020532 | -0.00018125 | 0.12307 | 0.12307 | 0.12307 | 0.99941 | -0.011559 | 0.99936 | -0.011097 | 55.9411
6 | -6.128 | -2.9535 | 6.1281 | 2.9527 | 7.9428e-05 | -0.00078609 | 0.19643 | 0.19642 | 0.19643 | 0.99971 | -0.0050121 | 0.99973 | -0.0047493 | 23.3291
7 | -6.5309 | -3.1477 | 6.5316 | 3.1413 | 0.00074703 | -0.0064311 | 0.20934 | 0.20925 | 0.20934 | 0.99973 | -0.0047493 | 0.99986 | -0.0024267 | 24.8625
8 | 3.7514 | 1.8093 | -3.751 | -1.8096 | 0.00034091 | -0.00031953 | 0.12031 | 0.12031 | 0.12031 | 0.99936 | -0.011097 | 0.99927 | -0.010313 | 54.6875
9 | 1.3567 | 0.63026 | -1.3566 | -0.63117 | 9.7934e-05 | -0.00090726 | 0.043214 | 0.043225 | 0.043225 | 0.99931 | -0.0033004 | 0.99924 | -0.0027281 | 19.6479
10 | -3.3123 | -1.5774 | 3.3128 | 1.5767 | 0.00052568 | -0.00068018 | 0.10598 | 0.10597 | 0.10598 | 0.99931 | -0.0033004 | 0.99946 | -0.0046306 | 48.1727
11 | 0.58056 | 0.27712 | -0.58051 | -0.27962 | 4.8784e-05 | -0.0025033 | 0.018585 | 0.018616 | 0.018616 | 0.99924 | -0.0027281 | 0.99916 | -0.0020122 | 8.4619
12 | 0.77603 | 0.35405 | -0.77594 | -0.35669 | 9.0561e-05 | -0.0026326 | 0.024642 | 0.024674 | 0.024674 | 0.99924 | -0.0027281 | 0.99913 | -0.0018363 | 11.2155
13 | -3.5122 | -1.6733 | 3.5126 | 1.6728 | 0.00045117 | -0.00050466 | 0.11237 | 0.11236 | 0.11237 | 0.99946 | -0.0046306 | 0.99958 | -0.0057085 | 51.076
14 | -6.7131 | -3.2292 | 6.7131 | 3.2288 | 4.428e-05 | -0.00035891 | 0.21507 | 0.21507 | 0.21507 | 0.99986 | -0.0024267 | 0.99987 | -0.0022925 | 25.5433
15 | -11.6207 | -5.564 | 11.622 | 5.5613 | 0.0013008 | -0.0027307 | 0.37198 | 0.37193 | 0.37198 | 0.99987 | -0.0022925 | 1 | 0 | 44.178
16 | 4.9076 | 2.3352 | -4.9074 | -2.3382 | 0.00018753 | -0.0030061 | 0.15691 | 0.15695 | 0.15695 | 0.99987 | -0.0022925 | 0.99982 | -0.0030812 | 18.64
17 | 1.3419 | 0.64762 | -1.3417 | -0.64896 | 0.00014344 | -0.0013394 | 0.043044 | 0.043061 | 0.043061 | 0.99927 | -0.010313 | 0.99917 | -0.0093867 | 19.5732
18 | 2.4092 | 1.162 | -2.4088 | -1.1629 | 0.00033293 | -0.00089681 | 0.077269 | 0.077281 | 0.077281 | 0.99927 | -0.010313 | 0.99915 | -0.0091188 | 35.1279
19 | 0.58051 | 0.27962 | -0.58048 | -0.28105 | 2.7939e-05 | -0.0014296 | 0.018616 | 0.018634 | 0.018634 | 0.99916 | -0.0020122 | 0.99912 | -0.0015956 | 8.4701
20 | 0.27708 | 0.1341 | -0.27708 | -0.13419 | 4.0762e-07 | -9.1871e-05 | 0.0088939 | 0.0088951 | 0.0088951 | 0.99912 | -0.0015956 | 0.99912 | -0.0015828 | 4.0432
21 | -0.15805 | -0.076545 | 0.15805 | 0.076349 | 7.7225e-06 | -0.00019582 | 0.0050744 | 0.0050719 | 0.0050744 | 0.999 | -0.0014559 | 0.99905 | -0.0011322 | 2.4164
22 | -0.15805 | -0.076349 | 0.15806 | 0.069427 | 9.8119e-06 | -0.0069224 | 0.0050719 | 0.0049881 | 0.0050719 | 0.99905 | -0.0011322 | 0.99911 | -0.0016147 | 2.3054
23 | -0.54651 | -0.25756 | 0.54653 | 0.2567 | 1.4848e-05 | -0.00086606 | 0.017456 | 0.017446 | 0.017456 | 0.99911 | -0.0016147 | 0.99913 | -0.0018363 | 7.9347
24 | -0.2294 | -0.10361 | 0.22941 | 0.099992 | 1.0664e-05 | -0.0036173 | 0.007273 | 0.0072306 | 0.007273 | 0.99909 | -0.0015089 | 0.99913 | -0.0018363 | 3.3059
25 | 0.2294 | 0.10361 | -0.22938 | -0.11037 | 2.0265e-05 | -0.0067567 | 0.007273 | 0.0073556 | 0.0073556 | 0.99909 | -0.0015089 | 0.99901 | -0.00080313 | 3.3434
26 | 0.22938 | 0.11037 | -0.22938 | -0.11109 | 2.2102e-06 | -0.00072758 | 0.0073556 | 0.0073647 | 0.0073647 | 0.99901 | -0.00080313 | 0.999 | -0.0007198 | 3.3476
27 | 0.21517 | 0.10332 | -0.21517 | -0.10421 | 2.3753e-06 | -0.00089207 | 0.0068915 | 0.0069027 | 0.0069027 | 0.99985 | -0.0016835 | 0.99984 | -0.0015882 | 3.1376
28 | -0.51539 | -0.24872 | 0.51543 | 0.24865 | 4.0801e-05 | -7.4572e-05 | 0.016522 | 0.016521 | 0.016522 | 0.99985 | -0.0016835 | 0.99993 | -0.0011541 | 7.8679
29 | 6.6535 | 3.1769 | -6.6532 | -3.18 | 0.00037101 | -0.0030769 | 0.21286 | 0.2129 | 0.2129 | 0.99993 | -0.0011541 | 0.99987 | -0.0022996 | 25.2849
30 | 0.76695 | 0.36693 | -0.76685 | -0.36968 | 9.3539e-05 | -0.0027445 | 0.024545 | 0.02458 | 0.02458 | 0.99993 | -0.0011541 | 0.99982 | -0.00011142 | 11.1726
31 | -7.9359 | -3.7925 | 7.9364 | 3.79 | 0.00044592 | -0.0024783 | 0.25392 | 0.25389 | 0.25392 | 0.99993 | -0.0011541 | 1 | 0 | 30.157
32 | 6.4695 | 3.091 | -6.4692 | -3.0933 | 0.00026321 | -0.0023216 | 0.20701 | 0.20704 | 0.20704 | 0.99987 | -0.0022996 | 0.99982 | -0.0031346 | 24.5888
33 | 0.68961 | 0.33227 | -0.68961 | -0.3323 | 8.6235e-07 | -3.1308e-05 | 0.022102 | 0.022102 | 0.022102 | 0.99982 | -0.00011142 | 0.99982 | -0.00010065 | 10.0464
34 | 4.5965 | 2.1907 | -4.5964 | -2.1926 | 0.00010238 | -0.0018823 | 0.14702 | 0.14705 | 0.14705 | 0.99978 | -0.0038294 | 0.99976 | -0.0042881 | 17.4638
35 | -4.5965 | -2.1907 | 4.5966 | 2.1877 | 0.00016668 | -0.0030662 | 0.14702 | 0.14698 | 0.14702 | 0.99978 | -0.0038294 | 0.99982 | -0.0030812 | 17.4609
36 | 4.4934 | 2.1427 | -4.4933 | -2.1435 | 3.86e-05 | -0.00074411 | 0.14374 | 0.14375 | 0.14375 | 0.99976 | -0.0042881 | 0.99975 | -0.004465 | 17.0725
37 | 4.2946 | 2.0472 | -4.2945 | -2.0482 | 4.7169e-05 | -0.00099961 | 0.13737 | 0.13739 | 0.13739 | 0.99975 | -0.004465 | 0.99973 | -0.0046912 | 16.3167
38 | 0.21487 | 0.1028 | -0.21486 | -0.10331 | 1.3711e-06 | -0.0005172 | 0.0068778 | 0.0068842 | 0.0068842 | 0.99973 | -0.0046912 | 0.99973 | -0.0046368 | 3.1292
39 | 4.0796 | 1.9454 | -4.0792 | -1.947 | 0.00045984 | -0.0015818 | 0.13051 | 0.13053 | 0.13053 | 0.99973 | -0.0046912 | 0.99961 | -0.0060046 | 36.0588
40 | 0.12696 | 0.060741 | -0.12696 | -0.06149 | 6.9369e-07 | -0.00074882 | 0.004064 | 0.0040734 | 0.0040734 | 0.99973 | -0.0046368 | 0.99972 | -0.0045899 | 1.8515
41 | 3.9089 | 1.8645 | -3.9087 | -1.8646 | 0.00013745 | -0.00011625 | 0.12507 | 0.12507 | 0.12507 | 0.99961 | -0.0060046 | 0.99958 | -0.0057085 | 56.8499
42 | -0.26797 | -0.12978 | 0.26798 | 0.12967 | 1.3521e-05 | -0.00011242 | 0.0086263 | 0.0086248 | 0.0086263 | 0.99637 | -0.021211 | 0.99642 | -0.020878 | 4.1078
43 | -0.26798 | -0.12967 | 0.26799 | 0.12604 | 1.5121e-05 | -0.0036243 | 0.0086248 | 0.0085796 | 0.0086248 | 0.99642 | -0.020878 | 0.99647 | -0.021353 | 3.9204
44 | -0.9835 | -0.46308 | 0.98364 | 0.46063 | 0.00013887 | -0.0024483 | 0.031492 | 0.031461 | 0.031492 | 0.99647 | -0.021353 | 0.9966 | -0.0225 | 14.3145
45 | 0.7155 | 0.33703 | -0.71548 | -0.33774 | 2.0963e-05 | -0.00070263 | 0.022912 | 0.022921 | 0.022921 | 0.99647 | -0.021353 | 0.99644 | -0.021113 | 10.4187
46 | 1.1928 | 0.55668 | -1.1894 | -0.55612 | 0.0033754 | 0.00055441 | 0.038004 | 0.038023 | 0.038023 | 0.99982 | -0.0031346 | 0.99682 | -0.024358 | 18.1064
47 | 5.2764 | 2.5367 | -5.2762 | -2.5398 | 0.00022741 | -0.0031119 | 0.16904 | 0.16908 | 0.16908 | 0.99982 | -0.0031346 | 0.99977 | -0.0040109 | 20.0804
48 | 0.98387 | 0.45658 | -0.98364 | -0.46063 | 0.00022904 | -0.0040499 | 0.031411 | 0.031461 | 0.031461 | 0.99682 | -0.024358 | 0.9966 | -0.0225 | 14.3006
49 | 4.8568 | 2.3366 | -4.8563 | -2.3376 | 0.00043046 | -0.00094885 | 0.15562 | 0.15564 | 0.15564 | 0.99977 | -0.0040109 | 0.99967 | -0.0050232 | 42.9933
50 | 0.35258 | 0.16198 | -0.35257 | -0.1634 | 1.013e-05 | -0.0014185 | 0.011241 | 0.011258 | 0.011258 | 0.99644 | -0.021113 | 0.99642 | -0.020889 | 5.1173
51 | 0.35257 | 0.1634 | -0.35252 | -0.17058 | 5.1814e-05 | -0.0071859 | 0.011258 | 0.011347 | 0.011347 | 0.99642 | -0.020889 | 0.99628 | -0.019672 | 5.1579
52 | -0.35252 | -0.17073 | 0.35252 | 0.17058 | 1.1048e-06 | -0.00015196 | 0.011349 | 0.011347 | 0.011349 | 0.99628 | -0.019645 | 0.99628 | -0.019672 | 5.1588
53 | -1.9119 | -0.92596 | 1.9127 | 0.9225 | 0.00077991 | -0.0034614 | 0.061409 | 0.061363 | 0.061409 | 0.99861 | -0.0058428 | 0.99898 | -0.0093792 | 27.9132
54 | -2.7777 | -1.3414 | 2.7795 | 1.3424 | 0.0018166 | 0.00098488 | 0.089136 | 0.089134 | 0.089136 | 0.99898 | -0.0093792 | 0.99967 | -0.0050232 | 42.4456
55 | -0.053251 | -0.02579 | 0.053251 | 0.025235 | 9.0935e-08 | -0.00055503 | 0.0017116 | 0.0017047 | 0.0017116 | 0.99789 | -0.014834 | 0.99789 | -0.014849 | 0.77802
56 | -0.053251 | -0.025235 | 0.053262 | 0.02254 | 1.1545e-05 | -0.0026958 | 0.0017047 | 0.0016727 | 0.0017047 | 0.99789 | -0.014849 | 0.99812 | -0.01301 | 0.81176
57 | -0.20891 | -0.097922 | 0.20917 | 0.094105 | 0.0002633 | -0.0038164 | 0.0066728 | 0.0066248 | 0.0066728 | 0.99812 | -0.01301 | 0.99946 | -0.0030548 | 3.1775
58 | -0.70734 | -0.34214 | 0.70746 | 0.34206 | 0.00011995 | -8.0295e-05 | 0.022713 | 0.022711 | 0.022713 | 0.99867 | -0.0074997 | 0.99885 | -0.0063755 | 10.8155
59 | 0.70734 | 0.34214 | -0.70733 | -0.34258 | 1.2866e-05 | -0.00044093 | 0.022713 | 0.022718 | 0.022718 | 0.99867 | -0.0074997 | 0.99866 | -0.0073415 | 10.3265
60 | -1.0694 | -0.51736 | 1.0694 | 0.51698 | 2.5077e-05 | -0.00037222 | 0.034334 | 0.034329 | 0.034334 | 0.99885 | -0.0063755 | 0.99887 | -0.0065791 | 15.6062
61 | -0.51128 | -0.24042 | 0.51128 | 0.24032 | 1.5426e-06 | -0.00010304 | 0.016319 | 0.016317 | 0.016319 | 0.99946 | -0.0030548 | 0.99946 | -0.0030793 | 7.4175
62 | -0.8154 | -0.38761 | 0.81546 | 0.38604 | 6.0367e-05 | -0.0015694 | 0.026077 | 0.026057 | 0.026077 | 0.99946 | -0.0030793 | 0.99953 | -0.0036948 | 11.8531
63 | 1.2598 | 0.60927 | -1.2597 | -0.61006 | 7.475e-05 | -0.00079409 | 0.04043 | 0.04044 | 0.04044 | 0.99917 | -0.0093867 | 0.99912 | -0.0088706 | 18.382
64 | 1.9455 | 0.93843 | -1.9452 | -0.93972 | 0.00030107 | -0.0012903 | 0.062406 | 0.062424 | 0.062424 | 0.99915 | -0.0091188 | 0.999 | -0.0077804 | 28.3744
65 | 1.8232 | 0.88065 | -1.823 | -0.88178 | 0.00022864 | -0.0011239 | 0.058508 | 0.058523 | 0.058523 | 0.999 | -0.0077804 | 0.99889 | -0.0066927 | 26.6012
66 | 0.6666 | 0.32281 | -0.6666 | -0.32285 | 1.1049e-06 | -4.2743e-05 | 0.0214 | 0.0214 | 0.0214 | 0.99912 | -0.0088706 | 0.99912 | -0.0088562 | 9.7273
67 | 1.4996 | 0.72517 | -1.4996 | -0.72531 | 1.9617e-05 | -0.00014523 | 0.048139 | 0.048141 | 0.048141 | 0.99889 | -0.0066927 | 0.99887 | -0.0065791 | 21.8824
68 | 0.58509 | 0.28168 | -0.58508 | -0.28243 | 1.4894e-05 | -0.00075266 | 0.018749 | 0.018758 | 0.018758 | 0.99982 | -0.00010065 | 0.9998 | 0.00011882 | 8.5266
69 | 0.28089 | 0.13511 | -0.28089 | -0.1356 | 2.2523e-06 | -0.00049612 | 0.0089997 | 0.0090059 | 0.0090059 | 0.9998 | 0.00011882 | 0.99979 | 0.00018789 | 4.0936
70 | 0.20222 | 0.097502 | -0.20222 | -0.097938 | 1.0265e-06 | -0.00043609 | 0.006482 | 0.0064875 | 0.0064875 | 0.99979 | 0.00018789 | 0.99978 | 0.0002319 | 2.9489
71 | -1.1747 | -0.56002 | 1.1747 | 0.56 | 1.7084e-06 | -2.1104e-05 | 0.037584 | 0.037584 | 0.037584 | 0.99953 | -0.0036948 | 0.99953 | -0.003707 | 17.0838
72 | -1.3598 | -0.64966 | 1.3599 | 0.64903 | 6.9937e-05 | -0.00063904 | 0.043525 | 0.043517 | 0.043525 | 0.99953 | -0.003707 | 0.99958 | -0.0041411 | 19.7841
73 | -1.5196 | -0.72638 | 1.5197 | 0.72601 | 5.216e-05 | -0.00037852 | 0.048642 | 0.048637 | 0.048642 | 0.99958 | -0.0041411 | 0.99961 | -0.0044312 | 22.11
74 | -1.6108 | -0.77016 | 1.6108 | 0.77006 | 1.5347e-05 | -9.8608e-05 | 0.051562 | 0.051561 | 0.051562 | 0.99961 | -0.0044312 | 0.99962 | -0.0045119 | 23.4374
75 | -1.7513 | -0.83811 | 1.7515 | 0.83754 | 0.00010567 | -0.00056948 | 0.056069 | 0.056062 | 0.056069 | 0.99962 | -0.0045119 | 0.99967 | -0.0050232 | 25.4861

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 19.8669 | 9.5044

## res_load
| p_mw | q_mvar
0 | 0.14421 | 0.069846
1 | 0.18025 | 0.087298
2 | 1.0608 | 0.51375
3 | 0.50992 | 0.24697
4 | 0.27987 | 0.13555
5 | 0.11409 | 0.055256
6 | 0.40275 | 0.19506
7 | 0.086096 | 0.041698
8 | 1.9556 | 0.94714
9 | 0.19936 | 0.096552
10 | 0.18148 | 0.087897
11 | 0.30341 | 0.14695
12 | 0.15805 | 0.076545
13 | 0.38845 | 0.18813
14 | 0.22938 | 0.11109
15 | 0.30022 | 0.1454
16 | 0.21517 | 0.10421
17 | 0.18369 | 0.088963
18 | 0.077242 | 0.03741
19 | 0.29459 | 0.14268
20 | 0.103 | 0.049886
21 | 0.31073 | 0.15049
22 | 0.19877 | 0.096267
23 | 0.087902 | 0.042573
24 | 0.17031 | 0.082486
25 | 0.26797 | 0.12978
26 | 0.20552 | 0.09954
27 | 0.41946 | 0.20315
28 | 0.3629 | 0.17576
29 | 0.35252 | 0.17073
30 | 1.9119 | 0.92596
31 | 0.865 | 0.41894
32 | 0.053251 | 0.02579
33 | 0.15564 | 0.075382
34 | 0.36195 | 0.1753
35 | 0.70733 | 0.34258
36 | 0.30211 | 0.14632
37 | 0.30412 | 0.14729
38 | 0.39612 | 0.19185
39 | 0.12696 | 0.06149
40 | 0.27708 | 0.13419
41 | 0.081952 | 0.039691
42 | 0.46336 | 0.22442
43 | 0.12197 | 0.059072
44 | 0.59311 | 0.28726
45 | 0.32335 | 0.15661
46 | 0.43015 | 0.20833
47 | 0.6666 | 0.32285
48 | 0.10452 | 0.050622
49 | 0.30419 | 0.14732
50 | 0.078671 | 0.038102
51 | 0.20222 | 0.097938
52 | 0.35922 | 0.17398
53 | 0.18514 | 0.089666
54 | 0.15973 | 0.077358
55 | 0.091165 | 0.044153
56 | 0.1405 | 0.068048
57 | 0.32539 | 0.15759

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1