## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_590_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_590_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_590_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_590_0_node_88 | 20 | n |  | TRUE
4 | bus_MV_590_0_node_107 | 20 | n |  | TRUE
5 | bus_MV_590_0_node_116 | 20 | n |  | TRUE
6 | bus_MV_590_0_node_85 | 20 | n |  | TRUE
7 | bus_MV_590_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_590_0_node_27 | 20 | n |  | TRUE
9 | bus_MV_590_0_node_29 | 20 | n |  | TRUE
10 | bus_MV_590_0_node_33 | 20 | n |  | TRUE
11 | bus_MV_590_0_node_4 | 20 | n |  | TRUE
12 | bus_MV_590_0_node_5 | 20 | n |  | TRUE
13 | bus_MV_590_0_node_9 | 20 | n |  | TRUE
14 | bus_MV_590_0_node_65 | 20 | n |  | TRUE
15 | bus_MV_590_0_node_15 | 20 | n |  | TRUE
16 | bus_MV_590_0_node_7 | 20 | n |  | TRUE
17 | bus_MV_590_0_node_125 | 20 | n |  | TRUE
18 | bus_MV_590_0_node_66 | 20 | n |  | TRUE
19 | bus_MV_590_0_node_124 | 20 | n |  | TRUE
20 | bus_MV_590_0_node_117 | 20 | n |  | TRUE
21 | bus_MV_590_0_node_96 | 20 | n |  | TRUE
22 | bus_MV_590_0_node_57 | 20 | n |  | TRUE
23 | bus_MV_590_0_node_58 | 20 | n |  | TRUE
24 | bus_MV_590_0_node_59 | 20 | n |  | TRUE
25 | bus_MV_590_0_node_10 | 20 | n |  | TRUE
26 | bus_MV_590_0_node_11 | 20 | n |  | TRUE
27 | bus_MV_590_0_node_12 | 20 | n |  | TRUE
28 | bus_MV_590_0_node_14 | 20 | n |  | TRUE
29 | bus_MV_590_0_node_16 | 20 | n |  | TRUE
30 | bus_MV_590_0_node_13 | 20 | n |  | TRUE
31 | bus_MV_590_0_node_54 | 20 | n |  | TRUE
32 | bus_MV_590_0_node_56 | 20 | n |  | TRUE
33 | bus_MV_590_0_node_60 | 20 | n |  | TRUE
34 | bus_MV_590_0_node_121 | 20 | n |  | TRUE
35 | bus_MV_590_0_node_120 | 20 | n |  | TRUE
36 | bus_MV_590_0_node_123 | 20 | n |  | TRUE
37 | bus_MV_590_0_node_53 | 20 | n |  | TRUE
38 | bus_MV_590_0_node_114 | 20 | n |  | TRUE
39 | bus_MV_590_0_node_51 | 20 | n |  | TRUE
40 | bus_MV_590_0_node_48 | 20 | n |  | TRUE
41 | bus_MV_590_0_node_50 | 20 | n |  | TRUE
42 | bus_MV_590_0_node_95 | 20 | n |  | TRUE
43 | bus_MV_590_0_node_122 | 20 | n |  | TRUE
44 | bus_MV_590_0_node_17 | 20 | n |  | TRUE
45 | bus_MV_590_0_node_19 | 20 | n |  | TRUE
46 | bus_MV_590_0_node_18 | 20 | n |  | TRUE
47 | bus_MV_590_0_node_24 | 20 | n |  | TRUE
48 | bus_MV_590_0_node_22 | 20 | n |  | TRUE
49 | bus_MV_590_0_node_78 | 20 | n |  | TRUE
50 | bus_MV_590_0_node_23 | 20 | n |  | TRUE
51 | bus_MV_590_0_node_26 | 20 | n |  | TRUE
52 | bus_MV_590_0_node_39 | 20 | n |  | TRUE
53 | bus_MV_590_0_node_25 | 20 | n |  | TRUE
54 | bus_MV_590_0_node_79 | 20 | n |  | TRUE
55 | bus_MV_590_0_node_104 | 20 | n |  | TRUE
56 | bus_MV_590_0_node_40 | 20 | n |  | TRUE
57 | bus_MV_590_0_node_21 | 20 | n |  | TRUE
58 | bus_MV_590_0_node_45 | 20 | n |  | TRUE
59 | bus_MV_590_0_node_35 | 20 | n |  | TRUE
60 | bus_MV_590_0_node_36 | 20 | n |  | TRUE
61 | bus_MV_590_0_node_77 | 20 | n |  | TRUE
62 | bus_MV_590_0_node_61 | 20 | n |  | TRUE
63 | bus_MV_590_0_node_112 | 20 | n |  | TRUE
64 | bus_MV_590_0_node_41 | 20 | n |  | TRUE
65 | bus_MV_590_0_node_43 | 20 | n |  | TRUE
66 | bus_MV_590_0_node_44 | 20 | n |  | TRUE
67 | bus_MV_590_0_node_46 | 20 | n |  | TRUE
68 | bus_MV_590_0_node_42 | 20 | n |  | TRUE
69 | bus_MV_590_0_node_84 | 20 | n |  | TRUE
70 | bus_MV_590_0_node_82 | 20 | n |  | TRUE
71 | bus_MV_590_0_node_80 | 20 | n |  | TRUE
72 | bus_MV_590_0_node_119 | 20 | n |  | TRUE
73 | bus_MV_590_0_node_74 | 20 | n |  | TRUE
74 | bus_MV_590_0_node_30 | 20 | n |  | TRUE
75 | bus_MV_590_0_node_34 | 20 | n |  | TRUE
76 | bus_MV_590_0_node_87 | 20 | n |  | TRUE
77 | bus_MV_590_0_node_31 | 20 | n |  | TRUE
78 | bus_MV_590_0_node_32 | 20 | n |  | TRUE
79 | bus_MV_590_0_node_126 | 20 | n |  | TRUE
80 | bus_MV_590_0_node_49 | 20 | n |  | TRUE
81 | bus_MV_590_0_node_64 | 20 | n |  | TRUE
82 | bus_MV_590_0_node_108 | 20 | n |  | TRUE
83 | bus_MV_590_0_node_70 | 20 | n |  | TRUE
84 | bus_MV_590_0_node_63 | 20 | n |  | TRUE
85 | bus_MV_590_0_node_105 | 20 | n |  | TRUE
86 | bus_MV_590_0_node_62 | 20 | n |  | TRUE
87 | bus_MV_590_0_node_69 | 20 | n |  | TRUE
88 | bus_MV_590_0_node_118 | 20 | n |  | TRUE
89 | bus_MV_590_0_node_55 | 20 | n |  | TRUE
90 | bus_MV_590_0_node_38 | 20 | n |  | TRUE
91 | bus_MV_590_0_node_37 | 20 | n |  | TRUE
92 | bus_MV_590_0_node_47 | 20 | n |  | TRUE
93 | bus_MV_590_0_node_72 | 20 | n |  | TRUE
94 | bus_MV_590_0_node_73 | 20 | n |  | TRUE
95 | bus_MV_590_0_node_106 | 20 | n |  | TRUE
96 | bus_MV_590_0_node_113 | 20 | n |  | TRUE
97 | bus_MV_590_0_node_110 | 20 | n |  | TRUE
98 | bus_MV_590_0_node_81 | 20 | n |  | TRUE
99 | bus_MV_590_0_node_52 | 20 | n |  | TRUE
100 | bus_MV_590_0_node_115 | 20 | n |  | TRUE
101 | bus_MV_590_0_node_94 | 20 | n |  | TRUE
102 | bus_MV_590_0_node_97 | 20 | n |  | TRUE
103 | bus_MV_590_0_node_101 | 20 | n |  | TRUE
104 | bus_MV_590_0_node_98 | 20 | n |  | TRUE
105 | bus_MV_590_0_node_99 | 20 | n |  | TRUE
106 | bus_MV_590_0_node_100 | 20 | n |  | TRUE
107 | bus_MV_590_0_node_103 | 20 | n |  | TRUE
108 | bus_MV_590_0_node_102 | 20 | n |  | TRUE
109 | bus_MV_590_0_node_67 | 20 | n |  | TRUE
110 | bus_MV_590_0_node_68 | 20 | n |  | TRUE
111 | bus_MV_590_0_node_71 | 20 | n |  | TRUE
112 | bus_MV_590_0_node_111 | 20 | n |  | TRUE
113 | bus_MV_590_0_node_109 | 20 | n |  | TRUE
114 | bus_MV_590_0_node_75 | 20 | n |  | TRUE
115 | bus_MV_590_0_node_76 | 20 | n |  | TRUE
116 | bus_MV_590_0_node_83 | 20 | n |  | TRUE
117 | bus_MV_590_0_node_86 | 20 | n |  | TRUE
118 | bus_MV_590_0_node_89 | 20 | n |  | TRUE
119 | bus_MV_590_0_node_90 | 20 | n |  | TRUE
120 | bus_MV_590_0_node_91 | 20 | n |  | TRUE
121 | bus_MV_590_0_node_92 | 20 | n |  | TRUE
122 | bus_MV_590_0_node_93 | 20 | n |  | TRUE
123 | bus_HV_590_0_node_106 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_590_0_load_0 | 0 | 0.35285 | 0.17089 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_590_0_load_88 | 3 | 0.35699 | 0.1729 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_590_0_load_107 | 4 | 0.14614 | 0.070781 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_590_0_load_116 | 5 | 3.7665 | 1.8242 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_590_0_load_3 | 7 | 0.37048 | 0.17943 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_590_0_load_4 | 11 | 0.27982 | 0.13552 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_590_0_load_65 | 14 | 0.19665 | 0.095241 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_590_0_load_125 | 17 | 0.35438 | 0.17163 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_590_0_load_124 | 19 | 0.10448 | 0.050601 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_590_0_load_117 | 20 | 0.34507 | 0.16713 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_590_0_load_57 | 22 | 0.33171 | 0.16065 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_590_0_load_10 | 25 | 0.23667 | 0.11463 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_590_0_load_56 | 32 | 0.18911 | 0.091591 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_590_0_load_60 | 33 | 0.29774 | 0.1442 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_590_0_load_120 | 35 | 0.11434 | 0.055378 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_590_0_load_123 | 36 | 0.16789 | 0.081314 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_590_0_load_114 | 38 | 0.34918 | 0.16911 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_590_0_load_48 | 40 | 0.19158 | 0.092788 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_590_0_load_50 | 41 | 0.20427 | 0.098933 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_590_0_load_122 | 43 | 0.088115 | 0.042676 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_590_0_load_17 | 44 | 0.38454 | 0.18624 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_590_0_load_18 | 46 | 0.086279 | 0.041787 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_590_0_load_78 | 49 | 0.076322 | 0.036964 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_590_0_load_39 | 52 | 0.26103 | 0.12642 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_590_0_load_79 | 54 | 0.07316 | 0.035433 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_590_0_load_104 | 55 | 0.22932 | 0.11107 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_590_0_load_40 | 56 | 0.31564 | 0.15287 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_590_0_load_45 | 58 | 0.28156 | 0.13637 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_590_0_load_35 | 59 | 0.33893 | 0.16415 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_590_0_load_61 | 62 | 0.18189 | 0.088095 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_590_0_load_46 | 67 | 0.33274 | 0.16115 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_590_0_load_84 | 69 | 0.27064 | 0.13108 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_590_0_load_80 | 71 | 0.087058 | 0.042164 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_590_0_load_119 | 72 | 0.36059 | 0.17464 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_590_0_load_34 | 75 | 0.31261 | 0.1514 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_590_0_load_87 | 76 | 0.30657 | 0.14848 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_590_0_load_126 | 79 | 0.22742 | 0.11014 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_590_0_load_64 | 81 | 0.23296 | 0.11283 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_590_0_load_108 | 82 | 0.17372 | 0.084136 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_590_0_load_62 | 86 | 0.0895 | 0.043347 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_590_0_load_118 | 88 | 0.28008 | 0.13565 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_590_0_load_47 | 92 | 0.41144 | 0.19927 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_590_0_load_72 | 93 | 0.35862 | 0.17369 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_590_0_load_106 | 95 | 0.071171 | 0.03447 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_590_0_load_113 | 96 | 0.38814 | 0.18799 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_590_0_load_81 | 98 | 0.093976 | 0.045515 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_590_0_load_94 | 101 | 0.073328 | 0.035514 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_590_0_load_101 | 103 | 0.35547 | 0.17216 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_590_0_load_98 | 104 | 0.075296 | 0.036468 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_590_0_load_103 | 107 | 1.2846 | 0.62218 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_590_0_load_102 | 108 | 0.085512 | 0.041415 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_590_0_load_67 | 109 | 0.17951 | 0.086941 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_590_0_load_109 | 113 | 0.60143 | 0.29129 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_590_0_load_75 | 114 | 0.47305 | 0.22911 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_590_0_load_83 | 116 | 0.091181 | 0.044161 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_590_0_load_86 | 117 | 0.074461 | 0.036063 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_590_0_load_90 | 119 | 0.11223 | 0.054355 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_590_0_load_91 | 120 | 0.19899 | 0.096374 | 0 | 0 |  | 1 | TRUE | wye
58 | MV_590_0_load_92 | 121 | 0.38206 | 0.18504 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 95 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_590_0_line_0 |  | 0 | 1 | 0.11158 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_590_0_line_1 |  | 1 | 2 | 0.033356 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_590_0_line_2 |  | 2 | 7 | 0.011353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_590_0_line_3 |  | 3 | 4 | 0.27838 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
4 | MV_590_0_line_4 |  | 3 | 5 | 0.13039 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
5 | MV_590_0_line_5 |  | 3 | 6 | 0.065793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_590_0_line_6 |  | 4 | 9 | 0.074265 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
7 | MV_590_0_line_7 |  | 5 | 112 | 0.0013795 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
8 | MV_590_0_line_8 |  | 6 | 117 | 0.016655 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_590_0_line_9 |  | 6 | 69 | 0.03594 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_590_0_line_10 |  | 6 | 76 | 0.033939 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_590_0_line_11 |  | 7 | 8 | 0.064074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_590_0_line_12 |  | 8 | 9 | 0.25849 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
13 | MV_590_0_line_13 |  | 8 | 10 | 0.28471 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
14 | MV_590_0_line_14 |  | 10 | 81 | 0.041372 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
15 | MV_590_0_line_15 |  | 11 | 12 | 0.096284 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
16 | MV_590_0_line_16 |  | 12 | 13 | 1.0024 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_590_0_line_17 |  | 12 | 14 | 0.3164 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
18 | MV_590_0_line_18 |  | 13 | 19 | 0.11543 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_590_0_line_19 |  | 14 | 15 | 0.067498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_590_0_line_20 |  | 15 | 28 | 0.2713 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
21 | MV_590_0_line_21 |  | 16 | 17 | 0.036125 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_590_0_line_22 |  | 16 | 18 | 0.25135 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
23 | MV_590_0_line_23 |  | 18 | 20 | 0.015233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_590_0_line_24 |  | 18 | 21 | 0.053805 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_590_0_line_25 |  | 21 | 102 | 0.054248 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_590_0_line_26 |  | 22 | 23 | 0.0736 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_590_0_line_27 |  | 23 | 24 | 0.13752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_590_0_line_28 |  | 24 | 103 | 0.068565 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_590_0_line_29 |  | 25 | 26 | 0.010077 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
30 | MV_590_0_line_30 |  | 25 | 27 | 0.11102 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
31 | MV_590_0_line_31 |  | 26 | 28 | 0.21426 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
32 | MV_590_0_line_32 |  | 27 | 29 | 0.020402 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
33 | MV_590_0_line_33 |  | 28 | 33 | 0.002192 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_590_0_line_34 |  | 28 | 30 | 0.16309 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_590_0_line_35 |  | 29 | 34 | 0.074222 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
36 | MV_590_0_line_36 |  | 29 | 35 | 0.10796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_590_0_line_37 |  | 30 | 31 | 0.31584 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_590_0_line_38 |  | 30 | 32 | 0.047055 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_590_0_line_39 |  | 31 | 36 | 0.009465 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_590_0_line_40 |  | 32 | 42 | 0.091096 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
41 | MV_590_0_line_41 |  | 34 | 43 | 0.019032 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
42 | MV_590_0_line_42 |  | 37 | 38 | 0.0059558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_590_0_line_43 |  | 37 | 39 | 0.42487 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_590_0_line_44 |  | 38 | 100 | 0.051791 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_590_0_line_45 |  | 39 | 40 | 0.30318 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
46 | MV_590_0_line_46 |  | 39 | 41 | 0.087444 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
47 | MV_590_0_line_47 |  | 40 | 78 | 0.013327 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
48 | MV_590_0_line_48 |  | 41 | 99 | 0.012355 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
49 | MV_590_0_line_49 |  | 42 | 102 | 0.19725 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_590_0_line_50 |  | 42 | 101 | 0.088581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_590_0_line_51 |  | 43 | 88 | 0.11516 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
52 | MV_590_0_line_52 |  | 44 | 45 | 0.046345 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_590_0_line_53 |  | 44 | 46 | 0.06827 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_590_0_line_54 |  | 45 | 47 | 0.18902 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_590_0_line_55 |  | 47 | 53 | 0.15823 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
56 | MV_590_0_line_56 |  | 47 | 54 | 0.019282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_590_0_line_57 |  | 47 | 48 | 0.075612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_590_0_line_58 |  | 48 | 49 | 0.0313 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_590_0_line_59 |  | 49 | 61 | 0.036829 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_590_0_line_60 |  | 50 | 51 | 0.17712 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_590_0_line_61 |  | 50 | 52 | 0.077569 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
62 | MV_590_0_line_62 |  | 51 | 56 | 0.10947 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
63 | MV_590_0_line_63 |  | 51 | 53 | 0.26771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_590_0_line_64 |  | 52 | 62 | 0.12652 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
65 | MV_590_0_line_65 |  | 52 | 63 | 0.15249 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
66 | MV_590_0_line_66 |  | 53 | 55 | 0.01442 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_590_0_line_67 |  | 56 | 73 | 0.092887 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
68 | MV_590_0_line_68 |  | 57 | 58 | 0.12981 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
69 | MV_590_0_line_69 |  | 57 | 59 | 0.33243 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_590_0_line_70 |  | 59 | 60 | 0.018249 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_590_0_line_71 |  | 60 | 90 | 0.30871 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_590_0_line_72 |  | 61 | 115 | 0.026485 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_590_0_line_73 |  | 62 | 86 | 0.018399 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
74 | MV_590_0_line_74 |  | 63 | 96 | 0.037178 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_590_0_line_75 |  | 63 | 97 | 0.041165 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
76 | MV_590_0_line_76 |  | 64 | 65 | 0.22272 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
77 | MV_590_0_line_77 |  | 64 | 66 | 0.24449 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_590_0_line_78 |  | 64 | 67 | 0.06636 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
79 | MV_590_0_line_79 |  | 65 | 71 | 0.052054 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_590_0_line_80 |  | 66 | 72 | 0.00623 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_590_0_line_81 |  | 68 | 69 | 0.032482 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_590_0_line_82 |  | 68 | 70 | 0.026644 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_590_0_line_83 |  | 70 | 98 | 0.013008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_590_0_line_84 |  | 72 | 73 | 0.06738 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_590_0_line_85 |  | 73 | 94 | 0.1261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_590_0_line_86 |  | 74 | 75 | 0.019011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_590_0_line_87 |  | 74 | 76 | 0.22722 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
88 | MV_590_0_line_88 |  | 76 | 87 | 0.051317 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_590_0_line_89 |  | 77 | 78 | 0.28465 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_590_0_line_90 |  | 77 | 79 | 0.033694 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_590_0_line_91 |  | 78 | 80 | 0.43547 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
92 | MV_590_0_line_92 |  | 80 | 88 | 0.028413 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
93 | MV_590_0_line_93 |  | 81 | 89 | 0.034329 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
94 | MV_590_0_line_94 |  | 82 | 83 | 0.021168 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_590_0_line_95 |  | 83 | 87 | 0.090372 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_590_0_line_96 |  | 83 | 110 | 0.095134 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_590_0_line_97 |  | 84 | 85 | 0.033417 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
98 | MV_590_0_line_98 |  | 84 | 86 | 0.054675 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
99 | MV_590_0_line_99 |  | 85 | 95 | 0.050274 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
100 | MV_590_0_line_100 |  | 89 | 99 | 0.1777 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
101 | MV_590_0_line_101 |  | 90 | 93 | 0.035375 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
102 | MV_590_0_line_102 |  | 90 | 91 | 0.48441 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_590_0_line_103 |  | 91 | 92 | 0.088082 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
104 | MV_590_0_line_104 |  | 93 | 94 | 0.010956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_590_0_line_105 |  | 97 | 113 | 0.020808 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
106 | MV_590_0_line_106 |  | 98 | 116 | 0.027259 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_590_0_line_107 |  | 100 | 122 | 0.11688 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_590_0_line_108 |  | 102 | 104 | 0.064028 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_590_0_line_109 |  | 102 | 103 | 0.13556 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
110 | MV_590_0_line_110 |  | 104 | 105 | 0.071973 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
111 | MV_590_0_line_111 |  | 105 | 106 | 0.13797 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
112 | MV_590_0_line_112 |  | 106 | 107 | 0.19282 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
113 | MV_590_0_line_113 |  | 107 | 108 | 0.020354 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
114 | MV_590_0_line_114 |  | 109 | 110 | 0.046465 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
115 | MV_590_0_line_115 |  | 111 | 112 | 0.050892 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
116 | MV_590_0_line_116 |  | 111 | 113 | 0.015742 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
117 | MV_590_0_line_117 |  | 114 | 115 | 0.042013 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
118 | MV_590_0_line_118 |  | 117 | 118 | 0.039854 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
119 | MV_590_0_line_119 |  | 118 | 119 | 0.022985 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
120 | MV_590_0_line_120 |  | 120 | 121 | 0.062288 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
121 | MV_590_0_line_121 |  | 121 | 122 | 0.03079 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_590_0_trafo_106 | 25 MVA 110/20 kV | 123 | 95 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2737278.6807 | 1253705.8959
1 | 2737276.445 | 1253594.3412
2 | 2737249.4598 | 1253574.809
3 | 2736936.8636 | 1253290.5353
4 | 2737164.3253 | 1253451.0307
5 | 2737020.3253 | 1253190.3561
6 | 2736871.2106 | 1253284.4235
7 | 2737238.9641 | 1253570.4062
8 | 2737299.7104 | 1253551.6521
9 | 2737200.9422 | 1253479.2748
10 | 2737385.5597 | 1253351.2689
11 | 2738572.6847 | 1253226.5143
12 | 2738552.9951 | 1253320.7633
13 | 2739409.5942 | 1253659.3522
14 | 2738252.8514 | 1253420.8882
15 | 2738187.6399 | 1253402.7498
16 | 2738353.5325 | 1253136.7981
17 | 2738376.8725 | 1253163.3344
18 | 2738103.0541 | 1253157.6841
19 | 2739481.6772 | 1253749.5108
20 | 2738091.1751 | 1253167.2605
21 | 2738074.7487 | 1253111.9265
22 | 2738388.1085 | 1252955.5937
23 | 2738326.2992 | 1252995.8207
24 | 2738213.4633 | 1253009.6778
25 | 2738087.8351 | 1253486.4221
26 | 2738077.8106 | 1253485.1317
27 | 2738099.0353 | 1253596.8076
28 | 2737965.5996 | 1253342.7635
29 | 2738099.6315 | 1253617.1959
30 | 2737882.7878 | 1253232.0666
31 | 2737854.1302 | 1253320.9706
32 | 2737856.9662 | 1253192.7293
33 | 2737964.9539 | 1253340.6688
34 | 2738097.7363 | 1253691.2981
35 | 2738046.7782 | 1253564.1149
36 | 2737863.5454 | 1253322.1797
37 | 2737569.9643 | 1252981.0626
38 | 2737568.4138 | 1252975.3122
39 | 2737647.8074 | 1253295.4161
40 | 2737582.4603 | 1253591.4713
41 | 2737569.0877 | 1253333.4894
42 | 2737892.5725 | 1253108.8806
43 | 2738093.2738 | 1253709.8
44 | 2736957.1402 | 1252659.5242
45 | 2736956.6373 | 1252705.7327
46 | 2736957.3307 | 1252591.2548
47 | 2736993.4776 | 1252812.7605
48 | 2736976.6832 | 1252872.0155
49 | 2737007.8856 | 1252874.4801
50 | 2736971.125 | 1252973.8806
51 | 2736824.9402 | 1252956.1086
52 | 2737048.6701 | 1252975.798
53 | 2736875.3061 | 1252827.8876
54 | 2737012.7328 | 1252813.7831
55 | 2736860.9392 | 1252826.7242
56 | 2736715.5758 | 1252951.2349
57 | 2736872.4996 | 1252300.8392
58 | 2736937.0596 | 1252188.2166
59 | 2736727.5744 | 1252600.0126
60 | 2736743.796 | 1252608.3716
61 | 2737044.6 | 1252877.38
62 | 2737174.6726 | 1252964.3703
63 | 2737065.1268 | 1253127.3959
64 | 2736708.031 | 1253208.5971
65 | 2736833.8884 | 1253081.7195
66 | 2736616.9516 | 1253050.7845
67 | 2736677.4944 | 1253267.5133
68 | 2736803.93 | 1253271.9802
69 | 2736835.8702 | 1253277.8875
70 | 2736795.6974 | 1253297.3245
71 | 2736884.1395 | 1253095.2548
72 | 2736617.7736 | 1253044.6088
73 | 2736626.5701 | 1252977.806
74 | 2736827.6656 | 1253541.8989
75 | 2736810.9103 | 1253550.3203
76 | 2736866.8242 | 1253318.0754
77 | 2737516.4647 | 1253768.8582
78 | 2737589.3012 | 1253602.7406
79 | 2737483.9085 | 1253759.8164
80 | 2737964.6729 | 1253671.3568
81 | 2737387.3268 | 1253309.9384
82 | 2736979.171 | 1253394.3903
83 | 2736981.253 | 1253373.8938
84 | 2737198.2837 | 1253033.5251
85 | 2737230.6024 | 1253024.6766
86 | 2737180.6176 | 1252981.7826
87 | 2736903.48 | 1253353.9887
88 | 2737979.0024 | 1253695.5129
89 | 2737392.0926 | 1253276.0066
90 | 2736652.0849 | 1252807.8162
91 | 2736513.0099 | 1252439.973
92 | 2736425.971 | 1252426.4559
93 | 2736643.4718 | 1252842.1268
94 | 2736640.9533 | 1252852.7896
95 | 2737278.7962 | 1253010.3643
96 | 2737100.3353 | 1253139.1171
97 | 2737068.3435 | 1253168.4302
98 | 2736808.3036 | 1253300.5332
99 | 2737558.1217 | 1253339.24
100 | 2737554.9313 | 1252925.3066
101 | 2737875.6008 | 1253021.9403
102 | 2738065.5176 | 1253058.4732
103 | 2738175.6049 | 1252979.3653
104 | 2738040.8882 | 1253002.2862
105 | 2738028.5849 | 1252931.373
106 | 2738090.6407 | 1252862.3888
107 | 2738277.0931 | 1252822.1285
108 | 2738296.1938 | 1252815.0979
109 | 2737063.6969 | 1253403.9506
110 | 2737062.0548 | 1253357.5143
111 | 2737070.5257 | 1253204.9143
112 | 2737021.6264 | 1253190.8146
113 | 2737069.6296 | 1253189.1989
114 | 2737085.0554 | 1252851.7497
115 | 2737043.2495 | 1252850.9356
116 | 2736834.7208 | 1253307.2571
117 | 2736873.3229 | 1253267.9033
118 | 2736879.1528 | 1253228.5668
119 | 2736882.0655 | 1253205.7687
120 | 2737726.3704 | 1252907.7953
121 | 2737665.234 | 1252919.7191
122 | 2737665.3421 | 1252889.1045
123 | 2737278.7962 | 1253010.3643

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99608 | -0.15507 | 0.35285 | 0.17089
1 | 0.99616 | -0.15459 | 0 | 0
2 | 0.99617 | -0.15473 | 0 | 0
3 | 0.99732 | -0.11281 | 0.35699 | 0.1729
4 | 0.99664 | -0.1532 | 0.14614 | 0.070781
5 | 0.99773 | -0.089034 | 3.7665 | 1.8242
6 | 0.99719 | -0.11158 | 0 | 0
7 | 0.99618 | -0.15478 | 0.37048 | 0.17943
8 | 0.99624 | -0.15533 | 0 | 0
9 | 0.99655 | -0.15369 | 0 | 0
10 | 0.99593 | -0.15695 | 0 | 0
11 | 0.9932 | -0.21865 | 0.27982 | 0.13552
12 | 0.99325 | -0.21832 | 0 | 0
13 | 0.99312 | -0.21782 | 0 | 0
14 | 0.99348 | -0.21617 | 0.19665 | 0.095241
15 | 0.99353 | -0.21654 | 0 | 0
16 | 0.99124 | -0.21189 | 0 | 0
17 | 0.99123 | -0.21174 | 0.35438 | 0.17163
18 | 0.99142 | -0.21077 | 0 | 0
19 | 0.9931 | -0.21797 | 0.10448 | 0.050601
20 | 0.99141 | -0.21071 | 0.34507 | 0.16713
21 | 0.99149 | -0.2103 | 0 | 0
22 | 0.99124 | -0.21091 | 0.33171 | 0.16065
23 | 0.99127 | -0.2112 | 0 | 0
24 | 0.99133 | -0.21173 | 0 | 0
25 | 0.99422 | -0.2125 | 0.23667 | 0.11463
26 | 0.99421 | -0.21253 | 0 | 0
27 | 0.9943 | -0.21214 | 0 | 0
28 | 0.99373 | -0.21794 | 0 | 0
29 | 0.99432 | -0.21207 | 0 | 0
30 | 0.99305 | -0.21188 | 0 | 0
31 | 0.99298 | -0.21131 | 0 | 0
32 | 0.99277 | -0.21378 | 0.18911 | 0.091591
33 | 0.99373 | -0.21793 | 0.29774 | 0.1442
34 | 0.99437 | -0.21182 | 0 | 0
35 | 0.9943 | -0.21193 | 0.11434 | 0.055378
36 | 0.99298 | -0.2113 | 0.16789 | 0.081314
37 | 0.99497 | -0.16432 | 0 | 0
38 | 0.99496 | -0.16426 | 0.34918 | 0.16911
39 | 0.99547 | -0.16883 | 0 | 0
40 | 0.99494 | -0.19973 | 0.19158 | 0.092788
41 | 0.99565 | -0.15836 | 0.20427 | 0.098933
42 | 0.99225 | -0.21725 | 0 | 0
43 | 0.99438 | -0.21175 | 0.088115 | 0.042676
44 | 0.99673 | -0.040422 | 0.38454 | 0.18624
45 | 0.99676 | -0.040682 | 0 | 0
46 | 0.99672 | -0.040493 | 0.086279 | 0.041787
47 | 0.99687 | -0.041713 | 0 | 0
48 | 0.99682 | -0.041232 | 0 | 0
49 | 0.9968 | -0.041031 | 0.076322 | 0.036964
50 | 0.9984 | -0.055042 | 0 | 0
51 | 0.99754 | -0.047605 | 0 | 0
52 | 0.99875 | -0.046246 | 0.26103 | 0.12642
53 | 0.99709 | -0.043663 | 0 | 0
54 | 0.99687 | -0.041696 | 0.07316 | 0.035433
55 | 0.99709 | -0.043623 | 0.22932 | 0.11107
56 | 0.99702 | -0.051252 | 0.31564 | 0.15287
57 | 0.99587 | -0.051186 | 0 | 0
58 | 0.9958 | -0.051632 | 0.28156 | 0.13637
59 | 0.99606 | -0.050035 | 0.33893 | 0.16415
60 | 0.99607 | -0.050171 | 0 | 0
61 | 0.99677 | -0.040826 | 0 | 0
62 | 0.99953 | -0.0021193 | 0.18189 | 0.088095
63 | 0.99802 | -0.087704 | 0 | 0
64 | 0.99639 | -0.053589 | 0 | 0
65 | 0.99637 | -0.053411 | 0 | 0
66 | 0.99652 | -0.054677 | 0 | 0
67 | 0.99635 | -0.053858 | 0.33274 | 0.16115
68 | 0.99716 | -0.11132 | 0 | 0
69 | 0.99717 | -0.11139 | 0.27064 | 0.13108
70 | 0.99715 | -0.11126 | 0 | 0
71 | 0.99636 | -0.053358 | 0.087058 | 0.042164
72 | 0.99653 | -0.054703 | 0.36059 | 0.17464
73 | 0.99663 | -0.053991 | 0 | 0
74 | 0.99701 | -0.11207 | 0 | 0
75 | 0.997 | -0.112 | 0.31261 | 0.1514
76 | 0.99715 | -0.1112 | 0.30657 | 0.14848
77 | 0.99485 | -0.19908 | 0 | 0
78 | 0.99493 | -0.19979 | 0 | 0
79 | 0.99484 | -0.19899 | 0.22742 | 0.11014
80 | 0.99458 | -0.20149 | 0 | 0
81 | 0.99589 | -0.15718 | 0.23296 | 0.11283
82 | 0.99707 | -0.11103 | 0.17372 | 0.084136
83 | 0.99707 | -0.11108 | 0 | 0
84 | 0.99975 | -0.0011345 | 0 | 0
85 | 0.99985 | -0.00068223 | 0 | 0
86 | 0.99958 | -0.0018725 | 0.0895 | 0.043347
87 | 0.99711 | -0.11144 | 0 | 0
88 | 0.99456 | -0.2016 | 0.28008 | 0.13565
89 | 0.99585 | -0.15736 | 0 | 0
90 | 0.99631 | -0.052389 | 0 | 0
91 | 0.99606 | -0.050167 | 0 | 0
92 | 0.99599 | -0.050609 | 0.41144 | 0.19927
93 | 0.99638 | -0.051884 | 0.35862 | 0.17369
94 | 0.9964 | -0.052053 | 0 | 0
95 | 1 | 0 | -18.6624 | -8.6691
96 | 0.998 | -0.087531 | 0.38814 | 0.18799
97 | 0.99793 | -0.088134 | 0 | 0
98 | 0.99715 | -0.11124 | 0.093976 | 0.045515
99 | 0.99566 | -0.1583 | 0 | 0
100 | 0.99492 | -0.16391 | 0 | 0
101 | 0.99225 | -0.21718 | 0.073328 | 0.035514
102 | 0.99154 | -0.21076 | 0 | 0
103 | 0.99136 | -0.21198 | 0.35547 | 0.17216
104 | 0.99142 | -0.20968 | 0.075296 | 0.036468
105 | 0.99129 | -0.20852 | 0 | 0
106 | 0.99105 | -0.20627 | 0 | 0
107 | 0.99071 | -0.20309 | 1.2846 | 0.62218
108 | 0.99071 | -0.20307 | 0.085512 | 0.041415
109 | 0.99703 | -0.11098 | 0.17951 | 0.086941
110 | 0.99705 | -0.11088 | 0 | 0
111 | 0.99785 | -0.08851 | 0 | 0
112 | 0.99774 | -0.08902 | 0 | 0
113 | 0.99788 | -0.088351 | 0.60143 | 0.29129
114 | 0.99673 | -0.04044 | 0.47305 | 0.22911
115 | 0.99676 | -0.040678 | 0 | 0
116 | 0.99715 | -0.11121 | 0.091181 | 0.044161
117 | 0.99718 | -0.11154 | 0.074461 | 0.036063
118 | 0.99718 | -0.11149 | 0 | 0
119 | 0.99717 | -0.11146 | 0.11223 | 0.054355
120 | 0.99479 | -0.16304 | 0.19899 | 0.096374
121 | 0.99481 | -0.16289 | 0.38206 | 0.18504
122 | 0.99483 | -0.1631 | 0 | 0
123 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.35285 | -0.17089 | 0.35287 | 0.17078 | 2.566e-05 | -0.0001161 | 0.011362 | 0.01136 | 0.011362 | 0.99608 | -0.15507 | 0.99616 | -0.15459 | 5.4105
1 | -0.35287 | -0.17078 | 0.35288 | 0.16999 | 5.742e-06 | -0.00078861 | 0.01136 | 0.01135 | 0.01136 | 0.99616 | -0.15459 | 0.99617 | -0.15473 | 5.1638
2 | -0.35288 | -0.16999 | 0.35288 | 0.16972 | 1.952e-06 | -0.00026842 | 0.01135 | 0.011347 | 0.01135 | 0.99617 | -0.15473 | 0.99618 | -0.15478 | 5.1593
3 | 7.542 | 3.3575 | -7.5391 | -3.3507 | 0.0028375 | 0.0068653 | 0.23896 | 0.23897 | 0.23897 | 0.99732 | -0.11281 | 0.99664 | -0.1532 | 18.5245
4 | -9.5142 | -4.2995 | 9.5164 | 4.3048 | 0.0021256 | 0.0053571 | 0.3022 | 0.3022 | 0.3022 | 0.99732 | -0.11281 | 0.99773 | -0.089034 | 23.4266
5 | 1.6153 | 0.76905 | -1.615 | -0.77054 | 0.00023561 | -0.0014924 | 0.051783 | 0.051802 | 0.051802 | 0.99732 | -0.11281 | 0.99719 | -0.11158 | 23.5465
6 | 7.393 | 3.2799 | -7.3923 | -3.2888 | 0.00062998 | -0.0089141 | 0.23427 | 0.23437 | 0.23437 | 0.99664 | -0.1532 | 0.99655 | -0.15369 | 18.3679
7 | -13.2829 | -6.129 | 13.2829 | 6.1289 | 3.8182e-05 | -0.00015107 | 0.42325 | 0.42325 | 0.42325 | 0.99773 | -0.089034 | 0.99774 | -0.08902 | 33.1704
8 | 0.18669 | 0.088532 | -0.18669 | -0.088927 | 7.9613e-07 | -0.00039518 | 0.0059815 | 0.0059864 | 0.0059864 | 0.99719 | -0.11158 | 0.99718 | -0.11154 | 2.7211
9 | 0.45581 | 0.21754 | -0.4558 | -0.2184 | 1.0264e-05 | -0.00085022 | 0.014621 | 0.014632 | 0.014632 | 0.99719 | -0.11158 | 0.99717 | -0.11139 | 6.6508
10 | 0.97253 | 0.46447 | -0.97249 | -0.46526 | 4.4119e-05 | -0.00079266 | 0.0312 | 0.03121 | 0.03121 | 0.99719 | -0.11158 | 0.99715 | -0.1112 | 14.1863
11 | -0.72336 | -0.34915 | 0.7234 | 0.34764 | 4.6303e-05 | -0.0015045 | 0.023276 | 0.023257 | 0.023276 | 0.99618 | -0.15478 | 0.99624 | -0.15533 | 10.5799
12 | -7.3902 | -3.3198 | 7.3923 | 3.2888 | 0.0021973 | -0.031011 | 0.23476 | 0.23437 | 0.23476 | 0.99624 | -0.15533 | 0.99655 | -0.15369 | 18.3978
13 | 6.6667 | 2.9722 | -6.6648 | -3.0065 | 0.0019717 | -0.034388 | 0.21151 | 0.21193 | 0.21193 | 0.99624 | -0.15533 | 0.99593 | -0.15695 | 16.6088
14 | 6.6648 | 3.0065 | -6.6645 | -3.0115 | 0.00028717 | -0.0049948 | 0.21193 | 0.21199 | 0.21199 | 0.99593 | -0.15695 | 0.99589 | -0.15718 | 16.6136
15 | -0.27982 | -0.13552 | 0.27983 | 0.13542 | 1.4007e-05 | -0.00010462 | 0.0090367 | 0.0090352 | 0.0090367 | 0.9932 | -0.21865 | 0.99325 | -0.21832 | 4.3032
16 | 0.10449 | 0.026861 | -0.10448 | -0.050466 | 1.4033e-05 | -0.023605 | 0.0031357 | 0.0033727 | 0.0033727 | 0.99325 | -0.21832 | 0.99312 | -0.21782 | 1.533
17 | -0.38433 | -0.16228 | 0.38441 | 0.16196 | 8.2847e-05 | -0.00032084 | 0.012125 | 0.012121 | 0.012125 | 0.99325 | -0.21832 | 0.99348 | -0.21617 | 5.7737
18 | 0.10448 | 0.050466 | -0.10448 | -0.050601 | 2.3406e-06 | -0.00013445 | 0.0033727 | 0.0033744 | 0.0033744 | 0.99312 | -0.21782 | 0.9931 | -0.21797 | 1.6069
19 | -0.58106 | -0.2572 | 0.58109 | 0.25562 | 3.0688e-05 | -0.0015816 | 0.018464 | 0.018445 | 0.018464 | 0.99348 | -0.21617 | 0.99353 | -0.21654 | 8.3926
20 | -0.58109 | -0.25562 | 0.58121 | 0.24926 | 0.00012273 | -0.006359 | 0.018445 | 0.018371 | 0.018445 | 0.99353 | -0.21654 | 0.99373 | -0.21794 | 8.3842
21 | 0.35439 | 0.17079 | -0.35438 | -0.17163 | 6.3359e-06 | -0.00084559 | 0.011457 | 0.011467 | 0.011467 | 0.99124 | -0.21189 | 0.99123 | -0.21174 | 5.2124
22 | -0.35439 | -0.17079 | 0.35444 | 0.17053 | 5.876e-05 | -0.00025807 | 0.011457 | 0.011453 | 0.011457 | 0.99124 | -0.21189 | 0.99142 | -0.21077 | 5.4555
23 | 0.34508 | 0.16677 | -0.34507 | -0.16713 | 2.5336e-06 | -0.00035673 | 0.01116 | 0.011164 | 0.011164 | 0.99142 | -0.21077 | 0.99141 | -0.21071 | 5.0746
24 | -0.69952 | -0.3373 | 0.69957 | 0.33727 | 4.9016e-05 | -3.2437e-05 | 0.022613 | 0.022612 | 0.022613 | 0.99142 | -0.21077 | 0.99149 | -0.2103 | 10.7679
25 | -0.69957 | -0.33727 | 0.69961 | 0.33601 | 3.7002e-05 | -0.0012624 | 0.022612 | 0.022596 | 0.022612 | 0.99149 | -0.2103 | 0.99154 | -0.21076 | 10.2781
26 | -0.33171 | -0.16065 | 0.33172 | 0.15893 | 1.1297e-05 | -0.0017233 | 0.010734 | 0.010712 | 0.010734 | 0.99124 | -0.21091 | 0.99127 | -0.2112 | 4.8789
27 | -0.33172 | -0.15893 | 0.33174 | 0.15571 | 2.0986e-05 | -0.0032203 | 0.010712 | 0.010672 | 0.010712 | 0.99127 | -0.2112 | 0.99133 | -0.21173 | 4.869
28 | -0.33174 | -0.15571 | 0.33175 | 0.15411 | 1.0405e-05 | -0.0016058 | 0.010672 | 0.010652 | 0.010672 | 0.99133 | -0.21173 | 0.99136 | -0.21198 | 4.8507
29 | 4.1517 | 1.9303 | -4.1516 | -1.9315 | 2.7517e-05 | -0.0012362 | 0.13294 | 0.13295 | 0.13295 | 0.99422 | -0.2125 | 0.99421 | -0.21253 | 10.4194
30 | -4.3883 | -2.0449 | 4.3887 | 2.0313 | 0.00033852 | -0.0136 | 0.14057 | 0.1404 | 0.14057 | 0.99422 | -0.2125 | 0.9943 | -0.21214 | 11.0165
31 | 4.1516 | 1.9315 | -4.1498 | -1.9374 | 0.0018305 | -0.005932 | 0.13295 | 0.13304 | 0.13304 | 0.99421 | -0.21253 | 0.99373 | -0.21794 | 36.7516
32 | -4.3887 | -2.0313 | 4.3887 | 2.0288 | 6.2123e-05 | -0.0024997 | 0.1404 | 0.14037 | 0.1404 | 0.9943 | -0.21214 | 0.99432 | -0.21207 | 11.0033
33 | 0.29774 | 0.14415 | -0.29774 | -0.1442 | 2.7027e-07 | -5.1602e-05 | 0.0096095 | 0.0096102 | 0.0096102 | 0.99373 | -0.21794 | 0.99373 | -0.21793 | 4.3683
34 | 3.2708 | 1.544 | -3.2684 | -1.5471 | 0.0024047 | -0.0031293 | 0.10507 | 0.10512 | 0.10512 | 0.99373 | -0.21794 | 0.99305 | -0.21188 | 47.7813
35 | -4.5031 | -2.0816 | 4.5033 | 2.0725 | 0.00023769 | -0.0090879 | 0.14403 | 0.14392 | 0.14403 | 0.99432 | -0.21207 | 0.99437 | -0.21182 | 11.2875
36 | 0.11434 | 0.052831 | -0.11434 | -0.055378 | 1.944e-06 | -0.0025478 | 0.0036569 | 0.0036886 | 0.0036886 | 0.99432 | -0.21207 | 0.9943 | -0.21193 | 1.6766
37 | 0.1679 | 0.073659 | -0.16789 | -0.081091 | 1.2178e-05 | -0.0074324 | 0.0053299 | 0.0054204 | 0.0054204 | 0.99305 | -0.21188 | 0.99298 | -0.21131 | 2.4638
38 | 3.1005 | 1.4735 | -3.0997 | -1.473 | 0.00083489 | 0.00046757 | 0.099791 | 0.099792 | 0.099792 | 0.99305 | -0.21188 | 0.99277 | -0.21378 | 47.52
39 | 0.16789 | 0.081091 | -0.16789 | -0.081314 | 3.7144e-07 | -0.00022272 | 0.0054204 | 0.0054232 | 0.0054232 | 0.99298 | -0.21131 | 0.99298 | -0.2113 | 2.4651
40 | 2.9106 | 1.3814 | -2.9092 | -1.3806 | 0.0014245 | 0.00078511 | 0.093682 | 0.093684 | 0.093684 | 0.99277 | -0.21378 | 0.99225 | -0.21725 | 44.6112
41 | -4.5033 | -2.0725 | 4.5034 | 2.0702 | 6.089e-05 | -0.0023305 | 0.14392 | 0.14389 | 0.14392 | 0.99437 | -0.21182 | 0.99438 | -0.21175 | 11.2787
42 | 0.93033 | 0.44563 | -0.93032 | -0.44577 | 7.1224e-06 | -0.00013866 | 0.029929 | 0.029931 | 0.029931 | 0.99497 | -0.16432 | 0.99496 | -0.16426 | 13.6049
43 | -0.93033 | -0.44563 | 0.93083 | 0.43573 | 0.00050595 | -0.0098975 | 0.029929 | 0.029804 | 0.029929 | 0.99497 | -0.16432 | 0.99547 | -0.16883 | 13.6041
44 | 0.58114 | 0.27666 | -0.58112 | -0.27787 | 2.4131e-05 | -0.0012169 | 0.018674 | 0.01869 | 0.01869 | 0.99496 | -0.16426 | 0.99492 | -0.16391 | 8.4953
45 | 5.2944 | 2.3898 | -5.2928 | -2.3865 | 0.0015356 | 0.0032993 | 0.16845 | 0.16846 | 0.16846 | 0.99547 | -0.16883 | 0.99494 | -0.19973 | 13.0586
46 | -6.2252 | -2.8255 | 6.2258 | 2.8269 | 0.00061345 | 0.00141 | 0.19825 | 0.19825 | 0.19825 | 0.99547 | -0.16883 | 0.99565 | -0.15836 | 15.3681
47 | 5.1012 | 2.2937 | -5.1012 | -2.2953 | 5.4232e-05 | -0.0016273 | 0.16228 | 0.1623 | 0.1623 | 0.99494 | -0.19973 | 0.99493 | -0.19979 | 12.7196
48 | -6.4301 | -2.9259 | 6.4302 | 2.9244 | 8.0074e-05 | -0.001494 | 0.20482 | 0.20481 | 0.20482 | 0.99565 | -0.15836 | 0.99566 | -0.1583 | 16.052
49 | 2.8358 | 1.3472 | -2.8336 | -1.3512 | 0.0021983 | -0.0039815 | 0.091339 | 0.091397 | 0.091397 | 0.99225 | -0.21725 | 0.99154 | -0.21076 | 41.5442
50 | 0.073328 | 0.033432 | -0.073328 | -0.035514 | 6.5715e-07 | -0.0020821 | 0.0023446 | 0.0023704 | 0.0023704 | 0.99225 | -0.21725 | 0.99225 | -0.21718 | 1.0774
51 | -4.5915 | -2.1129 | 4.5919 | 2.1137 | 0.00044255 | 0.00087519 | 0.14673 | 0.14673 | 0.14673 | 0.99438 | -0.21175 | 0.99456 | -0.2016 | 11.3743
52 | -0.47082 | -0.22795 | 0.47084 | 0.22685 | 1.4188e-05 | -0.0010951 | 0.01515 | 0.015136 | 0.01515 | 0.99673 | -0.040422 | 0.99676 | -0.040682 | 6.8865
53 | 0.08628 | 0.041706 | -0.086279 | -0.041787 | 9.3735e-07 | -8.038e-05 | 0.0027755 | 0.0027765 | 0.0027765 | 0.99673 | -0.040422 | 0.99672 | -0.040493 | 1.3221
54 | -0.47084 | -0.22685 | 0.4709 | 0.22239 | 5.76e-05 | -0.0044673 | 0.015136 | 0.01508 | 0.015136 | 0.99676 | -0.040682 | 0.99687 | -0.041713 | 6.8802
55 | -1.0935 | -0.51842 | 1.0938 | 0.51475 | 0.00025907 | -0.0036782 | 0.035044 | 0.034998 | 0.035044 | 0.99687 | -0.041713 | 0.99709 | -0.043663 | 15.9292
56 | 0.07316 | 0.034975 | -0.07316 | -0.035433 | 1.423e-07 | -0.00045747 | 0.0023482 | 0.002354 | 0.002354 | 0.99687 | -0.041713 | 0.99687 | -0.041696 | 1.07
57 | 0.54945 | 0.26106 | -0.54942 | -0.26285 | 3.1363e-05 | -0.0017846 | 0.017616 | 0.017638 | 0.017638 | 0.99687 | -0.041713 | 0.99682 | -0.041232 | 8.0173
58 | 0.54942 | 0.26285 | -0.54941 | -0.26358 | 1.3006e-05 | -0.00073869 | 0.017638 | 0.017647 | 0.017647 | 0.99682 | -0.041232 | 0.9968 | -0.041031 | 8.0215
59 | 0.47308 | 0.22662 | -0.47307 | -0.22749 | 1.1355e-05 | -0.00087031 | 0.015191 | 0.015202 | 0.015202 | 0.9968 | -0.041031 | 0.99677 | -0.040826 | 6.9102
60 | 3.8168 | 1.7861 | -3.8133 | -1.7892 | 0.0035119 | -0.0031701 | 0.12184 | 0.1219 | 0.1219 | 0.9984 | -0.055042 | 0.99754 | -0.047605 | 55.4071
61 | -3.8168 | -1.7861 | 3.8179 | 1.7872 | 0.0010571 | 0.001112 | 0.12184 | 0.12184 | 0.12184 | 0.9984 | -0.055042 | 0.99875 | -0.046246 | 34.8126
62 | 2.4896 | 1.1699 | -2.4883 | -1.1693 | 0.001236 | 0.00064421 | 0.079604 | 0.079605 | 0.079605 | 0.99754 | -0.047605 | 0.99702 | -0.051252 | 37.9073
63 | 1.3237 | 0.6193 | -1.3231 | -0.62547 | 0.00064042 | -0.0061677 | 0.042292 | 0.04237 | 0.04237 | 0.99754 | -0.047605 | 0.99709 | -0.043663 | 19.2592
64 | -18.3608 | -8.5216 | 18.3685 | 8.542 | 0.0077304 | 0.020439 | 0.58507 | 0.58506 | 0.58507 | 0.99875 | -0.046246 | 0.99953 | -0.0021193 | 45.354
65 | 14.2818 | 6.608 | -14.2762 | -6.5933 | 0.0056312 | 0.014723 | 0.45484 | 0.45485 | 0.45485 | 0.99875 | -0.046246 | 0.99802 | -0.087704 | 35.2595
66 | 0.22933 | 0.11072 | -0.22932 | -0.11107 | 1.0471e-06 | -0.00034199 | 0.0073728 | 0.0073771 | 0.0073771 | 0.99709 | -0.043663 | 0.99709 | -0.043623 | 3.3532
67 | 2.1727 | 1.0164 | -2.1719 | -1.016 | 0.0007983 | 0.00038984 | 0.069452 | 0.069453 | 0.069453 | 0.99702 | -0.051252 | 0.99663 | -0.053991 | 33.0728
68 | 0.28158 | 0.13623 | -0.28156 | -0.13637 | 1.902e-05 | -0.00014177 | 0.0090673 | 0.0090693 | 0.0090693 | 0.99587 | -0.051186 | 0.9958 | -0.051632 | 4.3187
69 | -0.28158 | -0.13623 | 0.28163 | 0.13586 | 4.8669e-05 | -0.00036317 | 0.0090673 | 0.0090623 | 0.0090673 | 0.99587 | -0.051186 | 0.99606 | -0.050035 | 4.3178
70 | -0.62056 | -0.30001 | 0.62057 | 0.29958 | 9.7197e-06 | -0.00042942 | 0.019977 | 0.019971 | 0.019977 | 0.99606 | -0.050035 | 0.99607 | -0.050171 | 9.0803
71 | -0.62057 | -0.29958 | 0.62074 | 0.29232 | 0.00016362 | -0.0072662 | 0.019971 | 0.01988 | 0.019971 | 0.99607 | -0.050171 | 0.99631 | -0.052389 | 9.0778
72 | 0.47307 | 0.22749 | -0.47306 | -0.22812 | 8.1758e-06 | -0.00062585 | 0.015202 | 0.01521 | 0.01521 | 0.99677 | -0.040826 | 0.99676 | -0.040678 | 6.9138
73 | -18.5504 | -8.6301 | 18.5514 | 8.6284 | 0.00099251 | -0.0017512 | 0.5909 | 0.59087 | 0.5909 | 0.99953 | -0.0021193 | 0.99958 | -0.0018725 | 46.3087
74 | 0.38815 | 0.1871 | -0.38814 | -0.18799 | 7.7168e-06 | -0.00088185 | 0.012463 | 0.012475 | 0.012475 | 0.99802 | -0.087704 | 0.998 | -0.087531 | 5.6703
75 | 13.8881 | 6.4062 | -13.8868 | -6.4106 | 0.0012449 | -0.004451 | 0.44239 | 0.44245 | 0.44245 | 0.99802 | -0.087704 | 0.99793 | -0.088134 | 34.6747
76 | 0.087061 | 0.035652 | -0.087059 | -0.040931 | 2.2576e-06 | -0.0052786 | 0.0027256 | 0.0027872 | 0.0027872 | 0.99639 | -0.053589 | 0.99637 | -0.053411 | 1.2669
77 | -0.41981 | -0.19673 | 0.41987 | 0.19096 | 5.8578e-05 | -0.0057787 | 0.013432 | 0.013362 | 0.013432 | 0.99639 | -0.053589 | 0.99652 | -0.054677 | 6.1055
78 | 0.33275 | 0.16108 | -0.33274 | -0.16115 | 1.3565e-05 | -7.015e-05 | 0.010711 | 0.010712 | 0.010712 | 0.99639 | -0.053589 | 0.99635 | -0.053858 | 5.1008
79 | 0.087059 | 0.040931 | -0.087058 | -0.042164 | 5.4281e-07 | -0.0012337 | 0.0027872 | 0.0028026 | 0.0028026 | 0.99637 | -0.053411 | 0.99636 | -0.053358 | 1.2739
80 | -0.41987 | -0.19096 | 0.41987 | 0.19081 | 1.4847e-06 | -0.00014728 | 0.013362 | 0.01336 | 0.013362 | 0.99652 | -0.054677 | 0.99653 | -0.054703 | 6.0735
81 | -0.18516 | -0.088088 | 0.18516 | 0.087317 | 1.5255e-06 | -0.00077069 | 0.005936 | 0.0059264 | 0.005936 | 0.99716 | -0.11132 | 0.99717 | -0.11139 | 2.6982
82 | 0.18516 | 0.088088 | -0.18516 | -0.08872 | 1.255e-06 | -0.00063217 | 0.005936 | 0.0059439 | 0.0059439 | 0.99716 | -0.11132 | 0.99715 | -0.11126 | 2.7018
83 | 0.18516 | 0.08872 | -0.18516 | -0.089028 | 6.1393e-07 | -0.00030864 | 0.0059439 | 0.0059477 | 0.0059477 | 0.99715 | -0.11126 | 0.99715 | -0.11124 | 2.7035
84 | -0.78046 | -0.36545 | 0.78054 | 0.36542 | 7.4815e-05 | -3.3027e-05 | 0.024964 | 0.024963 | 0.024964 | 0.99653 | -0.054703 | 0.99663 | -0.053991 | 11.8878
85 | 1.3914 | 0.6506 | -1.391 | -0.6535 | 0.00033349 | -0.002891 | 0.04449 | 0.044526 | 0.044526 | 0.99663 | -0.053991 | 0.9964 | -0.052053 | 20.2392
86 | 0.31261 | 0.15095 | -0.31261 | -0.1514 | 2.5656e-06 | -0.00045042 | 0.010051 | 0.010057 | 0.010057 | 0.99701 | -0.11207 | 0.997 | -0.112 | 4.5714
87 | -0.31261 | -0.15095 | 0.31265 | 0.15071 | 4.0889e-05 | -0.00024407 | 0.010051 | 0.010048 | 0.010051 | 0.99701 | -0.11207 | 0.99715 | -0.1112 | 4.7864
88 | 0.35326 | 0.16607 | -0.35325 | -0.16612 | 1.1677e-05 | -5.3597e-05 | 0.011301 | 0.011301 | 0.011301 | 0.99715 | -0.1112 | 0.99711 | -0.11144 | 5.3817
89 | -0.22742 | -0.10935 | 0.22744 | 0.10263 | 2.0142e-05 | -0.006721 | 0.0073223 | 0.0072398 | 0.0073223 | 0.99485 | -0.19908 | 0.99493 | -0.19979 | 3.3283
90 | 0.22742 | 0.10935 | -0.22742 | -0.11014 | 2.415e-06 | -0.00079549 | 0.0073223 | 0.0073323 | 0.0073323 | 0.99485 | -0.19908 | 0.99484 | -0.19899 | 3.3329
91 | 4.8737 | 2.1927 | -4.8721 | -2.2459 | 0.0016245 | -0.053236 | 0.15506 | 0.15571 | 0.15571 | 0.99493 | -0.19979 | 0.99458 | -0.20149 | 12.2033
92 | 4.8721 | 2.2459 | -4.872 | -2.2494 | 0.00010647 | -0.0034719 | 0.15571 | 0.15576 | 0.15576 | 0.99458 | -0.20149 | 0.99456 | -0.2016 | 12.2066
93 | 6.4315 | 2.8987 | -6.4313 | -2.9029 | 0.00022184 | -0.0041534 | 0.20449 | 0.20454 | 0.20454 | 0.99589 | -0.15718 | 0.99585 | -0.15736 | 16.0298
94 | -0.17372 | -0.084136 | 0.17372 | 0.083633 | 8.8154e-07 | -0.00050218 | 0.0055884 | 0.0055821 | 0.0055884 | 0.99707 | -0.11103 | 0.99707 | -0.11108 | 2.5402
95 | -0.35324 | -0.16826 | 0.35325 | 0.16612 | 1.5445e-05 | -0.0021406 | 0.011328 | 0.011301 | 0.011328 | 0.99707 | -0.11108 | 0.99711 | -0.11144 | 5.1491
96 | 0.17952 | 0.084631 | -0.17951 | -0.086887 | 4.2138e-06 | -0.0022568 | 0.0057461 | 0.0057742 | 0.0057742 | 0.99707 | -0.11108 | 0.99705 | -0.11088 | 2.6247
97 | -18.6438 | -8.6665 | 18.6457 | 8.6634 | 0.0018194 | -0.0031731 | 0.59366 | 0.59361 | 0.59366 | 0.99975 | -0.0011345 | 0.99985 | -0.00068223 | 46.525
98 | 18.6438 | 8.6665 | -18.6409 | -8.6717 | 0.0029775 | -0.0051894 | 0.59366 | 0.59374 | 0.59374 | 0.99975 | -0.0011345 | 0.99958 | -0.0018725 | 46.5315
99 | -18.6457 | -8.6634 | 18.6484 | 8.6586 | 0.0027366 | -0.0047757 | 0.59361 | 0.59353 | 0.59361 | 0.99985 | -0.00068223 | 1 | 0 | 46.521
100 | 6.4313 | 2.9029 | -6.4302 | -2.9244 | 0.0011501 | -0.021493 | 0.20454 | 0.20481 | 0.20481 | 0.99585 | -0.15736 | 0.99566 | -0.1583 | 16.0506
101 | -1.0323 | -0.48006 | 1.0324 | 0.48006 | 6.858e-05 | 1.0331e-06 | 0.032986 | 0.032986 | 0.032986 | 0.99631 | -0.052389 | 0.99638 | -0.051884 | 15.7078
102 | 0.41158 | 0.18774 | -0.41147 | -0.19918 | 0.00011229 | -0.011445 | 0.013107 | 0.013249 | 0.013249 | 0.99631 | -0.052389 | 0.99606 | -0.050167 | 6.0221
103 | 0.41147 | 0.19918 | -0.41144 | -0.19927 | 2.7549e-05 | -8.7063e-05 | 0.013249 | 0.01325 | 0.01325 | 0.99606 | -0.050167 | 0.99599 | -0.050609 | 6.3095
104 | -1.391 | -0.65375 | 1.391 | 0.6535 | 2.9e-05 | -0.0002511 | 0.04453 | 0.044526 | 0.04453 | 0.99638 | -0.051884 | 0.9964 | -0.052053 | 20.2407
105 | 13.8868 | 6.4106 | -13.8862 | -6.4129 | 0.0006294 | -0.0022495 | 0.44245 | 0.44248 | 0.44248 | 0.99793 | -0.088134 | 0.99788 | -0.088351 | 34.6771
106 | 0.091181 | 0.043514 | -0.091181 | -0.044161 | 3.1219e-07 | -0.00064705 | 0.0029249 | 0.002933 | 0.002933 | 0.99715 | -0.11124 | 0.99715 | -0.11121 | 1.3332
107 | 0.58112 | 0.27787 | -0.58107 | -0.28062 | 5.4606e-05 | -0.002746 | 0.01869 | 0.018724 | 0.018724 | 0.99492 | -0.16391 | 0.99483 | -0.1631 | 8.511
108 | 1.4467 | 0.68901 | -1.4465 | -0.69045 | 0.00018611 | -0.0014476 | 0.046652 | 0.046671 | 0.046671 | 0.99154 | -0.21076 | 0.99142 | -0.20968 | 21.2139
109 | 0.68734 | 0.32618 | -0.68722 | -0.32627 | 0.00011851 | -8.4847e-05 | 0.02215 | 0.022152 | 0.022152 | 0.99154 | -0.21076 | 0.99136 | -0.21198 | 10.5486
110 | 1.3712 | 0.65399 | -1.371 | -0.65562 | 0.0001881 | -0.0016331 | 0.044235 | 0.044256 | 0.044256 | 0.99142 | -0.20968 | 0.99129 | -0.20852 | 20.1162
111 | 1.371 | 0.65562 | -1.3707 | -0.65875 | 0.00036107 | -0.0031291 | 0.044256 | 0.044296 | 0.044296 | 0.99129 | -0.20852 | 0.99105 | -0.20627 | 20.1348
112 | 1.3707 | 0.65875 | -1.3702 | -0.66312 | 0.00050573 | -0.0043701 | 0.044296 | 0.044354 | 0.044354 | 0.99105 | -0.20627 | 0.99071 | -0.20309 | 20.1608
113 | 0.085512 | 0.040938 | -0.085512 | -0.041415 | 2.0781e-07 | -0.00047691 | 0.0027625 | 0.0027685 | 0.0027685 | 0.99071 | -0.20309 | 0.99071 | -0.20307 | 1.2584
114 | -0.17951 | -0.086941 | 0.17951 | 0.086887 | 2.7606e-06 | -5.3414e-05 | 0.0057749 | 0.0057742 | 0.0057749 | 0.99703 | -0.11098 | 0.99705 | -0.11088 | 2.75
115 | 13.2843 | 6.1233 | -13.2829 | -6.1289 | 0.0014083 | -0.0055741 | 0.42318 | 0.42325 | 0.42325 | 0.99785 | -0.08851 | 0.99774 | -0.08902 | 33.1703
116 | -13.2843 | -6.1233 | 13.2848 | 6.1216 | 0.00043552 | -0.0017245 | 0.42318 | 0.42315 | 0.42318 | 0.99785 | -0.08851 | 0.99788 | -0.088351 | 33.1642
117 | -0.47305 | -0.22911 | 0.47306 | 0.22812 | 1.2987e-05 | -0.00099273 | 0.015223 | 0.01521 | 0.015223 | 0.99673 | -0.04044 | 0.99676 | -0.040678 | 6.9195
118 | 0.11223 | 0.052864 | -0.11223 | -0.05381 | 6.8848e-07 | -0.000946 | 0.0035914 | 0.0036031 | 0.0036031 | 0.99718 | -0.11154 | 0.99718 | -0.11149 | 1.6378
119 | 0.11223 | 0.05381 | -0.11223 | -0.054355 | 3.9912e-07 | -0.00054558 | 0.0036031 | 0.00361 | 0.00361 | 0.99718 | -0.11149 | 0.99717 | -0.11146 | 1.6409
120 | -0.19899 | -0.096374 | 0.19899 | 0.096303 | 4.5677e-06 | -7.0728e-05 | 0.0064159 | 0.006415 | 0.0064159 | 0.99479 | -0.16304 | 0.99481 | -0.16289 | 3.0552
121 | -0.58105 | -0.28134 | 0.58107 | 0.28062 | 1.4418e-05 | -0.00072328 | 0.018733 | 0.018724 | 0.018733 | 0.99481 | -0.16289 | 0.99483 | -0.1631 | 8.5152

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 18.7336 | 8.7036

## res_load
| p_mw | q_mvar
0 | 0.35285 | 0.17089
1 | 0.35699 | 0.1729
2 | 0.14614 | 0.070781
3 | 3.7665 | 1.8242
4 | 0.37048 | 0.17943
5 | 0.27982 | 0.13552
6 | 0.19665 | 0.095241
7 | 0.35438 | 0.17163
8 | 0.10448 | 0.050601
9 | 0.34507 | 0.16713
10 | 0.33171 | 0.16065
11 | 0.23667 | 0.11463
12 | 0.18911 | 0.091591
13 | 0.29774 | 0.1442
14 | 0.11434 | 0.055378
15 | 0.16789 | 0.081314
16 | 0.34918 | 0.16911
17 | 0.19158 | 0.092788
18 | 0.20427 | 0.098933
19 | 0.088115 | 0.042676
20 | 0.38454 | 0.18624
21 | 0.086279 | 0.041787
22 | 0.076322 | 0.036964
23 | 0.26103 | 0.12642
24 | 0.07316 | 0.035433
25 | 0.22932 | 0.11107
26 | 0.31564 | 0.15287
27 | 0.28156 | 0.13637
28 | 0.33893 | 0.16415
29 | 0.18189 | 0.088095
30 | 0.33274 | 0.16115
31 | 0.27064 | 0.13108
32 | 0.087058 | 0.042164
33 | 0.36059 | 0.17464
34 | 0.31261 | 0.1514
35 | 0.30657 | 0.14848
36 | 0.22742 | 0.11014
37 | 0.23296 | 0.11283
38 | 0.17372 | 0.084136
39 | 0.0895 | 0.043347
40 | 0.28008 | 0.13565
41 | 0.41144 | 0.19927
42 | 0.35862 | 0.17369
43 | 0.071171 | 0.03447
44 | 0.38814 | 0.18799
45 | 0.093976 | 0.045515
46 | 0.073328 | 0.035514
47 | 0.35547 | 0.17216
48 | 0.075296 | 0.036468
49 | 1.2846 | 0.62218
50 | 0.085512 | 0.041415
51 | 0.17951 | 0.086941
52 | 0.60143 | 0.29129
53 | 0.47305 | 0.22911
54 | 0.091181 | 0.044161
55 | 0.074461 | 0.036063
56 | 0.11223 | 0.054355
57 | 0.19899 | 0.096374
58 | 0.38206 | 0.18504

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1