## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_591_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_591_0_node_92 | 20 | n |  | TRUE
2 | bus_MV_591_0_node_15 | 20 | n |  | TRUE
3 | bus_MV_591_0_node_44 | 20 | n |  | TRUE
4 | bus_MV_591_0_node_109 | 20 | n |  | TRUE
5 | bus_MV_591_0_node_1 | 20 | n |  | TRUE
6 | bus_MV_591_0_node_2 | 20 | n |  | TRUE
7 | bus_MV_591_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_591_0_node_4 | 20 | n |  | TRUE
9 | bus_MV_591_0_node_42 | 20 | n |  | TRUE
10 | bus_MV_591_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_591_0_node_97 | 20 | n |  | TRUE
12 | bus_MV_591_0_node_5 | 20 | n |  | TRUE
13 | bus_MV_591_0_node_6 | 20 | n |  | TRUE
14 | bus_MV_591_0_node_105 | 20 | n |  | TRUE
15 | bus_MV_591_0_node_8 | 20 | n |  | TRUE
16 | bus_MV_591_0_node_9 | 20 | n |  | TRUE
17 | bus_MV_591_0_node_47 | 20 | n |  | TRUE
18 | bus_MV_591_0_node_96 | 20 | n |  | TRUE
19 | bus_MV_591_0_node_41 | 20 | n |  | TRUE
20 | bus_MV_591_0_node_43 | 20 | n |  | TRUE
21 | bus_MV_591_0_node_10 | 20 | n |  | TRUE
22 | bus_MV_591_0_node_45 | 20 | n |  | TRUE
23 | bus_MV_591_0_node_46 | 20 | n |  | TRUE
24 | bus_MV_591_0_node_48 | 20 | n |  | TRUE
25 | bus_MV_591_0_node_49 | 20 | n |  | TRUE
26 | bus_MV_591_0_node_57 | 20 | n |  | TRUE
27 | bus_MV_591_0_node_11 | 20 | n |  | TRUE
28 | bus_MV_591_0_node_12 | 20 | n |  | TRUE
29 | bus_MV_591_0_node_107 | 20 | n |  | TRUE
30 | bus_MV_591_0_node_13 | 20 | n |  | TRUE
31 | bus_MV_591_0_node_18 | 20 | n |  | TRUE
32 | bus_MV_591_0_node_19 | 20 | n |  | TRUE
33 | bus_MV_591_0_node_16 | 20 | n |  | TRUE
34 | bus_MV_591_0_node_17 | 20 | n |  | TRUE
35 | bus_MV_591_0_node_23 | 20 | n |  | TRUE
36 | bus_MV_591_0_node_24 | 20 | n |  | TRUE
37 | bus_MV_591_0_node_25 | 20 | n |  | TRUE
38 | bus_MV_591_0_node_26 | 20 | n |  | TRUE
39 | bus_MV_591_0_node_22 | 20 | n |  | TRUE
40 | bus_MV_591_0_node_21 | 20 | n |  | TRUE
41 | bus_MV_591_0_node_20 | 20 | n |  | TRUE
42 | bus_MV_591_0_node_32 | 20 | n |  | TRUE
43 | bus_MV_591_0_node_33 | 20 | n |  | TRUE
44 | bus_MV_591_0_node_29 | 20 | n |  | TRUE
45 | bus_MV_591_0_node_106 | 20 | n |  | TRUE
46 | bus_MV_591_0_node_27 | 20 | n |  | TRUE
47 | bus_MV_591_0_node_30 | 20 | n |  | TRUE
48 | bus_MV_591_0_node_37 | 20 | n |  | TRUE
49 | bus_MV_591_0_node_28 | 20 | n |  | TRUE
50 | bus_MV_591_0_node_108 | 20 | n |  | TRUE
51 | bus_MV_591_0_node_31 | 20 | n |  | TRUE
52 | bus_MV_591_0_node_110 | 20 | n |  | TRUE
53 | bus_MV_591_0_node_34 | 20 | n |  | TRUE
54 | bus_MV_591_0_node_35 | 20 | n |  | TRUE
55 | bus_MV_591_0_node_36 | 20 | n |  | TRUE
56 | bus_MV_591_0_node_61 | 20 | n |  | TRUE
57 | bus_MV_591_0_node_38 | 20 | n |  | TRUE
58 | bus_MV_591_0_node_39 | 20 | n |  | TRUE
59 | bus_MV_591_0_node_40 | 20 | n |  | TRUE
60 | bus_MV_591_0_node_111 | 20 | n |  | TRUE
61 | bus_MV_591_0_node_81 | 20 | n |  | TRUE
62 | bus_MV_591_0_node_82 | 20 | n |  | TRUE
63 | bus_MV_591_0_node_80 | 20 | n |  | TRUE
64 | bus_MV_591_0_node_79 | 20 | n |  | TRUE
65 | bus_MV_591_0_node_101 | 20 | n |  | TRUE
66 | bus_MV_591_0_node_99 | 20 | n |  | TRUE
67 | bus_MV_591_0_node_83 | 20 | n |  | TRUE
68 | bus_MV_591_0_node_98 | 20 | n |  | TRUE
69 | bus_MV_591_0_node_103 | 20 | n |  | TRUE
70 | bus_MV_591_0_node_102 | 20 | n |  | TRUE
71 | bus_MV_591_0_node_50 | 20 | n |  | TRUE
72 | bus_MV_591_0_node_58 | 20 | n |  | TRUE
73 | bus_MV_591_0_node_51 | 20 | n |  | TRUE
74 | bus_MV_591_0_node_66 | 20 | n |  | TRUE
75 | bus_MV_591_0_node_67 | 20 | n |  | TRUE
76 | bus_MV_591_0_node_68 | 20 | n |  | TRUE
77 | bus_MV_591_0_node_60 | 20 | n |  | TRUE
78 | bus_MV_591_0_node_62 | 20 | n |  | TRUE
79 | bus_MV_591_0_node_69 | 20 | n |  | TRUE
80 | bus_MV_591_0_node_65 | 20 | n |  | TRUE
81 | bus_MV_591_0_node_63 | 20 | n |  | TRUE
82 | bus_MV_591_0_node_52 | 20 | n |  | TRUE
83 | bus_MV_591_0_node_53 | 20 | n |  | TRUE
84 | bus_MV_591_0_node_54 | 20 | n |  | TRUE
85 | bus_MV_591_0_node_55 | 20 | n |  | TRUE
86 | bus_MV_591_0_node_56 | 20 | n |  | TRUE
87 | bus_MV_591_0_node_59 | 20 | n |  | TRUE
88 | bus_MV_591_0_node_64 | 20 | n |  | TRUE
89 | bus_MV_591_0_node_93 | 20 | n |  | TRUE
90 | bus_MV_591_0_node_72 | 20 | n |  | TRUE
91 | bus_MV_591_0_node_70 | 20 | n |  | TRUE
92 | bus_MV_591_0_node_91 | 20 | n |  | TRUE
93 | bus_MV_591_0_node_88 | 20 | n |  | TRUE
94 | bus_MV_591_0_node_71 | 20 | n |  | TRUE
95 | bus_MV_591_0_node_73 | 20 | n |  | TRUE
96 | bus_MV_591_0_node_78 | 20 | n |  | TRUE
97 | bus_MV_591_0_node_94 | 20 | n |  | TRUE
98 | bus_MV_591_0_node_74 | 20 | n |  | TRUE
99 | bus_MV_591_0_node_75 | 20 | n |  | TRUE
100 | bus_MV_591_0_node_90 | 20 | n |  | TRUE
101 | bus_MV_591_0_node_87 | 20 | n |  | TRUE
102 | bus_MV_591_0_node_89 | 20 | n |  | TRUE
103 | bus_MV_591_0_node_85 | 20 | n |  | TRUE
104 | bus_MV_591_0_node_95 | 20 | n |  | TRUE
105 | bus_MV_591_0_node_77 | 20 | n |  | TRUE
106 | bus_MV_591_0_node_76 | 20 | n |  | TRUE
107 | bus_MV_591_0_node_100 | 20 | n |  | TRUE
108 | bus_MV_591_0_node_112 | 20 | n |  | TRUE
109 | bus_MV_591_0_node_104 | 20 | n |  | TRUE
110 | bus_MV_591_0_node_84 | 20 | n |  | TRUE
111 | bus_MV_591_0_node_86 | 20 | n |  | TRUE
112 | bus_HV_591_0_node_61 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_591_0_load_0 | 0 | 0.19943 | 0.096591 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_591_0_load_92 | 1 | 0.33727 | 0.16335 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_591_0_load_109 | 4 | 0.2413 | 0.11687 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_591_0_load_1 | 5 | 0.27542 | 0.13339 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_591_0_load_42 | 9 | 0.23787 | 0.1152 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_591_0_load_97 | 11 | 0.10354 | 0.050148 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_591_0_load_105 | 14 | 0.087674 | 0.042463 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_591_0_load_9 | 16 | 0.35903 | 0.17388 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_591_0_load_47 | 17 | 0.30882 | 0.14957 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_591_0_load_96 | 18 | 0.10184 | 0.049323 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_591_0_load_41 | 19 | 0.33226 | 0.16092 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_591_0_load_45 | 22 | 0.33624 | 0.16285 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_591_0_load_49 | 25 | 0.2909 | 0.14089 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_591_0_load_57 | 26 | 0.1995 | 0.096621 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_591_0_load_107 | 29 | 0.40013 | 0.19379 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_591_0_load_13 | 30 | 0.28995 | 0.14043 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_591_0_load_16 | 33 | 0.35495 | 0.17191 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_591_0_load_22 | 39 | 0.23 | 0.11139 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_591_0_load_20 | 41 | 0.25582 | 0.1239 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_591_0_load_32 | 42 | 0.37689 | 0.18254 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_591_0_load_33 | 43 | 0.27822 | 0.13475 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_591_0_load_106 | 45 | 0.34592 | 0.16754 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_591_0_load_37 | 48 | 0.31318 | 0.15168 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_591_0_load_108 | 50 | 0.41011 | 0.19863 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_591_0_load_110 | 52 | 0.28909 | 0.14001 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_591_0_load_34 | 53 | 0.38577 | 0.18684 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_591_0_load_61 | 56 | 0.20501 | 0.099293 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_591_0_load_38 | 57 | 0.36368 | 0.17614 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_591_0_load_111 | 60 | 0.1131 | 0.054775 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_591_0_load_79 | 64 | 0.32218 | 0.15604 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_591_0_load_101 | 65 | 0.38468 | 0.18631 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_591_0_load_98 | 68 | 0.2797 | 0.13546 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_591_0_load_102 | 70 | 0.088741 | 0.042979 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_591_0_load_66 | 74 | 0.2588 | 0.12534 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_591_0_load_68 | 76 | 0.39179 | 0.18975 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_591_0_load_62 | 78 | 0.40447 | 0.1959 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_591_0_load_65 | 80 | 0.18346 | 0.088852 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_591_0_load_63 | 81 | 0.26786 | 0.12973 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_591_0_load_52 | 82 | 0.29462 | 0.14269 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_591_0_load_53 | 83 | 0.3579 | 0.17334 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_591_0_load_64 | 88 | 0.39703 | 0.19229 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_591_0_load_93 | 89 | 0.075116 | 0.03638 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_591_0_load_91 | 92 | 0.071098 | 0.034434 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_591_0_load_73 | 95 | 0.39684 | 0.1922 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_591_0_load_94 | 97 | 0.092774 | 0.044933 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_591_0_load_90 | 100 | 0.19514 | 0.09451 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_591_0_load_89 | 102 | 0.40251 | 0.19494 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_591_0_load_95 | 104 | 0.17961 | 0.086991 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_591_0_load_76 | 106 | 0.40658 | 0.19691 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_591_0_load_100 | 107 | 0.12322 | 0.059679 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_591_0_load_112 | 108 | 0.10506 | 0.050882 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_591_0_load_104 | 109 | 0.35161 | 0.17029 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_591_0_load_84 | 110 | 0.26198 | 0.12688 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_591_0_line_0 |  | 0 | 1 | 0.12191 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_591_0_line_1 |  | 0 | 2 | 0.1444 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
2 | MV_591_0_line_2 |  | 1 | 3 | 0.027361 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_591_0_line_3 |  | 2 | 4 | 0.004836 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_591_0_line_4 |  | 3 | 20 | 0.21324 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_591_0_line_5 |  | 5 | 6 | 0.005346 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_591_0_line_6 |  | 6 | 7 | 0.17453 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_591_0_line_7 |  | 6 | 8 | 0.17682 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_591_0_line_8 |  | 7 | 9 | 0.004338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_591_0_line_9 |  | 8 | 10 | 0.13252 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_591_0_line_10 |  | 8 | 11 | 0.042864 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_591_0_line_11 |  | 9 | 20 | 0.008754 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_591_0_line_12 |  | 10 | 18 | 0.003011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_591_0_line_13 |  | 10 | 12 | 0.2755 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_591_0_line_14 |  | 12 | 13 | 0.26881 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_591_0_line_15 |  | 12 | 14 | 0.036237 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_591_0_line_16 |  | 13 | 15 | 0.20735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_591_0_line_17 |  | 13 | 16 | 0.055882 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
18 | MV_591_0_line_18 |  | 13 | 17 | 0.25802 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
19 | MV_591_0_line_19 |  | 15 | 19 | 0.009209 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_591_0_line_20 |  | 16 | 21 | 0.006195 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
21 | MV_591_0_line_21 |  | 17 | 23 | 0.026045 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
22 | MV_591_0_line_22 |  | 21 | 27 | 0.096027 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
23 | MV_591_0_line_23 |  | 21 | 28 | 0.19306 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_591_0_line_24 |  | 22 | 23 | 0.037574 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_591_0_line_25 |  | 23 | 24 | 0.12256 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
26 | MV_591_0_line_26 |  | 23 | 25 | 0.16667 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_591_0_line_27 |  | 24 | 26 | 0.13361 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
28 | MV_591_0_line_28 |  | 25 | 71 | 0.041378 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_591_0_line_29 |  | 26 | 72 | 0.004054 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
30 | MV_591_0_line_30 |  | 27 | 29 | 0.076526 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
31 | MV_591_0_line_31 |  | 28 | 30 | 0.019135 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_591_0_line_32 |  | 29 | 31 | 0.008948 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
33 | MV_591_0_line_33 |  | 31 | 32 | 0.10821 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
34 | MV_591_0_line_34 |  | 32 | 40 | 0.036185 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_591_0_line_35 |  | 32 | 41 | 0.007533 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_591_0_line_36 |  | 33 | 34 | 0.088966 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_591_0_line_37 |  | 34 | 35 | 0.14332 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_591_0_line_38 |  | 35 | 36 | 0.03073 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_591_0_line_39 |  | 35 | 37 | 0.24194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_591_0_line_40 |  | 35 | 38 | 0.63382 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
41 | MV_591_0_line_41 |  | 35 | 39 | 0.057639 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
42 | MV_591_0_line_42 |  | 36 | 42 | 0.075718 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
43 | MV_591_0_line_43 |  | 37 | 43 | 0.007089 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_591_0_line_44 |  | 38 | 44 | 0.39556 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_591_0_line_45 |  | 38 | 45 | 0.009052 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_591_0_line_46 |  | 39 | 40 | 0.019546 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
47 | MV_591_0_line_47 |  | 44 | 50 | 0.004705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_591_0_line_48 |  | 44 | 49 | 0.45493 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
49 | MV_591_0_line_49 |  | 46 | 47 | 0.077612 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_591_0_line_50 |  | 46 | 48 | 0.098729 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_591_0_line_51 |  | 47 | 51 | 0.39704 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
52 | MV_591_0_line_52 |  | 47 | 52 | 0.073899 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
53 | MV_591_0_line_53 |  | 47 | 49 | 0.18446 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
54 | MV_591_0_line_54 |  | 51 | 53 | 0.009353 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
55 | MV_591_0_line_55 |  | 53 | 54 | 0.031963 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
56 | MV_591_0_line_56 |  | 54 | 55 | 0.17431 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
57 | MV_591_0_line_57 |  | 55 | 56 | 0.008292 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
58 | MV_591_0_line_58 |  | 57 | 58 | 0.009229 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_591_0_line_59 |  | 58 | 59 | 0.30498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_591_0_line_60 |  | 59 | 60 | 0.013181 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_591_0_line_61 |  | 59 | 61 | 0.56564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_591_0_line_62 |  | 59 | 62 | 0.072776 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_591_0_line_63 |  | 61 | 65 | 0.009987 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_591_0_line_64 |  | 61 | 63 | 1.2585 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_591_0_line_65 |  | 62 | 66 | 0.055629 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_591_0_line_66 |  | 62 | 67 | 0.12715 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_591_0_line_67 |  | 62 | 68 | 0.060904 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_591_0_line_68 |  | 63 | 64 | 0.01204 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_591_0_line_69 |  | 64 | 90 | 0.098722 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_591_0_line_70 |  | 65 | 107 | 0.052269 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
71 | MV_591_0_line_71 |  | 66 | 108 | 0.00226 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
72 | MV_591_0_line_72 |  | 67 | 69 | 0.028342 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_591_0_line_73 |  | 67 | 70 | 0.03 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_591_0_line_74 |  | 69 | 109 | 0.00425 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_591_0_line_75 |  | 71 | 73 | 0.05792 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_591_0_line_76 |  | 72 | 87 | 0.18772 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_591_0_line_77 |  | 73 | 77 | 0.07529 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_591_0_line_78 |  | 73 | 78 | 0.008462 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_591_0_line_79 |  | 74 | 75 | 0.012433 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
80 | MV_591_0_line_80 |  | 74 | 76 | 0.03747 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
81 | MV_591_0_line_81 |  | 75 | 79 | 0.025505 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
82 | MV_591_0_line_82 |  | 76 | 89 | 0.082422 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
83 | MV_591_0_line_83 |  | 77 | 80 | 0.01847 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_591_0_line_84 |  | 78 | 81 | 0.037641 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_591_0_line_85 |  | 79 | 92 | 0.020622 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
86 | MV_591_0_line_86 |  | 82 | 83 | 0.003609 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_591_0_line_87 |  | 82 | 84 | 0.010944 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_591_0_line_88 |  | 83 | 85 | 0.03726 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_591_0_line_89 |  | 84 | 86 | 0.003967 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_591_0_line_90 |  | 85 | 87 | 0.09145 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_591_0_line_91 |  | 86 | 88 | 0.010845 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_591_0_line_92 |  | 87 | 89 | 0.017738 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
93 | MV_591_0_line_93 |  | 90 | 91 | 0.14338 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_591_0_line_94 |  | 91 | 94 | 0.087261 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_591_0_line_95 |  | 91 | 95 | 0.03883 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_591_0_line_96 |  | 92 | 93 | 0.017908 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
97 | MV_591_0_line_97 |  | 93 | 111 | 0.010915 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
98 | MV_591_0_line_98 |  | 94 | 96 | 0.035958 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_591_0_line_99 |  | 94 | 97 | 0.022731 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_591_0_line_100 |  | 95 | 98 | 0.010011 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_591_0_line_101 |  | 96 | 104 | 0.039122 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_591_0_line_102 |  | 96 | 105 | 0.047206 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_591_0_line_103 |  | 98 | 99 | 0.014431 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_591_0_line_104 |  | 99 | 100 | 0.020891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_591_0_line_105 |  | 100 | 101 | 0.018008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_591_0_line_106 |  | 101 | 102 | 0.020171 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_591_0_line_107 |  | 101 | 103 | 0.05248 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_591_0_line_108 |  | 103 | 110 | 0.065092 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
109 | MV_591_0_line_109 |  | 105 | 106 | 0.009703 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_591_0_line_110 |  | 110 | 111 | 0.007511 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_591_0_trafo_61 | 25 MVA 110/20 kV | 112 | 56 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2601770.563 | 1198864.8039
1 | 2601839.4023 | 1198965.4221
2 | 2601628.4478 | 1198890.4122
3 | 2601825.9491 | 1198989.2642
4 | 2601626.2995 | 1198894.7473
5 | 2601762.9498 | 1199077.0375
6 | 2601765.9585 | 1199072.6137
7 | 2601890.1938 | 1199168.4126
8 | 2601682.8654 | 1199199.781
9 | 2601892.9358 | 1199165.045
10 | 2601620.2464 | 1199188.1805
11 | 2601656.7637 | 1199233.7817
12 | 2601579.5392 | 1199236.9962
13 | 2601398.5106 | 1199240.3217
14 | 2601609.7028 | 1199247.7582
15 | 2601561.8319 | 1199290.5093
16 | 2601351.4196 | 1199210.0286
17 | 2601322.8562 | 1199487.0042
18 | 2601618.44 | 1199190.5894
19 | 2601571.0217 | 1199289.5889
20 | 2601899.2189 | 1199158.9326
21 | 2601347.5453 | 1199205.303
22 | 2601347.7572 | 1199531.7779
23 | 2601316.814 | 1199510.3376
24 | 2601227.4596 | 1199500.381
25 | 2601225.6873 | 1199649.8941
26 | 2601101.1788 | 1199456.7234
27 | 2601351.4031 | 1199109.497
28 | 2601444.5492 | 1199044.5718
29 | 2601348.6023 | 1199033.0221
30 | 2601453.5298 | 1199027.6648
31 | 2601354.2837 | 1199026.0974
32 | 2601285.1807 | 1198950.1424
33 | 2601315.3827 | 1198815.7323
34 | 2601334.7194 | 1198902.5716
35 | 2601195.5748 | 1198936.8955
36 | 2601176.9443 | 1198932.4008
37 | 2601073.5398 | 1199064.4198
38 | 2600932.4255 | 1198802.4355
39 | 2601252.2967 | 1198947.1342
40 | 2601269.5594 | 1198937.8771
41 | 2601278.4797 | 1198953.6206
42 | 2601102.2763 | 1198919.8363
43 | 2601079.7532 | 1199060.9746
44 | 2601004.6717 | 1198975.8168
45 | 2600941.4862 | 1198802.9927
46 | 2600680.3013 | 1199078.63
47 | 2600716.9102 | 1199131.0953
48 | 2600644.1422 | 1199012.2131
49 | 2600738.1835 | 1198989.6219
50 | 2601000.0273 | 1198974.9823
51 | 2600889.5098 | 1199154.0731
52 | 2600686.1896 | 1199198.3058
53 | 2600893.62 | 1199162.4782
54 | 2600902.6684 | 1199192.9735
55 | 2601054.8587 | 1199184.1697
56 | 2601063.1424 | 1199183.4373
57 | 2600897.4482 | 1198677.8195
58 | 2600888.3569 | 1198676.084
59 | 2600776.5682 | 1198833.843
60 | 2600763.3884 | 1198832.8187
61 | 2600657.216 | 1198770.5741
62 | 2600812.1518 | 1198871.3229
63 | 2600840.0256 | 1199472.6594
64 | 2600852.0243 | 1199471.5047
65 | 2600657.0495 | 1198760.5909
66 | 2600848.8784 | 1198898.0863
67 | 2600767.9109 | 1198965.5346
68 | 2600856.7289 | 1198852.1504
69 | 2600762.7759 | 1198993.4045
70 | 2600780.0777 | 1198982.8955
71 | 2601214.4352 | 1199689.7133
72 | 2601097.2124 | 1199455.8334
73 | 2601167.4252 | 1199688.5261
74 | 2600918.1366 | 1199641.8383
75 | 2600917.5791 | 1199654.256
76 | 2600919.9082 | 1199604.4185
77 | 2601157.5018 | 1199624.6345
78 | 2601165.8021 | 1199696.8302
79 | 2600903.4629 | 1199665.9937
80 | 2601139.5434 | 1199620.1066
81 | 2601158.4564 | 1199733.7376
82 | 2601040.5001 | 1199649.0608
83 | 2601037.0135 | 1199648.093
84 | 2601039.1737 | 1199659.9219
85 | 2601040.1637 | 1199610.9737
86 | 2601043.1171 | 1199660.4451
87 | 2601002.4647 | 1199555.0377
88 | 2601041.981 | 1199671.2285
89 | 2600984.7865 | 1199553.5842
90 | 2600900.0532 | 1199549.2306
91 | 2600800.6794 | 1199603.9692
92 | 2600903.1492 | 1199686.6134
93 | 2600902.6886 | 1199704.5142
94 | 2600754.8379 | 1199564.0313
95 | 2600798.642 | 1199642.7453
96 | 2600725.1625 | 1199557.8469
97 | 2600765.59 | 1199576.0043
98 | 2600798.3819 | 1199652.7506
99 | 2600794.6655 | 1199663.1002
100 | 2600795.9336 | 1199683.9527
101 | 2600797.7746 | 1199701.8658
102 | 2600817.929 | 1199702.6526
103 | 2600834.9617 | 1199719.2019
104 | 2600764.2848 | 1199557.8681
105 | 2600727.4804 | 1199595.0337
106 | 2600727.3119 | 1199604.7278
107 | 2600626.1802 | 1198718.4114
108 | 2600848.4746 | 1198900.3097
109 | 2600758.7331 | 1198992.0589
110 | 2600900.0447 | 1199720.3001
111 | 2600899.7565 | 1199712.796
112 | 2601063.1424 | 1199183.4373

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98975 | -0.14059 | 0.19943 | 0.096591
1 | 0.98985 | -0.13992 | 0.33727 | 0.16335
2 | 0.98968 | -0.14102 | 0 | 0
3 | 0.98988 | -0.14018 | 0 | 0
4 | 0.98968 | -0.14101 | 0.2413 | 0.11687
5 | 0.99033 | -0.14434 | 0.27542 | 0.13339
6 | 0.99033 | -0.14436 | 0 | 0
7 | 0.99011 | -0.14229 | 0 | 0
8 | 0.99063 | -0.147 | 0 | 0
9 | 0.9901 | -0.14224 | 0.23787 | 0.1152
10 | 0.99086 | -0.1491 | 0 | 0
11 | 0.99062 | -0.14695 | 0.10354 | 0.050148
12 | 0.99139 | -0.15373 | 0 | 0
13 | 0.99194 | -0.1584 | 0 | 0
14 | 0.99139 | -0.15369 | 0.087674 | 0.042463
15 | 0.99185 | -0.1576 | 0 | 0
16 | 0.99206 | -0.1562 | 0.35903 | 0.17388
17 | 0.99091 | -0.19304 | 0.30882 | 0.14957
18 | 0.99086 | -0.1491 | 0.10184 | 0.049323
19 | 0.99184 | -0.15756 | 0.33226 | 0.16092
20 | 0.99009 | -0.14216 | 0 | 0
21 | 0.99207 | -0.15595 | 0 | 0
22 | 0.99085 | -0.19368 | 0.33624 | 0.16285
23 | 0.99086 | -0.19383 | 0 | 0
24 | 0.9907 | -0.19684 | 0 | 0
25 | 0.99049 | -0.19626 | 0.2909 | 0.14089
26 | 0.99029 | -0.21077 | 0.1995 | 0.096621
27 | 0.99229 | -0.15193 | 0 | 0
28 | 0.992 | -0.1553 | 0 | 0
29 | 0.9927 | -0.13833 | 0.40013 | 0.19379
30 | 0.99199 | -0.15524 | 0.28995 | 0.14043
31 | 0.99272 | -0.13794 | 0 | 0
32 | 0.99298 | -0.13324 | 0 | 0
33 | 0.99328 | -0.12069 | 0.35495 | 0.17191
34 | 0.99334 | -0.1203 | 0 | 0
35 | 0.99344 | -0.11968 | 0 | 0
36 | 0.99343 | -0.11954 | 0 | 0
37 | 0.99336 | -0.11891 | 0 | 0
38 | 0.99517 | -0.088389 | 0 | 0
39 | 0.99311 | -0.13077 | 0.23 | 0.11139
40 | 0.99306 | -0.13164 | 0 | 0
41 | 0.99297 | -0.13322 | 0.25582 | 0.1239
42 | 0.99337 | -0.11989 | 0.37689 | 0.18254
43 | 0.99335 | -0.11889 | 0.27822 | 0.13475
44 | 0.99627 | -0.068257 | 0 | 0
45 | 0.99516 | -0.088351 | 0.34592 | 0.16754
46 | 0.99808 | -0.034316 | 0 | 0
47 | 0.99812 | -0.034592 | 0 | 0
48 | 0.99804 | -0.033952 | 0.31318 | 0.15168
49 | 0.99758 | -0.044319 | 0 | 0
50 | 0.99627 | -0.068234 | 0.41011 | 0.19863
51 | 0.99931 | -0.012689 | 0 | 0
52 | 0.99807 | -0.034851 | 0.28909 | 0.14001
53 | 0.99934 | -0.012173 | 0.38577 | 0.18684
54 | 0.99944 | -0.01036 | 0 | 0
55 | 0.99997 | -0.00047069 | 0 | 0
56 | 1 | 0 | -14.2393 | -6.5731
57 | 0.98395 | -0.18998 | 0.36368 | 0.17614
58 | 0.98395 | -0.19002 | 0 | 0
59 | 0.98409 | -0.19131 | 0 | 0
60 | 0.98409 | -0.1913 | 0.1131 | 0.054775
61 | 0.98504 | -0.19955 | 0 | 0
62 | 0.98402 | -0.19061 | 0 | 0
63 | 0.98797 | -0.2239 | 0 | 0
64 | 0.988 | -0.22412 | 0.32218 | 0.15604
65 | 0.98503 | -0.19949 | 0.38468 | 0.18631
66 | 0.98401 | -0.19054 | 0 | 0
67 | 0.98394 | -0.18994 | 0 | 0
68 | 0.98399 | -0.1904 | 0.2797 | 0.13546
69 | 0.98393 | -0.18982 | 0 | 0
70 | 0.98394 | -0.18991 | 0.088741 | 0.042979
71 | 0.99044 | -0.19585 | 0 | 0
72 | 0.99028 | -0.21086 | 0 | 0
73 | 0.99038 | -0.19526 | 0 | 0
74 | 0.98978 | -0.22309 | 0.2588 | 0.12534
75 | 0.98977 | -0.22329 | 0 | 0
76 | 0.98982 | -0.22242 | 0.39179 | 0.18975
77 | 0.99036 | -0.19509 | 0 | 0
78 | 0.99037 | -0.19519 | 0.40447 | 0.1959
79 | 0.98975 | -0.22372 | 0 | 0
80 | 0.99036 | -0.19505 | 0.18346 | 0.088852
81 | 0.99036 | -0.19507 | 0.26786 | 0.12973
82 | 0.98986 | -0.21367 | 0.29462 | 0.14269
83 | 0.98986 | -0.2137 | 0.3579 | 0.17334
84 | 0.98985 | -0.21361 | 0 | 0
85 | 0.98991 | -0.21417 | 0 | 0
86 | 0.98985 | -0.21359 | 0 | 0
87 | 0.99003 | -0.21533 | 0 | 0
88 | 0.98984 | -0.21354 | 0.39703 | 0.19229
89 | 0.99002 | -0.21567 | 0.075116 | 0.03638
90 | 0.98827 | -0.22631 | 0 | 0
91 | 0.98866 | -0.22946 | 0 | 0
92 | 0.98973 | -0.22407 | 0.071098 | 0.034434
93 | 0.98971 | -0.22436 | 0 | 0
94 | 0.98858 | -0.22876 | 0 | 0
95 | 0.98887 | -0.22786 | 0.39684 | 0.1922
96 | 0.98855 | -0.22851 | 0 | 0
97 | 0.98858 | -0.22873 | 0.092774 | 0.044933
98 | 0.98891 | -0.22821 | 0 | 0
99 | 0.98897 | -0.22871 | 0 | 0
100 | 0.98906 | -0.22943 | 0.19514 | 0.09451
101 | 0.98913 | -0.23009 | 0 | 0
102 | 0.98912 | -0.22999 | 0.40251 | 0.19494
103 | 0.98939 | -0.23229 | 0 | 0
104 | 0.98854 | -0.22842 | 0.17961 | 0.086991
105 | 0.98853 | -0.22827 | 0 | 0
106 | 0.98852 | -0.22823 | 0.40658 | 0.19691
107 | 0.98502 | -0.19957 | 0.12322 | 0.059679
108 | 0.98401 | -0.19054 | 0.10506 | 0.050882
109 | 0.98393 | -0.1898 | 0.35161 | 0.17029
110 | 0.98968 | -0.22473 | 0.26198 | 0.12688
111 | 0.9897 | -0.22454 | 0 | 0
112 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.44075 | -0.21319 | 0.44079 | 0.21307 | 4.4288e-05 | -0.00011485 | 0.01428 | 0.014278 | 0.01428 | 0.98975 | -0.14059 | 0.98985 | -0.13992 | 6.8
1 | 0.24132 | 0.11659 | -0.2413 | -0.11675 | 1.5725e-05 | -0.00015901 | 0.0078168 | 0.007819 | 0.007819 | 0.98975 | -0.14059 | 0.98968 | -0.14102 | 3.7233
2 | -0.77806 | -0.37642 | 0.77808 | 0.37578 | 2.3201e-05 | -0.00063322 | 0.025207 | 0.025199 | 0.025207 | 0.98985 | -0.13992 | 0.98988 | -0.14018 | 11.4577
3 | 0.2413 | 0.11675 | -0.2413 | -0.11687 | 3.9478e-07 | -0.00011298 | 0.007819 | 0.0078204 | 0.0078204 | 0.98968 | -0.14102 | 0.98968 | -0.14101 | 3.5547
4 | -0.77808 | -0.37578 | 0.77826 | 0.37085 | 0.00018031 | -0.0049365 | 0.025199 | 0.025136 | 0.025199 | 0.98988 | -0.14018 | 0.99009 | -0.14216 | 11.454
5 | -0.27542 | -0.13339 | 0.27542 | 0.13327 | 5.6782e-07 | -0.00012502 | 0.0089204 | 0.0089188 | 0.0089204 | 0.99033 | -0.14434 | 0.99033 | -0.14436 | 4.0547
6 | 1.0164 | 0.48174 | -1.0161 | -0.48575 | 0.00025085 | -0.0040116 | 0.032787 | 0.032838 | 0.032838 | 0.99033 | -0.14436 | 0.99011 | -0.14229 | 14.9263
7 | -1.2918 | -0.615 | 1.2922 | 0.61098 | 0.00041007 | -0.0040202 | 0.041705 | 0.041653 | 0.041705 | 0.99033 | -0.14436 | 0.99063 | -0.147 | 18.9569
8 | 1.0161 | 0.48575 | -1.0161 | -0.48585 | 6.245e-06 | -9.9682e-05 | 0.032838 | 0.032839 | 0.032839 | 0.99011 | -0.14229 | 0.9901 | -0.14224 | 14.9268
9 | -1.3958 | -0.66013 | 1.3961 | 0.65713 | 0.00035784 | -0.0029996 | 0.044993 | 0.044955 | 0.044993 | 0.99063 | -0.147 | 0.99086 | -0.1491 | 20.4515
10 | 0.10354 | 0.049144 | -0.10354 | -0.050148 | 6.4075e-07 | -0.0010041 | 0.0033399 | 0.0033526 | 0.0033526 | 0.99063 | -0.147 | 0.99062 | -0.14695 | 1.5239
11 | 0.77827 | 0.37064 | -0.77826 | -0.37085 | 7.3829e-06 | -0.0002027 | 0.025133 | 0.025136 | 0.025136 | 0.9901 | -0.14224 | 0.99009 | -0.14216 | 11.4254
12 | 0.10184 | 0.049252 | -0.10184 | -0.049323 | 4.3691e-08 | -7.057e-05 | 0.0032957 | 0.0032966 | 0.0032966 | 0.99086 | -0.1491 | 0.99086 | -0.1491 | 1.4985
13 | -1.498 | -0.70638 | 1.4988 | 0.70017 | 0.00085484 | -0.0062082 | 0.04825 | 0.04817 | 0.04825 | 0.99086 | -0.1491 | 0.99139 | -0.15373 | 21.9319
14 | -1.5865 | -0.74178 | 1.5874 | 0.73575 | 0.00093183 | -0.0060351 | 0.050996 | 0.050919 | 0.050996 | 0.99139 | -0.15373 | 0.99194 | -0.1584 | 23.18
15 | 0.087675 | 0.041612 | -0.087674 | -0.042463 | 3.8778e-07 | -0.00085026 | 0.0028259 | 0.0028366 | 0.0028366 | 0.99139 | -0.15373 | 0.99139 | -0.15369 | 1.2894
16 | 0.33229 | 0.15584 | -0.33226 | -0.1607 | 3.1761e-05 | -0.0048614 | 0.010681 | 0.010742 | 0.010742 | 0.99194 | -0.1584 | 0.99185 | -0.1576 | 4.8828
17 | -9.8494 | -4.6183 | 9.8504 | 4.6151 | 0.0010248 | -0.0032607 | 0.31659 | 0.31653 | 0.31659 | 0.99194 | -0.1584 | 0.99206 | -0.1562 | 37.5992
18 | 7.9297 | 3.7267 | -7.9237 | -3.7187 | 0.0059792 | 0.0080003 | 0.25499 | 0.25499 | 0.25499 | 0.99194 | -0.1584 | 0.99091 | -0.19304 | 31.0969
19 | 0.33226 | 0.1607 | -0.33226 | -0.16092 | 1.419e-06 | -0.00021588 | 0.010742 | 0.010745 | 0.010745 | 0.99185 | -0.1576 | 0.99184 | -0.15756 | 4.884
20 | -10.2094 | -4.789 | 10.2096 | 4.7886 | 0.00012207 | -0.00035377 | 0.32814 | 0.32814 | 0.32814 | 0.99206 | -0.1562 | 0.99207 | -0.15595 | 38.9716
21 | 7.6149 | 3.5692 | -7.6146 | -3.5709 | 0.00028612 | -0.0016911 | 0.245 | 0.24502 | 0.24502 | 0.99091 | -0.19304 | 0.99086 | -0.19383 | 29.1002
22 | -10.4995 | -4.9241 | 10.5015 | 4.9187 | 0.0020005 | -0.005386 | 0.33745 | 0.33736 | 0.33745 | 0.99207 | -0.15595 | 0.99229 | -0.15193 | 40.0769
23 | 0.28997 | 0.13545 | -0.28995 | -0.13998 | 2.2488e-05 | -0.0045296 | 0.0093128 | 0.0093694 | 0.0093694 | 0.99207 | -0.15595 | 0.992 | -0.1553 | 4.2588
24 | -0.33624 | -0.16285 | 0.33625 | 0.16197 | 5.9368e-06 | -0.00087902 | 0.010885 | 0.010874 | 0.010885 | 0.99085 | -0.19368 | 0.99086 | -0.19383 | 4.9476
25 | 6.1311 | 2.859 | -6.1303 | -2.8674 | 0.00087175 | -0.0083922 | 0.19709 | 0.1972 | 0.1972 | 0.99086 | -0.19383 | 0.9907 | -0.19684 | 23.4207
26 | 1.1472 | 0.54986 | -1.1468 | -0.5498 | 0.00040796 | 6.025e-05 | 0.037063 | 0.037066 | 0.037066 | 0.99086 | -0.19383 | 0.99049 | -0.19626 | 17.6503
27 | 6.1303 | 2.8674 | -6.1284 | -2.8651 | 0.0018519 | 0.0023419 | 0.1972 | 0.19721 | 0.19721 | 0.9907 | -0.19684 | 0.99029 | -0.21077 | 24.0496
28 | 0.8559 | 0.40891 | -0.85586 | -0.40987 | 4.2237e-05 | -0.00095667 | 0.027646 | 0.027658 | 0.027658 | 0.99049 | -0.19626 | 0.99044 | -0.19585 | 12.5717
29 | 5.9289 | 2.7685 | -5.9289 | -2.7687 | 2.6993e-05 | -0.00027897 | 0.19075 | 0.19075 | 0.19075 | 0.99029 | -0.21077 | 0.99028 | -0.21086 | 22.6543
30 | -10.5015 | -4.9187 | 10.5046 | 4.923 | 0.003104 | 0.0042989 | 0.33736 | 0.33736 | 0.33736 | 0.99229 | -0.15193 | 0.9927 | -0.13833 | 41.1413
31 | 0.28995 | 0.13998 | -0.28995 | -0.14043 | 2.2439e-06 | -0.00044892 | 0.0093694 | 0.0093751 | 0.0093751 | 0.992 | -0.1553 | 0.99199 | -0.15524 | 4.2614
32 | -10.9048 | -5.1168 | 10.905 | 5.1163 | 0.00020091 | -0.00048928 | 0.35028 | 0.35028 | 0.35028 | 0.9927 | -0.13833 | 0.99272 | -0.13794 | 41.6014
33 | -10.905 | -5.1163 | 10.9074 | 5.1104 | 0.002429 | -0.00592 | 0.35028 | 0.35017 | 0.35028 | 0.99272 | -0.13794 | 0.99298 | -0.13324 | 41.6004
34 | -11.1632 | -5.2341 | 11.1641 | 5.2321 | 0.00085068 | -0.0019453 | 0.35844 | 0.3584 | 0.35844 | 0.99298 | -0.13324 | 0.99306 | -0.13164 | 42.5695
35 | 0.25582 | 0.12372 | -0.25582 | -0.1239 | 6.8652e-07 | -0.00017714 | 0.0082612 | 0.0082635 | 0.0082635 | 0.99298 | -0.13324 | 0.99297 | -0.13322 | 3.7561
36 | -0.35495 | -0.17191 | 0.35497 | 0.17182 | 2.0822e-05 | -9.175e-05 | 0.011462 | 0.011461 | 0.011462 | 0.99328 | -0.12069 | 0.99334 | -0.1203 | 5.4581
37 | -0.35497 | -0.17182 | 0.355 | 0.17167 | 3.3532e-05 | -0.00014783 | 0.011461 | 0.011459 | 0.011461 | 0.99334 | -0.1203 | 0.99344 | -0.11968 | 5.4574
38 | 0.37692 | 0.18174 | -0.37691 | -0.18246 | 6.0699e-06 | -0.00072232 | 0.012159 | 0.012168 | 0.012168 | 0.99344 | -0.11968 | 0.99343 | -0.11954 | 5.531
39 | 0.27825 | 0.12889 | -0.27822 | -0.13458 | 2.5848e-05 | -0.0056929 | 0.0089107 | 0.0089816 | 0.0089816 | 0.99344 | -0.11968 | 0.99336 | -0.11891 | 4.0826
40 | -12.4074 | -5.8286 | 12.4258 | 5.7976 | 0.018377 | -0.031005 | 0.39834 | 0.39775 | 0.39834 | 0.99344 | -0.11968 | 0.99517 | -0.088389 | 47.3084
41 | 11.3973 | 5.3463 | -11.3945 | -5.3425 | 0.0027489 | 0.0038327 | 0.36581 | 0.36581 | 0.36581 | 0.99344 | -0.11968 | 0.99311 | -0.13077 | 44.6112
42 | 0.37691 | 0.18246 | -0.37689 | -0.18254 | 1.9977e-05 | -7.669e-05 | 0.012168 | 0.012169 | 0.012169 | 0.99343 | -0.11954 | 0.99337 | -0.11989 | 5.795
43 | 0.27822 | 0.13458 | -0.27822 | -0.13475 | 7.6362e-07 | -0.00016679 | 0.0089816 | 0.0089837 | 0.0089837 | 0.99336 | -0.11891 | 0.99335 | -0.11889 | 4.0835
44 | -12.7718 | -5.9649 | 12.7838 | 5.9461 | 0.012092 | -0.018864 | 0.40889 | 0.40853 | 0.40889 | 0.99517 | -0.088389 | 0.99627 | -0.068257 | 48.5621
45 | 0.34592 | 0.16732 | -0.34592 | -0.16754 | 1.5018e-06 | -0.0002136 | 0.011147 | 0.011149 | 0.011149 | 0.99517 | -0.088389 | 0.99516 | -0.088351 | 5.0679
46 | 11.1645 | 5.2311 | -11.1641 | -5.2321 | 0.00045944 | -0.001051 | 0.35838 | 0.3584 | 0.3584 | 0.99311 | -0.13077 | 0.99306 | -0.13164 | 42.5655
47 | 0.41011 | 0.19852 | -0.41011 | -0.19863 | 1.0949e-06 | -0.00011118 | 0.013202 | 0.013204 | 0.013204 | 0.99627 | -0.068257 | 0.99627 | -0.068234 | 6.0016
48 | -13.194 | -6.1446 | 13.2087 | 6.1236 | 0.014792 | -0.020966 | 0.42173 | 0.4213 | 0.42173 | 0.99627 | -0.068257 | 0.99758 | -0.044319 | 50.0863
49 | -0.31319 | -0.14934 | 0.3132 | 0.14749 | 1.0411e-05 | -0.0018429 | 0.010035 | 0.010013 | 0.010035 | 0.99808 | -0.034316 | 0.99812 | -0.034592 | 4.5616
50 | 0.31319 | 0.14934 | -0.31318 | -0.15168 | 1.3313e-05 | -0.0023442 | 0.010035 | 0.010065 | 0.010065 | 0.99808 | -0.034316 | 0.99804 | -0.033952 | 4.5749
51 | -13.817 | -6.4025 | 13.8311 | 6.3852 | 0.014083 | -0.017329 | 0.44043 | 0.44007 | 0.44043 | 0.99812 | -0.034592 | 0.99931 | -0.012689 | 52.3082
52 | 0.28911 | 0.13993 | -0.28909 | -0.14001 | 1.1363e-05 | -8.0767e-05 | 0.0092895 | 0.0092906 | 0.0092906 | 0.99812 | -0.034592 | 0.99807 | -0.034851 | 4.4241
53 | 13.2147 | 6.1151 | -13.2087 | -6.1236 | 0.0059894 | -0.0085347 | 0.42113 | 0.4213 | 0.4213 | 0.99812 | -0.034592 | 0.99758 | -0.044319 | 50.0362
54 | -13.8311 | -6.3852 | 13.8315 | 6.3848 | 0.00033146 | -0.00040934 | 0.44007 | 0.44006 | 0.44007 | 0.99931 | -0.012689 | 0.99934 | -0.012173 | 52.2646
55 | -14.2172 | -6.5716 | 14.2184 | 6.5703 | 0.0011973 | -0.00134 | 0.45244 | 0.45241 | 0.45244 | 0.99934 | -0.012173 | 0.99944 | -0.01036 | 53.7338
56 | -14.2184 | -6.5703 | 14.225 | 6.5629 | 0.0065266 | -0.0073186 | 0.45241 | 0.45225 | 0.45241 | 0.99944 | -0.01036 | 0.99997 | -0.00047069 | 53.7303
57 | -14.225 | -6.5629 | 14.2253 | 6.5626 | 0.00031035 | -0.00034861 | 0.45225 | 0.45224 | 0.45225 | 0.99997 | -0.00047069 | 1 | 0 | 53.7112
58 | -0.36368 | -0.17614 | 0.36369 | 0.17593 | 1.7313e-06 | -0.00021282 | 0.011856 | 0.011853 | 0.011856 | 0.98395 | -0.18998 | 0.98395 | -0.19002 | 5.3889
59 | -0.36369 | -0.17593 | 0.36374 | 0.16889 | 5.677e-05 | -0.0070341 | 0.011853 | 0.011764 | 0.011853 | 0.98395 | -0.19002 | 0.98409 | -0.19131 | 5.3876
60 | 0.1131 | 0.054471 | -0.1131 | -0.054775 | 2.3885e-07 | -0.00030471 | 0.0036823 | 0.0036862 | 0.0036862 | 0.98409 | -0.19131 | 0.98409 | -0.1913 | 1.6756
61 | -1.3021 | -0.6142 | 1.3034 | 0.60151 | 0.0013416 | -0.012694 | 0.042231 | 0.042069 | 0.042231 | 0.98409 | -0.19131 | 0.98504 | -0.19955 | 19.196
62 | 0.82523 | 0.39084 | -0.82516 | -0.3925 | 6.9759e-05 | -0.001662 | 0.026785 | 0.026806 | 0.026806 | 0.98409 | -0.19131 | 0.98402 | -0.19061 | 12.1846
63 | 0.50791 | 0.2457 | -0.50791 | -0.24593 | 3.6458e-06 | -0.00023029 | 0.016535 | 0.016538 | 0.016538 | 0.98504 | -0.19955 | 0.98503 | -0.19949 | 7.5172
64 | -1.8113 | -0.84721 | 1.8171 | 0.81967 | 0.0057346 | -0.027542 | 0.058602 | 0.058245 | 0.058602 | 0.98504 | -0.19955 | 0.98797 | -0.2239 | 26.6372
65 | 0.10506 | 0.049544 | -0.10506 | -0.05083 | 8.6642e-07 | -0.0012858 | 0.0034076 | 0.0034238 | 0.0034238 | 0.98402 | -0.19061 | 0.98401 | -0.19054 | 1.5563
66 | 0.44039 | 0.2089 | -0.44036 | -0.21183 | 3.4798e-05 | -0.002929 | 0.014299 | 0.014337 | 0.014337 | 0.98402 | -0.19061 | 0.98394 | -0.18994 | 6.5166
67 | 0.2797 | 0.13406 | -0.2797 | -0.13546 | 6.7452e-06 | -0.001406 | 0.0090993 | 0.0091172 | 0.0091172 | 0.98402 | -0.19061 | 0.98399 | -0.1904 | 4.1442
68 | -1.8171 | -0.81967 | 1.8171 | 0.8194 | 5.4525e-05 | -0.00026443 | 0.058245 | 0.058241 | 0.058245 | 0.98797 | -0.2239 | 0.988 | -0.22412 | 26.4748
69 | -2.1393 | -0.97544 | 2.1399 | 0.97332 | 0.00062173 | -0.002117 | 0.068697 | 0.06867 | 0.068697 | 0.988 | -0.22412 | 0.98827 | -0.22631 | 31.2261
70 | 0.12322 | 0.059619 | -0.12322 | -0.059679 | 1.499e-06 | -5.9605e-05 | 0.0040117 | 0.0040124 | 0.0040124 | 0.98503 | -0.19949 | 0.98502 | -0.19957 | 1.9107
71 | 0.10506 | 0.05083 | -0.10506 | -0.050882 | 3.5401e-08 | -5.2237e-05 | 0.0034238 | 0.0034245 | 0.0034245 | 0.98401 | -0.19054 | 0.98401 | -0.19054 | 1.5566
72 | 0.35162 | 0.16954 | -0.35161 | -0.1702 | 4.9663e-06 | -0.00065366 | 0.011453 | 0.011461 | 0.011461 | 0.98394 | -0.18994 | 0.98393 | -0.18982 | 5.2095
73 | 0.088741 | 0.042286 | -0.088741 | -0.042979 | 3.3414e-07 | -0.00069337 | 0.002884 | 0.0028928 | 0.0028928 | 0.98394 | -0.18994 | 0.98394 | -0.18991 | 1.3149
74 | 0.35161 | 0.1702 | -0.35161 | -0.17029 | 7.4535e-07 | -9.8017e-05 | 0.011461 | 0.011462 | 0.011462 | 0.98393 | -0.18982 | 0.98393 | -0.1898 | 5.2101
75 | 0.85586 | 0.40987 | -0.8558 | -0.41121 | 5.9186e-05 | -0.001339 | 0.027658 | 0.027675 | 0.027675 | 0.99044 | -0.19585 | 0.99038 | -0.19526 | 12.5795
76 | 5.9289 | 2.7687 | -5.9276 | -2.7817 | 0.0012511 | -0.012913 | 0.19075 | 0.19092 | 0.19092 | 0.99028 | -0.21086 | 0.99003 | -0.21533 | 22.6749
77 | 0.18346 | 0.086658 | -0.18346 | -0.08842 | 3.5287e-06 | -0.0017621 | 0.0059141 | 0.0059362 | 0.0059362 | 0.99038 | -0.19526 | 0.99036 | -0.19509 | 2.6983
78 | 0.67234 | 0.32455 | -0.67233 | -0.32474 | 5.3501e-06 | -0.00019658 | 0.021761 | 0.021764 | 0.021764 | 0.99038 | -0.19526 | 0.99037 | -0.19519 | 9.8925
79 | 4.1513 | 1.9286 | -4.1512 | -1.9295 | 4.0555e-05 | -0.00089337 | 0.1335 | 0.13351 | 0.13351 | 0.98978 | -0.22309 | 0.98977 | -0.22329 | 15.8567
80 | -4.4101 | -2.054 | 4.4102 | 2.0513 | 0.00013801 | -0.002678 | 0.14189 | 0.14185 | 0.14189 | 0.98978 | -0.22309 | 0.98982 | -0.22242 | 16.8513
81 | 4.1512 | 1.9295 | -4.1511 | -1.9314 | 8.3215e-05 | -0.0018326 | 0.13351 | 0.13354 | 0.13354 | 0.98977 | -0.22329 | 0.98975 | -0.22372 | 15.8595
82 | -4.802 | -2.241 | 4.8027 | 2.2419 | 0.00070161 | 0.00080672 | 0.15455 | 0.15455 | 0.15455 | 0.98982 | -0.22242 | 0.99002 | -0.21567 | 18.8473
83 | 0.18346 | 0.08842 | -0.18346 | -0.088852 | 8.6969e-07 | -0.00043227 | 0.0059362 | 0.0059417 | 0.0059417 | 0.99036 | -0.19509 | 0.99036 | -0.19505 | 2.7008
84 | 0.26786 | 0.12885 | -0.26786 | -0.12973 | 3.7769e-06 | -0.00088037 | 0.008664 | 0.0086751 | 0.0086751 | 0.99037 | -0.19519 | 0.99036 | -0.19507 | 3.9432
85 | 4.1511 | 1.9314 | -4.1511 | -1.9328 | 6.7306e-05 | -0.0014816 | 0.13354 | 0.13356 | 0.13356 | 0.98975 | -0.22372 | 0.98973 | -0.22407 | 15.8618
86 | -0.69165 | -0.33438 | 0.69165 | 0.33429 | 2.4183e-06 | -8.3713e-05 | 0.022404 | 0.022403 | 0.022404 | 0.98986 | -0.21367 | 0.98986 | -0.2137 | 10.1838
87 | 0.39703 | 0.19169 | -0.39703 | -0.19194 | 2.416e-06 | -0.00025531 | 0.012858 | 0.012861 | 0.012861 | 0.98986 | -0.21367 | 0.98985 | -0.21361 | 5.8459
88 | -1.0496 | -0.50763 | 1.0496 | 0.50678 | 5.7485e-05 | -0.00085467 | 0.034001 | 0.03399 | 0.034001 | 0.98986 | -0.2137 | 0.98991 | -0.21417 | 15.4548
89 | 0.39703 | 0.19194 | -0.39703 | -0.19204 | 8.7606e-07 | -9.2544e-05 | 0.012861 | 0.012862 | 0.012862 | 0.98985 | -0.21361 | 0.98985 | -0.21359 | 5.8464
90 | -1.0496 | -0.50678 | 1.0498 | 0.50468 | 0.00014093 | -0.0020981 | 0.03399 | 0.033962 | 0.03399 | 0.98991 | -0.21417 | 0.99003 | -0.21533 | 15.4498
91 | 0.39703 | 0.19204 | -0.39703 | -0.19229 | 2.3958e-06 | -0.00025299 | 0.012862 | 0.012865 | 0.012865 | 0.98985 | -0.21359 | 0.98984 | -0.21354 | 5.8479
92 | 4.8779 | 2.277 | -4.8778 | -2.2782 | 7.9982e-05 | -0.0012549 | 0.15696 | 0.15698 | 0.15698 | 0.99003 | -0.21533 | 0.99002 | -0.21567 | 18.6436
93 | -2.1399 | -0.97332 | 2.1408 | 0.97025 | 0.00090205 | -0.0030771 | 0.06867 | 0.068629 | 0.06867 | 0.98827 | -0.22631 | 0.98866 | -0.22946 | 31.2134
94 | 0.67905 | 0.32322 | -0.679 | -0.32524 | 5.6238e-05 | -0.0020196 | 0.021959 | 0.021985 | 0.021985 | 0.98866 | -0.22946 | 0.98858 | -0.22876 | 9.993
95 | -2.8199 | -1.2935 | 2.8204 | 1.2938 | 0.00056769 | 0.00031026 | 0.090585 | 0.090585 | 0.090585 | 0.98866 | -0.22946 | 0.98887 | -0.22786 | 43.1358
96 | 4.08 | 1.8984 | -4.0799 | -1.8997 | 5.6462e-05 | -0.0012884 | 0.13125 | 0.13127 | 0.13127 | 0.98973 | -0.22407 | 0.98971 | -0.22436 | 15.5901
97 | 4.0799 | 1.8997 | -4.0799 | -1.9005 | 3.4421e-05 | -0.00078524 | 0.13127 | 0.13128 | 0.13128 | 0.98971 | -0.22436 | 0.9897 | -0.22454 | 15.5913
98 | 0.58622 | 0.28083 | -0.5862 | -0.28167 | 1.7305e-05 | -0.00083388 | 0.018981 | 0.018992 | 0.018992 | 0.98858 | -0.22876 | 0.98855 | -0.22851 | 8.6326
99 | 0.092774 | 0.044402 | -0.092774 | -0.044933 | 2.7434e-07 | -0.00053031 | 0.0030034 | 0.0030101 | 0.0030101 | 0.98858 | -0.22876 | 0.98858 | -0.22873 | 1.3682
100 | -3.2173 | -1.486 | 3.2174 | 1.4858 | 0.00014304 | -0.00019131 | 0.10345 | 0.10345 | 0.10345 | 0.98887 | -0.22786 | 0.98891 | -0.22821 | 47.0247
101 | 0.17962 | 0.086079 | -0.17961 | -0.086991 | 1.7704e-06 | -0.00091229 | 0.0058163 | 0.0058279 | 0.0058279 | 0.98855 | -0.22851 | 0.98854 | -0.22842 | 2.649
102 | 0.40659 | 0.19559 | -0.40658 | -0.19669 | 1.0951e-05 | -0.0010982 | 0.013175 | 0.013189 | 0.013189 | 0.98855 | -0.22851 | 0.98853 | -0.22827 | 5.9952
103 | -3.2174 | -1.4858 | 3.2176 | 1.4855 | 0.00020617 | -0.00027581 | 0.10345 | 0.10345 | 0.10345 | 0.98891 | -0.22821 | 0.98897 | -0.22871 | 47.0234
104 | -3.2176 | -1.4855 | 3.2179 | 1.4851 | 0.00029844 | -0.00039937 | 0.10345 | 0.10344 | 0.10345 | 0.98897 | -0.22871 | 0.98906 | -0.22943 | 47.0215
105 | -3.4131 | -1.5796 | 3.4134 | 1.5793 | 0.00028966 | -0.00033471 | 0.10977 | 0.10976 | 0.10977 | 0.98906 | -0.22943 | 0.98913 | -0.23009 | 49.8948
106 | 0.40252 | 0.19447 | -0.40251 | -0.19494 | 4.5857e-06 | -0.00046984 | 0.013047 | 0.013052 | 0.013052 | 0.98913 | -0.23009 | 0.98912 | -0.22999 | 5.933
107 | -3.8159 | -1.7738 | 3.8169 | 1.7728 | 0.0010565 | -0.00091286 | 0.12281 | 0.12279 | 0.12281 | 0.98913 | -0.23009 | 0.98939 | -0.23229 | 55.822
108 | -3.8169 | -1.7728 | 3.8178 | 1.7738 | 0.00090098 | 0.00095044 | 0.12279 | 0.12279 | 0.12279 | 0.98939 | -0.23229 | 0.98968 | -0.22473 | 35.0838
109 | 0.40658 | 0.19669 | -0.40658 | -0.19691 | 2.2539e-06 | -0.00022572 | 0.013189 | 0.013192 | 0.013192 | 0.98853 | -0.22827 | 0.98852 | -0.22823 | 5.9965
110 | -4.0798 | -1.9007 | 4.0799 | 1.9005 | 6.2524e-05 | -0.00020695 | 0.13128 | 0.13128 | 0.13128 | 0.98968 | -0.22473 | 0.9897 | -0.22454 | 36.2657

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 14.4443 | 6.6724

## res_load
| p_mw | q_mvar
0 | 0.19943 | 0.096591
1 | 0.33727 | 0.16335
2 | 0.2413 | 0.11687
3 | 0.27542 | 0.13339
4 | 0.23787 | 0.1152
5 | 0.10354 | 0.050148
6 | 0.087674 | 0.042463
7 | 0.35903 | 0.17388
8 | 0.30882 | 0.14957
9 | 0.10184 | 0.049323
10 | 0.33226 | 0.16092
11 | 0.33624 | 0.16285
12 | 0.2909 | 0.14089
13 | 0.1995 | 0.096621
14 | 0.40013 | 0.19379
15 | 0.28995 | 0.14043
16 | 0.35495 | 0.17191
17 | 0.23 | 0.11139
18 | 0.25582 | 0.1239
19 | 0.37689 | 0.18254
20 | 0.27822 | 0.13475
21 | 0.34592 | 0.16754
22 | 0.31318 | 0.15168
23 | 0.41011 | 0.19863
24 | 0.28909 | 0.14001
25 | 0.38577 | 0.18684
26 | 0.20501 | 0.099293
27 | 0.36368 | 0.17614
28 | 0.1131 | 0.054775
29 | 0.32218 | 0.15604
30 | 0.38468 | 0.18631
31 | 0.2797 | 0.13546
32 | 0.088741 | 0.042979
33 | 0.2588 | 0.12534
34 | 0.39179 | 0.18975
35 | 0.40447 | 0.1959
36 | 0.18346 | 0.088852
37 | 0.26786 | 0.12973
38 | 0.29462 | 0.14269
39 | 0.3579 | 0.17334
40 | 0.39703 | 0.19229
41 | 0.075116 | 0.03638
42 | 0.071098 | 0.034434
43 | 0.39684 | 0.1922
44 | 0.092774 | 0.044933
45 | 0.19514 | 0.09451
46 | 0.40251 | 0.19494
47 | 0.17961 | 0.086991
48 | 0.40658 | 0.19691
49 | 0.12322 | 0.059679
50 | 0.10506 | 0.050882
51 | 0.35161 | 0.17029
52 | 0.26198 | 0.12688

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1