## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_592_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_592_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_592_0_node_5 | 20 | n |  | TRUE
3 | bus_MV_592_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_592_0_node_79 | 20 | n |  | TRUE
5 | bus_MV_592_0_node_141 | 20 | n |  | TRUE
6 | bus_MV_592_0_node_4 | 20 | n |  | TRUE
7 | bus_MV_592_0_node_166 | 20 | n |  | TRUE
8 | bus_MV_592_0_node_171 | 20 | n |  | TRUE
9 | bus_MV_592_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_592_0_node_7 | 20 | n |  | TRUE
11 | bus_MV_592_0_node_180 | 20 | n |  | TRUE
12 | bus_MV_592_0_node_8 | 20 | n |  | TRUE
13 | bus_MV_592_0_node_11 | 20 | n |  | TRUE
14 | bus_MV_592_0_node_19 | 20 | n |  | TRUE
15 | bus_MV_592_0_node_75 | 20 | n |  | TRUE
16 | bus_MV_592_0_node_170 | 20 | n |  | TRUE
17 | bus_MV_592_0_node_9 | 20 | n |  | TRUE
18 | bus_MV_592_0_node_165 | 20 | n |  | TRUE
19 | bus_MV_592_0_node_40 | 20 | n |  | TRUE
20 | bus_MV_592_0_node_12 | 20 | n |  | TRUE
21 | bus_MV_592_0_node_33 | 20 | n |  | TRUE
22 | bus_MV_592_0_node_13 | 20 | n |  | TRUE
23 | bus_MV_592_0_node_15 | 20 | n |  | TRUE
24 | bus_MV_592_0_node_25 | 20 | n |  | TRUE
25 | bus_MV_592_0_node_16 | 20 | n |  | TRUE
26 | bus_MV_592_0_node_131 | 20 | n |  | TRUE
27 | bus_MV_592_0_node_17 | 20 | n |  | TRUE
28 | bus_MV_592_0_node_133 | 20 | n |  | TRUE
29 | bus_MV_592_0_node_57 | 20 | n |  | TRUE
30 | bus_MV_592_0_node_10 | 20 | n |  | TRUE
31 | bus_MV_592_0_node_22 | 20 | n |  | TRUE
32 | bus_MV_592_0_node_132 | 20 | n |  | TRUE
33 | bus_MV_592_0_node_58 | 20 | n |  | TRUE
34 | bus_MV_592_0_node_116 | 20 | n |  | TRUE
35 | bus_MV_592_0_node_117 | 20 | n |  | TRUE
36 | bus_MV_592_0_node_20 | 20 | n |  | TRUE
37 | bus_MV_592_0_node_21 | 20 | n |  | TRUE
38 | bus_MV_592_0_node_24 | 20 | n |  | TRUE
39 | bus_MV_592_0_node_23 | 20 | n |  | TRUE
40 | bus_MV_592_0_node_142 | 20 | n |  | TRUE
41 | bus_MV_592_0_node_139 | 20 | n |  | TRUE
42 | bus_MV_592_0_node_78 | 20 | n |  | TRUE
43 | bus_MV_592_0_node_26 | 20 | n |  | TRUE
44 | bus_MV_592_0_node_27 | 20 | n |  | TRUE
45 | bus_MV_592_0_node_29 | 20 | n |  | TRUE
46 | bus_MV_592_0_node_28 | 20 | n |  | TRUE
47 | bus_MV_592_0_node_30 | 20 | n |  | TRUE
48 | bus_MV_592_0_node_44 | 20 | n |  | TRUE
49 | bus_MV_592_0_node_31 | 20 | n |  | TRUE
50 | bus_MV_592_0_node_43 | 20 | n |  | TRUE
51 | bus_MV_592_0_node_181 | 20 | n |  | TRUE
52 | bus_MV_592_0_node_34 | 20 | n |  | TRUE
53 | bus_MV_592_0_node_42 | 20 | n |  | TRUE
54 | bus_MV_592_0_node_49 | 20 | n |  | TRUE
55 | bus_MV_592_0_node_51 | 20 | n |  | TRUE
56 | bus_MV_592_0_node_47 | 20 | n |  | TRUE
57 | bus_MV_592_0_node_48 | 20 | n |  | TRUE
58 | bus_MV_592_0_node_140 | 20 | n |  | TRUE
59 | bus_MV_592_0_node_115 | 20 | n |  | TRUE
60 | bus_MV_592_0_node_114 | 20 | n |  | TRUE
61 | bus_MV_592_0_node_183 | 20 | n |  | TRUE
62 | bus_MV_592_0_node_35 | 20 | n |  | TRUE
63 | bus_MV_592_0_node_36 | 20 | n |  | TRUE
64 | bus_MV_592_0_node_37 | 20 | n |  | TRUE
65 | bus_MV_592_0_node_39 | 20 | n |  | TRUE
66 | bus_MV_592_0_node_172 | 20 | n |  | TRUE
67 | bus_MV_592_0_node_38 | 20 | n |  | TRUE
68 | bus_MV_592_0_node_41 | 20 | n |  | TRUE
69 | bus_MV_592_0_node_59 | 20 | n |  | TRUE
70 | bus_MV_592_0_node_138 | 20 | n |  | TRUE
71 | bus_MV_592_0_node_71 | 20 | n |  | TRUE
72 | bus_MV_592_0_node_74 | 20 | n |  | TRUE
73 | bus_MV_592_0_node_137 | 20 | n |  | TRUE
74 | bus_MV_592_0_node_62 | 20 | n |  | TRUE
75 | bus_MV_592_0_node_63 | 20 | n |  | TRUE
76 | bus_MV_592_0_node_65 | 20 | n |  | TRUE
77 | bus_MV_592_0_node_154 | 20 | n |  | TRUE
78 | bus_MV_592_0_node_164 | 20 | n |  | TRUE
79 | bus_MV_592_0_node_64 | 20 | n |  | TRUE
80 | bus_MV_592_0_node_113 | 20 | n |  | TRUE
81 | bus_MV_592_0_node_185 | 20 | n |  | TRUE
82 | bus_MV_592_0_node_70 | 20 | n |  | TRUE
83 | bus_MV_592_0_node_156 | 20 | n |  | TRUE
84 | bus_MV_592_0_node_153 | 20 | n |  | TRUE
85 | bus_MV_592_0_node_66 | 20 | n |  | TRUE
86 | bus_MV_592_0_node_67 | 20 | n |  | TRUE
87 | bus_MV_592_0_node_69 | 20 | n |  | TRUE
88 | bus_MV_592_0_node_68 | 20 | n |  | TRUE
89 | bus_MV_592_0_node_77 | 20 | n |  | TRUE
90 | bus_MV_592_0_node_136 | 20 | n |  | TRUE
91 | bus_MV_592_0_node_76 | 20 | n |  | TRUE
92 | bus_MV_592_0_node_135 | 20 | n |  | TRUE
93 | bus_MV_592_0_node_72 | 20 | n |  | TRUE
94 | bus_MV_592_0_node_184 | 20 | n |  | TRUE
95 | bus_MV_592_0_node_134 | 20 | n |  | TRUE
96 | bus_MV_592_0_node_162 | 20 | n |  | TRUE
97 | bus_MV_592_0_node_186 | 20 | n |  | TRUE
98 | bus_MV_592_0_node_160 | 20 | n |  | TRUE
99 | bus_MV_592_0_node_152 | 20 | n |  | TRUE
100 | bus_MV_592_0_node_155 | 20 | n |  | TRUE
101 | bus_MV_592_0_node_157 | 20 | n |  | TRUE
102 | bus_MV_592_0_node_163 | 20 | n |  | TRUE
103 | bus_MV_592_0_node_158 | 20 | n |  | TRUE
104 | bus_MV_592_0_node_159 | 20 | n |  | TRUE
105 | bus_MV_592_0_node_161 | 20 | n |  | TRUE
106 | bus_HV_592_0_node_15 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_592_0_load_0 | 0 | 0.34507 | 0.16712 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_592_0_load_79 | 4 | 0.3906 | 0.18918 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_592_0_load_141 | 5 | 0.08715 | 0.042208 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_592_0_load_166 | 7 | 0.25284 | 0.12246 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_592_0_load_171 | 8 | 0.31449 | 0.15232 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_592_0_load_180 | 11 | 0.2332 | 0.11295 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_592_0_load_19 | 14 | 0.33572 | 0.1626 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_592_0_load_75 | 15 | 0.17932 | 0.08685 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_592_0_load_170 | 16 | 0.21011 | 0.10176 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_592_0_load_40 | 19 | 0.38657 | 0.18722 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_592_0_load_33 | 21 | 0.30281 | 0.14666 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_592_0_load_25 | 24 | 0.36176 | 0.17521 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_592_0_load_131 | 26 | 0.07244 | 0.035084 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_592_0_load_133 | 28 | 0.52938 | 0.25639 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_592_0_load_57 | 29 | 0.26747 | 0.12954 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_592_0_load_10 | 30 | 0.37165 | 0.18 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_592_0_load_132 | 32 | 0.069738 | 0.033776 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_592_0_load_58 | 33 | 0.22791 | 0.11038 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_592_0_load_116 | 34 | 0.15324 | 0.074217 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_592_0_load_117 | 35 | 0.2455 | 0.1189 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_592_0_load_20 | 36 | 0.24096 | 0.1167 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_592_0_load_142 | 40 | 0.42828 | 0.20743 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_592_0_load_139 | 41 | 0.10194 | 0.049371 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_592_0_load_26 | 43 | 0.34423 | 0.16672 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_592_0_load_44 | 48 | 0.32919 | 0.15944 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_592_0_load_43 | 50 | 0.39586 | 0.19172 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_592_0_load_181 | 51 | 0.41042 | 0.19878 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_592_0_load_34 | 52 | 0.38295 | 0.18547 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_592_0_load_140 | 58 | 0.21546 | 0.10435 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_592_0_load_115 | 59 | 0.22842 | 0.11063 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_592_0_load_114 | 60 | 0.20502 | 0.099297 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_592_0_load_183 | 61 | 0.081244 | 0.039348 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_592_0_load_35 | 62 | 0.38097 | 0.18451 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_592_0_load_172 | 66 | 0.36498 | 0.17677 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_592_0_load_41 | 68 | 0.32425 | 0.15704 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_592_0_load_138 | 70 | 0.14356 | 0.069529 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_592_0_load_74 | 72 | 0.21533 | 0.10429 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_592_0_load_137 | 73 | 0.14858 | 0.071963 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_592_0_load_164 | 78 | 0.11821 | 0.057254 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_592_0_load_113 | 80 | 0.29556 | 0.14315 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_592_0_load_185 | 81 | 0.28165 | 0.13641 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_592_0_load_70 | 82 | 0.3683 | 0.17838 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_592_0_load_156 | 83 | 0.3113 | 0.15077 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_592_0_load_66 | 85 | 0.41012 | 0.19863 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_592_0_load_136 | 90 | 0.17418 | 0.08436 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_592_0_load_76 | 91 | 0.24001 | 0.11624 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_592_0_load_135 | 92 | 0.14666 | 0.071032 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_592_0_load_184 | 94 | 0.074302 | 0.035986 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_592_0_load_134 | 95 | 0.10577 | 0.051228 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_592_0_load_186 | 97 | 0.4001 | 0.19378 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_592_0_load_152 | 99 | 0.078403 | 0.037972 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_592_0_load_155 | 100 | 0.088803 | 0.043009 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_592_0_load_163 | 102 | 0.081617 | 0.039529 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_592_0_load_158 | 103 | 0.087592 | 0.042423 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_592_0_line_0 |  | 0 | 1 | 0.028238 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_592_0_line_1 |  | 1 | 2 | 0.21751 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_592_0_line_2 |  | 2 | 9 | 0.1483 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
3 | MV_592_0_line_3 |  | 2 | 10 | 0.3026 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
4 | MV_592_0_line_4 |  | 2 | 11 | 0.05978 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_592_0_line_5 |  | 3 | 4 | 0.045453 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
6 | MV_592_0_line_6 |  | 3 | 5 | 0.067479 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
7 | MV_592_0_line_7 |  | 5 | 8 | 0.17449 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
8 | MV_592_0_line_8 |  | 5 | 17 | 0.036691 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
9 | MV_592_0_line_9 |  | 6 | 7 | 0.14563 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
10 | MV_592_0_line_10 |  | 6 | 8 | 0.06742 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
11 | MV_592_0_line_11 |  | 7 | 18 | 0.038642 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
12 | MV_592_0_line_12 |  | 9 | 12 | 0.4137 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
13 | MV_592_0_line_13 |  | 9 | 13 | 0.24861 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_592_0_line_14 |  | 9 | 14 | 0.008536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_592_0_line_15 |  | 10 | 15 | 0.025886 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
16 | MV_592_0_line_16 |  | 12 | 16 | 0.014421 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_592_0_line_17 |  | 12 | 17 | 0.17575 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
18 | MV_592_0_line_18 |  | 13 | 30 | 0.040689 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_592_0_line_19 |  | 13 | 20 | 0.28077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_592_0_line_20 |  | 15 | 31 | 0.025322 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
21 | MV_592_0_line_21 |  | 18 | 19 | 0.27389 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
22 | MV_592_0_line_22 |  | 19 | 65 | 0.05777 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
23 | MV_592_0_line_23 |  | 20 | 21 | 0.059857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_592_0_line_24 |  | 22 | 23 | 0.28414 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_592_0_line_25 |  | 22 | 24 | 0.040388 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_592_0_line_26 |  | 23 | 25 | 0.28105 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
27 | MV_592_0_line_27 |  | 23 | 26 | 0.021786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_592_0_line_28 |  | 25 | 27 | 0.28394 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
29 | MV_592_0_line_29 |  | 25 | 28 | 0.0092099 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_592_0_line_30 |  | 26 | 32 | 0.062056 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_592_0_line_31 |  | 27 | 29 | 0.027963 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
32 | MV_592_0_line_32 |  | 29 | 33 | 0.2561 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
33 | MV_592_0_line_33 |  | 31 | 37 | 0.21842 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
34 | MV_592_0_line_34 |  | 33 | 69 | 0.09899 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
35 | MV_592_0_line_35 |  | 34 | 35 | 0.073996 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_592_0_line_36 |  | 35 | 95 | 0.17447 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_592_0_line_37 |  | 35 | 56 | 0.161 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
38 | MV_592_0_line_38 |  | 36 | 37 | 0.048668 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
39 | MV_592_0_line_39 |  | 37 | 38 | 0.23116 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
40 | MV_592_0_line_40 |  | 38 | 41 | 0.044272 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
41 | MV_592_0_line_41 |  | 38 | 39 | 0.084058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_592_0_line_42 |  | 39 | 40 | 0.20022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_592_0_line_43 |  | 41 | 42 | 0.011267 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
44 | MV_592_0_line_44 |  | 42 | 89 | 0.11604 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_592_0_line_45 |  | 43 | 44 | 0.044278 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_592_0_line_46 |  | 44 | 45 | 0.2616 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_592_0_line_47 |  | 45 | 47 | 0.41756 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_592_0_line_48 |  | 45 | 49 | 0.29039 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_592_0_line_49 |  | 45 | 50 | 0.045772 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_592_0_line_50 |  | 46 | 47 | 0.25848 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_592_0_line_51 |  | 46 | 48 | 0.031748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_592_0_line_52 |  | 47 | 51 | 0.017307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
53 | MV_592_0_line_53 |  | 49 | 52 | 0.003671 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
54 | MV_592_0_line_54 |  | 50 | 53 | 0.020214 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
55 | MV_592_0_line_55 |  | 51 | 54 | 0.23235 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_592_0_line_56 |  | 51 | 55 | 0.16717 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
57 | MV_592_0_line_57 |  | 53 | 67 | 0.17916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_592_0_line_58 |  | 54 | 60 | 0.048043 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_592_0_line_59 |  | 55 | 61 | 0.050255 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_592_0_line_60 |  | 55 | 57 | 0.035307 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_592_0_line_61 |  | 56 | 57 | 0.20615 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_592_0_line_62 |  | 56 | 58 | 0.026042 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_592_0_line_63 |  | 57 | 59 | 0.01981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_592_0_line_64 |  | 62 | 63 | 0.060704 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_592_0_line_65 |  | 63 | 64 | 0.29965 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
66 | MV_592_0_line_66 |  | 63 | 65 | 0.19028 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
67 | MV_592_0_line_67 |  | 64 | 66 | 0.012786 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_592_0_line_68 |  | 64 | 67 | 0.25254 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_592_0_line_69 |  | 67 | 68 | 0.020262 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
70 | MV_592_0_line_70 |  | 69 | 70 | 0.19288 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
71 | MV_592_0_line_71 |  | 70 | 71 | 0.086053 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
72 | MV_592_0_line_72 |  | 70 | 72 | 0.39138 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
73 | MV_592_0_line_73 |  | 70 | 73 | 0.044698 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
74 | MV_592_0_line_74 |  | 71 | 82 | 0.071898 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
75 | MV_592_0_line_75 |  | 72 | 74 | 0.082672 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
76 | MV_592_0_line_76 |  | 73 | 88 | 0.047626 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
77 | MV_592_0_line_77 |  | 74 | 75 | 0.33905 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_592_0_line_78 |  | 75 | 76 | 0.42111 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_592_0_line_79 |  | 75 | 77 | 0.33099 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_592_0_line_80 |  | 75 | 78 | 0.080581 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_592_0_line_81 |  | 76 | 81 | 0.016588 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
82 | MV_592_0_line_82 |  | 76 | 79 | 0.1413 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_592_0_line_83 |  | 77 | 83 | 0.028956 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_592_0_line_84 |  | 77 | 84 | 0.007093 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_592_0_line_85 |  | 79 | 80 | 0.056001 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_592_0_line_86 |  | 84 | 100 | 0.018352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_592_0_line_87 |  | 84 | 99 | 0.05161 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_592_0_line_88 |  | 85 | 86 | 0.003537 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_592_0_line_89 |  | 86 | 87 | 0.10991 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_592_0_line_90 |  | 87 | 90 | 0.0348 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_592_0_line_91 |  | 87 | 88 | 0.011374 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_592_0_line_92 |  | 88 | 89 | 0.17652 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
93 | MV_592_0_line_93 |  | 89 | 91 | 0.041415 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_592_0_line_94 |  | 90 | 92 | 0.034796 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_592_0_line_95 |  | 91 | 93 | 0.26677 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_592_0_line_96 |  | 93 | 94 | 0.024028 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_592_0_line_97 |  | 96 | 97 | 0.063862 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
98 | MV_592_0_line_98 |  | 96 | 98 | 0.3063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_592_0_line_99 |  | 98 | 103 | 0.080919 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_592_0_line_100 |  | 100 | 101 | 0.018136 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_592_0_line_101 |  | 101 | 102 | 0.018708 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_592_0_line_102 |  | 102 | 105 | 0.074479 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_592_0_line_103 |  | 103 | 104 | 0.010521 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_592_0_line_104 |  | 104 | 105 | 0.008788 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_592_0_trafo_15 | 25 MVA 110/20 kV | 106 | 23 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2602157.5675 | 1199154.6816
1 | 2602177.493 | 1199174.7437
2 | 2602310.1288 | 1199219.8494
3 | 2601974.3389 | 1198932.9795
4 | 2601983.0451 | 1198972.3234
5 | 2602041.0576 | 1198922.8767
6 | 2601900.4516 | 1198763.7104
7 | 2601794.9785 | 1198663.292
8 | 2601967.8672 | 1198764.4763
9 | 2602404.988 | 1199157.7302
10 | 2602341.5598 | 1199394.5882
11 | 2602268.2307 | 1199262.49
12 | 2602141.0869 | 1198948.3654
13 | 2602389.0426 | 1199046.1643
14 | 2602409.348 | 1199164.291
15 | 2602360.9272 | 1199377.353
16 | 2602151.7346 | 1198938.6083
17 | 2602076.7548 | 1198931.3566
18 | 2601823.6997 | 1198637.3532
19 | 2601973.5314 | 1198408.0765
20 | 2602479.7386 | 1198894.5302
21 | 2602434.5778 | 1198855.3348
22 | 2602627.8258 | 1198942.3729
23 | 2602704.6556 | 1198982.6722
24 | 2602592.4357 | 1198922.9128
25 | 2602710.9878 | 1199091.7111
26 | 2602725.4552 | 1198989.1517
27 | 2602773.288 | 1199082.0672
28 | 2602719.6116 | 1199089.7854
29 | 2602800.5122 | 1199087.7715
30 | 2602349.4316 | 1199036.5106
31 | 2602379.7541 | 1199360.3623
32 | 2602784.7033 | 1199007.6086
33 | 2603023.0455 | 1199214.5229
34 | 2602991.7821 | 1198823.1238
35 | 2603014.1292 | 1198752.5825
36 | 2602463.6134 | 1199480.4262
37 | 2602505.8464 | 1199456.2414
38 | 2602539.8411 | 1199379.4031
39 | 2602585.6451 | 1199338.7338
40 | 2602619.1764 | 1199180.1705
41 | 2602583.8628 | 1199377.0982
42 | 2602595.0385 | 1199378.5257
43 | 2602267.1131 | 1198802.5213
44 | 2602237.1634 | 1198769.8373
45 | 2602271.9834 | 1198603.3055
46 | 2602587.0294 | 1198384.135
47 | 2602609.0816 | 1198562.8509
48 | 2602561.4063 | 1198365.2919
49 | 2602467.8282 | 1198785.8784
50 | 2602240.5024 | 1198569.9984
51 | 2602619.0734 | 1198576.7848
52 | 2602469.9004 | 1198782.8443
53 | 2602226.4743 | 1198555.4078
54 | 2602825.7319 | 1198470.5864
55 | 2602784.1954 | 1198602.8492
56 | 2602929.6012 | 1198615.5571
57 | 2602797.9882 | 1198579.1872
58 | 2602949.7187 | 1198599.0246
59 | 2602814.0882 | 1198567.9379
60 | 2602851.0514 | 1198511.414
61 | 2602810.5748 | 1198645.6619
62 | 2602075.5062 | 1198204.7457
63 | 2602120.7247 | 1198245.3828
64 | 2602329.9606 | 1198257.5424
65 | 2602012.9737 | 1198365.7777
66 | 2602338.1655 | 1198247.7181
67 | 2602164.2254 | 1198427.5951
68 | 2602149.2065 | 1198413.9937
69 | 2603003.233 | 1199311.5095
70 | 2602871.3407 | 1199452.2493
71 | 2602850.9275 | 1199535.8458
72 | 2603192.7172 | 1199675.6228
73 | 2602826.6567 | 1199452.9887
74 | 2603271.8798 | 1199699.4553
75 | 2603468.3383 | 1199729.9245
76 | 2603353.9186 | 1199406.3649
77 | 2603593.7785 | 1199843.2135
78 | 2603449.4797 | 1199789.2666
79 | 2603426.597 | 1199471.6736
80 | 2603481.7308 | 1199460.9991
81 | 2603345.2014 | 1199392.2526
82 | 2602922.6797 | 1199540.4154
83 | 2603581.4497 | 1199817.0128
84 | 2603598.7619 | 1199848.2747
85 | 2602764.0223 | 1199351.5739
86 | 2602763.6172 | 1199355.0867
87 | 2602778.1258 | 1199444.7969
88 | 2602779.1408 | 1199456.1257
89 | 2602626.0822 | 1199476.3135
90 | 2602812.8165 | 1199442.0988
91 | 2602637.6753 | 1199516.0731
92 | 2602847.578 | 1199440.5583
93 | 2602669.5508 | 1199780.9289
94 | 2602692.2579 | 1199785.7636
95 | 2603171.7498 | 1198827.3911
96 | 2603883.9472 | 1199713.3887
97 | 2603938.724 | 1199746.2193
98 | 2603749.7287 | 1199840.0614
99 | 2603644.3872 | 1199824.1526
100 | 2603607.4515 | 1199864.4389
101 | 2603616.0391 | 1199880.4133
102 | 2603624.5822 | 1199897.0565
103 | 2603687.0304 | 1199889.0494
104 | 2603689.156 | 1199898.8559
105 | 2603680.7197 | 1199901.1965
106 | 2602704.6556 | 1198982.6722

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99275 | -0.18276 | 0.34507 | 0.16712
1 | 0.99276 | -0.18288 | 0 | 0
2 | 0.99286 | -0.18375 | 0 | 0
3 | 0.99179 | -0.20261 | 0 | 0
4 | 0.99177 | -0.2024 | 0.3906 | 0.18918
5 | 0.99184 | -0.20228 | 0.08715 | 0.042208
6 | 0.99123 | -0.223 | 0 | 0
7 | 0.99087 | -0.23493 | 0.25284 | 0.12246
8 | 0.99139 | -0.21748 | 0.31449 | 0.15232
9 | 0.99263 | -0.18784 | 0 | 0
10 | 0.99335 | -0.17467 | 0 | 0
11 | 0.99283 | -0.18392 | 0.2332 | 0.11295
12 | 0.9921 | -0.19752 | 0 | 0
13 | 0.99242 | -0.18599 | 0 | 0
14 | 0.99263 | -0.1878 | 0.33572 | 0.1626
15 | 0.99339 | -0.17389 | 0.17932 | 0.08685
16 | 0.9921 | -0.19748 | 0.21011 | 0.10176
17 | 0.99189 | -0.20146 | 0 | 0
18 | 0.99083 | -0.23564 | 0 | 0
19 | 0.9902 | -0.25693 | 0.38657 | 0.18722
20 | 0.99231 | -0.18505 | 0 | 0
21 | 0.99229 | -0.18483 | 0.30281 | 0.14666
22 | 0.99987 | 0.001151 | 0 | 0
23 | 1 | 0 | -13.6532 | -6.2945
24 | 0.99985 | 0.0013246 | 0.36176 | 0.17521
25 | 0.9992 | -0.014742 | 0 | 0
26 | 1 | 3.4639e-05 | 0.07244 | 0.035084
27 | 0.99842 | -0.029033 | 0 | 0
28 | 0.99919 | -0.014683 | 0.52938 | 0.25639
29 | 0.99834 | -0.030439 | 0.26747 | 0.12954
30 | 0.9924 | -0.18581 | 0.37165 | 0.18
31 | 0.99343 | -0.17311 | 0 | 0
32 | 0.99999 | 8.3485e-05 | 0.069738 | 0.033776
33 | 0.99678 | -0.083624 | 0.22791 | 0.11038
34 | 0.98435 | -0.22303 | 0.15324 | 0.074217
35 | 0.98436 | -0.22317 | 0.2455 | 0.1189
36 | 0.99377 | -0.16651 | 0.24096 | 0.1167
37 | 0.99379 | -0.16637 | 0 | 0
38 | 0.99419 | -0.15899 | 0 | 0
39 | 0.99414 | -0.15859 | 0 | 0
40 | 0.99403 | -0.15758 | 0.42828 | 0.20743
41 | 0.99427 | -0.1575 | 0.10194 | 0.049371
42 | 0.99429 | -0.15712 | 0 | 0
43 | 0.98606 | -0.23062 | 0.34423 | 0.16672
44 | 0.98608 | -0.23081 | 0 | 0
45 | 0.98619 | -0.23184 | 0 | 0
46 | 0.98502 | -0.22135 | 0 | 0
47 | 0.98513 | -0.22233 | 0 | 0
48 | 0.98501 | -0.22122 | 0.32919 | 0.15944
49 | 0.98605 | -0.23054 | 0 | 0
50 | 0.98635 | -0.23324 | 0.39586 | 0.19172
51 | 0.98509 | -0.22199 | 0.41042 | 0.19878
52 | 0.98605 | -0.23052 | 0.38295 | 0.18547
53 | 0.98643 | -0.23395 | 0 | 0
54 | 0.985 | -0.22261 | 0 | 0
55 | 0.98476 | -0.22429 | 0 | 0
56 | 0.98452 | -0.22213 | 0 | 0
57 | 0.98471 | -0.22389 | 0 | 0
58 | 0.98451 | -0.22206 | 0.21546 | 0.10435
59 | 0.98471 | -0.22384 | 0.22842 | 0.11063
60 | 0.98499 | -0.22249 | 0.20502 | 0.099297
61 | 0.98475 | -0.22424 | 0.081244 | 0.039348
62 | 0.98969 | -0.26247 | 0.38097 | 0.18451
63 | 0.98972 | -0.26275 | 0 | 0
64 | 0.98826 | -0.24999 | 0 | 0
65 | 0.99015 | -0.2579 | 0 | 0
66 | 0.98825 | -0.24993 | 0.36498 | 0.17677
67 | 0.98715 | -0.24023 | 0 | 0
68 | 0.98713 | -0.24031 | 0.32425 | 0.15704
69 | 0.99618 | -0.10385 | 0 | 0
70 | 0.99503 | -0.14334 | 0.14356 | 0.069529
71 | 0.99497 | -0.14372 | 0 | 0
72 | 0.99355 | -0.15432 | 0.21533 | 0.10429
73 | 0.99493 | -0.14508 | 0.14858 | 0.071963
74 | 0.99327 | -0.15643 | 0 | 0
75 | 0.99252 | -0.1502 | 0 | 0
76 | 0.99221 | -0.14751 | 0 | 0
77 | 0.99208 | -0.14638 | 0 | 0
78 | 0.99251 | -0.15009 | 0.11821 | 0.057254
79 | 0.99216 | -0.14703 | 0 | 0
80 | 0.99213 | -0.14683 | 0.29556 | 0.14315
81 | 0.9922 | -0.14756 | 0.28165 | 0.13641
82 | 0.99492 | -0.14405 | 0.3683 | 0.17838
83 | 0.99207 | -0.14627 | 0.3113 | 0.15077
84 | 0.99207 | -0.14633 | 0 | 0
85 | 0.99477 | -0.14625 | 0.41012 | 0.19863
86 | 0.99477 | -0.14627 | 0 | 0
87 | 0.99483 | -0.1468 | 0 | 0
88 | 0.99484 | -0.1469 | 0 | 0
89 | 0.9945 | -0.15316 | 0 | 0
90 | 0.99481 | -0.14667 | 0.17418 | 0.08436
91 | 0.99449 | -0.153 | 0.24001 | 0.11624
92 | 0.99481 | -0.14661 | 0.14666 | 0.071032
93 | 0.99445 | -0.15326 | 0 | 0
94 | 0.99445 | -0.15324 | 0.074302 | 0.035986
95 | 0.98433 | -0.2234 | 0.10577 | 0.051228
96 | 0.99177 | -0.1437 | 0 | 0
97 | 0.99172 | -0.14402 | 0.4001 | 0.19378
98 | 0.99193 | -0.14512 | 0 | 0
99 | 0.99207 | -0.14628 | 0.078403 | 0.037972
100 | 0.99205 | -0.14619 | 0.088803 | 0.043009
101 | 0.99204 | -0.14608 | 0 | 0
102 | 0.99203 | -0.14597 | 0.081617 | 0.039529
103 | 0.99197 | -0.14547 | 0.087592 | 0.042423
104 | 0.99198 | -0.14553 | 0 | 0
105 | 0.99198 | -0.14558 | 0 | 0
106 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.34507 | -0.16712 | 0.34507 | 0.16646 | 4.6823e-06 | -0.00066309 | 0.011149 | 0.011141 | 0.011149 | 0.99275 | -0.18276 | 0.99276 | -0.18288 | 5.0677
1 | -0.34507 | -0.16646 | 0.34511 | 0.16135 | 3.5831e-05 | -0.0051082 | 0.011141 | 0.011077 | 0.011141 | 0.99276 | -0.18288 | 0.99286 | -0.18375 | 5.0639
2 | 6.849 | 3.1698 | -6.8477 | -3.1798 | 0.0013075 | -0.0099661 | 0.21943 | 0.21957 | 0.21957 | 0.99286 | -0.18375 | 0.99263 | -0.18784 | 26.0768
3 | -7.4274 | -3.444 | 7.4305 | 3.4241 | 0.003134 | -0.019924 | 0.23804 | 0.23776 | 0.23804 | 0.99286 | -0.18375 | 0.99335 | -0.17467 | 28.2707
4 | 0.23321 | 0.11288 | -0.2332 | -0.11295 | 6.045e-06 | -6.6562e-05 | 0.0075331 | 0.007534 | 0.007534 | 0.99286 | -0.18375 | 0.99283 | -0.18392 | 3.5876
5 | 0.39061 | 0.18811 | -0.3906 | -0.18918 | 9.673e-06 | -0.0010646 | 0.012619 | 0.012633 | 0.012633 | 0.99179 | -0.20261 | 0.99177 | -0.2024 | 5.7421
6 | -0.39061 | -0.18811 | 0.39063 | 0.18805 | 1.9144e-05 | -6.7253e-05 | 0.012619 | 0.012618 | 0.012619 | 0.99179 | -0.20261 | 0.99184 | -0.20228 | 6.0091
7 | 5.1455 | 2.4173 | -5.1438 | -2.4153 | 0.0017027 | 0.002021 | 0.16546 | 0.16547 | 0.16547 | 0.99184 | -0.20228 | 0.99139 | -0.21748 | 20.1791
8 | -5.6233 | -2.6475 | 5.6235 | 2.645 | 0.00021968 | -0.0025562 | 0.1809 | 0.18086 | 0.1809 | 0.99184 | -0.20228 | 0.99189 | -0.20146 | 21.4844
9 | 4.8287 | 2.2623 | -4.8275 | -2.2608 | 0.0012518 | 0.0014421 | 0.1553 | 0.1553 | 0.1553 | 0.99123 | -0.223 | 0.99087 | -0.23493 | 18.9391
10 | -4.8287 | -2.2623 | 4.8293 | 2.263 | 0.00057949 | 0.00066748 | 0.1553 | 0.15529 | 0.1553 | 0.99123 | -0.223 | 0.99139 | -0.21748 | 18.9386
11 | 4.5746 | 2.1384 | -4.5745 | -2.1411 | 0.00015309 | -0.0027581 | 0.14712 | 0.14715 | 0.14715 | 0.99087 | -0.23493 | 0.99083 | -0.23564 | 17.4766
12 | 5.8373 | 2.7055 | -5.8347 | -2.7342 | 0.0026558 | -0.028689 | 0.18711 | 0.18749 | 0.18749 | 0.99263 | -0.18784 | 0.9921 | -0.19752 | 22.2671
13 | 0.67467 | 0.31191 | -0.67451 | -0.31771 | 0.00015559 | -0.0058012 | 0.021616 | 0.021688 | 0.021688 | 0.99263 | -0.18784 | 0.99242 | -0.18599 | 9.8581
14 | 0.33572 | 0.1624 | -0.33572 | -0.1626 | 1.3408e-06 | -0.00020042 | 0.010846 | 0.010848 | 0.010848 | 0.99263 | -0.18784 | 0.99263 | -0.1878 | 4.931
15 | -7.4305 | -3.4241 | 7.4308 | 3.4224 | 0.00026777 | -0.0017058 | 0.23776 | 0.23774 | 0.23776 | 0.99335 | -0.17467 | 0.99339 | -0.17389 | 28.2376
16 | 0.21011 | 0.10142 | -0.21011 | -0.10176 | 8.8781e-07 | -0.00033864 | 0.0067887 | 0.006793 | 0.006793 | 0.9921 | -0.19752 | 0.9921 | -0.19748 | 3.0877
17 | 5.6246 | 2.6327 | -5.6235 | -2.645 | 0.0010511 | -0.012249 | 0.1807 | 0.18086 | 0.18086 | 0.9921 | -0.19752 | 0.99189 | -0.20146 | 21.4803
18 | 0.37166 | 0.17905 | -0.37165 | -0.18 | 7.8299e-06 | -0.00095448 | 0.012 | 0.012012 | 0.012012 | 0.99242 | -0.18599 | 0.9924 | -0.18581 | 5.46
19 | 0.30285 | 0.13866 | -0.30282 | -0.14525 | 3.548e-05 | -0.0065912 | 0.0096888 | 0.0097703 | 0.0097703 | 0.99242 | -0.18599 | 0.99231 | -0.18505 | 4.4411
20 | -7.6101 | -3.5093 | 7.6104 | 3.5076 | 0.00027479 | -0.001657 | 0.24353 | 0.2435 | 0.24353 | 0.99339 | -0.17389 | 0.99343 | -0.17311 | 28.9224
21 | 4.5745 | 2.1411 | -4.5724 | -2.1388 | 0.0021139 | 0.0023649 | 0.14715 | 0.14716 | 0.14716 | 0.99083 | -0.23564 | 0.9902 | -0.25693 | 17.9465
22 | 4.1858 | 1.9516 | -4.1856 | -1.9557 | 0.00019173 | -0.0041515 | 0.13464 | 0.13469 | 0.13469 | 0.9902 | -0.25693 | 0.99015 | -0.2579 | 15.9969
23 | 0.30282 | 0.14525 | -0.30281 | -0.14666 | 7.642e-06 | -0.001405 | 0.0097703 | 0.0097881 | 0.0097881 | 0.99231 | -0.18505 | 0.99229 | -0.18483 | 4.4491
24 | -0.36177 | -0.17425 | 0.36182 | 0.16748 | 5.0611e-05 | -0.0067682 | 0.011593 | 0.011509 | 0.011593 | 0.99987 | 0.001151 | 1 | 0 | 5.2696
25 | 0.36177 | 0.17425 | -0.36176 | -0.17521 | 7.2542e-06 | -0.0009619 | 0.011593 | 0.011605 | 0.011605 | 0.99987 | 0.001151 | 0.99985 | 0.0013246 | 5.2751
26 | 13.1352 | 6.0496 | -13.1263 | -6.0629 | 0.008969 | -0.013222 | 0.41746 | 0.41772 | 0.41772 | 1 | 0 | 0.9992 | -0.014742 | 49.611
27 | 0.14218 | 0.066859 | -0.14218 | -0.067379 | 5.9912e-07 | -0.00051997 | 0.0045355 | 0.0045419 | 0.0045419 | 1 | 0 | 1 | 3.4639e-05 | 2.0645
28 | 12.5969 | 5.8067 | -12.5885 | -5.8207 | 0.0083498 | -0.013977 | 0.40074 | 0.401 | 0.401 | 0.9992 | -0.014742 | 0.99842 | -0.029033 | 47.6246
29 | 0.52938 | 0.25617 | -0.52938 | -0.25639 | 3.55e-06 | -0.00021849 | 0.016991 | 0.016993 | 0.016993 | 0.9992 | -0.014742 | 0.99919 | -0.014683 | 7.7243
30 | 0.069739 | 0.032294 | -0.069738 | -0.033776 | 4.1111e-07 | -0.0014815 | 0.0022186 | 0.0022369 | 0.0022369 | 1 | 3.4639e-05 | 0.99999 | 8.3485e-05 | 1.0168
31 | 12.5885 | 5.8207 | -12.5877 | -5.822 | 0.0008229 | -0.0013741 | 0.401 | 0.40102 | 0.40102 | 0.99842 | -0.029033 | 0.99834 | -0.030439 | 47.6276
32 | 12.3202 | 5.6925 | -12.3062 | -5.6728 | 0.014057 | 0.019692 | 0.39243 | 0.39244 | 0.39244 | 0.99834 | -0.030439 | 0.99678 | -0.083624 | 47.8586
33 | -7.6104 | -3.5076 | 7.6127 | 3.4933 | 0.0023681 | -0.014302 | 0.2435 | 0.2433 | 0.2435 | 0.99343 | -0.17311 | 0.99379 | -0.16637 | 28.9196
34 | 12.0783 | 5.5624 | -12.073 | -5.5551 | 0.0052323 | 0.007321 | 0.38511 | 0.38511 | 0.38511 | 0.99678 | -0.083624 | 0.99618 | -0.10385 | 46.9648
35 | -0.15324 | -0.074217 | 0.15324 | 0.072506 | 2.4523e-06 | -0.0017112 | 0.0049933 | 0.0049716 | 0.0049933 | 0.98435 | -0.22303 | 0.98436 | -0.22317 | 2.2697
36 | 0.10578 | 0.051029 | -0.10577 | -0.051228 | 3.6901e-06 | -0.0001995 | 0.0034441 | 0.0034467 | 0.0034467 | 0.98436 | -0.22317 | 0.98433 | -0.2234 | 1.6413
37 | -0.50452 | -0.24244 | 0.5046 | 0.2423 | 7.7284e-05 | -0.00013786 | 0.016415 | 0.016413 | 0.016415 | 0.98436 | -0.22317 | 0.98452 | -0.22213 | 7.8168
38 | -0.24096 | -0.1167 | 0.24097 | 0.11665 | 5.2443e-06 | -5.4095e-05 | 0.0077773 | 0.0077766 | 0.0077773 | 0.99377 | -0.16651 | 0.99379 | -0.16637 | 3.7035
39 | -7.8537 | -3.6099 | 7.8564 | 3.5949 | 0.0026645 | -0.015004 | 0.25108 | 0.25087 | 0.25108 | 0.99379 | -0.16637 | 0.99419 | -0.15899 | 29.8192
40 | -8.2847 | -3.7957 | 8.2853 | 3.7929 | 0.00056715 | -0.0028229 | 0.2646 | 0.26456 | 0.2646 | 0.99419 | -0.15899 | 0.99427 | -0.1575 | 31.4254
41 | 0.42835 | 0.20074 | -0.42833 | -0.20272 | 2.121e-05 | -0.0019773 | 0.013736 | 0.01376 | 0.01376 | 0.99419 | -0.15899 | 0.99414 | -0.15859 | 6.2547
42 | 0.42833 | 0.20272 | -0.42828 | -0.20743 | 5.0829e-05 | -0.0047091 | 0.01376 | 0.01382 | 0.01382 | 0.99414 | -0.15859 | 0.99403 | -0.15758 | 6.2816
43 | -8.3872 | -3.8422 | 8.3874 | 3.8415 | 0.00014791 | -0.00071519 | 0.26785 | 0.26784 | 0.26785 | 0.99427 | -0.1575 | 0.99429 | -0.15712 | 31.8111
44 | -8.3874 | -3.8415 | 8.3889 | 3.8342 | 0.0015228 | -0.0073688 | 0.26784 | 0.26773 | 0.26784 | 0.99429 | -0.15712 | 0.9945 | -0.15316 | 31.8099
45 | -0.34423 | -0.16672 | 0.34424 | 0.16569 | 7.4029e-06 | -0.0010257 | 0.011197 | 0.011184 | 0.011197 | 0.98606 | -0.23062 | 0.98608 | -0.23081 | 5.0898
46 | -0.34424 | -0.16569 | 0.34429 | 0.15963 | 4.3387e-05 | -0.006061 | 0.011184 | 0.011108 | 0.011184 | 0.98608 | -0.23081 | 0.98619 | -0.23184 | 5.0838
47 | 1.9773 | 0.92892 | -1.975 | -0.93793 | 0.0022839 | -0.0090083 | 0.063948 | 0.064069 | 0.064069 | 0.98619 | -0.23184 | 0.98513 | -0.22233 | 29.1223
48 | 0.38301 | 0.17866 | -0.38295 | -0.18539 | 5.9734e-05 | -0.0067245 | 0.012371 | 0.012456 | 0.012456 | 0.98619 | -0.23184 | 0.98605 | -0.23054 | 5.6618
49 | -2.7046 | -1.2672 | 2.7051 | 1.2663 | 0.00046699 | -0.00092453 | 0.087427 | 0.087414 | 0.087427 | 0.98619 | -0.23184 | 0.98635 | -0.23324 | 39.7397
50 | -0.3292 | -0.1587 | 0.32924 | 0.15273 | 3.9305e-05 | -0.0059771 | 0.01071 | 0.010635 | 0.01071 | 0.98502 | -0.22135 | 0.98513 | -0.22233 | 4.8683
51 | 0.3292 | 0.1587 | -0.32919 | -0.15944 | 4.8661e-06 | -0.00073403 | 0.01071 | 0.01072 | 0.01072 | 0.98502 | -0.22135 | 0.98501 | -0.22122 | 4.8726
52 | 1.6458 | 0.78521 | -1.6457 | -0.78559 | 6.5976e-05 | -0.00038144 | 0.053434 | 0.053439 | 0.053439 | 0.98513 | -0.22233 | 0.98509 | -0.22199 | 24.2906
53 | 0.38295 | 0.18539 | -0.38295 | -0.18547 | 7.6044e-07 | -8.4995e-05 | 0.012456 | 0.012457 | 0.012457 | 0.98605 | -0.23054 | 0.98605 | -0.23052 | 5.6623
54 | -3.1009 | -1.458 | 3.1012 | 1.4576 | 0.00027139 | -0.00038908 | 0.10029 | 0.10028 | 0.10029 | 0.98635 | -0.23324 | 0.98643 | -0.23395 | 45.5845
55 | 0.20504 | 0.097927 | -0.20502 | -0.098185 | 1.8365e-05 | -0.00025764 | 0.0066588 | 0.0066622 | 0.0066622 | 0.98509 | -0.22199 | 0.985 | -0.22261 | 3.1725
56 | 1.0302 | 0.48888 | -1.0299 | -0.48887 | 0.00033263 | 1.4757e-05 | 0.033417 | 0.03342 | 0.03342 | 0.98509 | -0.22199 | 0.98476 | -0.22429 | 15.9142
57 | -3.1012 | -1.4576 | 3.1036 | 1.4542 | 0.0024039 | -0.0034522 | 0.10028 | 0.10023 | 0.10028 | 0.98643 | -0.23395 | 0.98715 | -0.24023 | 45.5819
58 | 0.20502 | 0.098185 | -0.20502 | -0.099297 | 2.8528e-06 | -0.0011121 | 0.0066622 | 0.0066763 | 0.0066763 | 0.985 | -0.22261 | 0.98499 | -0.22249 | 3.0347
59 | 0.081245 | 0.038185 | -0.081244 | -0.039348 | 4.6719e-07 | -0.0011634 | 0.0026316 | 0.0026463 | 0.0026463 | 0.98476 | -0.22429 | 0.98475 | -0.22424 | 1.2028
60 | 0.94867 | 0.45069 | -0.94863 | -0.45149 | 4.4695e-05 | -0.0008042 | 0.030788 | 0.030799 | 0.030799 | 0.98476 | -0.22429 | 0.98471 | -0.22389 | 13.9994
61 | -0.72006 | -0.34605 | 0.72021 | 0.34132 | 0.00015062 | -0.0047272 | 0.023425 | 0.023364 | 0.023425 | 0.98452 | -0.22213 | 0.98471 | -0.22389 | 10.6476
62 | 0.21546 | 0.10375 | -0.21546 | -0.10435 | 1.7112e-06 | -0.00060218 | 0.0070118 | 0.0070195 | 0.0070195 | 0.98452 | -0.22213 | 0.98451 | -0.22206 | 3.1907
63 | 0.22842 | 0.11017 | -0.22842 | -0.11063 | 1.4628e-06 | -0.00045819 | 0.0074344 | 0.0074403 | 0.0074403 | 0.98471 | -0.22389 | 0.98471 | -0.22384 | 3.3819
64 | -0.38097 | -0.18451 | 0.38098 | 0.18309 | 1.2336e-05 | -0.001416 | 0.012347 | 0.012329 | 0.012347 | 0.98969 | -0.26247 | 0.98972 | -0.26275 | 5.6122
65 | 3.803 | 1.7778 | -3.797 | -1.783 | 0.0060018 | -0.0052174 | 0.12245 | 0.12253 | 0.12253 | 0.98972 | -0.26275 | 0.98826 | -0.24999 | 55.6962
66 | -4.184 | -1.9609 | 4.1856 | 1.9557 | 0.0016684 | -0.0051846 | 0.13477 | 0.13469 | 0.13477 | 0.98972 | -0.26275 | 0.99015 | -0.2579 | 37.2302
67 | 0.36499 | 0.17647 | -0.36498 | -0.17677 | 2.3946e-06 | -0.00029744 | 0.011842 | 0.011846 | 0.011846 | 0.98826 | -0.24999 | 0.98825 | -0.24993 | 5.3846
68 | 3.432 | 1.6065 | -3.4279 | -1.6112 | 0.0041335 | -0.0046562 | 0.11069 | 0.11076 | 0.11076 | 0.98826 | -0.24999 | 0.98715 | -0.24023 | 50.3469
69 | 0.32426 | 0.15702 | -0.32425 | -0.15704 | 4.0074e-06 | -2.1061e-05 | 0.010536 | 0.010536 | 0.010536 | 0.98715 | -0.24023 | 0.98713 | -0.24031 | 5.0172
70 | 12.073 | 5.5551 | -12.0628 | -5.5408 | 0.010195 | 0.014266 | 0.38511 | 0.38512 | 0.38512 | 0.99618 | -0.10385 | 0.99503 | -0.14334 | 46.9655
71 | 0.36834 | 0.17822 | -0.36832 | -0.1783 | 2.161e-05 | -8.8169e-05 | 0.011871 | 0.011873 | 0.011873 | 0.99503 | -0.14334 | 0.99497 | -0.14372 | 5.6537
72 | 1.9641 | 0.90377 | -1.9613 | -0.90252 | 0.0027438 | 0.0012567 | 0.062725 | 0.06273 | 0.06273 | 0.99503 | -0.14334 | 0.99355 | -0.15432 | 29.8716
73 | 9.5868 | 4.3893 | -9.5861 | -4.392 | 0.00076551 | -0.0026782 | 0.3059 | 0.30594 | 0.30594 | 0.99503 | -0.14334 | 0.99493 | -0.14508 | 36.3347
74 | 0.36832 | 0.1783 | -0.3683 | -0.17838 | 1.8059e-05 | -7.3654e-05 | 0.011873 | 0.011874 | 0.011874 | 0.99497 | -0.14372 | 0.99492 | -0.14405 | 5.6542
75 | 1.746 | 0.79823 | -1.7456 | -0.79804 | 0.00045831 | 0.00018968 | 0.05578 | 0.055781 | 0.055781 | 0.99355 | -0.15432 | 0.99327 | -0.15643 | 26.5626
76 | 9.4375 | 4.32 | -9.4367 | -4.3229 | 0.00079053 | -0.0028759 | 0.30115 | 0.30119 | 0.30119 | 0.99493 | -0.14508 | 0.99484 | -0.1469 | 35.7711
77 | 1.7456 | 0.79804 | -1.7441 | -0.8056 | 0.0014108 | -0.007562 | 0.055781 | 0.055878 | 0.055878 | 0.99327 | -0.15643 | 0.99252 | -0.1502 | 25.3992
78 | 0.57743 | 0.26507 | -0.57724 | -0.27491 | 0.00019325 | -0.0098443 | 0.01848 | 0.018602 | 0.018602 | 0.99252 | -0.1502 | 0.99221 | -0.14751 | 8.4553
79 | 1.0485 | 0.48517 | -1.048 | -0.49281 | 0.00050033 | -0.0076331 | 0.033602 | 0.033698 | 0.033698 | 0.99252 | -0.1502 | 0.99208 | -0.14638 | 15.3171
80 | 0.11822 | 0.055359 | -0.11821 | -0.057254 | 1.5603e-06 | -0.0018948 | 0.0037967 | 0.0038204 | 0.0038204 | 0.99252 | -0.1502 | 0.99251 | -0.15009 | 1.7365
81 | 0.28166 | 0.13639 | -0.28165 | -0.13641 | 2.45e-06 | -1.796e-05 | 0.0091049 | 0.0091051 | 0.0091051 | 0.99221 | -0.14751 | 0.9922 | -0.14756 | 4.3358
82 | 0.29558 | 0.13852 | -0.29557 | -0.14183 | 1.7089e-05 | -0.0033162 | 0.0094972 | 0.0095386 | 0.0095386 | 0.99221 | -0.14751 | 0.99216 | -0.14703 | 4.3357
83 | 0.3113 | 0.15009 | -0.3113 | -0.15077 | 3.9126e-06 | -0.00067929 | 0.010056 | 0.010065 | 0.010065 | 0.99208 | -0.14638 | 0.99207 | -0.14627 | 4.5749
84 | 0.73669 | 0.34272 | -0.73668 | -0.34288 | 5.2933e-06 | -0.00016511 | 0.023642 | 0.023644 | 0.023644 | 0.99208 | -0.14638 | 0.99207 | -0.14633 | 10.7474
85 | 0.29557 | 0.14183 | -0.29556 | -0.14315 | 6.814e-06 | -0.0013141 | 0.0095386 | 0.0095553 | 0.0095553 | 0.99216 | -0.14703 | 0.99213 | -0.14683 | 4.3433
86 | 0.65828 | 0.30612 | -0.65827 | -0.30655 | 1.0936e-05 | -0.000428 | 0.021125 | 0.02113 | 0.02113 | 0.99207 | -0.14633 | 0.99205 | -0.14619 | 9.6045
87 | 0.078403 | 0.03676 | -0.078403 | -0.037972 | 4.4006e-07 | -0.0012127 | 0.0025197 | 0.0025349 | 0.0025349 | 0.99207 | -0.14633 | 0.99207 | -0.14628 | 1.1522
88 | -0.41012 | -0.19863 | 0.41012 | 0.19855 | 8.2563e-07 | -8.3324e-05 | 0.013224 | 0.013223 | 0.013224 | 0.99477 | -0.14625 | 0.99477 | -0.14627 | 6.0108
89 | -0.41012 | -0.19855 | 0.41015 | 0.19596 | 2.559e-05 | -0.0025894 | 0.013223 | 0.01319 | 0.013223 | 0.99477 | -0.14627 | 0.99483 | -0.1468 | 6.0103
90 | 0.32085 | 0.15375 | -0.32084 | -0.15457 | 4.9567e-06 | -0.00082083 | 0.010324 | 0.010334 | 0.010334 | 0.99483 | -0.1468 | 0.99481 | -0.14667 | 4.6974
91 | -0.73099 | -0.34971 | 0.731 | 0.34944 | 8.3946e-06 | -0.00026628 | 0.023514 | 0.023511 | 0.023514 | 0.99483 | -0.1468 | 0.99484 | -0.1469 | 10.6882
92 | 8.7057 | 3.9735 | -8.7032 | -3.9845 | 0.0024923 | -0.011055 | 0.27768 | 0.27785 | 0.27785 | 0.99484 | -0.1469 | 0.9945 | -0.15316 | 32.9983
93 | 0.31433 | 0.15037 | -0.31432 | -0.15135 | 5.6629e-06 | -0.00097629 | 0.010114 | 0.010127 | 0.010127 | 0.9945 | -0.15316 | 0.99449 | -0.153 | 4.603
94 | 0.14666 | 0.07021 | -0.14666 | -0.071032 | 1.0365e-06 | -0.00082188 | 0.0047184 | 0.0047288 | 0.0047288 | 0.99481 | -0.14667 | 0.99481 | -0.14661 | 2.1494
95 | 0.074305 | 0.035106 | -0.074302 | -0.035419 | 2.7092e-06 | -0.00031326 | 0.0023855 | 0.0023894 | 0.0023894 | 0.99449 | -0.153 | 0.99445 | -0.15326 | 1.1378
96 | 0.074302 | 0.035419 | -0.074302 | -0.035986 | 1.8369e-07 | -0.00056729 | 0.0023894 | 0.0023966 | 0.0023966 | 0.99445 | -0.15326 | 0.99445 | -0.15324 | 1.0893
97 | 0.40012 | 0.19372 | -0.4001 | -0.19378 | 1.9052e-05 | -6.3052e-05 | 0.012939 | 0.01294 | 0.01294 | 0.99177 | -0.1437 | 0.99172 | -0.14402 | 6.1621
98 | -0.40012 | -0.19372 | 0.40019 | 0.18654 | 6.7986e-05 | -0.0071744 | 0.012939 | 0.01285 | 0.012939 | 0.99177 | -0.1437 | 0.99193 | -0.14512 | 5.8816
99 | -0.40019 | -0.18654 | 0.40021 | 0.18465 | 1.7804e-05 | -0.0018958 | 0.01285 | 0.012826 | 0.01285 | 0.99193 | -0.14512 | 0.99197 | -0.14547 | 5.8407
100 | 0.56946 | 0.26354 | -0.56946 | -0.26397 | 8.0745e-06 | -0.00042377 | 0.018259 | 0.018264 | 0.018264 | 0.99205 | -0.14619 | 0.99204 | -0.14608 | 8.302
101 | 0.56946 | 0.26397 | -0.56945 | -0.2644 | 8.3337e-06 | -0.00043711 | 0.018264 | 0.01827 | 0.01827 | 0.99204 | -0.14608 | 0.99203 | -0.14597 | 8.3044
102 | 0.48783 | 0.22487 | -0.48781 | -0.22662 | 2.4327e-05 | -0.0017427 | 0.015631 | 0.015653 | 0.015653 | 0.99203 | -0.14597 | 0.99198 | -0.14558 | 7.1148
103 | -0.4878 | -0.22707 | 0.4878 | 0.22682 | 3.4432e-06 | -0.00024617 | 0.015658 | 0.015655 | 0.015658 | 0.99197 | -0.14547 | 0.99198 | -0.14553 | 7.1174
104 | -0.4878 | -0.22682 | 0.48781 | 0.22662 | 2.8749e-06 | -0.00020562 | 0.015655 | 0.015653 | 0.015655 | 0.99198 | -0.14553 | 0.99198 | -0.14558 | 7.116

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 13.6532 | 6.2945

## res_load
| p_mw | q_mvar
0 | 0.34507 | 0.16712
1 | 0.3906 | 0.18918
2 | 0.08715 | 0.042208
3 | 0.25284 | 0.12246
4 | 0.31449 | 0.15232
5 | 0.2332 | 0.11295
6 | 0.33572 | 0.1626
7 | 0.17932 | 0.08685
8 | 0.21011 | 0.10176
9 | 0.38657 | 0.18722
10 | 0.30281 | 0.14666
11 | 0.36176 | 0.17521
12 | 0.07244 | 0.035084
13 | 0.52938 | 0.25639
14 | 0.26747 | 0.12954
15 | 0.37165 | 0.18
16 | 0.069738 | 0.033776
17 | 0.22791 | 0.11038
18 | 0.15324 | 0.074217
19 | 0.2455 | 0.1189
20 | 0.24096 | 0.1167
21 | 0.42828 | 0.20743
22 | 0.10194 | 0.049371
23 | 0.34423 | 0.16672
24 | 0.32919 | 0.15944
25 | 0.39586 | 0.19172
26 | 0.41042 | 0.19878
27 | 0.38295 | 0.18547
28 | 0.21546 | 0.10435
29 | 0.22842 | 0.11063
30 | 0.20502 | 0.099297
31 | 0.081244 | 0.039348
32 | 0.38097 | 0.18451
33 | 0.36498 | 0.17677
34 | 0.32425 | 0.15704
35 | 0.14356 | 0.069529
36 | 0.21533 | 0.10429
37 | 0.14858 | 0.071963
38 | 0.11821 | 0.057254
39 | 0.29556 | 0.14315
40 | 0.28165 | 0.13641
41 | 0.3683 | 0.17838
42 | 0.3113 | 0.15077
43 | 0.41012 | 0.19863
44 | 0.17418 | 0.08436
45 | 0.24001 | 0.11624
46 | 0.14666 | 0.071032
47 | 0.074302 | 0.035986
48 | 0.10577 | 0.051228
49 | 0.4001 | 0.19378
50 | 0.078403 | 0.037972
51 | 0.088803 | 0.043009
52 | 0.081617 | 0.039529
53 | 0.087592 | 0.042423

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1