## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_609_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_609_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_609_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_609_0_node_3 | 20 | n |  | TRUE
4 | bus_MV_609_0_node_28 | 20 | n |  | TRUE
5 | bus_MV_609_0_node_24 | 20 | n |  | TRUE
6 | bus_MV_609_0_node_111 | 20 | n |  | TRUE
7 | bus_MV_609_0_node_4 | 20 | n |  | TRUE
8 | bus_MV_609_0_node_6 | 20 | n |  | TRUE
9 | bus_MV_609_0_node_44 | 20 | n |  | TRUE
10 | bus_MV_609_0_node_115 | 20 | n |  | TRUE
11 | bus_MV_609_0_node_5 | 20 | n |  | TRUE
12 | bus_MV_609_0_node_118 | 20 | n |  | TRUE
13 | bus_MV_609_0_node_117 | 20 | n |  | TRUE
14 | bus_MV_609_0_node_15 | 20 | n |  | TRUE
15 | bus_MV_609_0_node_47 | 20 | n |  | TRUE
16 | bus_MV_609_0_node_60 | 20 | n |  | TRUE
17 | bus_MV_609_0_node_7 | 20 | n |  | TRUE
18 | bus_MV_609_0_node_10 | 20 | n |  | TRUE
19 | bus_MV_609_0_node_11 | 20 | n |  | TRUE
20 | bus_MV_609_0_node_9 | 20 | n |  | TRUE
21 | bus_MV_609_0_node_12 | 20 | n |  | TRUE
22 | bus_MV_609_0_node_13 | 20 | n |  | TRUE
23 | bus_MV_609_0_node_16 | 20 | n |  | TRUE
24 | bus_MV_609_0_node_14 | 20 | n |  | TRUE
25 | bus_MV_609_0_node_27 | 20 | n |  | TRUE
26 | bus_MV_609_0_node_19 | 20 | n |  | TRUE
27 | bus_MV_609_0_node_17 | 20 | n |  | TRUE
28 | bus_MV_609_0_node_18 | 20 | n |  | TRUE
29 | bus_MV_609_0_node_20 | 20 | n |  | TRUE
30 | bus_MV_609_0_node_72 | 20 | n |  | TRUE
31 | bus_MV_609_0_node_21 | 20 | n |  | TRUE
32 | bus_MV_609_0_node_23 | 20 | n |  | TRUE
33 | bus_MV_609_0_node_22 | 20 | n |  | TRUE
34 | bus_MV_609_0_node_108 | 20 | n |  | TRUE
35 | bus_MV_609_0_node_96 | 20 | n |  | TRUE
36 | bus_MV_609_0_node_68 | 20 | n |  | TRUE
37 | bus_MV_609_0_node_86 | 20 | n |  | TRUE
38 | bus_MV_609_0_node_95 | 20 | n |  | TRUE
39 | bus_MV_609_0_node_65 | 20 | n |  | TRUE
40 | bus_MV_609_0_node_84 | 20 | n |  | TRUE
41 | bus_MV_609_0_node_78 | 20 | n |  | TRUE
42 | bus_MV_609_0_node_29 | 20 | n |  | TRUE
43 | bus_MV_609_0_node_31 | 20 | n |  | TRUE
44 | bus_MV_609_0_node_32 | 20 | n |  | TRUE
45 | bus_MV_609_0_node_30 | 20 | n |  | TRUE
46 | bus_MV_609_0_node_36 | 20 | n |  | TRUE
47 | bus_MV_609_0_node_116 | 20 | n |  | TRUE
48 | bus_MV_609_0_node_34 | 20 | n |  | TRUE
49 | bus_MV_609_0_node_35 | 20 | n |  | TRUE
50 | bus_MV_609_0_node_33 | 20 | n |  | TRUE
51 | bus_MV_609_0_node_113 | 20 | n |  | TRUE
52 | bus_MV_609_0_node_71 | 20 | n |  | TRUE
53 | bus_MV_609_0_node_70 | 20 | n |  | TRUE
54 | bus_MV_609_0_node_37 | 20 | n |  | TRUE
55 | bus_MV_609_0_node_50 | 20 | n |  | TRUE
56 | bus_MV_609_0_node_69 | 20 | n |  | TRUE
57 | bus_MV_609_0_node_38 | 20 | n |  | TRUE
58 | bus_MV_609_0_node_51 | 20 | n |  | TRUE
59 | bus_MV_609_0_node_49 | 20 | n |  | TRUE
60 | bus_MV_609_0_node_64 | 20 | n |  | TRUE
61 | bus_MV_609_0_node_63 | 20 | n |  | TRUE
62 | bus_MV_609_0_node_39 | 20 | n |  | TRUE
63 | bus_MV_609_0_node_40 | 20 | n |  | TRUE
64 | bus_MV_609_0_node_73 | 20 | n |  | TRUE
65 | bus_MV_609_0_node_41 | 20 | n |  | TRUE
66 | bus_MV_609_0_node_42 | 20 | n |  | TRUE
67 | bus_MV_609_0_node_45 | 20 | n |  | TRUE
68 | bus_MV_609_0_node_61 | 20 | n |  | TRUE
69 | bus_MV_609_0_node_48 | 20 | n |  | TRUE
70 | bus_MV_609_0_node_81 | 20 | n |  | TRUE
71 | bus_MV_609_0_node_46 | 20 | n |  | TRUE
72 | bus_MV_609_0_node_62 | 20 | n |  | TRUE
73 | bus_MV_609_0_node_80 | 20 | n |  | TRUE
74 | bus_MV_609_0_node_52 | 20 | n |  | TRUE
75 | bus_MV_609_0_node_53 | 20 | n |  | TRUE
76 | bus_MV_609_0_node_112 | 20 | n |  | TRUE
77 | bus_MV_609_0_node_55 | 20 | n |  | TRUE
78 | bus_MV_609_0_node_82 | 20 | n |  | TRUE
79 | bus_MV_609_0_node_76 | 20 | n |  | TRUE
80 | bus_MV_609_0_node_74 | 20 | n |  | TRUE
81 | bus_MV_609_0_node_98 | 20 | n |  | TRUE
82 | bus_MV_609_0_node_99 | 20 | n |  | TRUE
83 | bus_MV_609_0_node_56 | 20 | n |  | TRUE
84 | bus_MV_609_0_node_57 | 20 | n |  | TRUE
85 | bus_MV_609_0_node_58 | 20 | n |  | TRUE
86 | bus_MV_609_0_node_59 | 20 | n |  | TRUE
87 | bus_MV_609_0_node_79 | 20 | n |  | TRUE
88 | bus_MV_609_0_node_66 | 20 | n |  | TRUE
89 | bus_MV_609_0_node_67 | 20 | n |  | TRUE
90 | bus_MV_609_0_node_105 | 20 | n |  | TRUE
91 | bus_MV_609_0_node_75 | 20 | n |  | TRUE
92 | bus_MV_609_0_node_77 | 20 | n |  | TRUE
93 | bus_MV_609_0_node_97 | 20 | n |  | TRUE
94 | bus_MV_609_0_node_103 | 20 | n |  | TRUE
95 | bus_MV_609_0_node_101 | 20 | n |  | TRUE
96 | bus_MV_609_0_node_83 | 20 | n |  | TRUE
97 | bus_MV_609_0_node_85 | 20 | n |  | TRUE
98 | bus_MV_609_0_node_87 | 20 | n |  | TRUE
99 | bus_MV_609_0_node_88 | 20 | n |  | TRUE
100 | bus_MV_609_0_node_89 | 20 | n |  | TRUE
101 | bus_MV_609_0_node_91 | 20 | n |  | TRUE
102 | bus_MV_609_0_node_104 | 20 | n |  | TRUE
103 | bus_MV_609_0_node_119 | 20 | n |  | TRUE
104 | bus_MV_609_0_node_90 | 20 | n |  | TRUE
105 | bus_MV_609_0_node_92 | 20 | n |  | TRUE
106 | bus_MV_609_0_node_110 | 20 | n |  | TRUE
107 | bus_MV_609_0_node_93 | 20 | n |  | TRUE
108 | bus_MV_609_0_node_94 | 20 | n |  | TRUE
109 | bus_MV_609_0_node_109 | 20 | n |  | TRUE
110 | bus_MV_609_0_node_100 | 20 | n |  | TRUE
111 | bus_MV_609_0_node_102 | 20 | n |  | TRUE
112 | bus_MV_609_0_node_114 | 20 | n |  | TRUE
113 | bus_HV_609_0_node_79 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_609_0_load_0 | 0 | 0.41044 | 0.19878 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_609_0_load_28 | 4 | 0.36735 | 0.17791 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_609_0_load_24 | 5 | 0.21684 | 0.10502 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_609_0_load_111 | 6 | 0.39036 | 0.18906 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_609_0_load_115 | 10 | 0.26422 | 0.12797 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_609_0_load_118 | 12 | 0.32951 | 0.15959 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_609_0_load_117 | 13 | 0.25536 | 0.12368 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_609_0_load_60 | 16 | 0.33914 | 0.16425 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_609_0_load_7 | 17 | 0.26727 | 0.12944 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_609_0_load_10 | 18 | 0.34419 | 0.1667 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_609_0_load_13 | 22 | 0.25879 | 0.12534 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_609_0_load_27 | 25 | 0.20677 | 0.10014 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_609_0_load_19 | 26 | 0.071428 | 0.034594 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_609_0_load_17 | 27 | 0.069226 | 0.033528 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_609_0_load_18 | 28 | 0.18866 | 0.091371 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_609_0_load_72 | 30 | 0.082003 | 0.039716 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_609_0_load_108 | 34 | 0.077497 | 0.037533 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_609_0_load_96 | 35 | 0.074755 | 0.036206 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_609_0_load_95 | 38 | 0.09063 | 0.043894 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_609_0_load_65 | 39 | 0.32097 | 0.15545 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_609_0_load_78 | 41 | 1.2427 | 0.60189 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_609_0_load_29 | 42 | 0.2184 | 0.10578 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_609_0_load_30 | 45 | 0.28434 | 0.13771 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_609_0_load_116 | 47 | 0.19674 | 0.095286 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_609_0_load_33 | 50 | 0.27798 | 0.13463 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_609_0_load_113 | 51 | 0.15323 | 0.074212 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_609_0_load_70 | 53 | 0.36993 | 0.17916 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_609_0_load_69 | 56 | 0.38789 | 0.18786 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_609_0_load_38 | 57 | 0.35652 | 0.17267 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_609_0_load_49 | 59 | 0.32205 | 0.15598 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_609_0_load_64 | 60 | 0.31847 | 0.15424 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_609_0_load_73 | 64 | 0.11834 | 0.057313 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_609_0_load_41 | 65 | 0.41228 | 0.19967 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_609_0_load_61 | 68 | 0.37367 | 0.18098 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_609_0_load_81 | 70 | 0.30989 | 0.15009 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_609_0_load_46 | 71 | 0.21435 | 0.10382 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_609_0_load_52 | 74 | 0.25082 | 0.12148 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_609_0_load_112 | 76 | 0.2614 | 0.1266 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_609_0_load_76 | 79 | 0.077449 | 0.03751 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_609_0_load_74 | 80 | 0.091144 | 0.044143 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_609_0_load_98 | 81 | 0.10506 | 0.050883 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_609_0_load_99 | 82 | 0.17378 | 0.084163 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_609_0_load_56 | 83 | 0.28182 | 0.13649 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_609_0_load_79 | 87 | 0.12969 | 0.062814 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_609_0_load_105 | 90 | 0.099454 | 0.048168 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_609_0_load_75 | 91 | 0.11514 | 0.055763 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_609_0_load_77 | 92 | 0.18388 | 0.089055 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_609_0_load_97 | 93 | 0.23236 | 0.11254 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_609_0_load_101 | 95 | 0.26069 | 0.12626 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_609_0_load_83 | 96 | 0.094056 | 0.045553 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_609_0_load_91 | 101 | 0.096309 | 0.046645 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_609_0_load_104 | 102 | 0.32961 | 0.15964 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_609_0_load_119 | 103 | 0.201 | 0.097348 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_609_0_load_92 | 105 | 0.075851 | 0.036736 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_609_0_load_110 | 106 | 0.071931 | 0.034838 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_609_0_load_109 | 109 | 1.5705 | 0.76062 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_609_0_load_114 | 112 | 0.090987 | 0.044067 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 87 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_609_0_line_0 |  | 0 | 1 | 0.009196 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_609_0_line_1 |  | 1 | 2 | 0.022607 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_609_0_line_2 |  | 2 | 3 | 0.30339 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_609_0_line_3 |  | 2 | 4 | 0.052658 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_609_0_line_4 |  | 3 | 5 | 0.063014 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
5 | MV_609_0_line_5 |  | 3 | 6 | 0.11465 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
6 | MV_609_0_line_6 |  | 5 | 14 | 0.014334 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
7 | MV_609_0_line_7 |  | 7 | 8 | 0.25509 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_609_0_line_8 |  | 7 | 9 | 0.88618 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_609_0_line_9 |  | 7 | 10 | 0.006471 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_609_0_line_10 |  | 8 | 13 | 0.086317 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
11 | MV_609_0_line_11 |  | 8 | 11 | 0.55019 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_609_0_line_12 |  | 9 | 15 | 0.19195 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_609_0_line_13 |  | 9 | 16 | 0.092227 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_609_0_line_14 |  | 11 | 12 | 0.020172 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_609_0_line_15 |  | 14 | 19 | 0.37063 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
16 | MV_609_0_line_16 |  | 14 | 24 | 0.48848 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_609_0_line_17 |  | 15 | 71 | 0.074765 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_609_0_line_18 |  | 15 | 69 | 0.16721 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_609_0_line_19 |  | 17 | 18 | 0.2127 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
20 | MV_609_0_line_20 |  | 18 | 19 | 0.018242 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
21 | MV_609_0_line_21 |  | 18 | 20 | 0.10869 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
22 | MV_609_0_line_22 |  | 20 | 21 | 0.06758 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
23 | MV_609_0_line_23 |  | 21 | 22 | 0.069328 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
24 | MV_609_0_line_24 |  | 21 | 23 | 0.15455 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_609_0_line_25 |  | 22 | 27 | 0.070709 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
26 | MV_609_0_line_26 |  | 23 | 26 | 0.013926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_609_0_line_27 |  | 24 | 25 | 0.053748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_609_0_line_28 |  | 27 | 28 | 0.040539 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
29 | MV_609_0_line_29 |  | 28 | 31 | 0.054386 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
30 | MV_609_0_line_30 |  | 29 | 30 | 0.065243 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_609_0_line_31 |  | 29 | 31 | 0.1173 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
32 | MV_609_0_line_32 |  | 29 | 32 | 0.23329 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
33 | MV_609_0_line_33 |  | 31 | 33 | 0.27458 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
34 | MV_609_0_line_34 |  | 32 | 34 | 0.091112 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_609_0_line_35 |  | 33 | 35 | 0.016604 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
36 | MV_609_0_line_36 |  | 34 | 41 | 0.18095 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
37 | MV_609_0_line_37 |  | 35 | 36 | 0.040875 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
38 | MV_609_0_line_38 |  | 36 | 89 | 0.021319 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
39 | MV_609_0_line_39 |  | 37 | 38 | 0.00086436 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_609_0_line_40 |  | 37 | 39 | 0.1925 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
41 | MV_609_0_line_41 |  | 37 | 40 | 0.07814 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
42 | MV_609_0_line_42 |  | 39 | 88 | 0.015195 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
43 | MV_609_0_line_43 |  | 40 | 96 | 0.060102 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
44 | MV_609_0_line_44 |  | 41 | 85 | 0.029933 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
45 | MV_609_0_line_45 |  | 42 | 43 | 0.32113 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
46 | MV_609_0_line_46 |  | 43 | 44 | 0.22197 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_609_0_line_47 |  | 43 | 45 | 0.057975 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
48 | MV_609_0_line_48 |  | 44 | 51 | 0.13952 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_609_0_line_49 |  | 44 | 52 | 0.49656 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_609_0_line_50 |  | 45 | 50 | 0.43111 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
51 | MV_609_0_line_51 |  | 46 | 47 | 0.010264 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_609_0_line_52 |  | 46 | 48 | 0.28152 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
53 | MV_609_0_line_53 |  | 46 | 49 | 0.36163 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
54 | MV_609_0_line_54 |  | 48 | 54 | 0.56175 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
55 | MV_609_0_line_55 |  | 48 | 50 | 0.058321 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
56 | MV_609_0_line_56 |  | 49 | 55 | 0.17957 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
57 | MV_609_0_line_57 |  | 49 | 56 | 0.04485 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
58 | MV_609_0_line_58 |  | 52 | 53 | 0.066835 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_609_0_line_59 |  | 54 | 57 | 0.10468 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
60 | MV_609_0_line_60 |  | 55 | 58 | 0.63684 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_609_0_line_61 |  | 55 | 59 | 0.14542 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
62 | MV_609_0_line_62 |  | 56 | 61 | 0.084696 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
63 | MV_609_0_line_63 |  | 57 | 62 | 0.040676 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_609_0_line_64 |  | 58 | 60 | 0.051755 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_609_0_line_65 |  | 61 | 72 | 0.2807 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
66 | MV_609_0_line_66 |  | 62 | 63 | 0.2302 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
67 | MV_609_0_line_67 |  | 63 | 64 | 0.075591 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_609_0_line_68 |  | 65 | 66 | 0.04739 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
69 | MV_609_0_line_69 |  | 66 | 67 | 0.26004 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
70 | MV_609_0_line_70 |  | 67 | 68 | 0.020128 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
71 | MV_609_0_line_71 |  | 68 | 72 | 0.072416 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
72 | MV_609_0_line_72 |  | 69 | 70 | 0.071365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_609_0_line_73 |  | 70 | 73 | 0.029347 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_609_0_line_74 |  | 72 | 78 | 0.22612 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
75 | MV_609_0_line_75 |  | 73 | 86 | 0.15659 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_609_0_line_76 |  | 74 | 75 | 0.083586 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
77 | MV_609_0_line_77 |  | 74 | 76 | 0.2355 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
78 | MV_609_0_line_78 |  | 75 | 77 | 0.3306 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
79 | MV_609_0_line_79 |  | 76 | 78 | 0.015536 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
80 | MV_609_0_line_80 |  | 77 | 79 | 0.036715 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
81 | MV_609_0_line_81 |  | 79 | 80 | 0.062416 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
82 | MV_609_0_line_82 |  | 80 | 91 | 0.039226 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
83 | MV_609_0_line_83 |  | 81 | 82 | 0.037072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
84 | MV_609_0_line_84 |  | 82 | 110 | 0.082381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_609_0_line_85 |  | 83 | 84 | 0.061283 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
86 | MV_609_0_line_86 |  | 84 | 85 | 0.32917 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
87 | MV_609_0_line_87 |  | 84 | 86 | 0.53221 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
88 | MV_609_0_line_88 |  | 86 | 87 | 0.043894 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
89 | MV_609_0_line_89 |  | 88 | 89 | 0.069333 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
90 | MV_609_0_line_90 |  | 89 | 90 | 0.056022 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_609_0_line_91 |  | 91 | 92 | 0.036681 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
92 | MV_609_0_line_92 |  | 92 | 93 | 0.076722 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
93 | MV_609_0_line_93 |  | 93 | 94 | 0.011901 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
94 | MV_609_0_line_94 |  | 93 | 95 | 0.039603 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
95 | MV_609_0_line_95 |  | 94 | 102 | 0.1061 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
96 | MV_609_0_line_96 |  | 95 | 110 | 0.076524 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
97 | MV_609_0_line_97 |  | 96 | 97 | 0.064045 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
98 | MV_609_0_line_98 |  | 97 | 98 | 0.06739 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
99 | MV_609_0_line_99 |  | 97 | 99 | 0.5657 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
100 | MV_609_0_line_100 |  | 97 | 100 | 0.30811 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
101 | MV_609_0_line_101 |  | 98 | 101 | 0.054404 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
102 | MV_609_0_line_102 |  | 99 | 102 | 0.01487 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
103 | MV_609_0_line_103 |  | 100 | 103 | 0.055239 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
104 | MV_609_0_line_104 |  | 100 | 104 | 0.23462 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
105 | MV_609_0_line_105 |  | 101 | 106 | 0.39979 | 0.119 | 0.32 | 11 | 0 | 0.645 | 1 | 1 | ol | TRUE
106 | MV_609_0_line_106 |  | 104 | 105 | 0.054132 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
107 | MV_609_0_line_107 |  | 105 | 107 | 0.0043934 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_609_0_line_108 |  | 107 | 108 | 0.046008 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
109 | MV_609_0_line_109 |  | 108 | 109 | 0.0017045 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
110 | MV_609_0_line_110 |  | 110 | 111 | 0.13185 | 0.103 | 0.058 | 500 | 0 | 0.638 | 1 | 1 | cs | TRUE
111 | MV_609_0_line_111 |  | 111 | 112 | 0.07121 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_609_0_trafo_79 | 25 MVA 110/20 kV | 113 | 87 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2586320.898 | 1219604.5625
1 | 2586318.2779 | 1219613.3736
2 | 2586298.6402 | 1219609.6947
3 | 2586111.6449 | 1219733.3125
4 | 2586251.4056 | 1219586.1462
5 | 2586074.8162 | 1219682.114
6 | 2586071.988 | 1219840.8898
7 | 2586830.3555 | 1219959.5447
8 | 2586984.9395 | 1220098.7718
9 | 2587149.0314 | 1219442.3359
10 | 2586827.4519 | 1219953.7589
11 | 2586551.8399 | 1219980.5163
12 | 2586535.9316 | 1219968.0564
13 | 2587027.1705 | 1220023.4913
14 | 2586086.1388 | 1219673.2823
15 | 2587251.4747 | 1219304.9911
16 | 2587058.91 | 1219422.7389
17 | 2586195.0326 | 1219193.9966
18 | 2586114.0504 | 1219390.6766
19 | 2586105.3012 | 1219406.6952
20 | 2586150.6882 | 1219288.3432
21 | 2586215.1301 | 1219267.403
22 | 2586280.9656 | 1219245.104
23 | 2586251.6134 | 1219417.5822
24 | 2585906.7177 | 1219549.7245
25 | 2585940.8872 | 1219565.8445
26 | 2586246.2435 | 1219430.4315
27 | 2586350.2831 | 1219244.1139
28 | 2586388.6533 | 1219257.1957
29 | 2586418.844 | 1219388.4795
30 | 2586394.9145 | 1219449.1762
31 | 2586440.7518 | 1219273.2409
32 | 2586477.1189 | 1219162.5831
33 | 2586420.0311 | 1219036.1635
34 | 2586567.9087 | 1219161.904
35 | 2586411.7603 | 1219021.766
36 | 2586391.3995 | 1218986.3229
37 | 2586555.2785 | 1218785.6779
38 | 2586556.0736 | 1218785.339
39 | 2586447.8091 | 1218945.3811
40 | 2586597.1579 | 1218767.8283
41 | 2586733.6276 | 1219089.2331
42 | 2588587.9087 | 1218465.7377
43 | 2588850.0664 | 1218651.1993
44 | 2588912.4676 | 1218577.4176
45 | 2588812.5627 | 1218695.4955
46 | 2588335.8062 | 1218892.2178
47 | 2588325.8629 | 1218894.8723
48 | 2588464.9916 | 1219023.5397
49 | 2588190.7443 | 1219192.5999
50 | 2588522.0223 | 1219014.0011
51 | 2589040.8465 | 1218559.4125
52 | 2589345.992 | 1218589.6611
53 | 2589369.0633 | 1218526.9392
54 | 2588901.8851 | 1219266.6542
55 | 2588183.7456 | 1219366.0911
56 | 2588146.213 | 1219186.8412
57 | 2588942.0347 | 1219169.9792
58 | 2587880.7127 | 1219583.8402
59 | 2588328.8223 | 1219356.0974
60 | 2587849.6699 | 1219542.3689
61 | 2588062.4192 | 1219199.1723
62 | 2588978.4617 | 1219188.2883
63 | 2589190.5773 | 1219277.5813
64 | 2589219.6963 | 1219207.8245
65 | 2587614.8818 | 1219400.2296
66 | 2587600.3317 | 1219445.3304
67 | 2587768.1583 | 1219246.7005
68 | 2587782.9445 | 1219234.274
69 | 2587228.2201 | 1219193.7441
70 | 2587251.8493 | 1219126.404
71 | 2587325.3556 | 1219317.484
72 | 2587850.3397 | 1219207.2864
73 | 2587262.3906 | 1219099.0606
74 | 2587601.8733 | 1218848.5962
75 | 2587629.4597 | 1218769.6933
76 | 2587803.548 | 1218970.2023
77 | 2587337.1771 | 1218739.4052
78 | 2587806.5313 | 1218985.4494
79 | 2587300.9988 | 1218733.1518
80 | 2587239.5662 | 1218722.1193
81 | 2587188.8079 | 1218824.2764
82 | 2587151.7963 | 1218822.1684
83 | 2586871.9361 | 1219133.3222
84 | 2586915.7693 | 1219176.1497
85 | 2586755.928 | 1219069.266
86 | 2587138.0473 | 1219049.3676
87 | 2587139.1263 | 1219093.222
88 | 2586441.1322 | 1218959.0376
89 | 2586376.1278 | 1218978.0755
90 | 2586343.5347 | 1218935.0515
91 | 2587200.9587 | 1218715.1813
92 | 2587164.8471 | 1218708.7457
93 | 2587088.3465 | 1218702.9218
94 | 2587082.0209 | 1218694.075
95 | 2587081.1635 | 1218741.8549
96 | 2586652.2465 | 1218743.7969
97 | 2586710.846 | 1218717.9546
98 | 2586685.162 | 1218655.6322
99 | 2586962.7193 | 1218674.2029
100 | 2586825.2995 | 1218789.4398
101 | 2586647.0193 | 1218648.3329
102 | 2586977.4787 | 1218675.984
103 | 2586805.1355 | 1218737.9996
104 | 2586746.3893 | 1218930.3077
105 | 2586746.8828 | 1218876.1776
106 | 2586278.3093 | 1218493.7952
107 | 2586746.8729 | 1218871.7842
108 | 2586747.2631 | 1218825.7792
109 | 2586748.793 | 1218825.0278
110 | 2587069.549 | 1218817.484
111 | 2587021.1581 | 1218908.2419
112 | 2586956.2802 | 1218896.2776
113 | 2587139.1263 | 1219093.222

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99297 | -0.1718 | 0.41044 | 0.19878
1 | 0.99297 | -0.17185 | 0 | 0
2 | 0.99298 | -0.17196 | 0 | 0
3 | 0.99328 | -0.17471 | 0 | 0
4 | 0.99296 | -0.17173 | 0.36735 | 0.17791
5 | 0.99333 | -0.17428 | 0.21684 | 0.10502
6 | 0.99323 | -0.17602 | 0.39036 | 0.18906
7 | 0.9978 | 0.013152 | 0 | 0
8 | 0.99761 | 0.014673 | 0 | 0
9 | 0.99875 | 0.0058414 | 0 | 0
10 | 0.99779 | 0.013172 | 0.26422 | 0.12797
11 | 0.99738 | 0.016605 | 0 | 0
12 | 0.99737 | 0.016685 | 0.32951 | 0.15959
13 | 0.99756 | 0.014405 | 0.25536 | 0.12368
14 | 0.99334 | -0.17416 | 0 | 0
15 | 0.99903 | 0.0036638 | 0 | 0
16 | 0.99871 | 0.0062101 | 0.33914 | 0.16425
17 | 0.99356 | -0.17107 | 0.26727 | 0.12944
18 | 0.99367 | -0.17037 | 0.34419 | 0.1667
19 | 0.99366 | -0.17055 | 0 | 0
20 | 0.99383 | -0.16118 | 0 | 0
21 | 0.99388 | -0.16097 | 0 | 0
22 | 0.99393 | -0.16074 | 0.25879 | 0.12534
23 | 0.99386 | -0.16111 | 0 | 0
24 | 0.99321 | -0.17316 | 0 | 0
25 | 0.99319 | -0.17303 | 0.20677 | 0.10014
26 | 0.99386 | -0.1611 | 0.071428 | 0.034594
27 | 0.99399 | -0.16048 | 0.069226 | 0.033528
28 | 0.99403 | -0.16032 | 0.18866 | 0.091371
29 | 0.99474 | -0.13695 | 0 | 0
30 | 0.99473 | -0.13689 | 0.082003 | 0.039716
31 | 0.99408 | -0.1601 | 0 | 0
32 | 0.99607 | -0.090683 | 0 | 0
33 | 0.99356 | -0.17007 | 0 | 0
34 | 0.9963 | -0.086337 | 0.077497 | 0.037533
35 | 0.99353 | -0.17067 | 0.074755 | 0.036206
36 | 0.99345 | -0.17214 | 0 | 0
37 | 0.99248 | -0.20317 | 0 | 0
38 | 0.99248 | -0.20317 | 0.09063 | 0.043894
39 | 0.99326 | -0.17591 | 0.32097 | 0.15545
40 | 0.99235 | -0.20582 | 0 | 0
41 | 0.99734 | -0.050294 | 1.2427 | 0.60189
42 | 0.98769 | -0.36112 | 0.2184 | 0.10578
43 | 0.98774 | -0.35842 | 0 | 0
44 | 0.9876 | -0.35727 | 0 | 0
45 | 0.98776 | -0.35835 | 0.28434 | 0.13771
46 | 0.98824 | -0.34006 | 0 | 0
47 | 0.98824 | -0.34004 | 0.19674 | 0.095286
48 | 0.98808 | -0.341 | 0 | 0
49 | 0.98847 | -0.33866 | 0 | 0
50 | 0.98806 | -0.34112 | 0.27798 | 0.13463
51 | 0.98757 | -0.35702 | 0.15323 | 0.074212
52 | 0.98736 | -0.35525 | 0 | 0
53 | 0.98733 | -0.35495 | 0.36993 | 0.17916
54 | 0.98799 | -0.34154 | 0 | 0
55 | 0.98844 | -0.33886 | 0 | 0
56 | 0.98851 | -0.33843 | 0.38789 | 0.18786
57 | 0.98796 | -0.34346 | 0.35652 | 0.17267
58 | 0.98818 | -0.33673 | 0 | 0
59 | 0.9884 | -0.34066 | 0.32205 | 0.15598
60 | 0.98816 | -0.33653 | 0.31847 | 0.15424
61 | 0.98868 | -0.32843 | 0 | 0
62 | 0.98795 | -0.34343 | 0 | 0
63 | 0.98792 | -0.34316 | 0 | 0
64 | 0.98791 | -0.34305 | 0.11834 | 0.057313
65 | 0.98883 | -0.33157 | 0.41228 | 0.19967
66 | 0.98886 | -0.331 | 0 | 0
67 | 0.98893 | -0.32688 | 0 | 0
68 | 0.98893 | -0.32687 | 0.37367 | 0.18098
69 | 0.99933 | 0.0014031 | 0 | 0
70 | 0.99946 | 0.0004516 | 0.30989 | 0.15009
71 | 0.99901 | 0.0038516 | 0.21435 | 0.10382
72 | 0.98895 | -0.32679 | 0 | 0
73 | 0.99952 | -4.6272e-05 | 0 | 0
74 | 0.99019 | -0.25362 | 0.25082 | 0.12148
75 | 0.99042 | -0.23959 | 0 | 0
76 | 0.98956 | -0.29091 | 0.2614 | 0.1266
77 | 0.99089 | -0.23707 | 0 | 0
78 | 0.98952 | -0.29321 | 0 | 0
79 | 0.99092 | -0.2364 | 0.077449 | 0.03751
80 | 0.99098 | -0.23524 | 0.091144 | 0.044143
81 | 0.99119 | -0.22732 | 0.10506 | 0.050883
82 | 0.99119 | -0.22736 | 0.17378 | 0.084163
83 | 0.99831 | -0.031585 | 0.28182 | 0.13649
84 | 0.99834 | -0.031375 | 0 | 0
85 | 0.99742 | -0.048719 | 0 | 0
86 | 0.99986 | -0.0026796 | 0 | 0
87 | 1 | 0 | -14.9493 | -6.7341
88 | 0.99329 | -0.17537 | 0 | 0
89 | 0.99341 | -0.17291 | 0 | 0
90 | 0.99341 | -0.17284 | 0.099454 | 0.048168
91 | 0.99102 | -0.2345 | 0.11514 | 0.055763
92 | 0.99106 | -0.23378 | 0.18388 | 0.089055
93 | 0.99124 | -0.22741 | 0.23236 | 0.11254
94 | 0.99125 | -0.22713 | 0 | 0
95 | 0.99123 | -0.22751 | 0.26069 | 0.12626
96 | 0.99224 | -0.20786 | 0.094056 | 0.045553
97 | 0.99213 | -0.21001 | 0 | 0
98 | 0.99213 | -0.21003 | 0 | 0
99 | 0.9914 | -0.22425 | 0 | 0
100 | 0.99201 | -0.21227 | 0 | 0
101 | 0.99212 | -0.21004 | 0.096309 | 0.046645
102 | 0.99138 | -0.22462 | 0.32961 | 0.15964
103 | 0.992 | -0.21229 | 0.201 | 0.097348
104 | 0.99183 | -0.21528 | 0 | 0
105 | 0.99172 | -0.2142 | 0.075851 | 0.036736
106 | 0.9921 | -0.21114 | 0.071931 | 0.034838
107 | 0.99171 | -0.21412 | 0 | 0
108 | 0.99162 | -0.21324 | 0 | 0
109 | 0.99162 | -0.21321 | 1.5705 | 0.76062
110 | 0.99122 | -0.22763 | 0 | 0
111 | 0.99122 | -0.22766 | 0 | 0
112 | 0.99121 | -0.22758 | 0.090987 | 0.044067
113 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.41044 | -0.19878 | 0.41044 | 0.19857 | 2.1575e-06 | -0.00021585 | 0.013258 | 0.013255 | 0.013258 | 0.99297 | -0.1718 | 0.99297 | -0.17185 | 6.0264
1 | -0.41044 | -0.19857 | 0.41045 | 0.19804 | 5.3001e-06 | -0.00053063 | 0.013255 | 0.013249 | 0.013255 | 0.99297 | -0.17185 | 0.99298 | -0.17196 | 6.0251
2 | -0.7778 | -0.37472 | 0.77806 | 0.36765 | 0.00025425 | -0.0070693 | 0.025099 | 0.02501 | 0.025099 | 0.99298 | -0.17196 | 0.99328 | -0.17471 | 11.4087
3 | 0.36736 | 0.17668 | -0.36735 | -0.17791 | 9.8855e-06 | -0.0012367 | 0.011851 | 0.011866 | 0.011866 | 0.99298 | -0.17196 | 0.99296 | -0.17173 | 5.3938
4 | -1.1684 | -0.55658 | 1.1685 | 0.55448 | 4.303e-05 | -0.0021017 | 0.037614 | 0.037587 | 0.037614 | 0.99328 | -0.17471 | 0.99333 | -0.17428 | 10.3905
5 | 0.39038 | 0.18894 | -0.39036 | -0.18906 | 1.6724e-05 | -0.00012301 | 0.012604 | 0.012606 | 0.012606 | 0.99328 | -0.17471 | 0.99323 | -0.17602 | 3.6018
6 | -1.3853 | -0.6595 | 1.3853 | 0.65903 | 1.3763e-05 | -0.00047521 | 0.044589 | 0.044583 | 0.044589 | 0.99333 | -0.17428 | 0.99334 | -0.17416 | 12.3174
7 | 0.58508 | 0.26362 | -0.58497 | -0.26965 | 0.00011784 | -0.0060276 | 0.018566 | 0.018639 | 0.018639 | 0.9978 | 0.013152 | 0.99761 | 0.014673 | 8.4722
8 | -0.8493 | -0.39143 | 0.85016 | 0.3706 | 0.00085795 | -0.020831 | 0.027056 | 0.026806 | 0.027056 | 0.9978 | 0.013152 | 0.99875 | 0.0058414 | 12.298
9 | 0.26422 | 0.12781 | -0.26422 | -0.12797 | 6.2306e-07 | -0.00015364 | 0.0084916 | 0.0084936 | 0.0084936 | 0.9978 | 0.013152 | 0.99779 | 0.013172 | 3.8607
10 | 0.25537 | 0.12358 | -0.25536 | -0.12368 | 1.0366e-05 | -9.6055e-05 | 0.0082095 | 0.0082108 | 0.0082108 | 0.99761 | 0.014673 | 0.99756 | 0.014405 | 3.9099
11 | 0.32959 | 0.14606 | -0.32951 | -0.15911 | 8.1135e-05 | -0.013047 | 0.010432 | 0.010591 | 0.010591 | 0.99761 | 0.014673 | 0.99738 | 0.016605 | 4.814
12 | -1.1893 | -0.53266 | 1.1897 | 0.5282 | 0.00036303 | -0.0044652 | 0.037666 | 0.037612 | 0.037666 | 0.99875 | 0.0058414 | 0.99903 | 0.0036638 | 17.1209
13 | 0.33915 | 0.16206 | -0.33914 | -0.16425 | 1.457e-05 | -0.0021921 | 0.010864 | 0.010892 | 0.010892 | 0.99875 | 0.0058414 | 0.99871 | 0.0062101 | 4.9509
14 | 0.32951 | 0.15911 | -0.32951 | -0.15959 | 3.0223e-06 | -0.0004782 | 0.010591 | 0.010597 | 0.010597 | 0.99738 | 0.016605 | 0.99737 | 0.016685 | 4.8168
15 | -1.5921 | -0.74641 | 1.5926 | 0.7342 | 0.00046607 | -0.012211 | 0.051102 | 0.050948 | 0.051102 | 0.99334 | -0.17416 | 0.99366 | -0.17055 | 14.1165
16 | 0.2068 | 0.087382 | -0.20678 | -0.09888 | 2.8332e-05 | -0.011498 | 0.0065245 | 0.0066617 | 0.0066617 | 0.99334 | -0.17416 | 0.99321 | -0.17316 | 3.0281
17 | 0.21436 | 0.10204 | -0.21435 | -0.10382 | 4.7121e-06 | -0.0017802 | 0.0068599 | 0.0068822 | 0.0068822 | 0.99903 | 0.0036638 | 0.99901 | 0.0038516 | 3.1283
18 | -1.404 | -0.63023 | 1.4045 | 0.62638 | 0.00044097 | -0.0038549 | 0.04447 | 0.044423 | 0.04447 | 0.99903 | 0.0036638 | 0.99933 | 0.0014031 | 20.2136
19 | -0.26727 | -0.12944 | 0.26729 | 0.12921 | 2.8201e-05 | -0.00023303 | 0.0086281 | 0.0086249 | 0.0086281 | 0.99356 | -0.17107 | 0.99367 | -0.17037 | 4.1086
20 | 1.5926 | 0.7336 | -1.5926 | -0.7342 | 2.2867e-05 | -0.00060129 | 0.050941 | 0.050948 | 0.050948 | 0.99367 | -0.17037 | 0.99366 | -0.17055 | 14.074
21 | -2.2041 | -1.0295 | 2.2043 | 1.0299 | 0.00019381 | 0.00037279 | 0.070673 | 0.070671 | 0.070673 | 0.99367 | -0.17037 | 0.99383 | -0.16118 | 10.9571
22 | -2.2043 | -1.0299 | 2.2044 | 1.0257 | 0.00010422 | -0.0041355 | 0.070671 | 0.07062 | 0.070671 | 0.99383 | -0.16118 | 0.99388 | -0.16097 | 11.077
23 | -2.2758 | -1.0598 | 2.276 | 1.0556 | 0.00011382 | -0.004239 | 0.072919 | 0.072866 | 0.072919 | 0.99388 | -0.16097 | 0.99393 | -0.16074 | 11.4292
24 | 0.071429 | 0.034084 | -0.071428 | -0.034266 | 1.4565e-06 | -0.00018133 | 0.0022988 | 0.0023011 | 0.0023011 | 0.99388 | -0.16097 | 0.99386 | -0.16111 | 1.0957
25 | -2.5347 | -1.1809 | 2.5349 | 1.1766 | 0.00014402 | -0.0043082 | 0.081216 | 0.081162 | 0.081216 | 0.99393 | -0.16074 | 0.99399 | -0.16048 | 12.7298
26 | 0.071428 | 0.034266 | -0.071428 | -0.034594 | 9.8615e-08 | -0.0003284 | 0.0023011 | 0.0023052 | 0.0023052 | 0.99386 | -0.16111 | 0.99386 | -0.1611 | 1.0478
27 | 0.20678 | 0.09888 | -0.20677 | -0.10014 | 3.192e-06 | -0.001265 | 0.0066617 | 0.0066777 | 0.0066777 | 0.99321 | -0.17316 | 0.99319 | -0.17303 | 3.0353
28 | -2.6041 | -1.2101 | 2.6042 | 1.2077 | 8.7088e-05 | -0.0024677 | 0.083396 | 0.083365 | 0.083396 | 0.99399 | -0.16048 | 0.99403 | -0.16032 | 13.0715
29 | -2.7929 | -1.299 | 2.793 | 1.2957 | 0.00013441 | -0.003301 | 0.089452 | 0.089411 | 0.089452 | 0.99403 | -0.16032 | 0.99408 | -0.1601 | 14.0207
30 | 0.082003 | 0.038175 | -0.082003 | -0.039716 | 6.0452e-07 | -0.0015412 | 0.002625 | 0.0026442 | 0.0026442 | 0.99474 | -0.13695 | 0.99473 | -0.13689 | 1.2019
31 | 11.4836 | 5.1596 | -11.478 | -5.1518 | 0.0055804 | 0.0077791 | 0.36535 | 0.36535 | 0.36535 | 0.99474 | -0.13695 | 0.99408 | -0.1601 | 44.5551
32 | -11.5656 | -5.1977 | 11.5769 | 5.2134 | 0.011258 | 0.015701 | 0.36797 | 0.36797 | 0.36797 | 0.99474 | -0.13695 | 0.99607 | -0.090683 | 44.8748
33 | 8.6851 | 3.856 | -8.6812 | -3.8732 | 0.0038297 | -0.017204 | 0.27595 | 0.2762 | 0.2762 | 0.99408 | -0.1601 | 0.99356 | -0.17007 | 32.8023
34 | -11.5769 | -5.2134 | 11.5791 | 5.2086 | 0.0022571 | -0.0048362 | 0.36797 | 0.36788 | 0.36797 | 0.99607 | -0.090683 | 0.9963 | -0.086337 | 43.7014
35 | 8.6812 | 3.8732 | -8.681 | -3.8743 | 0.0002318 | -0.0010395 | 0.2762 | 0.27621 | 0.27621 | 0.99356 | -0.17007 | 0.99353 | -0.17067 | 32.8041
36 | -11.6566 | -5.2461 | 11.6655 | 5.2585 | 0.0088468 | 0.012343 | 0.37038 | 0.37037 | 0.37038 | 0.9963 | -0.086337 | 0.99734 | -0.050294 | 45.168
37 | 8.6062 | 3.8381 | -8.6057 | -3.8406 | 0.00056083 | -0.0025676 | 0.2738 | 0.27383 | 0.27383 | 0.99353 | -0.17067 | 0.99345 | -0.17214 | 32.5219
38 | 8.6057 | 3.8406 | -8.6054 | -3.842 | 0.00029257 | -0.0013389 | 0.27383 | 0.27385 | 0.27385 | 0.99345 | -0.17214 | 0.99341 | -0.17291 | 32.5242
39 | 0.09063 | 0.043874 | -0.09063 | -0.043894 | 9.9116e-09 | -2.0326e-05 | 0.0029287 | 0.002929 | 0.002929 | 0.99248 | -0.20317 | 0.99248 | -0.20317 | 1.3314
40 | -8.1792 | -3.6388 | 8.1838 | 3.645 | 0.0046512 | 0.0062429 | 0.26038 | 0.26038 | 0.26038 | 0.99248 | -0.20317 | 0.99326 | -0.17591 | 31.7538
41 | 8.0885 | 3.5949 | -8.0876 | -3.5999 | 0.00094807 | -0.0050096 | 0.25745 | 0.25752 | 0.25752 | 0.99248 | -0.20317 | 0.99235 | -0.20582 | 30.5847
42 | -8.5048 | -3.8005 | 8.505 | 3.7995 | 0.00020381 | -0.00095828 | 0.27074 | 0.27072 | 0.27074 | 0.99326 | -0.17591 | 0.99329 | -0.17537 | 32.1538
43 | 8.0876 | 3.5999 | -8.0869 | -3.6038 | 0.00072957 | -0.0038518 | 0.25752 | 0.25758 | 0.25758 | 0.99235 | -0.20582 | 0.99224 | -0.20786 | 30.5911
44 | -12.9082 | -5.8604 | 12.9092 | 5.8589 | 0.00092221 | -0.0014284 | 0.41033 | 0.4103 | 0.41033 | 0.99734 | -0.050294 | 0.99742 | -0.048719 | 48.7323
45 | -0.2184 | -0.10578 | 0.2184 | 0.10536 | 5.7623e-06 | -0.00041756 | 0.0070924 | 0.0070869 | 0.0070924 | 0.98769 | -0.36112 | 0.98774 | -0.35842 | 1.0996
46 | 0.52335 | 0.2319 | -0.52327 | -0.23704 | 8.3241e-05 | -0.0051451 | 0.01673 | 0.016791 | 0.016791 | 0.98774 | -0.35842 | 0.9876 | -0.35727 | 7.6325
47 | -0.74176 | -0.33726 | 0.74177 | 0.33371 | 1.0141e-05 | -0.0035483 | 0.023814 | 0.023771 | 0.023814 | 0.98774 | -0.35842 | 0.98776 | -0.35835 | 3.7326
48 | 0.15323 | 0.070965 | -0.15323 | -0.074212 | 4.5753e-06 | -0.0032476 | 0.0049361 | 0.0049767 | 0.0049767 | 0.9876 | -0.35727 | 0.98757 | -0.35702 | 2.2621
49 | 0.37003 | 0.16608 | -0.36994 | -0.17761 | 9.4281e-05 | -0.011533 | 0.011856 | 0.011998 | 0.011998 | 0.9876 | -0.35727 | 0.98736 | -0.35525 | 5.4536
50 | -1.0261 | -0.47142 | 1.0263 | 0.47129 | 0.00016759 | -0.00013095 | 0.033002 | 0.032995 | 0.033002 | 0.98776 | -0.35835 | 0.98806 | -0.34112 | 5.1165
51 | 0.19674 | 0.095046 | -0.19674 | -0.095286 | 5.5845e-07 | -0.00023917 | 0.0063825 | 0.0063855 | 0.0063855 | 0.98824 | -0.34006 | 0.98824 | -0.34004 | 2.9025
52 | 1.7795 | 0.77261 | -1.7792 | -0.78972 | 0.00028034 | -0.017114 | 0.056668 | 0.056871 | 0.056871 | 0.98824 | -0.34006 | 0.98808 | -0.341 | 8.9139
53 | -1.9762 | -0.86765 | 1.9767 | 0.84571 | 0.00044234 | -0.021947 | 0.063046 | 0.062788 | 0.063046 | 0.98824 | -0.34006 | 0.98847 | -0.33866 | 9.8818
54 | 0.47491 | 0.18736 | -0.47487 | -0.22179 | 3.9618e-05 | -0.034434 | 0.014916 | 0.015314 | 0.015314 | 0.98808 | -0.341 | 0.98799 | -0.34154 | 2.4003
55 | 1.3043 | 0.60236 | -1.3043 | -0.60592 | 3.1782e-05 | -0.0035596 | 0.041973 | 0.042017 | 0.042017 | 0.98808 | -0.341 | 0.98806 | -0.34112 | 6.5857
56 | 0.64064 | 0.283 | -0.64062 | -0.29401 | 2.3362e-05 | -0.011011 | 0.020453 | 0.020586 | 0.020586 | 0.98847 | -0.33866 | 0.98844 | -0.33886 | 3.2266
57 | -2.6173 | -1.1287 | 2.6174 | 1.126 | 9.599e-05 | -0.0026995 | 0.083241 | 0.083209 | 0.083241 | 0.98847 | -0.33866 | 0.98851 | -0.33843 | 13.0471
58 | 0.36994 | 0.17761 | -0.36993 | -0.17916 | 1.2865e-05 | -0.0015518 | 0.011998 | 0.012018 | 0.012018 | 0.98736 | -0.35525 | 0.98733 | -0.35495 | 5.4626
59 | 0.47487 | 0.22179 | -0.47486 | -0.22191 | 8.7649e-06 | -0.00011767 | 0.015314 | 0.015315 | 0.015315 | 0.98799 | -0.34154 | 0.98796 | -0.34346 | 2.3745
60 | 0.31856 | 0.13821 | -0.31848 | -0.15304 | 8.8973e-05 | -0.014825 | 0.010142 | 0.010322 | 0.010322 | 0.98844 | -0.33886 | 0.98818 | -0.33673 | 4.6918
61 | 0.32205 | 0.15579 | -0.32205 | -0.15598 | 5.6689e-06 | -0.00018114 | 0.010448 | 0.010451 | 0.010451 | 0.98844 | -0.33886 | 0.9884 | -0.34066 | 1.6203
62 | -3.0053 | -1.3139 | 3.0056 | 1.3145 | 0.0002774 | 0.00063154 | 0.095784 | 0.095783 | 0.095784 | 0.98851 | -0.33843 | 0.98868 | -0.32843 | 14.8502
63 | 0.11834 | 0.049241 | -0.11834 | -0.050189 | 7.6388e-07 | -0.00094771 | 0.0037453 | 0.003756 | 0.003756 | 0.98796 | -0.34346 | 0.98795 | -0.34343 | 1.7073
64 | 0.31848 | 0.15304 | -0.31847 | -0.15424 | 7.3723e-06 | -0.0012044 | 0.010322 | 0.010337 | 0.010337 | 0.98818 | -0.33673 | 0.98816 | -0.33653 | 4.6988
65 | -3.0056 | -1.3145 | 3.0064 | 1.2977 | 0.00079408 | -0.016797 | 0.095783 | 0.095582 | 0.095783 | 0.98868 | -0.32843 | 0.98895 | -0.32679 | 15.013
66 | 0.11834 | 0.050189 | -0.11834 | -0.055552 | 4.4081e-06 | -0.0053633 | 0.003756 | 0.0038199 | 0.0038199 | 0.98795 | -0.34343 | 0.98792 | -0.34316 | 1.7363
67 | 0.11834 | 0.055552 | -0.11834 | -0.057313 | 1.481e-06 | -0.001761 | 0.0038199 | 0.0038421 | 0.0038421 | 0.98792 | -0.34316 | 0.98791 | -0.34305 | 1.7464
68 | -0.41228 | -0.19967 | 0.41228 | 0.19963 | 7.7798e-06 | -4.9332e-05 | 0.013373 | 0.013372 | 0.013373 | 0.98883 | -0.33157 | 0.98886 | -0.331 | 3.8209
69 | -0.41228 | -0.19963 | 0.4123 | 0.19932 | 1.6595e-05 | -0.00030689 | 0.013372 | 0.013368 | 0.013372 | 0.98886 | -0.331 | 0.98893 | -0.32688 | 2.0732
70 | -0.4123 | -0.19932 | 0.4123 | 0.19808 | 1.1101e-06 | -0.0012362 | 0.013368 | 0.013352 | 0.013368 | 0.98893 | -0.32688 | 0.98893 | -0.32687 | 2.0953
71 | -0.78597 | -0.37906 | 0.78599 | 0.37462 | 1.4486e-05 | -0.0044418 | 0.025472 | 0.025416 | 0.025472 | 0.98893 | -0.32687 | 0.98895 | -0.32679 | 3.9924
72 | -1.4045 | -0.62638 | 1.4047 | 0.62473 | 0.00018793 | -0.0016461 | 0.044423 | 0.044403 | 0.044423 | 0.99933 | 0.0014031 | 0.99946 | 0.0004516 | 20.1922
73 | -1.7146 | -0.77482 | 1.7147 | 0.77415 | 0.00011569 | -0.00066567 | 0.054344 | 0.054335 | 0.054344 | 0.99946 | 0.0004516 | 0.99952 | -4.6272e-05 | 24.7017
74 | -3.7923 | -1.6723 | 3.7935 | 1.6752 | 0.0011815 | 0.0028714 | 0.12098 | 0.12098 | 0.12098 | 0.98895 | -0.32679 | 0.98952 | -0.29321 | 18.7572
75 | -1.7147 | -0.77415 | 1.7153 | 0.7706 | 0.00061669 | -0.0035536 | 0.054335 | 0.054291 | 0.054335 | 0.99952 | -4.6272e-05 | 0.99986 | -0.0026796 | 24.6979
76 | -4.3072 | -1.9269 | 4.3078 | 1.9283 | 0.0005647 | 0.0014052 | 0.13756 | 0.13756 | 0.13756 | 0.99019 | -0.25362 | 0.99042 | -0.23959 | 21.3279
77 | 4.0564 | 1.8055 | -4.055 | -1.802 | 0.0014088 | 0.0034693 | 0.12944 | 0.12945 | 0.12945 | 0.99019 | -0.25362 | 0.98956 | -0.29091 | 20.0694
78 | -4.3078 | -1.9283 | 4.3097 | 1.909 | 0.0019298 | -0.019299 | 0.13756 | 0.13732 | 0.13756 | 0.99042 | -0.23959 | 0.99089 | -0.23707 | 21.5617
79 | 3.7936 | 1.6754 | -3.7935 | -1.6752 | 8.1178e-05 | 0.00019727 | 0.12098 | 0.12098 | 0.12098 | 0.98956 | -0.29091 | 0.98952 | -0.29321 | 18.7566
80 | -4.3097 | -1.909 | 4.3099 | 1.9064 | 0.00012667 | -0.0026381 | 0.13732 | 0.13729 | 0.13732 | 0.99089 | -0.23707 | 0.99092 | -0.2364 | 16.309
81 | -4.3873 | -1.9439 | 4.3875 | 1.9394 | 0.00022313 | -0.004478 | 0.13979 | 0.13974 | 0.13979 | 0.99092 | -0.2364 | 0.99098 | -0.23524 | 16.6027
82 | -4.4787 | -1.9836 | 4.4788 | 1.9808 | 0.00014612 | -0.0028092 | 0.14269 | 0.14265 | 0.14269 | 0.99098 | -0.23524 | 0.99102 | -0.2345 | 16.9463
83 | -0.10506 | -0.050883 | 0.10506 | 0.050013 | 5.7017e-07 | -0.00086943 | 0.0033997 | 0.0033888 | 0.0033997 | 0.99119 | -0.22732 | 0.99119 | -0.22736 | 1.5453
84 | -0.27884 | -0.13418 | 0.27884 | 0.13225 | 8.9081e-06 | -0.0019299 | 0.0090121 | 0.0089878 | 0.0090121 | 0.99119 | -0.22736 | 0.99122 | -0.22763 | 4.0964
85 | -0.28182 | -0.13649 | 0.28183 | 0.13643 | 8.9513e-06 | -6.7308e-05 | 0.0090548 | 0.0090539 | 0.0090548 | 0.99831 | -0.031585 | 0.99834 | -0.031375 | 4.3118
86 | 12.9193 | 5.8432 | -12.9092 | -5.8589 | 0.010133 | -0.01574 | 0.41 | 0.4103 | 0.4103 | 0.99834 | -0.031375 | 0.99742 | -0.048719 | 48.7291
87 | -13.2011 | -5.9796 | 13.2182 | 5.9547 | 0.017083 | -0.024907 | 0.41905 | 0.41857 | 0.41905 | 0.99834 | -0.031375 | 0.99986 | -0.0026796 | 49.7685
88 | -14.9335 | -6.7253 | 14.9353 | 6.7236 | 0.0017959 | -0.0017045 | 0.47286 | 0.47282 | 0.47286 | 0.99986 | -0.0026796 | 1 | 0 | 56.159
89 | -8.505 | -3.7995 | 8.5059 | 3.7951 | 0.00092968 | -0.0043736 | 0.27072 | 0.27066 | 0.27072 | 0.99329 | -0.17537 | 0.99341 | -0.17291 | 32.1522
90 | 0.099454 | 0.046848 | -0.099454 | -0.048168 | 7.6721e-07 | -0.0013198 | 0.0031946 | 0.0032111 | 0.0032111 | 0.99341 | -0.17291 | 0.99341 | -0.17284 | 1.4596
91 | -4.594 | -2.0365 | 4.5941 | 2.0339 | 0.00014379 | -0.0026205 | 0.14638 | 0.14635 | 0.14638 | 0.99102 | -0.2345 | 0.99106 | -0.23378 | 17.3845
92 | -4.778 | -2.123 | 4.7786 | 2.1237 | 0.00063418 | 0.00072306 | 0.15229 | 0.15229 | 0.15229 | 0.99106 | -0.23378 | 0.99124 | -0.22741 | 18.5723
93 | -5.6415 | -2.5203 | 5.6416 | 2.5194 | 7.0516e-05 | -0.00082869 | 0.17995 | 0.17993 | 0.17995 | 0.99124 | -0.22741 | 0.99125 | -0.22713 | 21.3712
94 | 0.63053 | 0.28405 | -0.63052 | -0.28702 | 2.9448e-06 | -0.0029703 | 0.02014 | 0.020176 | 0.020176 | 0.99124 | -0.22741 | 0.99123 | -0.22751 | 2.3962
95 | -5.6416 | -2.5194 | 5.6422 | 2.5121 | 0.00062832 | -0.0073896 | 0.17993 | 0.17984 | 0.17993 | 0.99125 | -0.22713 | 0.99138 | -0.22462 | 21.3699
96 | 0.36983 | 0.16076 | -0.36983 | -0.1665 | 1.9426e-06 | -0.0057428 | 0.011744 | 0.011812 | 0.011812 | 0.99123 | -0.22751 | 0.99122 | -0.22763 | 1.4028
97 | 7.9928 | 3.5582 | -7.9921 | -3.5623 | 0.00075952 | -0.0041199 | 0.25454 | 0.2546 | 0.2546 | 0.99224 | -0.20786 | 0.99213 | -0.21001 | 30.2369
98 | 0.16824 | 0.073408 | -0.16824 | -0.077576 | 5.9947e-07 | -0.0041675 | 0.0053409 | 0.0053906 | 0.0053906 | 0.99213 | -0.21001 | 0.99213 | -0.21003 | 0.84492
99 | 5.9757 | 2.6316 | -5.9719 | -2.6707 | 0.0037464 | -0.039073 | 0.18998 | 0.19049 | 0.19049 | 0.99213 | -0.21001 | 0.9914 | -0.22425 | 22.623
100 | 1.8482 | 0.85733 | -1.848 | -0.88031 | 0.00019909 | -0.022986 | 0.059279 | 0.059566 | 0.059566 | 0.99213 | -0.21001 | 0.99201 | -0.21227 | 7.0743
101 | 0.16824 | 0.077576 | -0.16824 | -0.08094 | 4.9226e-07 | -0.0033644 | 0.0053906 | 0.0054323 | 0.0054323 | 0.99213 | -0.21003 | 0.99212 | -0.21004 | 0.85146
102 | 5.9719 | 2.6707 | -5.9718 | -2.6717 | 9.8746e-05 | -0.001026 | 0.19049 | 0.1905 | 0.1905 | 0.9914 | -0.22425 | 0.99138 | -0.22462 | 22.6246
103 | 0.201 | 0.093933 | -0.201 | -0.097348 | 7.1618e-07 | -0.0034151 | 0.0064563 | 0.006499 | 0.006499 | 0.99201 | -0.21227 | 0.992 | -0.21229 | 1.0187
104 | 1.647 | 0.78638 | -1.6467 | -0.79497 | 0.00024272 | -0.008596 | 0.05311 | 0.053221 | 0.053221 | 0.99201 | -0.21227 | 0.99183 | -0.21528 | 12.6415
105 | 0.071931 | 0.034296 | -0.071931 | -0.034838 | 7.6959e-07 | -0.00054187 | 0.0023187 | 0.0023255 | 0.0023255 | 0.99212 | -0.21004 | 0.9921 | -0.21114 | 0.36055
106 | 1.6467 | 0.79497 | -1.6465 | -0.79618 | 0.00020475 | -0.0012106 | 0.053221 | 0.053237 | 0.053237 | 0.99183 | -0.21528 | 0.99172 | -0.2142 | 24.1986
107 | 1.5707 | 0.75945 | -1.5706 | -0.75955 | 1.5127e-05 | -9.868e-05 | 0.050784 | 0.050785 | 0.050785 | 0.99172 | -0.2142 | 0.99171 | -0.21412 | 23.0841
108 | 1.5706 | 0.75955 | -1.5705 | -0.76058 | 0.00015846 | -0.0010333 | 0.050785 | 0.050799 | 0.050799 | 0.99171 | -0.21412 | 0.99162 | -0.21324 | 23.0903
109 | 1.5705 | 0.76058 | -1.5705 | -0.76062 | 5.8719e-06 | -3.8275e-05 | 0.050799 | 0.050799 | 0.050799 | 0.99162 | -0.21324 | 0.99162 | -0.21321 | 23.0905
110 | 0.090988 | 0.034257 | -0.090988 | -0.042397 | 3.3684e-07 | -0.0081396 | 0.0028314 | 0.0029234 | 0.0029234 | 0.99122 | -0.22763 | 0.99122 | -0.22766 | 0.45821
111 | 0.090988 | 0.042397 | -0.090987 | -0.044067 | 8.1822e-07 | -0.0016702 | 0.0029234 | 0.0029443 | 0.0029443 | 0.99122 | -0.22766 | 0.99121 | -0.22758 | 1.3383

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 15.079 | 6.7969

## res_load
| p_mw | q_mvar
0 | 0.41044 | 0.19878
1 | 0.36735 | 0.17791
2 | 0.21684 | 0.10502
3 | 0.39036 | 0.18906
4 | 0.26422 | 0.12797
5 | 0.32951 | 0.15959
6 | 0.25536 | 0.12368
7 | 0.33914 | 0.16425
8 | 0.26727 | 0.12944
9 | 0.34419 | 0.1667
10 | 0.25879 | 0.12534
11 | 0.20677 | 0.10014
12 | 0.071428 | 0.034594
13 | 0.069226 | 0.033528
14 | 0.18866 | 0.091371
15 | 0.082003 | 0.039716
16 | 0.077497 | 0.037533
17 | 0.074755 | 0.036206
18 | 0.09063 | 0.043894
19 | 0.32097 | 0.15545
20 | 1.2427 | 0.60189
21 | 0.2184 | 0.10578
22 | 0.28434 | 0.13771
23 | 0.19674 | 0.095286
24 | 0.27798 | 0.13463
25 | 0.15323 | 0.074212
26 | 0.36993 | 0.17916
27 | 0.38789 | 0.18786
28 | 0.35652 | 0.17267
29 | 0.32205 | 0.15598
30 | 0.31847 | 0.15424
31 | 0.11834 | 0.057313
32 | 0.41228 | 0.19967
33 | 0.37367 | 0.18098
34 | 0.30989 | 0.15009
35 | 0.21435 | 0.10382
36 | 0.25082 | 0.12148
37 | 0.2614 | 0.1266
38 | 0.077449 | 0.03751
39 | 0.091144 | 0.044143
40 | 0.10506 | 0.050883
41 | 0.17378 | 0.084163
42 | 0.28182 | 0.13649
43 | 0.12969 | 0.062814
44 | 0.099454 | 0.048168
45 | 0.11514 | 0.055763
46 | 0.18388 | 0.089055
47 | 0.23236 | 0.11254
48 | 0.26069 | 0.12626
49 | 0.094056 | 0.045553
50 | 0.096309 | 0.046645
51 | 0.32961 | 0.15964
52 | 0.201 | 0.097348
53 | 0.075851 | 0.036736
54 | 0.071931 | 0.034838
55 | 1.5705 | 0.76062
56 | 0.090987 | 0.044067

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1