## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_611_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_611_0_node_2 | 20 | n |  | TRUE
2 | bus_MV_611_0_node_7 | 20 | n |  | TRUE
3 | bus_MV_611_0_node_1 | 20 | n |  | TRUE
4 | bus_MV_611_0_node_3 | 20 | n |  | TRUE
5 | bus_MV_611_0_node_4 | 20 | n |  | TRUE
6 | bus_MV_611_0_node_9 | 20 | n |  | TRUE
7 | bus_MV_611_0_node_10 | 20 | n |  | TRUE
8 | bus_MV_611_0_node_46 | 20 | n |  | TRUE
9 | bus_MV_611_0_node_31 | 20 | n |  | TRUE
10 | bus_MV_611_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_611_0_node_6 | 20 | n |  | TRUE
12 | bus_MV_611_0_node_33 | 20 | n |  | TRUE
13 | bus_MV_611_0_node_8 | 20 | n |  | TRUE
14 | bus_MV_611_0_node_27 | 20 | n |  | TRUE
15 | bus_MV_611_0_node_30 | 20 | n |  | TRUE
16 | bus_MV_611_0_node_35 | 20 | n |  | TRUE
17 | bus_MV_611_0_node_21 | 20 | n |  | TRUE
18 | bus_MV_611_0_node_36 | 20 | n |  | TRUE
19 | bus_MV_611_0_node_32 | 20 | n |  | TRUE
20 | bus_MV_611_0_node_28 | 20 | n |  | TRUE
21 | bus_MV_611_0_node_34 | 20 | n |  | TRUE
22 | bus_MV_611_0_node_22 | 20 | n |  | TRUE
23 | bus_MV_611_0_node_26 | 20 | n |  | TRUE
24 | bus_MV_611_0_node_44 | 20 | n |  | TRUE
25 | bus_MV_611_0_node_38 | 20 | n |  | TRUE
26 | bus_MV_611_0_node_20 | 20 | n |  | TRUE
27 | bus_MV_611_0_node_43 | 20 | n |  | TRUE
28 | bus_MV_611_0_node_17 | 20 | n |  | TRUE
29 | bus_MV_611_0_node_19 | 20 | n |  | TRUE
30 | bus_MV_611_0_node_11 | 20 | n |  | TRUE
31 | bus_MV_611_0_node_12 | 20 | n |  | TRUE
32 | bus_MV_611_0_node_13 | 20 | n |  | TRUE
33 | bus_MV_611_0_node_14 | 20 | n |  | TRUE
34 | bus_MV_611_0_node_15 | 20 | n |  | TRUE
35 | bus_MV_611_0_node_39 | 20 | n |  | TRUE
36 | bus_MV_611_0_node_37 | 20 | n |  | TRUE
37 | bus_MV_611_0_node_40 | 20 | n |  | TRUE
38 | bus_MV_611_0_node_16 | 20 | n |  | TRUE
39 | bus_MV_611_0_node_18 | 20 | n |  | TRUE
40 | bus_MV_611_0_node_25 | 20 | n |  | TRUE
41 | bus_MV_611_0_node_24 | 20 | n |  | TRUE
42 | bus_MV_611_0_node_42 | 20 | n |  | TRUE
43 | bus_MV_611_0_node_45 | 20 | n |  | TRUE
44 | bus_MV_611_0_node_23 | 20 | n |  | TRUE
45 | bus_MV_611_0_node_41 | 20 | n |  | TRUE
46 | bus_MV_611_0_node_29 | 20 | n |  | TRUE
47 | bus_MV_611_0_node_47 | 20 | n |  | TRUE
48 | bus_HV_611_0_node_3 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_611_0_load_0 | 0 | 0.33266 | 0.16111 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_611_0_load_9 | 6 | 0.82074 | 0.3975 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_611_0_load_46 | 8 | 3.1789 | 1.5396 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_611_0_load_31 | 9 | 0.39226 | 0.18998 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_611_0_load_33 | 12 | 0.09931 | 0.048098 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_611_0_load_27 | 14 | 0.13889 | 0.067267 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_611_0_load_30 | 15 | 0.13909 | 0.067364 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_611_0_load_36 | 18 | 0.13798 | 0.066829 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_611_0_load_28 | 20 | 0.6516 | 0.31558 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_611_0_load_34 | 21 | 0.25418 | 0.12311 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_611_0_load_22 | 22 | 1.6756 | 0.81151 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_611_0_load_26 | 23 | 0.16385 | 0.079358 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_611_0_load_38 | 25 | 0.16903 | 0.081867 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_611_0_load_43 | 27 | 0.06959 | 0.033704 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_611_0_load_19 | 29 | 3.3195 | 1.6077 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_611_0_load_11 | 30 | 0.2168 | 0.105 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_611_0_load_13 | 32 | 0.10623 | 0.051449 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_611_0_load_14 | 33 | 0.22975 | 0.11127 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_611_0_load_15 | 34 | 0.32442 | 0.15712 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_611_0_load_37 | 36 | 0.77535 | 0.37552 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_611_0_load_16 | 38 | 0.39453 | 0.19108 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_611_0_load_24 | 41 | 0.075547 | 0.036589 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_611_0_load_45 | 43 | 0.38205 | 0.18504 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_611_0_load_23 | 44 | 0.18184 | 0.08807 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_611_0_load_41 | 45 | 0.17231 | 0.083452 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_611_0_load_29 | 46 | 1.0816 | 0.52386 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_611_0_load_47 | 47 | 0.17809 | 0.086253 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_611_0_line_0 |  | 0 | 1 | 0.012393 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_611_0_line_1 |  | 1 | 2 | 0.10819 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_611_0_line_2 |  | 1 | 3 | 0.086252 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
3 | MV_611_0_line_3 |  | 2 | 9 | 0.15564 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_611_0_line_4 |  | 3 | 4 | 0.08773 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
5 | MV_611_0_line_5 |  | 3 | 5 | 0.10025 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
6 | MV_611_0_line_6 |  | 4 | 6 | 0.13311 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
7 | MV_611_0_line_7 |  | 4 | 7 | 0.27194 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_611_0_line_8 |  | 5 | 8 | 0.00050183 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
9 | MV_611_0_line_9 |  | 6 | 16 | 0.19314 | 0.2376 | 0.344 | 10.3 | 0 | 0.41 | 1 | 1 | ol | TRUE
10 | MV_611_0_line_10 |  | 7 | 17 | 0.14429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_611_0_line_11 |  | 7 | 18 | 0.02119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_611_0_line_12 |  | 8 | 12 | 0.065873 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
13 | MV_611_0_line_13 |  | 8 | 19 | 0.28636 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
14 | MV_611_0_line_14 |  | 10 | 11 | 0.092917 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_611_0_line_15 |  | 10 | 12 | 0.017071 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_611_0_line_16 |  | 11 | 13 | 0.072815 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_611_0_line_17 |  | 11 | 14 | 0.034053 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_611_0_line_18 |  | 13 | 15 | 0.071777 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
19 | MV_611_0_line_19 |  | 14 | 20 | 0.023805 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
20 | MV_611_0_line_20 |  | 16 | 22 | 0.15275 | 0.122 | 0.112 | 304 | 0 | 0.421 | 1 | 1 | cs | TRUE
21 | MV_611_0_line_21 |  | 16 | 23 | 0.15234 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_611_0_line_22 |  | 17 | 24 | 0.006243 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_611_0_line_23 |  | 17 | 25 | 0.065523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
24 | MV_611_0_line_24 |  | 19 | 21 | 0.046117 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
25 | MV_611_0_line_25 |  | 20 | 46 | 0.0076005 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_611_0_line_26 |  | 22 | 39 | 0.0051731 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
27 | MV_611_0_line_27 |  | 23 | 40 | 0.086625 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_611_0_line_28 |  | 24 | 43 | 0.049067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_611_0_line_29 |  | 25 | 36 | 0.045436 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_611_0_line_30 |  | 26 | 27 | 0.057569 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_611_0_line_31 |  | 26 | 28 | 0.14882 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_611_0_line_32 |  | 27 | 42 | 0.068772 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_611_0_line_33 |  | 28 | 29 | 0.0031771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_611_0_line_34 |  | 29 | 39 | 0.10875 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
35 | MV_611_0_line_35 |  | 30 | 31 | 0.060655 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_611_0_line_36 |  | 30 | 32 | 0.13686 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
37 | MV_611_0_line_37 |  | 31 | 33 | 0.14031 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_611_0_line_38 |  | 32 | 34 | 0.03932 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_611_0_line_39 |  | 33 | 35 | 0.089865 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_611_0_line_40 |  | 34 | 36 | 0.0015303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_611_0_line_41 |  | 35 | 37 | 0.28562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_611_0_line_42 |  | 37 | 47 | 0.082886 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_611_0_line_43 |  | 38 | 39 | 0.016114 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_611_0_line_44 |  | 40 | 41 | 0.15498 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_611_0_line_45 |  | 42 | 45 | 0.0066926 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
46 | MV_611_0_line_46 |  | 42 | 44 | 0.20635 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_611_0_trafo_3 | 25 MVA 110/20 kV | 48 | 4 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2588573.8072 | 1223483.4925
1 | 2588585.1681 | 1223488.5179
2 | 2588565.156 | 1223554.3616
3 | 2588616.5496 | 1223408.1773
4 | 2588660.0041 | 1223331.9049
5 | 2588691.3355 | 1223438.3179
6 | 2588784.6903 | 1223378.5184
7 | 2588420.1558 | 1223245.6309
8 | 2588691.7975 | 1223438.514
9 | 2588708.1087 | 1223615.9017
10 | 2588701.8506 | 1223516.4433
11 | 2588755.6265 | 1223552.2505
12 | 2588709.9381 | 1223501.84
13 | 2588801.0366 | 1223571.1753
14 | 2588769.0735 | 1223520.9645
15 | 2588829.2933 | 1223505.1945
16 | 2588864.4447 | 1223202.6188
17 | 2588316.4841 | 1223162.6866
18 | 2588410.2972 | 1223264.3755
19 | 2588701.1722 | 1223724.7215
20 | 2588778.4737 | 1223499.0937
21 | 2588742.0604 | 1223745.7349
22 | 2588720.9087 | 1223150.3608
23 | 2588926.2002 | 1223064.2422
24 | 2588315.524 | 1223156.5183
25 | 2588267.6528 | 1223203.6199
26 | 2588493.6404 | 1223026.5711
27 | 2588516.8377 | 1222973.8826
28 | 2588611.106 | 1223109.6808
29 | 2588614.0709 | 1223110.8225
30 | 2588274.474 | 1223376.7832
31 | 2588246.3257 | 1223429.6699
32 | 2588226.6974 | 1223279.4472
33 | 2588117.9732 | 1223373.1385
34 | 2588244.344 | 1223244.3939
35 | 2588037.3552 | 1223333.433
36 | 2588245.1035 | 1223243.0654
37 | 2587810.846 | 1223204.1315
38 | 2588710.2299 | 1223163.622
39 | 2588716.0478 | 1223148.5911
40 | 2588976.6479 | 1222993.8316
41 | 2588858.783 | 1222893.1946
42 | 2588554.6593 | 1222930.7859
43 | 2588275.7301 | 1223184.3688
44 | 2588653.4793 | 1222749.6347
45 | 2588551.9704 | 1222936.9146
46 | 2588781.475 | 1223492.1108
47 | 2587741.5105 | 1223158.4149
48 | 2588660.0041 | 1223331.9049

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99963 | -0.0049587 | 0.33266 | 0.16111
1 | 0.99964 | -0.0050079 | 0 | 0
2 | 0.99958 | -0.0045343 | 0 | 0
3 | 0.99976 | -0.004203 | 0 | 0
4 | 1 | 0 | -15.6965 | -7.5278
5 | 0.99951 | -0.0084388 | 0 | 0
6 | 0.9996 | -0.0069929 | 0.82074 | 0.3975
7 | 0.99913 | 0.0076661 | 0 | 0
8 | 0.99951 | -0.0084545 | 3.1789 | 1.5396
9 | 0.99951 | -0.0038217 | 0.39226 | 0.18998
10 | 0.9992 | -0.0097779 | 0 | 0
11 | 0.99896 | -0.0075743 | 0 | 0
12 | 0.99924 | -0.010181 | 0.09931 | 0.048098
13 | 0.99895 | -0.0074649 | 0 | 0
14 | 0.99888 | -0.0068124 | 0.13889 | 0.067267
15 | 0.99894 | -0.0073491 | 0.13909 | 0.067364
16 | 0.99842 | -0.045577 | 0 | 0
17 | 0.99869 | 0.011551 | 0 | 0
18 | 0.99913 | 0.0077008 | 0.13798 | 0.066829
19 | 0.99937 | -0.009366 | 0 | 0
20 | 0.99883 | -0.0063184 | 0.6516 | 0.31558
21 | 0.99936 | -0.0092272 | 0.25418 | 0.12311
22 | 0.99802 | -0.052362 | 1.6756 | 0.81151
23 | 0.99837 | -0.045213 | 0.16385 | 0.079358
24 | 0.99869 | 0.011579 | 0 | 0
25 | 0.99853 | 0.013031 | 0.16903 | 0.081867
26 | 0.99714 | -0.056767 | 0 | 0
27 | 0.99711 | -0.056484 | 0.06959 | 0.033704
28 | 0.99722 | -0.057477 | 0 | 0
29 | 0.99722 | -0.057491 | 3.3195 | 1.6077
30 | 0.99827 | 0.015158 | 0.2168 | 0.105
31 | 0.99824 | 0.015397 | 0 | 0
32 | 0.99838 | 0.014284 | 0.10623 | 0.051449
33 | 0.99817 | 0.015972 | 0.22975 | 0.11127
34 | 0.99842 | 0.013988 | 0.32442 | 0.15712
35 | 0.99815 | 0.016107 | 0 | 0
36 | 0.99842 | 0.01397 | 0.77535 | 0.37552
37 | 0.99809 | 0.01662 | 0 | 0
38 | 0.998 | -0.052407 | 0.39453 | 0.19108
39 | 0.99801 | -0.052483 | 0 | 0
40 | 0.99836 | -0.04516 | 0 | 0
41 | 0.99835 | -0.045038 | 0.075547 | 0.036589
42 | 0.99708 | -0.056196 | 0 | 0
43 | 0.99867 | 0.011802 | 0.38205 | 0.18504
44 | 0.99701 | -0.056654 | 0.18184 | 0.08807
45 | 0.99708 | -0.056182 | 0.17231 | 0.083452
46 | 0.99882 | -0.0062198 | 1.0816 | 0.52386
47 | 0.99807 | 0.016792 | 0.17809 | 0.086253
48 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.33266 | -0.16111 | 0.33266 | 0.16082 | 1.8843e-06 | -0.00029512 | 0.010674 | 0.01067 | 0.010674 | 0.99963 | -0.0049587 | 0.99964 | -0.0050079 | 4.8518
1 | 0.39232 | 0.1837 | -0.39229 | -0.18628 | 2.2661e-05 | -0.0025745 | 0.01251 | 0.012542 | 0.012542 | 0.99964 | -0.0050079 | 0.99958 | -0.0045343 | 5.7007
2 | -0.72497 | -0.34452 | 0.72506 | 0.34447 | 8.2563e-05 | -5.1191e-05 | 0.023179 | 0.023178 | 0.023179 | 0.99964 | -0.0050079 | 0.99976 | -0.004203 | 11.0379
3 | 0.39229 | 0.18628 | -0.39226 | -0.18998 | 3.2802e-05 | -0.0037029 | 0.012542 | 0.012588 | 0.012588 | 0.99958 | -0.0045343 | 0.99951 | -0.0038217 | 5.7218
4 | -6.2713 | -3.018 | 6.2726 | 3.0159 | 0.0012964 | -0.0021605 | 0.20096 | 0.20092 | 0.20096 | 0.99976 | -0.004203 | 1 | 0 | 47.7334
5 | 5.5462 | 2.6736 | -5.545 | -2.6763 | 0.00116 | -0.002762 | 0.17778 | 0.17783 | 0.17783 | 0.99976 | -0.004203 | 0.99951 | -0.0084388 | 42.2394
6 | 6.886 | 3.3141 | -6.8836 | -3.317 | 0.0023717 | -0.0029058 | 0.2206 | 0.22067 | 0.22067 | 1 | 0 | 0.9996 | -0.0069929 | 52.4153
7 | 2.5239 | 1.1873 | -2.5216 | -1.1931 | 0.002356 | -0.0057884 | 0.080518 | 0.080598 | 0.080598 | 1 | 0 | 0.99913 | 0.0076661 | 36.6356
8 | 5.545 | 2.6763 | -5.545 | -2.6764 | 7.6647e-06 | -1.1629e-05 | 0.17783 | 0.17783 | 0.17783 | 0.99951 | -0.0084388 | 0.99951 | -0.0084545 | 49.1238
9 | 6.0629 | 2.9195 | -6.0577 | -2.9122 | 0.0051991 | 0.0072778 | 0.19433 | 0.19434 | 0.19434 | 0.9996 | -0.0069929 | 0.99842 | -0.045577 | 47.399
10 | 2.3836 | 1.1268 | -2.3825 | -1.1299 | 0.0011184 | -0.0031059 | 0.076175 | 0.076217 | 0.076217 | 0.99913 | 0.0076661 | 0.99869 | 0.011551 | 34.6443
11 | 0.13799 | 0.066324 | -0.13798 | -0.066829 | 5.543e-07 | -0.00050489 | 0.0044234 | 0.0044297 | 0.0044297 | 0.99913 | 0.0076661 | 0.99913 | 0.0077008 | 2.0135
12 | 2.1119 | 1.0151 | -2.1114 | -1.0148 | 0.00053755 | 0.00025816 | 0.067676 | 0.067677 | 0.067677 | 0.99951 | -0.0084545 | 0.99924 | -0.010181 | 32.2271
13 | 0.25422 | 0.12169 | -0.25418 | -0.12201 | 3.3824e-05 | -0.00032029 | 0.00814 | 0.0081443 | 0.0081443 | 0.99951 | -0.0084545 | 0.99937 | -0.009366 | 3.8782
14 | 2.012 | 0.96709 | -2.0115 | -0.96915 | 0.00051619 | -0.0020613 | 0.064494 | 0.064522 | 0.064522 | 0.9992 | -0.0097779 | 0.99896 | -0.0075743 | 29.3281
15 | -2.012 | -0.96709 | 2.0121 | 0.96671 | 9.4784e-05 | -0.00037883 | 0.064494 | 0.064489 | 0.064494 | 0.9992 | -0.0097779 | 0.99924 | -0.010181 | 29.3155
16 | 0.13909 | 0.06392 | -0.13909 | -0.065655 | 1.9112e-06 | -0.0017343 | 0.0044236 | 0.0044447 | 0.0044447 | 0.99896 | -0.0075743 | 0.99895 | -0.0074649 | 2.0203
17 | 1.8724 | 0.90523 | -1.8722 | -0.90599 | 0.00016423 | -0.00076259 | 0.060099 | 0.060109 | 0.060109 | 0.99896 | -0.0075743 | 0.99888 | -0.0068124 | 27.3224
18 | 0.13909 | 0.065655 | -0.13909 | -0.067364 | 1.9021e-06 | -0.0017096 | 0.0044447 | 0.0044661 | 0.0044661 | 0.99895 | -0.0074649 | 0.99894 | -0.0073491 | 2.03
19 | 1.7333 | 0.83872 | -1.7332 | -0.83926 | 9.8432e-05 | -0.00053788 | 0.055649 | 0.055657 | 0.055657 | 0.99888 | -0.0068124 | 0.99883 | -0.0063184 | 25.2985
20 | 5.8182 | 2.8056 | -5.8163 | -2.8097 | 0.0019508 | -0.0040238 | 0.18676 | 0.18684 | 0.18684 | 0.99842 | -0.045577 | 0.99802 | -0.052362 | 44.3789
21 | 0.23941 | 0.10658 | -0.2394 | -0.1102 | 1.1743e-05 | -0.0036221 | 0.0075771 | 0.0076204 | 0.0076204 | 0.99842 | -0.045577 | 0.99837 | -0.045213 | 3.4638
22 | 0.38206 | 0.18372 | -0.38206 | -0.18387 | 1.2517e-06 | -0.0001483 | 0.012254 | 0.012256 | 0.012256 | 0.99869 | 0.011551 | 0.99869 | 0.011579 | 5.5709
23 | 2.0004 | 0.94614 | -2 | -0.9476 | 0.00035799 | -0.0014539 | 0.063963 | 0.063983 | 0.063983 | 0.99869 | 0.011551 | 0.99853 | 0.013031 | 29.0831
24 | 0.25418 | 0.12201 | -0.25418 | -0.12311 | 4.0906e-06 | -0.0010985 | 0.0081443 | 0.0081581 | 0.0081581 | 0.99937 | -0.009366 | 0.99936 | -0.0092272 | 3.7082
25 | 1.0816 | 0.52368 | -1.0816 | -0.52386 | 1.2241e-05 | -0.00017741 | 0.034732 | 0.034734 | 0.034734 | 0.99883 | -0.0063184 | 0.99882 | -0.0062198 | 15.7884
26 | 4.1407 | 1.9982 | -4.1407 | -1.9983 | 4.4189e-05 | -0.00014465 | 0.13299 | 0.13299 | 0.13299 | 0.99802 | -0.052362 | 0.99801 | -0.052483 | 36.7369
27 | 0.075549 | 0.03084 | -0.075548 | -0.032901 | 6.5006e-07 | -0.0020613 | 0.0023595 | 0.0023826 | 0.0023826 | 0.99837 | -0.045213 | 0.99836 | -0.04516 | 1.083
28 | 0.38206 | 0.18387 | -0.38205 | -0.18504 | 9.8513e-06 | -0.0011655 | 0.012256 | 0.012271 | 0.012271 | 0.99869 | 0.011579 | 0.99867 | 0.011802 | 5.5776
29 | 1.831 | 0.86573 | -1.8308 | -0.86675 | 0.00020801 | -0.0010198 | 0.058553 | 0.058567 | 0.058567 | 0.99853 | 0.013031 | 0.99842 | 0.01397 | 26.6212
30 | 0.42378 | 0.20184 | -0.42376 | -0.2032 | 1.421e-05 | -0.0013624 | 0.013589 | 0.013606 | 0.013606 | 0.99714 | -0.056767 | 0.99711 | -0.056484 | 6.1846
31 | -0.42378 | -0.20184 | 0.42381 | 0.19832 | 3.657e-05 | -0.0035225 | 0.013589 | 0.013545 | 0.013589 | 0.99714 | -0.056767 | 0.99722 | -0.057477 | 6.1768
32 | 0.35417 | 0.1695 | -0.35416 | -0.17113 | 1.1885e-05 | -0.001629 | 0.011367 | 0.011388 | 0.011388 | 0.99711 | -0.056484 | 0.99708 | -0.056196 | 5.1763
33 | -0.42381 | -0.19832 | 0.42382 | 0.19824 | 7.7814e-07 | -7.5204e-05 | 0.013545 | 0.013544 | 0.013545 | 0.99722 | -0.057477 | 0.99722 | -0.057491 | 6.1569
34 | -3.7434 | -1.806 | 3.7462 | 1.8076 | 0.0028046 | 0.0016275 | 0.12031 | 0.12031 | 0.12031 | 0.99722 | -0.057491 | 0.99801 | -0.052483 | 57.2925
35 | 0.40791 | 0.18186 | -0.40789 | -0.1833 | 1.3524e-05 | -0.0014392 | 0.012915 | 0.012932 | 0.012932 | 0.99827 | 0.015158 | 0.99824 | 0.015397 | 5.8781
36 | -0.6247 | -0.28686 | 0.62477 | 0.28363 | 7.2052e-05 | -0.0032353 | 0.019878 | 0.019839 | 0.019878 | 0.99827 | 0.015158 | 0.99838 | 0.014284 | 9.0356
37 | 0.40789 | 0.1833 | -0.40786 | -0.18663 | 3.1422e-05 | -0.0033288 | 0.012932 | 0.012972 | 0.012972 | 0.99824 | 0.015397 | 0.99817 | 0.015972 | 5.8962
38 | -0.731 | -0.33507 | 0.73103 | 0.33415 | 2.8364e-05 | -0.0009274 | 0.023251 | 0.02324 | 0.023251 | 0.99838 | 0.014284 | 0.99842 | 0.013988 | 10.5687
39 | 0.17811 | 0.075356 | -0.17811 | -0.077493 | 3.7693e-06 | -0.0021366 | 0.0055931 | 0.0056175 | 0.0056175 | 0.99817 | 0.015972 | 0.99815 | 0.016107 | 2.5534
40 | -1.0554 | -0.49127 | 1.0555 | 0.49123 | 2.3146e-06 | -3.5735e-05 | 0.03366 | 0.03366 | 0.03366 | 0.99842 | 0.013988 | 0.99842 | 0.01397 | 15.3001
41 | 0.17811 | 0.077493 | -0.17809 | -0.084283 | 1.2204e-05 | -0.0067901 | 0.0056175 | 0.0056987 | 0.0056987 | 0.99815 | 0.016107 | 0.99809 | 0.01662 | 2.5903
42 | 0.17809 | 0.084283 | -0.17809 | -0.086253 | 3.609e-06 | -0.0019703 | 0.0056987 | 0.0057233 | 0.0057233 | 0.99809 | 0.01662 | 0.99807 | 0.016792 | 2.6015
43 | -0.39453 | -0.19108 | 0.39453 | 0.1907 | 3.4574e-06 | -0.00038218 | 0.01268 | 0.012675 | 0.01268 | 0.998 | -0.052407 | 0.99801 | -0.052483 | 5.7635
44 | 0.075548 | 0.032901 | -0.075547 | -0.036589 | 1.1962e-06 | -0.0036879 | 0.0023826 | 0.0024272 | 0.0024272 | 0.99836 | -0.04516 | 0.99835 | -0.045038 | 1.1033
45 | 0.17231 | 0.083293 | -0.17231 | -0.083452 | 2.7442e-07 | -0.00015878 | 0.0055409 | 0.0055429 | 0.0055429 | 0.99708 | -0.056196 | 0.99708 | -0.056182 | 2.5195
46 | 0.18185 | 0.087833 | -0.18184 | -0.08807 | 1.2576e-05 | -0.00023701 | 0.005847 | 0.0058501 | 0.0058501 | 0.99708 | -0.056196 | 0.99701 | -0.056654 | 2.7858

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 15.6965 | 7.5278

## res_load
| p_mw | q_mvar
0 | 0.33266 | 0.16111
1 | 0.82074 | 0.3975
2 | 3.1789 | 1.5396
3 | 0.39226 | 0.18998
4 | 0.09931 | 0.048098
5 | 0.13889 | 0.067267
6 | 0.13909 | 0.067364
7 | 0.13798 | 0.066829
8 | 0.6516 | 0.31558
9 | 0.25418 | 0.12311
10 | 1.6756 | 0.81151
11 | 0.16385 | 0.079358
12 | 0.16903 | 0.081867
13 | 0.06959 | 0.033704
14 | 3.3195 | 1.6077
15 | 0.2168 | 0.105
16 | 0.10623 | 0.051449
17 | 0.22975 | 0.11127
18 | 0.32442 | 0.15712
19 | 0.77535 | 0.37552
20 | 0.39453 | 0.19108
21 | 0.075547 | 0.036589
22 | 0.38205 | 0.18504
23 | 0.18184 | 0.08807
24 | 0.17231 | 0.083452
25 | 1.0816 | 0.52386
26 | 0.17809 | 0.086253

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1