## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_613_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_613_0_node_1 | 20 | n |  | TRUE
2 | bus_MV_613_0_node_2 | 20 | n |  | TRUE
3 | bus_MV_613_0_node_4 | 20 | n |  | TRUE
4 | bus_MV_613_0_node_8 | 20 | n |  | TRUE
5 | bus_MV_613_0_node_6 | 20 | n |  | TRUE
6 | bus_MV_613_0_node_3 | 20 | n |  | TRUE
7 | bus_MV_613_0_node_18 | 20 | n |  | TRUE
8 | bus_MV_613_0_node_5 | 20 | n |  | TRUE
9 | bus_MV_613_0_node_58 | 20 | n |  | TRUE
10 | bus_MV_613_0_node_113 | 20 | n |  | TRUE
11 | bus_MV_613_0_node_21 | 20 | n |  | TRUE
12 | bus_MV_613_0_node_55 | 20 | n |  | TRUE
13 | bus_MV_613_0_node_9 | 20 | n |  | TRUE
14 | bus_MV_613_0_node_10 | 20 | n |  | TRUE
15 | bus_MV_613_0_node_11 | 20 | n |  | TRUE
16 | bus_MV_613_0_node_24 | 20 | n |  | TRUE
17 | bus_MV_613_0_node_93 | 20 | n |  | TRUE
18 | bus_MV_613_0_node_99 | 20 | n |  | TRUE
19 | bus_MV_613_0_node_98 | 20 | n |  | TRUE
20 | bus_MV_613_0_node_51 | 20 | n |  | TRUE
21 | bus_MV_613_0_node_53 | 20 | n |  | TRUE
22 | bus_MV_613_0_node_110 | 20 | n |  | TRUE
23 | bus_MV_613_0_node_106 | 20 | n |  | TRUE
24 | bus_MV_613_0_node_107 | 20 | n |  | TRUE
25 | bus_MV_613_0_node_13 | 20 | n |  | TRUE
26 | bus_MV_613_0_node_14 | 20 | n |  | TRUE
27 | bus_MV_613_0_node_15 | 20 | n |  | TRUE
28 | bus_MV_613_0_node_17 | 20 | n |  | TRUE
29 | bus_MV_613_0_node_34 | 20 | n |  | TRUE
30 | bus_MV_613_0_node_112 | 20 | n |  | TRUE
31 | bus_MV_613_0_node_33 | 20 | n |  | TRUE
32 | bus_MV_613_0_node_27 | 20 | n |  | TRUE
33 | bus_MV_613_0_node_16 | 20 | n |  | TRUE
34 | bus_MV_613_0_node_96 | 20 | n |  | TRUE
35 | bus_MV_613_0_node_95 | 20 | n |  | TRUE
36 | bus_MV_613_0_node_89 | 20 | n |  | TRUE
37 | bus_MV_613_0_node_88 | 20 | n |  | TRUE
38 | bus_MV_613_0_node_100 | 20 | n |  | TRUE
39 | bus_MV_613_0_node_87 | 20 | n |  | TRUE
40 | bus_MV_613_0_node_19 | 20 | n |  | TRUE
41 | bus_MV_613_0_node_20 | 20 | n |  | TRUE
42 | bus_MV_613_0_node_23 | 20 | n |  | TRUE
43 | bus_MV_613_0_node_22 | 20 | n |  | TRUE
44 | bus_MV_613_0_node_80 | 20 | n |  | TRUE
45 | bus_MV_613_0_node_90 | 20 | n |  | TRUE
46 | bus_MV_613_0_node_69 | 20 | n |  | TRUE
47 | bus_MV_613_0_node_94 | 20 | n |  | TRUE
48 | bus_MV_613_0_node_109 | 20 | n |  | TRUE
49 | bus_MV_613_0_node_25 | 20 | n |  | TRUE
50 | bus_MV_613_0_node_26 | 20 | n |  | TRUE
51 | bus_MV_613_0_node_35 | 20 | n |  | TRUE
52 | bus_MV_613_0_node_36 | 20 | n |  | TRUE
53 | bus_MV_613_0_node_57 | 20 | n |  | TRUE
54 | bus_MV_613_0_node_74 | 20 | n |  | TRUE
55 | bus_MV_613_0_node_73 | 20 | n |  | TRUE
56 | bus_MV_613_0_node_28 | 20 | n |  | TRUE
57 | bus_MV_613_0_node_29 | 20 | n |  | TRUE
58 | bus_MV_613_0_node_30 | 20 | n |  | TRUE
59 | bus_MV_613_0_node_31 | 20 | n |  | TRUE
60 | bus_MV_613_0_node_32 | 20 | n |  | TRUE
61 | bus_MV_613_0_node_40 | 20 | n |  | TRUE
62 | bus_MV_613_0_node_42 | 20 | n |  | TRUE
63 | bus_MV_613_0_node_38 | 20 | n |  | TRUE
64 | bus_MV_613_0_node_77 | 20 | n |  | TRUE
65 | bus_MV_613_0_node_76 | 20 | n |  | TRUE
66 | bus_MV_613_0_node_78 | 20 | n |  | TRUE
67 | bus_MV_613_0_node_63 | 20 | n |  | TRUE
68 | bus_MV_613_0_node_37 | 20 | n |  | TRUE
69 | bus_MV_613_0_node_39 | 20 | n |  | TRUE
70 | bus_MV_613_0_node_41 | 20 | n |  | TRUE
71 | bus_MV_613_0_node_43 | 20 | n |  | TRUE
72 | bus_MV_613_0_node_54 | 20 | n |  | TRUE
73 | bus_MV_613_0_node_50 | 20 | n |  | TRUE
74 | bus_MV_613_0_node_44 | 20 | n |  | TRUE
75 | bus_MV_613_0_node_45 | 20 | n |  | TRUE
76 | bus_MV_613_0_node_46 | 20 | n |  | TRUE
77 | bus_MV_613_0_node_64 | 20 | n |  | TRUE
78 | bus_MV_613_0_node_47 | 20 | n |  | TRUE
79 | bus_MV_613_0_node_65 | 20 | n |  | TRUE
80 | bus_MV_613_0_node_66 | 20 | n |  | TRUE
81 | bus_MV_613_0_node_48 | 20 | n |  | TRUE
82 | bus_MV_613_0_node_52 | 20 | n |  | TRUE
83 | bus_MV_613_0_node_49 | 20 | n |  | TRUE
84 | bus_MV_613_0_node_72 | 20 | n |  | TRUE
85 | bus_MV_613_0_node_111 | 20 | n |  | TRUE
86 | bus_MV_613_0_node_115 | 20 | n |  | TRUE
87 | bus_MV_613_0_node_59 | 20 | n |  | TRUE
88 | bus_MV_613_0_node_60 | 20 | n |  | TRUE
89 | bus_MV_613_0_node_62 | 20 | n |  | TRUE
90 | bus_MV_613_0_node_61 | 20 | n |  | TRUE
91 | bus_MV_613_0_node_67 | 20 | n |  | TRUE
92 | bus_MV_613_0_node_105 | 20 | n |  | TRUE
93 | bus_MV_613_0_node_68 | 20 | n |  | TRUE
94 | bus_MV_613_0_node_104 | 20 | n |  | TRUE
95 | bus_MV_613_0_node_97 | 20 | n |  | TRUE
96 | bus_MV_613_0_node_71 | 20 | n |  | TRUE
97 | bus_MV_613_0_node_70 | 20 | n |  | TRUE
98 | bus_MV_613_0_node_79 | 20 | n |  | TRUE
99 | bus_MV_613_0_node_84 | 20 | n |  | TRUE
100 | bus_MV_613_0_node_81 | 20 | n |  | TRUE
101 | bus_MV_613_0_node_82 | 20 | n |  | TRUE
102 | bus_MV_613_0_node_114 | 20 | n |  | TRUE
103 | bus_MV_613_0_node_75 | 20 | n |  | TRUE
104 | bus_MV_613_0_node_86 | 20 | n |  | TRUE
105 | bus_MV_613_0_node_83 | 20 | n |  | TRUE
106 | bus_MV_613_0_node_102 | 20 | n |  | TRUE
107 | bus_MV_613_0_node_92 | 20 | n |  | TRUE
108 | bus_MV_613_0_node_108 | 20 | n |  | TRUE
109 | bus_MV_613_0_node_103 | 20 | n |  | TRUE
110 | bus_HV_613_0_node_49 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_613_0_load_0 | 0 | 0.3683 | 0.17838 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_613_0_load_8 | 4 | 0.40416 | 0.19574 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_613_0_load_6 | 5 | 0.26619 | 0.12892 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_613_0_load_18 | 7 | 0.25594 | 0.12396 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_613_0_load_58 | 9 | 0.096224 | 0.046603 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_613_0_load_113 | 10 | 0.35283 | 0.17089 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_613_0_load_9 | 13 | 0.16804 | 0.081383 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_613_0_load_24 | 16 | 0.38355 | 0.18576 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_613_0_load_93 | 17 | 0.22503 | 0.10899 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_613_0_load_99 | 18 | 0.38696 | 0.18741 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_613_0_load_110 | 22 | 0.7797 | 0.37763 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_613_0_load_106 | 23 | 0.74701 | 0.36179 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_613_0_load_107 | 24 | 0.78037 | 0.37795 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_613_0_load_13 | 25 | 0.37668 | 0.18243 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_613_0_load_112 | 30 | 0.078375 | 0.037959 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_613_0_load_33 | 31 | 0.077514 | 0.037542 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_613_0_load_96 | 34 | 0.19482 | 0.094358 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_613_0_load_95 | 35 | 0.072074 | 0.034907 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_613_0_load_89 | 36 | 0.19195 | 0.092963 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_613_0_load_87 | 39 | 0.26333 | 0.12754 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_613_0_load_19 | 40 | 0.35497 | 0.17192 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_613_0_load_80 | 44 | 0.11325 | 0.05485 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_613_0_load_90 | 45 | 0.10479 | 0.050753 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_613_0_load_109 | 48 | 0.42557 | 0.20611 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_613_0_load_25 | 49 | 0.26807 | 0.12983 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_613_0_load_26 | 50 | 0.33508 | 0.16228 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_613_0_load_57 | 53 | 0.20759 | 0.10054 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_613_0_load_73 | 55 | 0.10311 | 0.049937 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_613_0_load_28 | 56 | 1.2614 | 0.61094 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_613_0_load_29 | 57 | 0.1353 | 0.065531 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_613_0_load_31 | 59 | 0.19265 | 0.093303 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_613_0_load_32 | 60 | 0.15009 | 0.072692 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_613_0_load_42 | 62 | 0.3821 | 0.18506 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_613_0_load_38 | 63 | 0.8762 | 0.42436 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_613_0_load_78 | 66 | 0.12106 | 0.058632 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_613_0_load_37 | 68 | 0.96835 | 0.46899 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_613_0_load_43 | 71 | 0.096656 | 0.046812 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_613_0_load_44 | 74 | 1.0691 | 0.5178 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_613_0_load_45 | 75 | 0.35637 | 0.1726 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_613_0_load_65 | 79 | 0.072785 | 0.035251 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_613_0_load_48 | 81 | 0.10685 | 0.051748 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_613_0_load_49 | 83 | 0.097928 | 0.047429 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_613_0_load_72 | 84 | 0.11087 | 0.053695 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_613_0_load_111 | 85 | 1.2214 | 0.59157 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_613_0_load_115 | 86 | 0.41065 | 0.19889 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_613_0_load_59 | 87 | 0.1488 | 0.072065 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_613_0_load_67 | 91 | 0.1292 | 0.062574 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_613_0_load_105 | 92 | 0.13572 | 0.065733 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_613_0_load_97 | 95 | 0.35247 | 0.17071 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_613_0_load_79 | 98 | 0.14223 | 0.068884 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_613_0_load_84 | 99 | 0.37248 | 0.1804 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_613_0_load_81 | 100 | 0.086523 | 0.041905 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_613_0_load_82 | 101 | 0.090125 | 0.043649 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_613_0_load_114 | 102 | 0.40064 | 0.19404 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_613_0_load_75 | 103 | 0.074921 | 0.036286 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_613_0_load_102 | 106 | 0.10508 | 0.050891 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_613_0_load_108 | 108 | 1.2522 | 0.60646 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_613_0_load_103 | 109 | 0.10523 | 0.050967 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 83 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_613_0_line_0 |  | 0 | 1 | 0.004674 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
1 | MV_613_0_line_1 |  | 1 | 2 | 0.19026 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_613_0_line_2 |  | 1 | 3 | 0.47578 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_613_0_line_3 |  | 2 | 4 | 0.026371 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
4 | MV_613_0_line_4 |  | 2 | 5 | 0.65732 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
5 | MV_613_0_line_5 |  | 3 | 8 | 0.1635 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
6 | MV_613_0_line_6 |  | 3 | 9 | 0.035086 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
7 | MV_613_0_line_7 |  | 3 | 6 | 0.021342 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_613_0_line_8 |  | 6 | 7 | 0.006735 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_613_0_line_9 |  | 8 | 10 | 0.006212 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
10 | MV_613_0_line_10 |  | 9 | 11 | 0.029728 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
11 | MV_613_0_line_11 |  | 10 | 12 | 0.022145 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
12 | MV_613_0_line_12 |  | 11 | 43 | 0.031992 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
13 | MV_613_0_line_13 |  | 11 | 41 | 0.086068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_613_0_line_14 |  | 12 | 21 | 0.24364 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
15 | MV_613_0_line_15 |  | 13 | 14 | 0.063524 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
16 | MV_613_0_line_16 |  | 14 | 15 | 0.1468 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
17 | MV_613_0_line_17 |  | 15 | 18 | 0.048913 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_613_0_line_18 |  | 16 | 17 | 0.36265 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
19 | MV_613_0_line_19 |  | 17 | 47 | 0.039739 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
20 | MV_613_0_line_20 |  | 17 | 48 | 0.10928 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
21 | MV_613_0_line_21 |  | 18 | 19 | 0.059368 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_613_0_line_22 |  | 19 | 95 | 0.041941 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_613_0_line_23 |  | 20 | 21 | 0.10296 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
24 | MV_613_0_line_24 |  | 20 | 22 | 0.030874 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
25 | MV_613_0_line_25 |  | 21 | 84 | 0.069759 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_613_0_line_26 |  | 21 | 82 | 0.03365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
27 | MV_613_0_line_27 |  | 22 | 85 | 0.021326 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
28 | MV_613_0_line_28 |  | 23 | 24 | 0.00025876 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_613_0_line_29 |  | 24 | 108 | 0.019371 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_613_0_line_30 |  | 25 | 26 | 0.03445 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_613_0_line_31 |  | 26 | 27 | 0.071085 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_613_0_line_32 |  | 26 | 28 | 0.050098 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
33 | MV_613_0_line_33 |  | 27 | 30 | 0.0052793 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
34 | MV_613_0_line_34 |  | 28 | 36 | 0.024562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
35 | MV_613_0_line_35 |  | 28 | 37 | 0.006507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
36 | MV_613_0_line_36 |  | 29 | 30 | 0.054178 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_613_0_line_37 |  | 29 | 31 | 0.10429 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
38 | MV_613_0_line_38 |  | 29 | 32 | 0.12335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
39 | MV_613_0_line_39 |  | 31 | 34 | 0.14129 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
40 | MV_613_0_line_40 |  | 32 | 50 | 0.007795 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
41 | MV_613_0_line_41 |  | 33 | 34 | 0.006857 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
42 | MV_613_0_line_42 |  | 33 | 35 | 0.032562 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
43 | MV_613_0_line_43 |  | 36 | 38 | 0.059021 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
44 | MV_613_0_line_44 |  | 37 | 39 | 0.015958 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_613_0_line_45 |  | 38 | 64 | 0.040335 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_613_0_line_46 |  | 40 | 41 | 0.004706 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_613_0_line_47 |  | 41 | 42 | 0.065167 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_613_0_line_48 |  | 42 | 45 | 0.011723 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_613_0_line_49 |  | 43 | 44 | 0.018424 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
50 | MV_613_0_line_50 |  | 44 | 46 | 0.028569 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
51 | MV_613_0_line_51 |  | 46 | 93 | 0.098657 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
52 | MV_613_0_line_52 |  | 47 | 57 | 0.091233 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
53 | MV_613_0_line_53 |  | 48 | 108 | 0.045618 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
54 | MV_613_0_line_54 |  | 48 | 107 | 0.035169 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
55 | MV_613_0_line_55 |  | 49 | 50 | 0.074186 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_613_0_line_56 |  | 51 | 52 | 0.12653 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_613_0_line_57 |  | 51 | 53 | 0.016423 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_613_0_line_58 |  | 52 | 54 | 0.046656 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_613_0_line_59 |  | 52 | 55 | 0.010543 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_613_0_line_60 |  | 54 | 64 | 0.037019 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_613_0_line_61 |  | 54 | 65 | 0.024157 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_613_0_line_62 |  | 54 | 66 | 0.0026931 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_613_0_line_63 |  | 55 | 67 | 0.0064542 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_613_0_line_64 |  | 56 | 57 | 0.00071326 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
65 | MV_613_0_line_65 |  | 56 | 58 | 0.058099 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
66 | MV_613_0_line_66 |  | 58 | 59 | 0.014318 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
67 | MV_613_0_line_67 |  | 59 | 60 | 0.014972 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
68 | MV_613_0_line_68 |  | 60 | 61 | 0.047415 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
69 | MV_613_0_line_69 |  | 61 | 62 | 0.019769 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_613_0_line_70 |  | 61 | 63 | 0.037293 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
71 | MV_613_0_line_71 |  | 63 | 68 | 0.0036455 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
72 | MV_613_0_line_72 |  | 64 | 102 | 0.010828 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_613_0_line_73 |  | 65 | 103 | 0.0024068 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
74 | MV_613_0_line_74 |  | 67 | 88 | 0.035468 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_613_0_line_75 |  | 68 | 69 | 0.033354 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
76 | MV_613_0_line_76 |  | 69 | 70 | 0.021345 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
77 | MV_613_0_line_77 |  | 70 | 71 | 0.012001 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
78 | MV_613_0_line_78 |  | 71 | 72 | 0.03009 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
79 | MV_613_0_line_79 |  | 72 | 73 | 0.073996 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
80 | MV_613_0_line_80 |  | 73 | 83 | 0.0047132 | 0.0515 | 0.029 | 1000 | 0 | 1.276 | 1 | 1 | cs | TRUE
81 | MV_613_0_line_81 |  | 74 | 75 | 0.0068571 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_613_0_line_82 |  | 74 | 76 | 0.049981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
83 | MV_613_0_line_83 |  | 75 | 77 | 0.070218 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_613_0_line_84 |  | 76 | 78 | 0.035916 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
85 | MV_613_0_line_85 |  | 77 | 79 | 0.014067 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_613_0_line_86 |  | 77 | 80 | 0.10146 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_613_0_line_87 |  | 78 | 81 | 0.032199 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_613_0_line_88 |  | 79 | 95 | 0.069809 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
89 | MV_613_0_line_89 |  | 80 | 86 | 0.041607 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
90 | MV_613_0_line_90 |  | 81 | 82 | 0.023472 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_613_0_line_91 |  | 85 | 107 | 0.055004 | 0.0595 | 0.16 | 22 | 0 | 1.29 | 1 | 1 | ol | TRUE
92 | MV_613_0_line_92 |  | 87 | 88 | 0.02074 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_613_0_line_93 |  | 88 | 89 | 0.050813 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_613_0_line_94 |  | 89 | 92 | 0.022705 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_613_0_line_95 |  | 89 | 90 | 0.033072 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
96 | MV_613_0_line_96 |  | 90 | 91 | 0.030891 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_613_0_line_97 |  | 91 | 93 | 0.010392 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
98 | MV_613_0_line_98 |  | 92 | 94 | 0.028977 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
99 | MV_613_0_line_99 |  | 93 | 96 | 0.15077 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
100 | MV_613_0_line_100 |  | 94 | 109 | 0.049058 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
101 | MV_613_0_line_101 |  | 96 | 100 | 0.02981 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
102 | MV_613_0_line_102 |  | 97 | 98 | 0.0064855 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
103 | MV_613_0_line_103 |  | 97 | 99 | 0.095978 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
104 | MV_613_0_line_104 |  | 99 | 101 | 0.033027 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_613_0_line_105 |  | 101 | 105 | 0.016476 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
106 | MV_613_0_line_106 |  | 102 | 104 | 0.041685 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
107 | MV_613_0_line_107 |  | 104 | 106 | 0.019748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
108 | MV_613_0_line_108 |  | 104 | 105 | 0.045982 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_613_0_trafo_49 | 25 MVA 110/20 kV | 110 | 83 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2665135.0679 | 1258545.4221
1 | 2665130.9941 | 1258547.7345
2 | 2664998.7926 | 1258662.3765
3 | 2665317.342 | 1258736.6254
4 | 2665016.5353 | 1258681.8856
5 | 2664364.9186 | 1258488.3692
6 | 2665303.9385 | 1258728.416
7 | 2665298.0934 | 1258725.2492
8 | 2665268.3216 | 1258856.6059
9 | 2665318.7833 | 1258701.5819
10 | 2665273.6919 | 1258859.7563
11 | 2665324.4429 | 1258672.4902
12 | 2665271.9161 | 1258877.9056
13 | 2665063.4789 | 1259278.1821
14 | 2665034.5581 | 1259247.1304
15 | 2665015.9934 | 1259150.3112
16 | 2665169.8062 | 1259632.1334
17 | 2665259.5649 | 1259280.7683
18 | 2664973.6086 | 1259125.8968
19 | 2664922.1647 | 1259096.2641
20 | 2665225.2448 | 1259081.0622
21 | 2665168.1705 | 1259041.6381
22 | 2665254.5089 | 1259090.9013
23 | 2665232.8715 | 1259154.3401
24 | 2665233.1156 | 1259154.4259
25 | 2665617.1677 | 1258913.5241
26 | 2665584.1514 | 1258923.3561
27 | 2665546.0841 | 1258951.1216
28 | 2665572.5925 | 1258874.6146
29 | 2665492.1618 | 1258957.9854
30 | 2665544.9875 | 1258945.9574
31 | 2665481.7937 | 1259046.9299
32 | 2665395.798 | 1258947.8795
33 | 2665619.4138 | 1259098.2083
34 | 2665612.7609 | 1259099.947
35 | 2665628.0296 | 1259129.61
36 | 2665573.2478 | 1258851.2124
37 | 2665566.3304 | 1258876.4466
38 | 2665548.3986 | 1258801.4153
39 | 2665550.987 | 1258880.8303
40 | 2665299.9358 | 1258608.8622
41 | 2665299.7407 | 1258613.5635
42 | 2665346.7396 | 1258630.4166
43 | 2665346.0718 | 1258663.5779
44 | 2665355.2291 | 1258647.5902
45 | 2665352.98 | 1258620.493
46 | 2665372.155 | 1258624.7486
47 | 2665299.2144 | 1259283.4147
48 | 2665294.0277 | 1259177.0676
49 | 2665318.8068 | 1258968.7184
50 | 2665391.6093 | 1258954.4602
51 | 2665438.4153 | 1258871.272
52 | 2665459.7563 | 1258775.9159
53 | 2665426.9999 | 1258883.0545
54 | 2665505.6462 | 1258767.4951
55 | 2665457.8333 | 1258765.5499
56 | 2665334.9056 | 1259198.8256
57 | 2665334.2963 | 1259199.1965
58 | 2665384.6272 | 1259168.7734
59 | 2665370.9251 | 1259164.4857
60 | 2665376.7872 | 1259150.7084
61 | 2665395.3799 | 1259107.0915
62 | 2665403.5703 | 1259089.0989
63 | 2665360.0165 | 1259095.251
64 | 2665542.1836 | 1258761.5618
65 | 2665519.1742 | 1258766.4774
66 | 2665505.119 | 1258764.8542
67 | 2665456.6619 | 1258759.2028
68 | 2665356.5597 | 1259094.0936
69 | 2665324.9561 | 1259083.43
70 | 2665333.0216 | 1259063.66
71 | 2665322.0407 | 1259058.8182
72 | 2665294.508 | 1259046.6783
73 | 2665243.1801 | 1259034.4034
74 | 2665052.7313 | 1259027.713
75 | 2665046.8449 | 1259024.196
76 | 2665095.6371 | 1259053.3487
77 | 2664986.5668 | 1258988.1805
78 | 2665125.5552 | 1259073.3035
79 | 2664979.3664 | 1259000.2647
80 | 2665016.0129 | 1258907.089
81 | 2665141.8967 | 1259045.559
82 | 2665153.8088 | 1259025.3348
83 | 2665247.6399 | 1259035.928
84 | 2665134.0435 | 1259102.2745
85 | 2665274.7227 | 1259097.6975
86 | 2665051.5829 | 1258928.6732
87 | 2665430.7132 | 1258768.7833
88 | 2665429.8732 | 1258748.6768
89 | 2665383.2302 | 1258750.8742
90 | 2665380.1216 | 1258725.8772
91 | 2665395.6529 | 1258699.1747
92 | 2665375.712 | 1258772.0426
93 | 2665400.8779 | 1258690.1914
94 | 2665363.3627 | 1258798.2562
95 | 2664943.633 | 1259060.2347
96 | 2665410.0993 | 1258580.2685
97 | 2665514.9297 | 1258569.7532
98 | 2665521.4124 | 1258569.9448
99 | 2665508.7579 | 1258665.5327
100 | 2665390.4006 | 1258600.4801
101 | 2665519.7334 | 1258696.6598
102 | 2665542.2891 | 1258758.8388
103 | 2665516.8007 | 1258766.8769
104 | 2665545.4936 | 1258717.2772
105 | 2665524.4314 | 1258712.4516
106 | 2665564.7565 | 1258713.8849
107 | 2665304.9636 | 1259143.6424
108 | 2665251.389 | 1259160.8532
109 | 2665342.5499 | 1258842.6799
110 | 2665247.6399 | 1259035.928

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99625 | -0.070916 | 0.3683 | 0.17838
1 | 0.99625 | -0.070937 | 0 | 0
2 | 0.99609 | -0.069437 | 0 | 0
3 | 0.99688 | -0.076553 | 0 | 0
4 | 0.99607 | -0.069566 | 0.40416 | 0.19574
5 | 0.99575 | -0.07159 | 0.26619 | 0.12892
6 | 0.99687 | -0.076488 | 0 | 0
7 | 0.99687 | -0.076467 | 0.25594 | 0.12396
8 | 0.99704 | -0.075868 | 0 | 0
9 | 0.99685 | -0.076666 | 0.096224 | 0.046603
10 | 0.99705 | -0.075842 | 0.35283 | 0.17089
11 | 0.99683 | -0.076759 | 0 | 0
12 | 0.99707 | -0.075742 | 0 | 0
13 | 0.99622 | -0.069438 | 0.16804 | 0.081383
14 | 0.99623 | -0.069564 | 0 | 0
15 | 0.99626 | -0.069831 | 0 | 0
16 | 0.99812 | -0.032652 | 0.38355 | 0.18576
17 | 0.99839 | -0.030959 | 0.22503 | 0.10899
18 | 0.99627 | -0.069912 | 0.38696 | 0.18741
19 | 0.99631 | -0.070283 | 0 | 0
20 | 0.99748 | -0.073932 | 0 | 0
21 | 0.99732 | -0.07462 | 0 | 0
22 | 0.99753 | -0.073725 | 0.7797 | 0.37763
23 | 0.99756 | -0.062509 | 0.74701 | 0.36179
24 | 0.99756 | -0.062511 | 0.78037 | 0.37795
25 | 0.99498 | -0.06768 | 0.37668 | 0.18243
26 | 0.995 | -0.067836 | 0 | 0
27 | 0.9949 | -0.06699 | 0 | 0
28 | 0.99509 | -0.068652 | 0 | 0
29 | 0.9948 | -0.067585 | 0 | 0
30 | 0.9949 | -0.066926 | 0.078375 | 0.037959
31 | 0.99475 | -0.067166 | 0.077514 | 0.037542
32 | 0.9947 | -0.066699 | 0 | 0
33 | 0.99468 | -0.067634 | 0 | 0
34 | 0.99468 | -0.067639 | 0.19482 | 0.094358
35 | 0.99467 | -0.067606 | 0.072074 | 0.034907
36 | 0.99514 | -0.069129 | 0.19195 | 0.092963
37 | 0.99508 | -0.068632 | 0 | 0
38 | 0.99528 | -0.070406 | 0 | 0
39 | 0.99508 | -0.068581 | 0.26333 | 0.12754
40 | 0.99678 | -0.076279 | 0.35497 | 0.17192
41 | 0.99678 | -0.076299 | 0 | 0
42 | 0.99677 | -0.076221 | 0 | 0
43 | 0.99681 | -0.076848 | 0 | 0
44 | 0.9968 | -0.076899 | 0.11325 | 0.05485
45 | 0.99677 | -0.076206 | 0.10479 | 0.050753
46 | 0.99678 | -0.076976 | 0 | 0
47 | 0.99849 | -0.030557 | 0 | 0
48 | 0.99784 | -0.061325 | 0.42557 | 0.20611
49 | 0.99466 | -0.066886 | 0.26807 | 0.12983
50 | 0.9947 | -0.066642 | 0.33508 | 0.16228
51 | 0.99572 | -0.072157 | 0 | 0
52 | 0.99575 | -0.072459 | 0 | 0
53 | 0.99571 | -0.072117 | 0.20759 | 0.10054
54 | 0.99556 | -0.070733 | 0 | 0
55 | 0.9958 | -0.072873 | 0.10311 | 0.049937
56 | 0.99896 | -0.0041746 | 1.2614 | 0.61094
57 | 0.99896 | -0.0041818 | 0.1353 | 0.065531
58 | 0.99912 | -0.003541 | 0 | 0
59 | 0.99916 | -0.0033843 | 0.19265 | 0.093303
60 | 0.9992 | -0.0032187 | 0.15009 | 0.072692
61 | 0.99933 | -0.0026888 | 0 | 0
62 | 0.99932 | -0.0025986 | 0.3821 | 0.18506
63 | 0.99944 | -0.0022621 | 0.8762 | 0.42436
64 | 0.99542 | -0.069446 | 0 | 0
65 | 0.99556 | -0.070711 | 0 | 0
66 | 0.99556 | -0.070729 | 0.12106 | 0.058632
67 | 0.99583 | -0.073134 | 0 | 0
68 | 0.99945 | -0.0022185 | 0.96835 | 0.46899
69 | 0.99955 | -0.0018001 | 0 | 0
70 | 0.99962 | -0.0015318 | 0 | 0
71 | 0.99966 | -0.0013807 | 0.096656 | 0.046812
72 | 0.99975 | -0.00099988 | 0 | 0
73 | 0.99999 | -6.0022e-05 | 0 | 0
74 | 0.99669 | -0.06876 | 1.0691 | 0.5178
75 | 0.99667 | -0.06862 | 0.35637 | 0.1726
76 | 0.99687 | -0.070416 | 0 | 0
77 | 0.99648 | -0.069878 | 0 | 0
78 | 0.997 | -0.071603 | 0 | 0
79 | 0.99647 | -0.06972 | 0.072785 | 0.035251
80 | 0.99643 | -0.069384 | 0 | 0
81 | 0.99711 | -0.072666 | 0.10685 | 0.051748
82 | 0.9972 | -0.073469 | 0 | 0
83 | 1 | 0 | -19.3689 | -9.1828
84 | 0.99732 | -0.07453 | 0.11087 | 0.053695
85 | 0.99757 | -0.073571 | 1.2214 | 0.59157
86 | 0.9964 | -0.069592 | 0.41065 | 0.19889
87 | 0.99598 | -0.074531 | 0.1488 | 0.072065
88 | 0.99598 | -0.074568 | 0 | 0
89 | 0.99622 | -0.076707 | 0 | 0
90 | 0.99638 | -0.078188 | 0 | 0
91 | 0.99653 | -0.07957 | 0.1292 | 0.062574
92 | 0.99621 | -0.076645 | 0.13572 | 0.065733
93 | 0.99656 | -0.079328 | 0 | 0
94 | 0.99621 | -0.076611 | 0 | 0
95 | 0.99634 | -0.070542 | 0.35247 | 0.17071
96 | 0.99654 | -0.079195 | 0 | 0
97 | 0.99525 | -0.06919 | 0 | 0
98 | 0.99525 | -0.069179 | 0.14223 | 0.068884
99 | 0.99528 | -0.069022 | 0.37248 | 0.1804
100 | 0.99654 | -0.079165 | 0.086523 | 0.041905
101 | 0.9953 | -0.069226 | 0.090125 | 0.043649
102 | 0.99541 | -0.069303 | 0.40064 | 0.19404
103 | 0.99556 | -0.070709 | 0.074921 | 0.036286
104 | 0.99535 | -0.069675 | 0 | 0
105 | 0.99532 | -0.069345 | 0 | 0
106 | 0.99535 | -0.06965 | 0.10508 | 0.050891
107 | 0.99778 | -0.061604 | 0 | 0
108 | 0.9976 | -0.062867 | 1.2522 | 0.60646
109 | 0.9962 | -0.07655 | 0.10523 | 0.050967
110 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.3683 | -0.17838 | 0.3683 | 0.17827 | 8.7726e-07 | -0.0001105 | 0.011858 | 0.011856 | 0.011858 | 0.99625 | -0.070916 | 0.99625 | -0.070937 | 5.3899
1 | 0.67056 | 0.31944 | -0.67045 | -0.32392 | 0.00011797 | -0.004473 | 0.021522 | 0.021579 | 0.021579 | 0.99625 | -0.070937 | 0.99609 | -0.069437 | 9.8086
2 | -1.0389 | -0.49771 | 1.0396 | 0.48664 | 0.00070469 | -0.011073 | 0.033379 | 0.033239 | 0.033379 | 0.99625 | -0.070937 | 0.99688 | -0.076553 | 15.1721
3 | 0.40417 | 0.19572 | -0.40416 | -0.19574 | 7.958e-06 | -2.625e-05 | 0.013014 | 0.013015 | 0.013015 | 0.99609 | -0.069437 | 0.99607 | -0.069566 | 6.1974
4 | 0.26628 | 0.1282 | -0.26619 | -0.12892 | 8.601e-05 | -0.00072445 | 0.0085648 | 0.0085746 | 0.0085746 | 0.99609 | -0.069437 | 0.99575 | -0.07159 | 4.0832
5 | -6.0521 | -2.8537 | 6.0531 | 2.8338 | 0.00094716 | -0.019888 | 0.19376 | 0.19351 | 0.19376 | 0.99688 | -0.076553 | 0.99704 | -0.075868 | 15.1851
6 | 4.7566 | 2.2438 | -4.7565 | -2.2481 | 0.00012578 | -0.0043107 | 0.1523 | 0.15235 | 0.15235 | 0.99688 | -0.076553 | 0.99685 | -0.076666 | 11.9397
7 | 0.25595 | 0.12329 | -0.25594 | -0.1238 | 1.9297e-06 | -0.0005058 | 0.0082267 | 0.0082331 | 0.0082331 | 0.99688 | -0.076553 | 0.99687 | -0.076488 | 3.7423
8 | 0.25594 | 0.1238 | -0.25594 | -0.12396 | 6.0961e-07 | -0.00015962 | 0.0082331 | 0.0082351 | 0.0082351 | 0.99687 | -0.076488 | 0.99687 | -0.076467 | 3.7432
9 | -6.0531 | -2.8338 | 6.0531 | 2.8331 | 3.5938e-05 | -0.00075578 | 0.19351 | 0.1935 | 0.19351 | 0.99704 | -0.075868 | 0.99705 | -0.075842 | 15.1654
10 | 4.6602 | 2.2015 | -4.6601 | -2.2052 | 0.00010235 | -0.0036545 | 0.14926 | 0.1493 | 0.1493 | 0.99685 | -0.076666 | 0.99683 | -0.076759 | 11.7007
11 | -6.4059 | -3.004 | 6.4061 | 3.0013 | 0.00014355 | -0.0026856 | 0.20485 | 0.20482 | 0.20485 | 0.99705 | -0.075842 | 0.99707 | -0.075742 | 16.0541
12 | 4.2004 | 1.9865 | -4.2003 | -1.9904 | 8.9523e-05 | -0.0039442 | 0.13456 | 0.13461 | 0.13461 | 0.99683 | -0.076759 | 0.99681 | -0.076848 | 10.5491
13 | 0.45979 | 0.2187 | -0.45976 | -0.22074 | 2.5023e-05 | -0.0020344 | 0.014745 | 0.01477 | 0.01477 | 0.99683 | -0.076759 | 0.99678 | -0.076299 | 6.7137
14 | -6.4061 | -3.0013 | 6.4076 | 2.9717 | 0.0015762 | -0.029557 | 0.20482 | 0.20444 | 0.20482 | 0.99707 | -0.075742 | 0.99732 | -0.07462 | 16.0515
15 | -0.16804 | -0.081383 | 0.16804 | 0.079879 | 2.4736e-06 | -0.0015045 | 0.0054102 | 0.0053913 | 0.0054102 | 0.99622 | -0.069438 | 0.99623 | -0.069564 | 2.4592
16 | -0.16804 | -0.079879 | 0.16804 | 0.076402 | 5.651e-06 | -0.003477 | 0.0053913 | 0.0053488 | 0.0053913 | 0.99623 | -0.069564 | 0.99626 | -0.069831 | 2.4506
17 | -0.16804 | -0.076402 | 0.16805 | 0.075243 | 1.8634e-06 | -0.0011586 | 0.0053488 | 0.005335 | 0.0053488 | 0.99626 | -0.069831 | 0.99627 | -0.069912 | 2.4313
18 | -0.38355 | -0.18576 | 0.38365 | 0.18539 | 9.8117e-05 | -0.00036996 | 0.012326 | 0.01232 | 0.012326 | 0.99812 | -0.032652 | 0.99839 | -0.030959 | 5.8693
19 | -15.2685 | -7.2329 | 15.2699 | 7.2287 | 0.001465 | -0.0041533 | 0.4885 | 0.48844 | 0.4885 | 0.99839 | -0.030959 | 0.99849 | -0.030557 | 38.284
20 | 14.6598 | 6.9385 | -14.6555 | -6.9273 | 0.0042898 | 0.011235 | 0.46895 | 0.46896 | 0.46896 | 0.99839 | -0.030959 | 0.99784 | -0.061325 | 36.3534
21 | -0.55501 | -0.26266 | 0.55503 | 0.26126 | 2.5063e-05 | -0.0013996 | 0.017792 | 0.017774 | 0.017792 | 0.99627 | -0.069912 | 0.99631 | -0.070283 | 8.0871
22 | -0.55503 | -0.26126 | 0.55505 | 0.26027 | 1.7676e-05 | -0.00098879 | 0.017774 | 0.017762 | 0.017774 | 0.99631 | -0.070283 | 0.99634 | -0.070542 | 8.0792
23 | 9.4457 | 4.4125 | -9.4442 | -4.4246 | 0.0014489 | -0.012056 | 0.30172 | 0.30188 | 0.30188 | 0.99748 | -0.073932 | 0.99732 | -0.07462 | 23.658
24 | -9.4457 | -4.4125 | 9.4461 | 4.4089 | 0.00043416 | -0.0036159 | 0.30172 | 0.30167 | 0.30172 | 0.99748 | -0.073932 | 0.99753 | -0.073725 | 23.6456
25 | 0.11087 | 0.052039 | -0.11087 | -0.053695 | 1.1771e-06 | -0.0016563 | 0.003545 | 0.0035656 | 0.0035656 | 0.99732 | -0.07462 | 0.99732 | -0.07453 | 1.6207
26 | 2.9257 | 1.4008 | -2.9253 | -1.4015 | 0.00039606 | -0.00068156 | 0.093891 | 0.093901 | 0.093901 | 0.99732 | -0.07462 | 0.9972 | -0.073469 | 42.6822
27 | -10.2258 | -4.7865 | 10.2262 | 4.7841 | 0.00035171 | -0.0024687 | 0.32674 | 0.32671 | 0.32674 | 0.99753 | -0.073725 | 0.99757 | -0.073571 | 25.6065
28 | -0.74701 | -0.36179 | 0.74701 | 0.36179 | 1.9908e-07 | -6.0889e-06 | 0.024019 | 0.024019 | 0.024019 | 0.99756 | -0.062509 | 0.99756 | -0.062511 | 10.9177
29 | -1.5274 | -0.73974 | 1.5274 | 0.7393 | 6.2363e-05 | -0.00044176 | 0.04911 | 0.049105 | 0.04911 | 0.99756 | -0.062511 | 0.9976 | -0.062867 | 22.3229
30 | -0.37668 | -0.18243 | 0.37668 | 0.18162 | 6.7756e-06 | -0.0008123 | 0.012143 | 0.012133 | 0.012143 | 0.99498 | -0.06768 | 0.995 | -0.067836 | 5.5195
31 | 1.0262 | 0.48839 | -1.0261 | -0.49004 | 0.00010325 | -0.0016495 | 0.032974 | 0.032995 | 0.032995 | 0.995 | -0.067836 | 0.9949 | -0.06699 | 14.9976
32 | -1.4029 | -0.67002 | 1.4031 | 0.66887 | 0.00013603 | -0.001144 | 0.045106 | 0.045091 | 0.045106 | 0.995 | -0.067836 | 0.99509 | -0.068652 | 20.5029
33 | 1.0261 | 0.49004 | -1.0261 | -0.49017 | 7.673e-06 | -0.00012249 | 0.032995 | 0.032996 | 0.032996 | 0.9949 | -0.06699 | 0.9949 | -0.066926 | 14.9983
34 | -1.6664 | -0.79588 | 1.6665 | 0.79532 | 9.4098e-05 | -0.00055282 | 0.053573 | 0.053566 | 0.053573 | 0.99509 | -0.068652 | 0.99514 | -0.069129 | 24.3513
35 | 0.26333 | 0.12701 | -0.26333 | -0.12716 | 6.2502e-07 | -0.00015365 | 0.0084814 | 0.0084833 | 0.0084833 | 0.99509 | -0.068652 | 0.99508 | -0.068632 | 3.856
36 | -0.94767 | -0.45222 | 0.94776 | 0.45221 | 8.9619e-05 | -7.8783e-06 | 0.03047 | 0.03047 | 0.03047 | 0.9948 | -0.067585 | 0.9949 | -0.066926 | 14.5097
37 | 0.34445 | 0.16326 | -0.34443 | -0.16572 | 1.7083e-05 | -0.0024591 | 0.011061 | 0.011092 | 0.011092 | 0.9948 | -0.067585 | 0.99475 | -0.067166 | 5.0419
38 | 0.60322 | 0.28895 | -0.60316 | -0.29185 | 6.215e-05 | -0.0028958 | 0.019409 | 0.019446 | 0.019446 | 0.9948 | -0.067585 | 0.9947 | -0.066699 | 8.839
39 | 0.26692 | 0.12818 | -0.2669 | -0.12833 | 1.8592e-05 | -0.00015525 | 0.0085927 | 0.0085948 | 0.0085948 | 0.99475 | -0.067166 | 0.99468 | -0.067639 | 4.0928
40 | 0.60316 | 0.29185 | -0.60315 | -0.29203 | 3.9355e-06 | -0.00018298 | 0.019446 | 0.019448 | 0.019448 | 0.9947 | -0.066699 | 0.9947 | -0.066642 | 8.8401
41 | -0.072075 | -0.034138 | 0.072075 | 0.033976 | 4.9004e-08 | -0.00016197 | 0.0023145 | 0.0023125 | 0.0023145 | 0.99468 | -0.067634 | 0.99468 | -0.067639 | 1.0521
42 | 0.072075 | 0.034138 | -0.072074 | -0.034907 | 2.3384e-07 | -0.00076913 | 0.0023145 | 0.0023242 | 0.0023242 | 0.99468 | -0.067634 | 0.99467 | -0.067606 | 1.0564
43 | -1.8584 | -0.88829 | 1.8587 | 0.88698 | 0.00028124 | -0.0013123 | 0.059752 | 0.059735 | 0.059752 | 0.99514 | -0.069129 | 0.99528 | -0.070406 | 27.1601
44 | 0.26333 | 0.12716 | -0.26333 | -0.12754 | 1.534e-06 | -0.00037681 | 0.0084833 | 0.0084881 | 0.0084881 | 0.99508 | -0.068632 | 0.99508 | -0.068581 | 3.8582
45 | -1.8587 | -0.88698 | 1.859 | 0.88709 | 0.00025643 | 0.00011291 | 0.059735 | 0.059734 | 0.059735 | 0.99528 | -0.070406 | 0.99542 | -0.069446 | 28.4451
46 | -0.35497 | -0.17192 | 0.35497 | 0.17181 | 8.1962e-07 | -0.00011139 | 0.011422 | 0.011421 | 0.011422 | 0.99678 | -0.076279 | 0.99678 | -0.076299 | 5.192
47 | 0.10479 | 0.048929 | -0.10479 | -0.050475 | 9.8153e-07 | -0.0015456 | 0.0033494 | 0.0033686 | 0.0033686 | 0.99678 | -0.076299 | 0.99677 | -0.076221 | 1.5312
48 | 0.10479 | 0.050475 | -0.10479 | -0.050753 | 1.7777e-07 | -0.00027803 | 0.0033686 | 0.0033721 | 0.0033721 | 0.99677 | -0.076221 | 0.99677 | -0.076206 | 1.5328
49 | 4.2003 | 1.9904 | -4.2002 | -1.9927 | 5.1588e-05 | -0.0022715 | 0.13461 | 0.13463 | 0.13463 | 0.99681 | -0.076848 | 0.9968 | -0.076899 | 10.5513
50 | 4.087 | 1.9378 | -4.0869 | -1.9413 | 7.5762e-05 | -0.0035244 | 0.13099 | 0.13103 | 0.13103 | 0.9968 | -0.076899 | 0.99678 | -0.076976 | 10.2692
51 | 4.0869 | 1.9413 | -4.0861 | -1.9441 | 0.00081844 | -0.0027673 | 0.13103 | 0.13108 | 0.13108 | 0.99678 | -0.076976 | 0.99656 | -0.079328 | 36.209
52 | -15.2699 | -7.2287 | 15.2738 | 7.2389 | 0.0038852 | 0.010196 | 0.48844 | 0.48844 | 0.48844 | 0.99849 | -0.030557 | 0.99896 | -0.0041818 | 37.8638
53 | 2.7803 | 1.3461 | -2.7796 | -1.3458 | 0.00064908 | 0.00035235 | 0.089365 | 0.089365 | 0.089365 | 0.99784 | -0.061325 | 0.9976 | -0.062867 | 42.5549
54 | 11.4496 | 5.375 | -11.4489 | -5.379 | 0.00072765 | -0.0039904 | 0.36592 | 0.36597 | 0.36597 | 0.99784 | -0.061325 | 0.99778 | -0.061604 | 28.6814
55 | -0.26807 | -0.12983 | 0.26808 | 0.12975 | 9.8757e-06 | -8.1437e-05 | 0.0086444 | 0.0086433 | 0.0086444 | 0.99466 | -0.066886 | 0.9947 | -0.066642 | 4.1164
56 | -0.20759 | -0.10015 | 0.2076 | 0.097161 | 7.5002e-06 | -0.002993 | 0.0066823 | 0.006645 | 0.0066823 | 0.99572 | -0.072157 | 0.99575 | -0.072459 | 3.0374
57 | 0.20759 | 0.10015 | -0.20759 | -0.10054 | 9.7973e-07 | -0.00038847 | 0.0066823 | 0.0066872 | 0.0066872 | 0.99572 | -0.072157 | 0.99571 | -0.072117 | 3.0396
58 | 3.1667 | 1.5143 | -3.1661 | -1.5152 | 0.00064508 | -0.00091297 | 0.10176 | 0.10177 | 0.10177 | 0.99575 | -0.072459 | 0.99556 | -0.070733 | 46.2612
59 | -3.3743 | -1.6114 | 3.3745 | 1.6112 | 0.0001654 | -0.00020054 | 0.10841 | 0.1084 | 0.10841 | 0.99575 | -0.072459 | 0.9958 | -0.072873 | 49.2753
60 | 2.9701 | 1.421 | -2.9696 | -1.4217 | 0.00045049 | -0.00074229 | 0.095469 | 0.09548 | 0.09548 | 0.99556 | -0.070733 | 0.99542 | -0.069446 | 43.4001
61 | 0.074921 | 0.035657 | -0.074921 | -0.036229 | 1.8722e-07 | -0.0005716 | 0.0024059 | 0.0024131 | 0.0024131 | 0.99556 | -0.070733 | 0.99556 | -0.070711 | 1.0969
62 | 0.12106 | 0.058568 | -0.12106 | -0.058632 | 5.4702e-08 | -6.3715e-05 | 0.0038995 | 0.0039003 | 0.0039003 | 0.99556 | -0.070733 | 0.99556 | -0.070729 | 1.7729
63 | -3.4776 | -1.6612 | 3.4777 | 1.661 | 0.00010755 | -0.00012091 | 0.11172 | 0.11172 | 0.11172 | 0.9958 | -0.072873 | 0.99583 | -0.073134 | 50.7835
64 | 15.4091 | 7.3044 | -15.4091 | -7.3045 | 2.6761e-05 | -7.4377e-05 | 0.49278 | 0.49278 | 0.49278 | 0.99896 | -0.0041746 | 0.99896 | -0.0041818 | 38.6194
65 | -16.6706 | -7.9153 | 16.6731 | 7.9095 | 0.0025523 | -0.0058496 | 0.53328 | 0.53319 | 0.53328 | 0.99896 | -0.0041746 | 0.99912 | -0.003541 | 41.7934
66 | -16.6731 | -7.9095 | 16.6738 | 7.908 | 0.00062887 | -0.001442 | 0.53319 | 0.53317 | 0.53319 | 0.99912 | -0.003541 | 0.99916 | -0.0033843 | 41.7863
67 | -16.8664 | -8.0013 | 16.8671 | 7.9998 | 0.0006729 | -0.0014995 | 0.53936 | 0.53933 | 0.53936 | 0.99916 | -0.0033843 | 0.9992 | -0.0032187 | 42.2692
68 | -17.0172 | -8.0725 | 17.0193 | 8.0678 | 0.0021688 | -0.0047283 | 0.54415 | 0.54408 | 0.54415 | 0.9992 | -0.0032187 | 0.99933 | -0.0026888 | 42.645
69 | 0.38211 | 0.18459 | -0.3821 | -0.18506 | 3.9677e-06 | -0.0004702 | 0.012258 | 0.012264 | 0.012264 | 0.99933 | -0.0026888 | 0.99932 | -0.0025986 | 5.5747
70 | -17.4014 | -8.2524 | 17.4032 | 8.2487 | 0.0017831 | -0.0036765 | 0.55633 | 0.55628 | 0.55633 | 0.99933 | -0.0026888 | 0.99944 | -0.0022621 | 43.5999
71 | -18.2794 | -8.6731 | 18.2796 | 8.6727 | 0.00019235 | -0.00034928 | 0.5844 | 0.58439 | 0.5844 | 0.99944 | -0.0022621 | 0.99945 | -0.0022185 | 45.799
72 | 1.1107 | 0.53461 | -1.1106 | -0.53486 | 1.8473e-05 | -0.00025069 | 0.035746 | 0.03575 | 0.03575 | 0.99542 | -0.069446 | 0.99541 | -0.069303 | 16.2498
73 | 0.074921 | 0.036229 | -0.074921 | -0.036286 | 1.8717e-08 | -5.6951e-05 | 0.0024131 | 0.0024138 | 0.0024138 | 0.99556 | -0.070711 | 0.99556 | -0.070709 | 1.0972
74 | -3.4777 | -1.661 | 3.4783 | 1.6604 | 0.00059095 | -0.00066462 | 0.11172 | 0.11171 | 0.11172 | 0.99583 | -0.073134 | 0.99598 | -0.074568 | 50.7826
75 | -19.248 | -9.1417 | 19.2499 | 9.1386 | 0.0019519 | -0.0030881 | 0.61547 | 0.61541 | 0.61547 | 0.99945 | -0.0022185 | 0.99955 | -0.0018001 | 48.234
76 | -19.2499 | -9.1386 | 19.2512 | 9.1366 | 0.0012489 | -0.0019768 | 0.61541 | 0.61538 | 0.61541 | 0.99955 | -0.0018001 | 0.99962 | -0.0015318 | 48.2299
77 | -19.2512 | -9.1366 | 19.2519 | 9.1355 | 0.00070214 | -0.0011116 | 0.61538 | 0.61536 | 0.61538 | 0.99962 | -0.0015318 | 0.99966 | -0.0013807 | 48.2273
78 | -19.3485 | -9.1823 | 19.3503 | 9.1796 | 0.0017781 | -0.0027778 | 0.61846 | 0.61842 | 0.61846 | 0.99966 | -0.0013807 | 0.99975 | -0.00099988 | 48.4689
79 | -19.3503 | -9.1796 | 19.3547 | 9.1727 | 0.0043713 | -0.0068346 | 0.61842 | 0.6183 | 0.61842 | 0.99975 | -0.00099988 | 0.99999 | -6.0022e-05 | 48.4652
80 | -19.3547 | -9.1727 | 19.3549 | 9.1723 | 0.00027838 | -0.00043551 | 0.6183 | 0.61829 | 0.6183 | 0.99999 | -6.0022e-05 | 1 | 0 | 48.4562
81 | 1.7478 | 0.83485 | -1.7477 | -0.835 | 2.8811e-05 | -0.00015409 | 0.0561 | 0.056102 | 0.056102 | 0.99669 | -0.06876 | 0.99667 | -0.06862 | 25.5009
82 | -2.8169 | -1.3527 | 2.8174 | 1.3516 | 0.00054647 | -0.0010236 | 0.090506 | 0.090491 | 0.090506 | 0.99669 | -0.06876 | 0.99687 | -0.070416 | 41.1391
83 | 1.3914 | 0.6624 | -1.3911 | -0.66233 | 0.00024924 | 7.2859e-05 | 0.044633 | 0.044634 | 0.044634 | 0.99667 | -0.06862 | 0.99648 | -0.069878 | 21.2544
84 | -2.8174 | -1.3516 | 2.8178 | 1.3509 | 0.00039258 | -0.00073583 | 0.090491 | 0.09048 | 0.090491 | 0.99687 | -0.070416 | 0.997 | -0.071603 | 41.1323
85 | 0.98043 | 0.46588 | -0.98041 | -0.46621 | 1.8572e-05 | -0.00032799 | 0.031446 | 0.03145 | 0.03145 | 0.99648 | -0.069878 | 0.99647 | -0.06972 | 14.2955
86 | 0.41068 | 0.19645 | -0.41066 | -0.19884 | 2.3613e-05 | -0.0023983 | 0.013188 | 0.013219 | 0.013219 | 0.99648 | -0.069878 | 0.99643 | -0.069384 | 6.0084
87 | -2.8178 | -1.3509 | 2.8182 | 1.3502 | 0.00035188 | -0.0006599 | 0.09048 | 0.090471 | 0.09048 | 0.997 | -0.071603 | 0.99711 | -0.072666 | 41.1275
88 | 0.90763 | 0.43096 | -0.90752 | -0.43098 | 0.00010538 | -1.6732e-05 | 0.029107 | 0.029108 | 0.029108 | 0.99647 | -0.06972 | 0.99634 | -0.070542 | 13.8611
89 | 0.41066 | 0.19884 | -0.41065 | -0.19889 | 1.2953e-05 | -4.1201e-05 | 0.013219 | 0.013219 | 0.013219 | 0.99643 | -0.069384 | 0.9964 | -0.069592 | 6.2948
90 | -2.925 | -1.402 | 2.9253 | 1.4015 | 0.00027631 | -0.00047527 | 0.093908 | 0.093901 | 0.093908 | 0.99711 | -0.072666 | 0.9972 | -0.073469 | 42.6854
91 | -11.4476 | -5.3756 | 11.4489 | 5.379 | 0.001315 | 0.0033849 | 0.36598 | 0.36597 | 0.36598 | 0.99757 | -0.073571 | 0.99778 | -0.061604 | 28.3703
92 | -0.1488 | -0.072065 | 0.1488 | 0.071574 | 6.3494e-07 | -0.00049102 | 0.0047919 | 0.0047857 | 0.0047919 | 0.99598 | -0.074531 | 0.99598 | -0.074568 | 2.1781
93 | -3.6271 | -1.732 | 3.628 | 1.731 | 0.00092052 | -0.00093073 | 0.1165 | 0.11648 | 0.1165 | 0.99598 | -0.074568 | 0.99622 | -0.076707 | 52.9531
94 | 0.24096 | 0.11431 | -0.24096 | -0.11485 | 1.8119e-06 | -0.00053748 | 0.0077282 | 0.0077349 | 0.0077349 | 0.99622 | -0.076707 | 0.99621 | -0.076645 | 3.5159
95 | -3.8689 | -1.8453 | 3.8696 | 1.8448 | 0.00068111 | -0.00058176 | 0.12421 | 0.1242 | 0.12421 | 0.99622 | -0.076707 | 0.99638 | -0.078188 | 56.4591
96 | -3.8696 | -1.8448 | 3.8703 | 1.8442 | 0.0006361 | -0.00054365 | 0.1242 | 0.12419 | 0.1242 | 0.99638 | -0.078188 | 0.99653 | -0.07957 | 56.4547
97 | -3.9995 | -1.9068 | 3.9995 | 1.9065 | 8.2687e-05 | -0.00029397 | 0.12835 | 0.12835 | 0.12835 | 0.99653 | -0.07957 | 0.99656 | -0.079328 | 35.4557
98 | 0.10524 | 0.049119 | -0.10524 | -0.049805 | 4.392e-07 | -0.00068649 | 0.0033653 | 0.0033737 | 0.0033737 | 0.99621 | -0.076645 | 0.99621 | -0.076611 | 1.5335
99 | 0.086524 | 0.037624 | -0.086523 | -0.041198 | 1.5267e-06 | -0.0035745 | 0.0027331 | 0.002776 | 0.002776 | 0.99656 | -0.079328 | 0.99654 | -0.079195 | 1.2618
100 | 0.10524 | 0.049805 | -0.10523 | -0.050967 | 7.4863e-07 | -0.0011622 | 0.0033737 | 0.0033883 | 0.0033883 | 0.99621 | -0.076611 | 0.9962 | -0.07655 | 1.5401
101 | 0.086523 | 0.041198 | -0.086523 | -0.041905 | 3.0766e-07 | -0.00070674 | 0.002776 | 0.0027849 | 0.0027849 | 0.99654 | -0.079195 | 0.99654 | -0.079165 | 1.2658
102 | 0.14223 | 0.06873 | -0.14223 | -0.068884 | 1.8182e-07 | -0.00015333 | 0.0045817 | 0.0045837 | 0.0045837 | 0.99525 | -0.06919 | 0.99525 | -0.069179 | 2.0835
103 | -0.14223 | -0.06873 | 0.14223 | 0.068619 | 3.5887e-06 | -0.00011125 | 0.0045817 | 0.0045803 | 0.0045817 | 0.99525 | -0.06919 | 0.99528 | -0.069022 | 2.1818
104 | -0.51472 | -0.24902 | 0.51473 | 0.24824 | 1.212e-05 | -0.00077755 | 0.016584 | 0.016575 | 0.016584 | 0.99528 | -0.069022 | 0.9953 | -0.069226 | 7.5384
105 | -0.60485 | -0.29189 | 0.60486 | 0.29151 | 8.3435e-06 | -0.00038722 | 0.019479 | 0.019474 | 0.019479 | 0.9953 | -0.069226 | 0.99532 | -0.069345 | 8.8541
106 | 0.71 | 0.34082 | -0.70996 | -0.34085 | 3.8745e-05 | -2.5036e-05 | 0.02284 | 0.022841 | 0.022841 | 0.99541 | -0.069303 | 0.99535 | -0.069675 | 10.8765
107 | 0.10508 | 0.050424 | -0.10508 | -0.050891 | 3.0174e-07 | -0.00046704 | 0.0033802 | 0.0033861 | 0.0033861 | 0.99535 | -0.069675 | 0.99535 | -0.06965 | 1.5391
108 | 0.60488 | 0.29043 | -0.60486 | -0.29151 | 2.3263e-05 | -0.0010807 | 0.01946 | 0.019474 | 0.019474 | 0.99535 | -0.069675 | 0.99532 | -0.069345 | 8.8518

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 19.4669 | 9.2302

## res_load
| p_mw | q_mvar
0 | 0.3683 | 0.17838
1 | 0.40416 | 0.19574
2 | 0.26619 | 0.12892
3 | 0.25594 | 0.12396
4 | 0.096224 | 0.046603
5 | 0.35283 | 0.17089
6 | 0.16804 | 0.081383
7 | 0.38355 | 0.18576
8 | 0.22503 | 0.10899
9 | 0.38696 | 0.18741
10 | 0.7797 | 0.37763
11 | 0.74701 | 0.36179
12 | 0.78037 | 0.37795
13 | 0.37668 | 0.18243
14 | 0.078375 | 0.037959
15 | 0.077514 | 0.037542
16 | 0.19482 | 0.094358
17 | 0.072074 | 0.034907
18 | 0.19195 | 0.092963
19 | 0.26333 | 0.12754
20 | 0.35497 | 0.17192
21 | 0.11325 | 0.05485
22 | 0.10479 | 0.050753
23 | 0.42557 | 0.20611
24 | 0.26807 | 0.12983
25 | 0.33508 | 0.16228
26 | 0.20759 | 0.10054
27 | 0.10311 | 0.049937
28 | 1.2614 | 0.61094
29 | 0.1353 | 0.065531
30 | 0.19265 | 0.093303
31 | 0.15009 | 0.072692
32 | 0.3821 | 0.18506
33 | 0.8762 | 0.42436
34 | 0.12106 | 0.058632
35 | 0.96835 | 0.46899
36 | 0.096656 | 0.046812
37 | 1.0691 | 0.5178
38 | 0.35637 | 0.1726
39 | 0.072785 | 0.035251
40 | 0.10685 | 0.051748
41 | 0.097928 | 0.047429
42 | 0.11087 | 0.053695
43 | 1.2214 | 0.59157
44 | 0.41065 | 0.19889
45 | 0.1488 | 0.072065
46 | 0.1292 | 0.062574
47 | 0.13572 | 0.065733
48 | 0.35247 | 0.17071
49 | 0.14223 | 0.068884
50 | 0.37248 | 0.1804
51 | 0.086523 | 0.041905
52 | 0.090125 | 0.043649
53 | 0.40064 | 0.19404
54 | 0.074921 | 0.036286
55 | 0.10508 | 0.050891
56 | 1.2522 | 0.60646
57 | 0.10523 | 0.050967

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1