## bus
| name | vn_kv | type | zone | in_service
0 | bus_MV_617_0_node_0 | 20 | n |  | TRUE
1 | bus_MV_617_0_node_93 | 20 | n |  | TRUE
2 | bus_MV_617_0_node_94 | 20 | n |  | TRUE
3 | bus_MV_617_0_node_96 | 20 | n |  | TRUE
4 | bus_MV_617_0_node_109 | 20 | n |  | TRUE
5 | bus_MV_617_0_node_95 | 20 | n |  | TRUE
6 | bus_MV_617_0_node_92 | 20 | n |  | TRUE
7 | bus_MV_617_0_node_3 | 20 | n |  | TRUE
8 | bus_MV_617_0_node_4 | 20 | n |  | TRUE
9 | bus_MV_617_0_node_6 | 20 | n |  | TRUE
10 | bus_MV_617_0_node_5 | 20 | n |  | TRUE
11 | bus_MV_617_0_node_7 | 20 | n |  | TRUE
12 | bus_MV_617_0_node_30 | 20 | n |  | TRUE
13 | bus_MV_617_0_node_28 | 20 | n |  | TRUE
14 | bus_MV_617_0_node_21 | 20 | n |  | TRUE
15 | bus_MV_617_0_node_97 | 20 | n |  | TRUE
16 | bus_MV_617_0_node_86 | 20 | n |  | TRUE
17 | bus_MV_617_0_node_29 | 20 | n |  | TRUE
18 | bus_MV_617_0_node_8 | 20 | n |  | TRUE
19 | bus_MV_617_0_node_46 | 20 | n |  | TRUE
20 | bus_MV_617_0_node_57 | 20 | n |  | TRUE
21 | bus_MV_617_0_node_44 | 20 | n |  | TRUE
22 | bus_MV_617_0_node_11 | 20 | n |  | TRUE
23 | bus_MV_617_0_node_12 | 20 | n |  | TRUE
24 | bus_MV_617_0_node_17 | 20 | n |  | TRUE
25 | bus_MV_617_0_node_18 | 20 | n |  | TRUE
26 | bus_MV_617_0_node_19 | 20 | n |  | TRUE
27 | bus_MV_617_0_node_13 | 20 | n |  | TRUE
28 | bus_MV_617_0_node_14 | 20 | n |  | TRUE
29 | bus_MV_617_0_node_102 | 20 | n |  | TRUE
30 | bus_MV_617_0_node_103 | 20 | n |  | TRUE
31 | bus_MV_617_0_node_88 | 20 | n |  | TRUE
32 | bus_MV_617_0_node_15 | 20 | n |  | TRUE
33 | bus_MV_617_0_node_49 | 20 | n |  | TRUE
34 | bus_MV_617_0_node_48 | 20 | n |  | TRUE
35 | bus_MV_617_0_node_105 | 20 | n |  | TRUE
36 | bus_MV_617_0_node_50 | 20 | n |  | TRUE
37 | bus_MV_617_0_node_16 | 20 | n |  | TRUE
38 | bus_MV_617_0_node_20 | 20 | n |  | TRUE
39 | bus_MV_617_0_node_61 | 20 | n |  | TRUE
40 | bus_MV_617_0_node_58 | 20 | n |  | TRUE
41 | bus_MV_617_0_node_43 | 20 | n |  | TRUE
42 | bus_MV_617_0_node_47 | 20 | n |  | TRUE
43 | bus_MV_617_0_node_39 | 20 | n |  | TRUE
44 | bus_MV_617_0_node_22 | 20 | n |  | TRUE
45 | bus_MV_617_0_node_23 | 20 | n |  | TRUE
46 | bus_MV_617_0_node_37 | 20 | n |  | TRUE
47 | bus_MV_617_0_node_24 | 20 | n |  | TRUE
48 | bus_MV_617_0_node_35 | 20 | n |  | TRUE
49 | bus_MV_617_0_node_106 | 20 | n |  | TRUE
50 | bus_MV_617_0_node_25 | 20 | n |  | TRUE
51 | bus_MV_617_0_node_26 | 20 | n |  | TRUE
52 | bus_MV_617_0_node_27 | 20 | n |  | TRUE
53 | bus_MV_617_0_node_76 | 20 | n |  | TRUE
54 | bus_MV_617_0_node_84 | 20 | n |  | TRUE
55 | bus_MV_617_0_node_73 | 20 | n |  | TRUE
56 | bus_MV_617_0_node_98 | 20 | n |  | TRUE
57 | bus_MV_617_0_node_83 | 20 | n |  | TRUE
58 | bus_MV_617_0_node_31 | 20 | n |  | TRUE
59 | bus_MV_617_0_node_32 | 20 | n |  | TRUE
60 | bus_MV_617_0_node_33 | 20 | n |  | TRUE
61 | bus_MV_617_0_node_34 | 20 | n |  | TRUE
62 | bus_MV_617_0_node_70 | 20 | n |  | TRUE
63 | bus_MV_617_0_node_72 | 20 | n |  | TRUE
64 | bus_MV_617_0_node_69 | 20 | n |  | TRUE
65 | bus_MV_617_0_node_36 | 20 | n |  | TRUE
66 | bus_MV_617_0_node_38 | 20 | n |  | TRUE
67 | bus_MV_617_0_node_51 | 20 | n |  | TRUE
68 | bus_MV_617_0_node_59 | 20 | n |  | TRUE
69 | bus_MV_617_0_node_53 | 20 | n |  | TRUE
70 | bus_MV_617_0_node_54 | 20 | n |  | TRUE
71 | bus_MV_617_0_node_90 | 20 | n |  | TRUE
72 | bus_MV_617_0_node_55 | 20 | n |  | TRUE
73 | bus_MV_617_0_node_113 | 20 | n |  | TRUE
74 | bus_MV_617_0_node_107 | 20 | n |  | TRUE
75 | bus_MV_617_0_node_52 | 20 | n |  | TRUE
76 | bus_MV_617_0_node_60 | 20 | n |  | TRUE
77 | bus_MV_617_0_node_40 | 20 | n |  | TRUE
78 | bus_MV_617_0_node_45 | 20 | n |  | TRUE
79 | bus_MV_617_0_node_111 | 20 | n |  | TRUE
80 | bus_MV_617_0_node_56 | 20 | n |  | TRUE
81 | bus_MV_617_0_node_110 | 20 | n |  | TRUE
82 | bus_MV_617_0_node_62 | 20 | n |  | TRUE
83 | bus_MV_617_0_node_63 | 20 | n |  | TRUE
84 | bus_MV_617_0_node_64 | 20 | n |  | TRUE
85 | bus_MV_617_0_node_65 | 20 | n |  | TRUE
86 | bus_MV_617_0_node_85 | 20 | n |  | TRUE
87 | bus_MV_617_0_node_79 | 20 | n |  | TRUE
88 | bus_MV_617_0_node_66 | 20 | n |  | TRUE
89 | bus_MV_617_0_node_100 | 20 | n |  | TRUE
90 | bus_MV_617_0_node_67 | 20 | n |  | TRUE
91 | bus_MV_617_0_node_80 | 20 | n |  | TRUE
92 | bus_MV_617_0_node_75 | 20 | n |  | TRUE
93 | bus_MV_617_0_node_104 | 20 | n |  | TRUE
94 | bus_MV_617_0_node_112 | 20 | n |  | TRUE
95 | bus_MV_617_0_node_68 | 20 | n |  | TRUE
96 | bus_MV_617_0_node_89 | 20 | n |  | TRUE
97 | bus_MV_617_0_node_99 | 20 | n |  | TRUE
98 | bus_MV_617_0_node_87 | 20 | n |  | TRUE
99 | bus_MV_617_0_node_71 | 20 | n |  | TRUE
100 | bus_MV_617_0_node_74 | 20 | n |  | TRUE
101 | bus_MV_617_0_node_77 | 20 | n |  | TRUE
102 | bus_MV_617_0_node_78 | 20 | n |  | TRUE
103 | bus_MV_617_0_node_81 | 20 | n |  | TRUE
104 | bus_MV_617_0_node_82 | 20 | n |  | TRUE
105 | bus_MV_617_0_node_108 | 20 | n |  | TRUE
106 | bus_MV_617_0_node_91 | 20 | n |  | TRUE
107 | bus_HV_617_0_node_99 | 110 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV_617_0_load_0 | 0 | 0.19113 | 0.092571 | 0 | 0 |  | 1 | TRUE | wye
1 | MV_617_0_load_96 | 3 | 0.52159 | 0.25262 | 0 | 0 |  | 1 | TRUE | wye
2 | MV_617_0_load_109 | 4 | 0.35276 | 0.17085 | 0 | 0 |  | 1 | TRUE | wye
3 | MV_617_0_load_3 | 7 | 0.19534 | 0.094609 | 0 | 0 |  | 1 | TRUE | wye
4 | MV_617_0_load_28 | 13 | 0.36113 | 0.17491 | 0 | 0 |  | 1 | TRUE | wye
5 | MV_617_0_load_21 | 14 | 0.38455 | 0.18625 | 0 | 0 |  | 1 | TRUE | wye
6 | MV_617_0_load_86 | 16 | 0.6437 | 0.31176 | 0 | 0 |  | 1 | TRUE | wye
7 | MV_617_0_load_29 | 17 | 0.092009 | 0.044562 | 0 | 0 |  | 1 | TRUE | wye
8 | MV_617_0_load_8 | 18 | 0.28018 | 0.1357 | 0 | 0 |  | 1 | TRUE | wye
9 | MV_617_0_load_57 | 20 | 0.39165 | 0.18968 | 0 | 0 |  | 1 | TRUE | wye
10 | MV_617_0_load_12 | 23 | 0.40203 | 0.19471 | 0 | 0 |  | 1 | TRUE | wye
11 | MV_617_0_load_17 | 24 | 0.28297 | 0.13705 | 0 | 0 |  | 1 | TRUE | wye
12 | MV_617_0_load_13 | 27 | 0.38155 | 0.18479 | 0 | 0 |  | 1 | TRUE | wye
13 | MV_617_0_load_103 | 30 | 0.32184 | 0.15587 | 0 | 0 |  | 1 | TRUE | wye
14 | MV_617_0_load_48 | 34 | 0.41252 | 0.19979 | 0 | 0 |  | 1 | TRUE | wye
15 | MV_617_0_load_105 | 35 | 0.33551 | 0.16249 | 0 | 0 |  | 1 | TRUE | wye
16 | MV_617_0_load_16 | 37 | 0.41052 | 0.19882 | 0 | 0 |  | 1 | TRUE | wye
17 | MV_617_0_load_61 | 39 | 0.074553 | 0.036108 | 0 | 0 |  | 1 | TRUE | wye
18 | MV_617_0_load_58 | 40 | 0.087077 | 0.042173 | 0 | 0 |  | 1 | TRUE | wye
19 | MV_617_0_load_43 | 41 | 0.26836 | 0.12997 | 0 | 0 |  | 1 | TRUE | wye
20 | MV_617_0_load_22 | 44 | 0.33823 | 0.16381 | 0 | 0 |  | 1 | TRUE | wye
21 | MV_617_0_load_37 | 46 | 0.22788 | 0.11037 | 0 | 0 |  | 1 | TRUE | wye
22 | MV_617_0_load_35 | 48 | 0.26424 | 0.12798 | 0 | 0 |  | 1 | TRUE | wye
23 | MV_617_0_load_106 | 49 | 0.3646 | 0.17658 | 0 | 0 |  | 1 | TRUE | wye
24 | MV_617_0_load_25 | 50 | 0.38844 | 0.18813 | 0 | 0 |  | 1 | TRUE | wye
25 | MV_617_0_load_26 | 51 | 0.090404 | 0.043784 | 0 | 0 |  | 1 | TRUE | wye
26 | MV_617_0_load_27 | 52 | 0.070731 | 0.034256 | 0 | 0 |  | 1 | TRUE | wye
27 | MV_617_0_load_98 | 56 | 0.96938 | 0.46949 | 0 | 0 |  | 1 | TRUE | wye
28 | MV_617_0_load_31 | 58 | 0.27022 | 0.13088 | 0 | 0 |  | 1 | TRUE | wye
29 | MV_617_0_load_34 | 61 | 2.2141 | 1.0724 | 0 | 0 |  | 1 | TRUE | wye
30 | MV_617_0_load_72 | 63 | 0.1202 | 0.058217 | 0 | 0 |  | 1 | TRUE | wye
31 | MV_617_0_load_69 | 64 | 0.3221 | 0.156 | 0 | 0 |  | 1 | TRUE | wye
32 | MV_617_0_load_51 | 67 | 0.37307 | 0.18069 | 0 | 0 |  | 1 | TRUE | wye
33 | MV_617_0_load_90 | 71 | 0.10608 | 0.051379 | 0 | 0 |  | 1 | TRUE | wye
34 | MV_617_0_load_113 | 73 | 0.35969 | 0.1742 | 0 | 0 |  | 1 | TRUE | wye
35 | MV_617_0_load_107 | 74 | 0.38335 | 0.18566 | 0 | 0 |  | 1 | TRUE | wye
36 | MV_617_0_load_60 | 76 | 0.08005 | 0.03877 | 0 | 0 |  | 1 | TRUE | wye
37 | MV_617_0_load_40 | 77 | 0.26281 | 0.12729 | 0 | 0 |  | 1 | TRUE | wye
38 | MV_617_0_load_111 | 79 | 0.2871 | 0.13905 | 0 | 0 |  | 1 | TRUE | wye
39 | MV_617_0_load_110 | 81 | 0.10964 | 0.053099 | 0 | 0 |  | 1 | TRUE | wye
40 | MV_617_0_load_62 | 82 | 0.77288 | 0.37432 | 0 | 0 |  | 1 | TRUE | wye
41 | MV_617_0_load_64 | 84 | 0.75505 | 0.36569 | 0 | 0 |  | 1 | TRUE | wye
42 | MV_617_0_load_85 | 86 | 0.78314 | 0.37929 | 0 | 0 |  | 1 | TRUE | wye
43 | MV_617_0_load_79 | 87 | 0.29045 | 0.14067 | 0 | 0 |  | 1 | TRUE | wye
44 | MV_617_0_load_66 | 88 | 0.37067 | 0.17953 | 0 | 0 |  | 1 | TRUE | wye
45 | MV_617_0_load_100 | 89 | 0.1458 | 0.070615 | 0 | 0 |  | 1 | TRUE | wye
46 | MV_617_0_load_67 | 90 | 0.54917 | 0.26598 | 0 | 0 |  | 1 | TRUE | wye
47 | MV_617_0_load_80 | 91 | 0.55004 | 0.2664 | 0 | 0 |  | 1 | TRUE | wye
48 | MV_617_0_load_75 | 92 | 0.76413 | 0.37008 | 0 | 0 |  | 1 | TRUE | wye
49 | MV_617_0_load_112 | 94 | 0.41267 | 0.19987 | 0 | 0 |  | 1 | TRUE | wye
50 | MV_617_0_load_68 | 95 | 0.6653 | 0.32222 | 0 | 0 |  | 1 | TRUE | wye
51 | MV_617_0_load_87 | 98 | 0.33309 | 0.16132 | 0 | 0 |  | 1 | TRUE | wye
52 | MV_617_0_load_77 | 101 | 0.097545 | 0.047243 | 0 | 0 |  | 1 | TRUE | wye
53 | MV_617_0_load_78 | 102 | 0.09209 | 0.044601 | 0 | 0 |  | 1 | TRUE | wye
54 | MV_617_0_load_81 | 103 | 1.1836 | 0.57323 | 0 | 0 |  | 1 | TRUE | wye
55 | MV_617_0_load_82 | 104 | 0.28795 | 0.13946 | 0 | 0 |  | 1 | TRUE | wye
56 | MV_617_0_load_108 | 105 | 0.26706 | 0.12934 | 0 | 0 |  | 1 | TRUE | wye
57 | MV_617_0_load_91 | 106 | 0.10064 | 0.048744 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 97 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | MV_617_0_line_0 |  | 0 | 1 | 0.53824 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
1 | MV_617_0_line_1 |  | 1 | 2 | 0.20555 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
2 | MV_617_0_line_2 |  | 1 | 3 | 0.11751 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
3 | MV_617_0_line_3 |  | 2 | 6 | 0.26233 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
4 | MV_617_0_line_4 |  | 2 | 105 | 0.050885 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
5 | MV_617_0_line_5 |  | 4 | 5 | 0.042521 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
6 | MV_617_0_line_6 |  | 5 | 6 | 0.2466 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
7 | MV_617_0_line_7 |  | 6 | 106 | 0.036381 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
8 | MV_617_0_line_8 |  | 7 | 8 | 0.061699 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
9 | MV_617_0_line_9 |  | 8 | 9 | 0.68287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
10 | MV_617_0_line_10 |  | 9 | 12 | 0.10523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
11 | MV_617_0_line_11 |  | 9 | 13 | 0.027983 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
12 | MV_617_0_line_12 |  | 9 | 10 | 0.43303 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
13 | MV_617_0_line_13 |  | 10 | 11 | 0.29328 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
14 | MV_617_0_line_14 |  | 11 | 14 | 0.017717 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
15 | MV_617_0_line_15 |  | 12 | 15 | 0.016722 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
16 | MV_617_0_line_16 |  | 12 | 16 | 0.059837 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
17 | MV_617_0_line_17 |  | 13 | 17 | 0.015833 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
18 | MV_617_0_line_18 |  | 15 | 56 | 0.063053 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
19 | MV_617_0_line_19 |  | 16 | 57 | 0.040555 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
20 | MV_617_0_line_20 |  | 18 | 19 | 0.35434 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
21 | MV_617_0_line_21 |  | 19 | 20 | 0.016602 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
22 | MV_617_0_line_22 |  | 19 | 21 | 0.47462 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
23 | MV_617_0_line_23 |  | 20 | 77 | 0.40153 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
24 | MV_617_0_line_24 |  | 21 | 41 | 0.14764 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
25 | MV_617_0_line_25 |  | 22 | 23 | 0.077807 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
26 | MV_617_0_line_26 |  | 22 | 24 | 0.31772 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
27 | MV_617_0_line_27 |  | 24 | 25 | 0.063014 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
28 | MV_617_0_line_28 |  | 25 | 26 | 0.30119 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
29 | MV_617_0_line_29 |  | 26 | 38 | 0.1695 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
30 | MV_617_0_line_30 |  | 26 | 39 | 0.051313 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
31 | MV_617_0_line_31 |  | 27 | 28 | 0.031035 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
32 | MV_617_0_line_32 |  | 28 | 29 | 0.15614 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
33 | MV_617_0_line_33 |  | 29 | 30 | 0.026418 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
34 | MV_617_0_line_34 |  | 29 | 31 | 0.25951 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
35 | MV_617_0_line_35 |  | 30 | 32 | 0.1357 | 0.1188 | 0.172 | 20.6 | 0 | 0.82 | 1 | 1 | ol | TRUE
36 | MV_617_0_line_36 |  | 30 | 36 | 0.028142 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
37 | MV_617_0_line_37 |  | 31 | 98 | 0.03891 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
38 | MV_617_0_line_38 |  | 32 | 33 | 0.15669 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
39 | MV_617_0_line_39 |  | 32 | 34 | 0.00523 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
40 | MV_617_0_line_40 |  | 33 | 35 | 0.02499 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
41 | MV_617_0_line_41 |  | 35 | 47 | 0.3983 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
42 | MV_617_0_line_42 |  | 35 | 45 | 0.10051 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
43 | MV_617_0_line_43 |  | 36 | 37 | 0.10363 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
44 | MV_617_0_line_44 |  | 38 | 40 | 0.032155 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
45 | MV_617_0_line_45 |  | 39 | 42 | 0.11219 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
46 | MV_617_0_line_46 |  | 40 | 43 | 0.027397 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
47 | MV_617_0_line_47 |  | 41 | 78 | 0.05986 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
48 | MV_617_0_line_48 |  | 42 | 79 | 0.009909 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
49 | MV_617_0_line_49 |  | 42 | 78 | 0.22335 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
50 | MV_617_0_line_50 |  | 43 | 68 | 0.031266 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
51 | MV_617_0_line_51 |  | 43 | 65 | 0.1352 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
52 | MV_617_0_line_52 |  | 44 | 45 | 0.024717 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
53 | MV_617_0_line_53 |  | 44 | 46 | 0.20016 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
54 | MV_617_0_line_54 |  | 46 | 48 | 0.14554 | 0.306 | 0.35 | 10 | 0 | 0.35 | 1 | 1 | ol | TRUE
55 | MV_617_0_line_55 |  | 47 | 49 | 0.069935 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
56 | MV_617_0_line_56 |  | 48 | 65 | 0.009748 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
57 | MV_617_0_line_57 |  | 50 | 51 | 0.088636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
58 | MV_617_0_line_58 |  | 51 | 52 | 0.096353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
59 | MV_617_0_line_59 |  | 52 | 53 | 0.047803 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
60 | MV_617_0_line_60 |  | 53 | 54 | 0.25078 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
61 | MV_617_0_line_61 |  | 53 | 55 | 0.081593 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
62 | MV_617_0_line_62 |  | 54 | 105 | 0.019387 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
63 | MV_617_0_line_63 |  | 55 | 101 | 0.054558 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
64 | MV_617_0_line_64 |  | 55 | 99 | 0.055492 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
65 | MV_617_0_line_65 |  | 56 | 97 | 0.075153 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
66 | MV_617_0_line_66 |  | 57 | 104 | 0.003926 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
67 | MV_617_0_line_67 |  | 58 | 59 | 0.016597 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
68 | MV_617_0_line_68 |  | 59 | 60 | 0.031087 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
69 | MV_617_0_line_69 |  | 60 | 61 | 0.020657 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
70 | MV_617_0_line_70 |  | 61 | 62 | 0.051948 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
71 | MV_617_0_line_71 |  | 62 | 63 | 0.012158 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
72 | MV_617_0_line_72 |  | 62 | 64 | 0.012752 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
73 | MV_617_0_line_73 |  | 63 | 92 | 0.0055693 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
74 | MV_617_0_line_74 |  | 64 | 99 | 0.052536 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
75 | MV_617_0_line_75 |  | 65 | 66 | 0.16365 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
76 | MV_617_0_line_76 |  | 66 | 67 | 0.071376 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
77 | MV_617_0_line_77 |  | 67 | 75 | 0.020702 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
78 | MV_617_0_line_78 |  | 68 | 76 | 0.013014 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
79 | MV_617_0_line_79 |  | 69 | 70 | 0.35636 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
80 | MV_617_0_line_80 |  | 69 | 71 | 0.035771 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
81 | MV_617_0_line_81 |  | 70 | 72 | 0.47507 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
82 | MV_617_0_line_82 |  | 70 | 73 | 0.11552 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
83 | MV_617_0_line_83 |  | 71 | 75 | 0.090187 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
84 | MV_617_0_line_84 |  | 72 | 74 | 0.081284 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
85 | MV_617_0_line_85 |  | 75 | 80 | 0.088544 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
86 | MV_617_0_line_86 |  | 80 | 81 | 0.012914 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
87 | MV_617_0_line_87 |  | 82 | 83 | 0.0020582 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
88 | MV_617_0_line_88 |  | 83 | 84 | 0.037457 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
89 | MV_617_0_line_89 |  | 83 | 85 | 0.10353 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
90 | MV_617_0_line_90 |  | 84 | 88 | 0.036794 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
91 | MV_617_0_line_91 |  | 85 | 89 | 0.037329 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
92 | MV_617_0_line_92 |  | 86 | 87 | 0.0021287 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
93 | MV_617_0_line_93 |  | 87 | 100 | 0.0015428 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
94 | MV_617_0_line_94 |  | 88 | 90 | 0.040028 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
95 | MV_617_0_line_95 |  | 89 | 93 | 0.091581 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
96 | MV_617_0_line_96 |  | 90 | 95 | 0.0024063 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
97 | MV_617_0_line_97 |  | 91 | 92 | 0.058373 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
98 | MV_617_0_line_98 |  | 92 | 103 | 0.078151 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
99 | MV_617_0_line_99 |  | 93 | 94 | 0.054102 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
100 | MV_617_0_line_100 |  | 95 | 96 | 0.12998 | 0.5939 | 0.372 | 9.5 | 0 | 0.21 | 1 | 1 | ol | TRUE
101 | MV_617_0_line_101 |  | 96 | 97 | 0.091895 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
102 | MV_617_0_line_102 |  | 96 | 98 | 0.031258 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE
103 | MV_617_0_line_103 |  | 99 | 100 | 0.11839 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
104 | MV_617_0_line_104 |  | 100 | 102 | 0.058185 | 0.445 | 0.132 | 190 | 0 | 0.22 | 1 | 1 | cs | TRUE
105 | MV_617_0_line_105 |  | 103 | 104 | 0.030854 | 0.061 | 0.056 | 608 | 0 | 0.842 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | MV_617_0_trafo_99 | 25 MVA 110/20 kV | 107 | 97 | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | hv | 0 | -9 | 9 | 1.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## bus_geodata
| x | y | coords
0 | 2636717.2382 | 1237951.9869
1 | 2637255.0818 | 1237931.2749
2 | 2637381.1044 | 1237806.5758
3 | 2637339.0992 | 1238013.425
4 | 2637386.2747 | 1238227.9864
5 | 2637417.6199 | 1238199.2543
6 | 2637470.4142 | 1237993.523
7 | 2637283.5784 | 1237242.6403
8 | 2637342.6789 | 1237260.7559
9 | 2637760.1674 | 1237491.5827
10 | 2637687.1381 | 1237165.2909
11 | 2637865.5154 | 1237272.4807
12 | 2637848.6044 | 1237535.3504
13 | 2637768.8419 | 1237464.9782
14 | 2637859.0553 | 1237288.9834
15 | 2637863.0704 | 1237530.3394
16 | 2637830.6694 | 1237592.4159
17 | 2637783.8951 | 1237469.8864
18 | 2638502.8038 | 1236338.7388
19 | 2638818.9722 | 1236498.7173
20 | 2638834.5047 | 1236504.7003
21 | 2638645.027 | 1236828.3037
22 | 2638215.9452 | 1236599.1972
23 | 2638217.6618 | 1236521.6927
24 | 2638439.3067 | 1236825.1461
25 | 2638483.4474 | 1236782.9383
26 | 2638551.4945 | 1237057.2524
27 | 2638258.4125 | 1237849.8169
28 | 2638227.5203 | 1237846.0157
29 | 2638230.3553 | 1237689.9017
30 | 2638256.0935 | 1237683.6299
31 | 2638129.9323 | 1237609.706
32 | 2638383.979 | 1237729.0274
33 | 2638405.0512 | 1237623.0296
34 | 2638386.4145 | 1237724.3957
35 | 2638412.8604 | 1237599.2872
36 | 2638284.1294 | 1237681.1866
37 | 2638281.0521 | 1237577.6012
38 | 2638466.0504 | 1237136.3602
39 | 2638540.9032 | 1237106.9677
40 | 2638436.068 | 1237124.7421
41 | 2638774.448 | 1236899.3578
42 | 2638645.6238 | 1237147.2203
43 | 2638410.5222 | 1237114.8432
44 | 2638457.0407 | 1237482.2542
45 | 2638446.1018 | 1237504.4308
46 | 2638508.3527 | 1237288.786
47 | 2638801.7112 | 1237685.5223
48 | 2638369.6467 | 1237244.7059
49 | 2638837.3341 | 1237745.7042
50 | 2637787.6005 | 1238039.6485
51 | 2637724.0407 | 1237977.8714
52 | 2637651.3361 | 1237916.222
53 | 2637617.3522 | 1237882.6028
54 | 2637433.6348 | 1237820.7931
55 | 2637682.4475 | 1237833.3616
56 | 2637922.3406 | 1237551.8426
57 | 2637818.0611 | 1237630.9611
58 | 2637684.3798 | 1237750.7653
59 | 2637693.7096 | 1237737.0386
60 | 2637711.2037 | 1237711.311
61 | 2637728.1947 | 1237723.0598
62 | 2637770.9226 | 1237752.6051
63 | 2637776.7389 | 1237741.9287
64 | 2637763.7241 | 1237763.1307
65 | 2638360.7992 | 1237240.5573
66 | 2638228.4336 | 1237167.8255
67 | 2638195.8569 | 1237231.3341
68 | 2638422.0359 | 1237085.7659
69 | 2638074.6788 | 1237191.5985
70 | 2637973.7213 | 1236962.5193
71 | 2638106.3495 | 1237208.227
72 | 2637662.6132 | 1237089.6989
73 | 2638025.2172 | 1236859.1164
74 | 2637606.5429 | 1237148.5479
75 | 2638186.4027 | 1237249.7628
76 | 2638426.454 | 1237073.5249
77 | 2639235.5799 | 1236485.6098
78 | 2638739.1328 | 1236947.7582
79 | 2638643.7977 | 1237156.9591
80 | 2638139.4302 | 1237322.6742
81 | 2638142.2923 | 1237335.2672
82 | 2637989.3936 | 1237845.2244
83 | 2637990.5437 | 1237843.5175
84 | 2638011.6482 | 1237812.5713
85 | 2638057.2548 | 1237906.3395
86 | 2637827.2096 | 1237872.4244
87 | 2637825.6066 | 1237871.0238
88 | 2638031.9661 | 1237781.9163
89 | 2638086.4405 | 1237929.6967
90 | 2638048.2406 | 1237745.419
91 | 2637831.3195 | 1237763.7231
92 | 2637779.4033 | 1237737.038
93 | 2638098.9227 | 1238020.4231
94 | 2638049.2983 | 1238041.9746
95 | 2638049.0624 | 1237743.1574
96 | 2638076.4451 | 1237616.0895
97 | 2637992.2552 | 1237579.3722
98 | 2638095.5466 | 1237591.3073
99 | 2637727.8049 | 1237801.24
100 | 2637824.4448 | 1237870.0086
101 | 2637637.07 | 1237803.0711
102 | 2637789.7596 | 1237916.725
103 | 2637806.6563 | 1237663.8185
104 | 2637816.7737 | 1237634.67
105 | 2637422.3322 | 1237836.5652
106 | 2637483.0948 | 1237967.404
107 | 2637992.2552 | 1237579.3722

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9976 | -0.0036013 | 0.19113 | 0.092571
1 | 0.9978 | -0.0023377 | 0 | 0
2 | 0.99798 | -0.0040207 | 0 | 0
3 | 0.99772 | -0.0016116 | 0.52159 | 0.25262
4 | 0.99769 | -0.0019417 | 0.35276 | 0.17085
5 | 0.99772 | -0.0017595 | 0 | 0
6 | 0.99783 | -0.0027579 | 0 | 0
7 | 0.9993 | -0.0043083 | 0.19534 | 0.094609
8 | 0.99932 | -0.0044498 | 0 | 0
9 | 0.99949 | -0.0056287 | 0 | 0
10 | 0.99928 | -0.0039815 | 0 | 0
11 | 0.99913 | -0.0027034 | 0 | 0
12 | 0.99962 | -0.0066767 | 0 | 0
13 | 0.99947 | -0.0054781 | 0.36113 | 0.17491
14 | 0.99912 | -0.002622 | 0.38455 | 0.18625
15 | 0.99966 | -0.0059864 | 0 | 0
16 | 0.9995 | -0.0088906 | 0.6437 | 0.31176
17 | 0.99947 | -0.0054608 | 0.092009 | 0.044562
18 | 0.99335 | -0.072869 | 0.28018 | 0.1357
19 | 0.99354 | -0.071647 | 0 | 0
20 | 0.99353 | -0.071516 | 0.39165 | 0.18968
21 | 0.99411 | -0.076811 | 0 | 0
22 | 0.99467 | -0.076216 | 0 | 0
23 | 0.99463 | -0.075842 | 0.40203 | 0.19471
24 | 0.99492 | -0.0746 | 0.28297 | 0.13705
25 | 0.99497 | -0.07511 | 0 | 0
26 | 0.99523 | -0.077463 | 0 | 0
27 | 0.99916 | -0.013303 | 0.38155 | 0.18479
28 | 0.99917 | -0.013444 | 0 | 0
29 | 0.99929 | -0.012712 | 0 | 0
30 | 0.99925 | -0.013377 | 0.32184 | 0.15587
31 | 0.99968 | -0.005786 | 0 | 0
32 | 0.99886 | -0.026285 | 0 | 0
33 | 0.99868 | -0.029539 | 0 | 0
34 | 0.99886 | -0.02626 | 0.41252 | 0.19979
35 | 0.99865 | -0.030057 | 0.33551 | 0.16249
36 | 0.99923 | -0.013517 | 0 | 0
37 | 0.99915 | -0.014032 | 0.41052 | 0.19882
38 | 0.99572 | -0.081702 | 0 | 0
39 | 0.99513 | -0.076559 | 0.074553 | 0.036108
40 | 0.99581 | -0.0825 | 0.087077 | 0.042173
41 | 0.99437 | -0.074962 | 0.26836 | 0.12997
42 | 0.99481 | -0.078793 | 0 | 0
43 | 0.99589 | -0.083208 | 0 | 0
44 | 0.99805 | -0.044414 | 0.33823 | 0.16381
45 | 0.99811 | -0.043739 | 0 | 0
46 | 0.99705 | -0.06973 | 0.22788 | 0.11037
47 | 0.99837 | -0.031828 | 0 | 0
48 | 0.99636 | -0.087202 | 0.26424 | 0.12798
49 | 0.99832 | -0.032137 | 0.3646 | 0.17658
50 | 0.99841 | -0.0076246 | 0.38844 | 0.18813
51 | 0.99846 | -0.0080318 | 0.090404 | 0.043784
52 | 0.99851 | -0.0085654 | 0.070731 | 0.034256
53 | 0.99855 | -0.0088654 | 0 | 0
54 | 0.99809 | -0.0049675 | 0 | 0
55 | 0.99875 | -0.010621 | 0 | 0
56 | 0.99981 | -0.0033823 | 0.96938 | 0.46949
57 | 0.99942 | -0.010291 | 0 | 0
58 | 0.99899 | -0.012518 | 0.27022 | 0.13088
59 | 0.99899 | -0.012571 | 0 | 0
60 | 0.999 | -0.01267 | 0 | 0
61 | 0.99901 | -0.012736 | 2.2141 | 1.0724
62 | 0.99917 | -0.014275 | 0 | 0
63 | 0.99921 | -0.013849 | 0.1202 | 0.058217
64 | 0.99912 | -0.013766 | 0.3221 | 0.156
65 | 0.99631 | -0.086805 | 0 | 0
66 | 0.99603 | -0.084447 | 0 | 0
67 | 0.99585 | -0.085751 | 0.37307 | 0.18069
68 | 0.99589 | -0.083179 | 0 | 0
69 | 0.99564 | -0.086364 | 0 | 0
70 | 0.99531 | -0.083526 | 0 | 0
71 | 0.99568 | -0.086638 | 0.10608 | 0.051379
72 | 0.99508 | -0.081501 | 0 | 0
73 | 0.99523 | -0.084034 | 0.35969 | 0.1742
74 | 0.99502 | -0.081882 | 0.38335 | 0.18566
75 | 0.99583 | -0.085543 | 0 | 0
76 | 0.99589 | -0.083167 | 0.08005 | 0.03877
77 | 0.99332 | -0.072816 | 0.26281 | 0.12729
78 | 0.99447 | -0.075782 | 0 | 0
79 | 0.99481 | -0.078758 | 0.2871 | 0.13905
80 | 0.99581 | -0.085434 | 0 | 0
81 | 0.99581 | -0.085417 | 0.10964 | 0.053099
82 | 0.99856 | -0.0069481 | 0.77288 | 0.37432
83 | 0.99856 | -0.0069672 | 0 | 0
84 | 0.99863 | -0.0075559 | 0.75505 | 0.36569
85 | 0.99849 | -0.0062884 | 0 | 0
86 | 0.99872 | -0.010196 | 0.78314 | 0.37929
87 | 0.99872 | -0.010216 | 0.29045 | 0.14067
88 | 0.99872 | -0.0084652 | 0.37067 | 0.17953
89 | 0.99846 | -0.0060397 | 0.1458 | 0.070615
90 | 0.99885 | -0.0096299 | 0.54917 | 0.26598
91 | 0.99918 | -0.013334 | 0.55004 | 0.2664
92 | 0.99922 | -0.013716 | 0.76413 | 0.37008
93 | 0.99839 | -0.0064988 | 0 | 0
94 | 0.99835 | -0.0067696 | 0.41267 | 0.19987
95 | 0.99886 | -0.0097157 | 0.6653 | 0.32222
96 | 0.99978 | -0.003867 | 0 | 0
97 | 1 | 0 | -22.4657 | -10.6507
98 | 0.99973 | -0.0047441 | 0.33309 | 0.16132
99 | 0.9989 | -0.011869 | 0 | 0
100 | 0.99872 | -0.010236 | 0 | 0
101 | 0.99875 | -0.01056 | 0.097545 | 0.047243
102 | 0.99872 | -0.010175 | 0.09209 | 0.044601
103 | 0.99935 | -0.011458 | 1.1836 | 0.57323
104 | 0.99941 | -0.010427 | 0.28795 | 0.13946
105 | 0.99806 | -0.0046621 | 0.26706 | 0.12934
106 | 0.99783 | -0.0027149 | 0.10064 | 0.048744
107 | 0.99997 | 149.9981 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.19113 | -0.092571 | 0.19117 | 0.091954 | 3.617e-05 | -0.00061694 | 0.0061454 | 0.0061374 | 0.0061454 | 0.9976 | -0.0036013 | 0.9978 | -0.0023377 | 2.9264
1 | -0.71281 | -0.34179 | 0.71295 | 0.33695 | 0.00014316 | -0.0048447 | 0.022871 | 0.02281 | 0.022871 | 0.9978 | -0.0023377 | 0.99798 | -0.0040207 | 10.3958
2 | 0.52164 | 0.24984 | -0.52159 | -0.25262 | 4.4016e-05 | -0.0027799 | 0.016733 | 0.016768 | 0.016768 | 0.9978 | -0.0023377 | 0.99772 | -0.0016116 | 7.622
3 | 0.45353 | 0.20662 | -0.45345 | -0.21283 | 7.316e-05 | -0.0062154 | 0.014416 | 0.014492 | 0.014492 | 0.99798 | -0.0040207 | 0.99783 | -0.0027579 | 6.5871
4 | -1.1665 | -0.54357 | 1.1666 | 0.54239 | 9.4096e-05 | -0.0011822 | 0.037225 | 0.03721 | 0.037225 | 0.99798 | -0.0040207 | 0.99806 | -0.0046621 | 16.9205
5 | -0.35276 | -0.17085 | 0.35277 | 0.1708 | 9.7434e-06 | -4.4426e-05 | 0.011341 | 0.01134 | 0.011341 | 0.99769 | -0.0019417 | 0.99772 | -0.0017595 | 5.4004
6 | -0.35277 | -0.1708 | 0.35281 | 0.16495 | 4.2064e-05 | -0.0058492 | 0.01134 | 0.011267 | 0.01134 | 0.99772 | -0.0017595 | 0.99783 | -0.0027579 | 5.1547
7 | 0.10064 | 0.047879 | -0.10064 | -0.048744 | 5.0663e-07 | -0.00086472 | 0.0032243 | 0.0032352 | 0.0032352 | 0.99783 | -0.0027579 | 0.99783 | -0.0027149 | 1.4705
8 | -0.19534 | -0.094609 | 0.19535 | 0.093139 | 3.2286e-06 | -0.0014701 | 0.00627 | 0.0062516 | 0.00627 | 0.9993 | -0.0043083 | 0.99932 | -0.0044498 | 2.85
9 | -0.19535 | -0.093139 | 0.19538 | 0.076864 | 3.4525e-05 | -0.016274 | 0.0062516 | 0.006064 | 0.0062516 | 0.99932 | -0.0044498 | 0.99949 | -0.0056287 | 2.8416
10 | -1.0332 | -0.46384 | 1.0334 | 0.46137 | 0.00015019 | -0.0024658 | 0.032711 | 0.032682 | 0.032711 | 0.99949 | -0.0056287 | 0.99962 | -0.0066767 | 14.8687
11 | 0.45315 | 0.21842 | -0.45314 | -0.21909 | 7.8905e-06 | -0.00066508 | 0.014529 | 0.014538 | 0.014538 | 0.99949 | -0.0056287 | 0.99947 | -0.0054781 | 6.608
12 | 0.3847 | 0.16855 | -0.38461 | -0.17885 | 8.592e-05 | -0.010301 | 0.012131 | 0.012253 | 0.012253 | 0.99949 | -0.0056287 | 0.99928 | -0.0039815 | 5.5697
13 | 0.38461 | 0.17885 | -0.38455 | -0.18582 | 5.9199e-05 | -0.0069737 | 0.012253 | 0.01234 | 0.01234 | 0.99928 | -0.0039815 | 0.99913 | -0.0027034 | 5.609
14 | 0.38455 | 0.18582 | -0.38455 | -0.18625 | 3.6031e-06 | -0.00042121 | 0.01234 | 0.012345 | 0.012345 | 0.99913 | -0.0027034 | 0.99912 | -0.002622 | 5.6115
15 | -10.6423 | -5.0496 | 10.6427 | 5.0486 | 0.0003541 | -0.00095163 | 0.34017 | 0.34016 | 0.34017 | 0.99962 | -0.0066767 | 0.99966 | -0.0059864 | 40.4007
16 | 9.609 | 4.5882 | -9.6079 | -4.5918 | 0.0010356 | -0.003617 | 0.3075 | 0.30756 | 0.30756 | 0.99962 | -0.0066767 | 0.9995 | -0.0088906 | 36.5272
17 | 0.09201 | 0.044185 | -0.092009 | -0.044562 | 1.84e-07 | -0.00037758 | 0.002948 | 0.0029528 | 0.0029528 | 0.99947 | -0.0054781 | 0.99947 | -0.0054608 | 1.3422
18 | -10.6427 | -5.0486 | 10.644 | 5.045 | 0.0013349 | -0.0035894 | 0.34016 | 0.3401 | 0.34016 | 0.99966 | -0.0059864 | 0.99981 | -0.0033823 | 40.3989
19 | 8.9642 | 4.2801 | -8.9636 | -4.2826 | 0.00061097 | -0.0025343 | 0.2869 | 0.28694 | 0.28694 | 0.9995 | -0.0088906 | 0.99942 | -0.010291 | 34.0785
20 | -0.28018 | -0.1357 | 0.28023 | 0.13531 | 5.1643e-05 | -0.00038513 | 0.009047 | 0.0090417 | 0.009047 | 0.99335 | -0.072869 | 0.99354 | -0.071647 | 4.3081
21 | 0.65452 | 0.31614 | -0.65451 | -0.31653 | 9.888e-06 | -0.00038835 | 0.021119 | 0.021124 | 0.021124 | 0.99354 | -0.071647 | 0.99353 | -0.071516 | 9.602
22 | -0.93475 | -0.45145 | 0.93533 | 0.44043 | 0.00057372 | -0.011022 | 0.030161 | 0.030021 | 0.030161 | 0.99354 | -0.071647 | 0.99411 | -0.076811 | 13.7096
23 | 0.26286 | 0.12685 | -0.26281 | -0.12729 | 5.1487e-05 | -0.00044081 | 0.0084804 | 0.0084864 | 0.0084864 | 0.99353 | -0.071516 | 0.99332 | -0.072816 | 4.0412
24 | -0.93533 | -0.44043 | 0.93556 | 0.4404 | 0.00023707 | -2.5741e-05 | 0.030021 | 0.030019 | 0.030021 | 0.99411 | -0.076811 | 0.99437 | -0.074962 | 14.2958
25 | 0.40205 | 0.19288 | -0.40203 | -0.19471 | 1.7428e-05 | -0.0018327 | 0.012942 | 0.012965 | 0.012965 | 0.99467 | -0.076216 | 0.99463 | -0.075842 | 5.8931
26 | -0.40205 | -0.19288 | 0.40214 | 0.19256 | 9.4776e-05 | -0.00031599 | 0.012942 | 0.012937 | 0.012942 | 0.99467 | -0.076216 | 0.99492 | -0.0746 | 6.1627
27 | -0.68512 | -0.32961 | 0.68516 | 0.32814 | 4.0902e-05 | -0.0014772 | 0.02206 | 0.022041 | 0.02206 | 0.99492 | -0.0746 | 0.99497 | -0.07511 | 10.0271
28 | -0.68516 | -0.32814 | 0.68535 | 0.32107 | 0.00019455 | -0.0070633 | 0.022041 | 0.021952 | 0.022041 | 0.99497 | -0.07511 | 0.99523 | -0.077463 | 10.0186
29 | -2.2521 | -1.0588 | 2.2533 | 1.0552 | 0.0011782 | -0.0036609 | 0.072184 | 0.072135 | 0.072184 | 0.99523 | -0.077463 | 0.99572 | -0.081702 | 32.811
30 | 1.5668 | 0.73777 | -1.5666 | -0.73893 | 0.0001729 | -0.0011621 | 0.050232 | 0.050247 | 0.050247 | 0.99523 | -0.077463 | 0.99513 | -0.076559 | 22.8394
31 | -0.38155 | -0.18479 | 0.38155 | 0.18405 | 6.211e-06 | -0.00073792 | 0.012248 | 0.012239 | 0.012248 | 0.99916 | -0.013303 | 0.99917 | -0.013444 | 5.5675
32 | -0.38155 | -0.18405 | 0.38159 | 0.18389 | 4.1664e-05 | -0.00016002 | 0.012239 | 0.012237 | 0.012239 | 0.99917 | -0.013444 | 0.99929 | -0.012712 | 5.8281
33 | 6.4413 | 3.0382 | -6.4411 | -3.04 | 0.00020465 | -0.0018276 | 0.20574 | 0.20576 | 0.20576 | 0.99929 | -0.012712 | 0.99925 | -0.013377 | 24.4371
34 | -6.8228 | -3.2221 | 6.8251 | 3.2043 | 0.0022538 | -0.017738 | 0.21797 | 0.21773 | 0.21797 | 0.99929 | -0.012712 | 0.99968 | -0.005786 | 25.8874
35 | 5.7087 | 2.6854 | -5.707 | -2.6835 | 0.0016066 | 0.0019754 | 0.18225 | 0.18226 | 0.18226 | 0.99925 | -0.013377 | 0.99886 | -0.026285 | 22.2266
36 | 0.41056 | 0.19869 | -0.41055 | -0.19872 | 8.706e-06 | -2.8092e-05 | 0.013177 | 0.013177 | 0.013177 | 0.99925 | -0.013377 | 0.99923 | -0.013517 | 6.2748
37 | -6.8251 | -3.2043 | 6.8254 | 3.2017 | 0.0003375 | -0.0026613 | 0.21773 | 0.21769 | 0.21773 | 0.99968 | -0.005786 | 0.99973 | -0.0047441 | 25.8584
38 | 5.2945 | 2.4838 | -5.2937 | -2.495 | 0.00081982 | -0.01119 | 0.16901 | 0.16916 | 0.16916 | 0.99886 | -0.026285 | 0.99868 | -0.029539 | 20.0904
39 | 0.41252 | 0.19967 | -0.41252 | -0.19979 | 1.225e-06 | -0.00012422 | 0.013245 | 0.013247 | 0.013247 | 0.99886 | -0.026285 | 0.99886 | -0.02626 | 6.0212
40 | 5.2937 | 2.495 | -5.2936 | -2.4968 | 0.00013088 | -0.0017841 | 0.16916 | 0.16918 | 0.16918 | 0.99868 | -0.029539 | 0.99865 | -0.030057 | 20.0932
41 | 0.36471 | 0.1761 | -0.36462 | -0.17651 | 9.7312e-05 | -0.00041312 | 0.011707 | 0.011713 | 0.011713 | 0.99865 | -0.030057 | 0.99837 | -0.031828 | 5.5777
42 | 4.5934 | 2.1582 | -4.5914 | -2.156 | 0.0019858 | 0.0021455 | 0.1467 | 0.1467 | 0.1467 | 0.99865 | -0.030057 | 0.99811 | -0.043739 | 41.9156
43 | 0.41055 | 0.19872 | -0.41052 | -0.19882 | 3.2064e-05 | -0.00010343 | 0.013177 | 0.013179 | 0.013179 | 0.99923 | -0.013517 | 0.99915 | -0.014032 | 6.2756
44 | -2.2533 | -1.0552 | 2.2535 | 1.0545 | 0.00022334 | -0.000695 | 0.072135 | 0.072125 | 0.072135 | 0.99572 | -0.081702 | 0.99581 | -0.0825 | 32.7885
45 | 1.492 | 0.70282 | -1.4916 | -0.70267 | 0.00045757 | 0.00015402 | 0.047844 | 0.047845 | 0.047845 | 0.99513 | -0.076559 | 0.99481 | -0.078793 | 22.7835
46 | -2.3406 | -1.0967 | 2.3408 | 1.0961 | 0.00020533 | -0.00058781 | 0.07493 | 0.074922 | 0.07493 | 0.99581 | -0.0825 | 0.99589 | -0.083208 | 34.059
47 | -1.2039 | -0.57038 | 1.204 | 0.569 | 0.00011948 | -0.0013779 | 0.038675 | 0.038657 | 0.038675 | 0.99437 | -0.074962 | 0.99447 | -0.075782 | 17.5796
48 | 0.2871 | 0.13881 | -0.2871 | -0.13905 | 1.1331e-06 | -0.0002338 | 0.0092537 | 0.0092567 | 0.0092567 | 0.99481 | -0.078793 | 0.99481 | -0.078758 | 4.2076
49 | 1.2045 | 0.56386 | -1.204 | -0.569 | 0.00044484 | -0.0051438 | 0.038592 | 0.038657 | 0.038657 | 0.99481 | -0.078793 | 0.99447 | -0.075782 | 17.5716
50 | 0.080051 | 0.037722 | -0.080051 | -0.038462 | 2.7563e-07 | -0.00074031 | 0.0025651 | 0.0025743 | 0.0025743 | 0.99589 | -0.083208 | 0.99589 | -0.083179 | 1.1702
51 | -2.4209 | -1.1338 | 2.4219 | 1.1309 | 0.0010832 | -0.0028817 | 0.077487 | 0.077448 | 0.077487 | 0.99589 | -0.083208 | 0.99631 | -0.086805 | 35.2214
52 | -4.5911 | -2.1567 | 4.5914 | 2.156 | 0.00025696 | -0.00065796 | 0.14671 | 0.1467 | 0.14671 | 0.99805 | -0.044414 | 0.99811 | -0.043739 | 40.529
53 | 4.2529 | 1.9929 | -4.2495 | -1.9892 | 0.0033909 | 0.0036282 | 0.13585 | 0.13585 | 0.13585 | 0.99805 | -0.044414 | 0.99705 | -0.06973 | 38.814
54 | 4.0216 | 1.8789 | -4.0194 | -1.8765 | 0.0022068 | 0.0023425 | 0.12852 | 0.12852 | 0.12852 | 0.99705 | -0.06973 | 0.99636 | -0.087202 | 36.7202
55 | 0.36462 | 0.17651 | -0.3646 | -0.17658 | 1.7097e-05 | -7.2504e-05 | 0.011713 | 0.011714 | 0.011714 | 0.99837 | -0.031828 | 0.99832 | -0.032137 | 5.5782
56 | 3.7552 | 1.7486 | -3.755 | -1.7487 | 0.00018745 | -0.00017544 | 0.12002 | 0.12002 | 0.12002 | 0.99636 | -0.087202 | 0.99631 | -0.086805 | 54.5537
57 | -0.38844 | -0.18813 | 0.38845 | 0.18602 | 1.8387e-05 | -0.0021042 | 0.012479 | 0.012452 | 0.012479 | 0.99841 | -0.0076246 | 0.99846 | -0.0080318 | 5.6722
58 | -0.47886 | -0.22981 | 0.47889 | 0.22752 | 3.0278e-05 | -0.0022846 | 0.015357 | 0.015328 | 0.015357 | 0.99846 | -0.0080318 | 0.99851 | -0.0085654 | 6.9803
59 | -0.54962 | -0.26178 | 0.54964 | 0.26065 | 1.9752e-05 | -0.0011321 | 0.0176 | 0.017586 | 0.0176 | 0.99851 | -0.0085654 | 0.99855 | -0.0088654 | 8
60 | 1.4344 | 0.66552 | -1.4337 | -0.67128 | 0.00070073 | -0.0057597 | 0.045713 | 0.045786 | 0.045786 | 0.99855 | -0.0088654 | 0.99809 | -0.0049675 | 20.812
61 | -1.984 | -0.92617 | 1.9845 | 0.92436 | 0.00043628 | -0.0018135 | 0.063299 | 0.063275 | 0.063299 | 0.99855 | -0.0088654 | 0.99875 | -0.010621 | 28.7722
62 | 1.4337 | 0.67128 | -1.4336 | -0.67173 | 5.4265e-05 | -0.00044501 | 0.045786 | 0.045792 | 0.045792 | 0.99809 | -0.0049675 | 0.99806 | -0.0046621 | 20.8145
63 | 0.097545 | 0.045944 | -0.097545 | -0.047243 | 7.1107e-07 | -0.0012992 | 0.0031165 | 0.0031327 | 0.0031327 | 0.99875 | -0.010621 | 0.99875 | -0.01056 | 1.4239
64 | -2.082 | -0.9703 | 2.0823 | 0.96908 | 0.00032646 | -0.001225 | 0.066392 | 0.066376 | 0.066392 | 0.99875 | -0.010621 | 0.9989 | -0.011869 | 30.178
65 | -11.6134 | -5.5145 | 11.6153 | 5.5105 | 0.0018946 | -0.0040015 | 0.3712 | 0.37113 | 0.3712 | 0.99981 | -0.0033823 | 1 | 0 | 44.0851
66 | 8.9636 | 4.2826 | -8.9635 | -4.2828 | 5.9155e-05 | -0.0002453 | 0.28694 | 0.28694 | 0.28694 | 0.99942 | -0.010291 | 0.99941 | -0.010427 | 34.0789
67 | -0.27022 | -0.13088 | 0.27023 | 0.13048 | 1.667e-06 | -0.00039498 | 0.0086763 | 0.0086713 | 0.0086763 | 0.99899 | -0.012518 | 0.99899 | -0.012571 | 3.9438
68 | -0.27023 | -0.13048 | 0.27023 | 0.12974 | 3.1172e-06 | -0.00073982 | 0.0086713 | 0.008662 | 0.0086713 | 0.99899 | -0.012571 | 0.999 | -0.01267 | 3.9415
69 | -0.27023 | -0.12974 | 0.27023 | 0.12925 | 2.0677e-06 | -0.00049162 | 0.008662 | 0.0086558 | 0.008662 | 0.999 | -0.01267 | 0.99901 | -0.012736 | 3.9373
70 | -2.4844 | -1.2016 | 2.4848 | 1.2005 | 0.00044092 | -0.0011073 | 0.079744 | 0.079729 | 0.079744 | 0.99901 | -0.012736 | 0.99917 | -0.014275 | 36.2474
71 | -6.0561 | -2.8846 | 6.0563 | 2.8844 | 0.00022056 | -0.00025614 | 0.1938 | 0.1938 | 0.1938 | 0.99917 | -0.014275 | 0.99921 | -0.013849 | 53.5371
72 | 3.5713 | 1.6842 | -3.5711 | -1.6844 | 0.00022155 | -0.00023822 | 0.11408 | 0.11408 | 0.11408 | 0.99917 | -0.014275 | 0.99912 | -0.013766 | 51.8552
73 | -6.1765 | -2.9426 | 6.1766 | 2.9422 | 3.9817e-05 | -0.0003883 | 0.19766 | 0.19765 | 0.19766 | 0.99921 | -0.013849 | 0.99922 | -0.013716 | 23.4748
74 | 3.249 | 1.5284 | -3.2482 | -1.5294 | 0.00075493 | -0.0010279 | 0.10374 | 0.10376 | 0.10376 | 0.99912 | -0.013766 | 0.9989 | -0.011869 | 47.1622
75 | 1.333 | 0.61782 | -1.3326 | -0.62158 | 0.00039637 | -0.0037599 | 0.042571 | 0.042618 | 0.042618 | 0.99631 | -0.086805 | 0.99603 | -0.084447 | 19.3718
76 | 1.3326 | 0.62158 | -1.3324 | -0.62152 | 0.00023099 | 6.0162e-05 | 0.042618 | 0.042619 | 0.042619 | 0.99603 | -0.084447 | 0.99585 | -0.085751 | 20.2947
77 | 0.95934 | 0.44083 | -0.95932 | -0.44131 | 2.5891e-05 | -0.0004825 | 0.030605 | 0.030611 | 0.030611 | 0.99585 | -0.085751 | 0.99583 | -0.085543 | 13.9139
78 | 0.080051 | 0.038462 | -0.08005 | -0.03877 | 1.1531e-07 | -0.00030814 | 0.0025743 | 0.0025782 | 0.0025782 | 0.99589 | -0.083179 | 0.99589 | -0.083167 | 1.1719
79 | 0.74345 | 0.34011 | -0.74318 | -0.34846 | 0.00026846 | -0.0083521 | 0.023704 | 0.023807 | 0.023807 | 0.99564 | -0.086364 | 0.99531 | -0.083526 | 10.8212
80 | -0.74345 | -0.34011 | 0.74348 | 0.33927 | 2.682e-05 | -0.00083871 | 0.023704 | 0.023694 | 0.023704 | 0.99564 | -0.086364 | 0.99568 | -0.086638 | 10.7745
81 | 0.38347 | 0.17438 | -0.38337 | -0.18558 | 9.5736e-05 | -0.011206 | 0.012218 | 0.012356 | 0.012356 | 0.99531 | -0.083526 | 0.99508 | -0.081501 | 5.6165
82 | 0.35971 | 0.17408 | -0.35969 | -0.1742 | 2.7653e-05 | -0.00011928 | 0.011591 | 0.011592 | 0.011592 | 0.99531 | -0.083526 | 0.99523 | -0.084034 | 5.5201
83 | -0.84956 | -0.39065 | 0.84968 | 0.39062 | 0.00011809 | -3.2783e-05 | 0.02711 | 0.027109 | 0.02711 | 0.99568 | -0.086638 | 0.99583 | -0.085543 | 12.9097
84 | 0.38337 | 0.18558 | -0.38335 | -0.18566 | 2.2114e-05 | -8.2227e-05 | 0.012356 | 0.012358 | 0.012358 | 0.99508 | -0.081501 | 0.99502 | -0.081882 | 5.8846
85 | 0.10964 | 0.050697 | -0.10964 | -0.052793 | 1.46e-06 | -0.002096 | 0.0035016 | 0.0035275 | 0.0035275 | 0.99583 | -0.085543 | 0.99581 | -0.085434 | 1.6034
86 | 0.10964 | 0.052793 | -0.10964 | -0.053099 | 2.1476e-07 | -0.0003057 | 0.0035275 | 0.0035314 | 0.0035314 | 0.99581 | -0.085434 | 0.99581 | -0.085417 | 1.6052
87 | -0.77288 | -0.37432 | 0.77288 | 0.37427 | 1.6934e-06 | -4.8499e-05 | 0.024826 | 0.024825 | 0.024826 | 0.99856 | -0.0069481 | 0.99856 | -0.0069672 | 11.2845
88 | -1.3315 | -0.64127 | 1.3316 | 0.64041 | 9.125e-05 | -0.00086476 | 0.042723 | 0.042712 | 0.042723 | 0.99856 | -0.0069672 | 0.99863 | -0.0075559 | 19.4196
89 | 0.55858 | 0.267 | -0.55854 | -0.26945 | 4.4353e-05 | -0.0024515 | 0.017898 | 0.017929 | 0.017929 | 0.99856 | -0.0069672 | 0.99849 | -0.0062884 | 8.1495
90 | -2.0866 | -1.0061 | 2.0868 | 1.0053 | 0.00022022 | -0.00081084 | 0.066963 | 0.066952 | 0.066963 | 0.99863 | -0.0075559 | 0.99872 | -0.0084652 | 30.4379
91 | 0.55854 | 0.26945 | -0.55852 | -0.27034 | 1.6029e-05 | -0.0008838 | 0.017929 | 0.01794 | 0.01794 | 0.99849 | -0.0062884 | 0.99846 | -0.0060397 | 8.1546
92 | -0.78314 | -0.37929 | 0.78314 | 0.37924 | 1.7977e-06 | -5.0162e-05 | 0.025152 | 0.025151 | 0.025152 | 0.99872 | -0.010196 | 0.99872 | -0.010216 | 11.4325
93 | -1.0736 | -0.51991 | 1.0736 | 0.51988 | 2.4485e-06 | -3.6017e-05 | 0.034479 | 0.034478 | 0.034479 | 0.99872 | -0.010216 | 0.99872 | -0.010236 | 15.6722
94 | -2.4575 | -1.1848 | 2.4578 | 1.184 | 0.00033225 | -0.00085485 | 0.078857 | 0.078845 | 0.078857 | 0.99872 | -0.0084652 | 0.99885 | -0.0096299 | 35.8441
95 | 0.41272 | 0.19972 | -0.41269 | -0.19981 | 2.8676e-05 | -9.1024e-05 | 0.013256 | 0.013258 | 0.013258 | 0.99846 | -0.0060397 | 0.99839 | -0.0064988 | 6.3131
96 | -3.007 | -1.4499 | 3.007 | 1.4499 | 2.9902e-05 | -4.8451e-05 | 0.09648 | 0.096479 | 0.09648 | 0.99885 | -0.0096299 | 0.99886 | -0.0097157 | 43.8546
97 | -0.55004 | -0.2664 | 0.55006 | 0.26501 | 2.4271e-05 | -0.0013843 | 0.017657 | 0.017639 | 0.017657 | 0.99918 | -0.013334 | 0.99922 | -0.013716 | 8.0259
98 | -7.4908 | -3.5773 | 7.4916 | 3.5721 | 0.00082228 | -0.0052076 | 0.23982 | 0.23975 | 0.23982 | 0.99922 | -0.013716 | 0.99935 | -0.011458 | 28.4821
99 | 0.41269 | 0.19981 | -0.41267 | -0.19987 | 1.6944e-05 | -5.3764e-05 | 0.013258 | 0.013258 | 0.013258 | 0.99839 | -0.0064988 | 0.99835 | -0.0067696 | 6.3135
100 | -3.6723 | -1.7721 | 3.6755 | 1.774 | 0.0032161 | 0.0018595 | 0.11784 | 0.11784 | 0.11784 | 0.99886 | -0.0097157 | 0.99978 | -0.003867 | 56.1158
101 | -10.8344 | -5.1348 | 10.8364 | 5.1297 | 0.0020149 | -0.0051698 | 0.34619 | 0.3461 | 0.34619 | 0.99978 | -0.003867 | 1 | 0 | 41.1146
102 | 7.1588 | 3.3609 | -7.1585 | -3.363 | 0.00029831 | -0.0021132 | 0.22835 | 0.22838 | 0.22838 | 0.99978 | -0.003867 | 0.99973 | -0.0047441 | 27.1232
103 | 1.1659 | 0.56034 | -1.1657 | -0.56309 | 0.00022109 | -0.0027544 | 0.037383 | 0.037419 | 0.037419 | 0.9989 | -0.011869 | 0.99872 | -0.010236 | 17.0085
104 | 0.092091 | 0.043216 | -0.09209 | -0.044601 | 6.7549e-07 | -0.0013855 | 0.0029404 | 0.0029576 | 0.0029576 | 0.99872 | -0.010236 | 0.99872 | -0.010175 | 1.3444
105 | -8.6752 | -4.1453 | 8.6756 | 4.1434 | 0.00043549 | -0.0019547 | 0.27773 | 0.2777 | 0.27773 | 0.99935 | -0.011458 | 0.99941 | -0.010427 | 32.9849

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.6518e-14 | 1.7507e-14 | 0.013999 | 0.0105 | 0.013999 | 0.0105 | 1.6678e-16 | 0.00050517 | 0.99997 | 149.9981 | 1 | 0 | 0.069998

## res_ext_grid
| p_mw | q_mvar
0 | 22.4657 | 10.6507

## res_load
| p_mw | q_mvar
0 | 0.19113 | 0.092571
1 | 0.52159 | 0.25262
2 | 0.35276 | 0.17085
3 | 0.19534 | 0.094609
4 | 0.36113 | 0.17491
5 | 0.38455 | 0.18625
6 | 0.6437 | 0.31176
7 | 0.092009 | 0.044562
8 | 0.28018 | 0.1357
9 | 0.39165 | 0.18968
10 | 0.40203 | 0.19471
11 | 0.28297 | 0.13705
12 | 0.38155 | 0.18479
13 | 0.32184 | 0.15587
14 | 0.41252 | 0.19979
15 | 0.33551 | 0.16249
16 | 0.41052 | 0.19882
17 | 0.074553 | 0.036108
18 | 0.087077 | 0.042173
19 | 0.26836 | 0.12997
20 | 0.33823 | 0.16381
21 | 0.22788 | 0.11037
22 | 0.26424 | 0.12798
23 | 0.3646 | 0.17658
24 | 0.38844 | 0.18813
25 | 0.090404 | 0.043784
26 | 0.070731 | 0.034256
27 | 0.96938 | 0.46949
28 | 0.27022 | 0.13088
29 | 2.2141 | 1.0724
30 | 0.1202 | 0.058217
31 | 0.3221 | 0.156
32 | 0.37307 | 0.18069
33 | 0.10608 | 0.051379
34 | 0.35969 | 0.1742
35 | 0.38335 | 0.18566
36 | 0.08005 | 0.03877
37 | 0.26281 | 0.12729
38 | 0.2871 | 0.13905
39 | 0.10964 | 0.053099
40 | 0.77288 | 0.37432
41 | 0.75505 | 0.36569
42 | 0.78314 | 0.37929
43 | 0.29045 | 0.14067
44 | 0.37067 | 0.17953
45 | 0.1458 | 0.070615
46 | 0.54917 | 0.26598
47 | 0.55004 | 0.2664
48 | 0.76413 | 0.37008
49 | 0.41267 | 0.19987
50 | 0.6653 | 0.32222
51 | 0.33309 | 0.16132
52 | 0.097545 | 0.047243
53 | 0.09209 | 0.044601
54 | 1.1836 | 0.57323
55 | 0.28795 | 0.13946
56 | 0.26706 | 0.12934
57 | 0.10064 | 0.048744

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | bus_geodata | x | float64
59 | bus_geodata | y | float64
60 | bus_geodata | coords | object
61 | res_bus | vm_pu | float64
62 | res_bus | va_degree | float64
63 | res_bus | p_mw | float64
64 | res_bus | q_mvar | float64
65 | res_line | p_from_mw | float64
66 | res_line | q_from_mvar | float64
67 | res_line | p_to_mw | float64
68 | res_line | q_to_mvar | float64
69 | res_line | pl_mw | float64
70 | res_line | ql_mvar | float64
71 | res_line | i_from_ka | float64
72 | res_line | i_to_ka | float64
73 | res_line | i_ka | float64
74 | res_line | vm_from_pu | float64
75 | res_line | va_from_degree | float64
76 | res_line | vm_to_pu | float64
77 | res_line | va_to_degree | float64
78 | res_line | loading_percent | float64
79 | res_trafo | p_hv_mw | float64
80 | res_trafo | q_hv_mvar | float64
81 | res_trafo | p_lv_mw | float64
82 | res_trafo | q_lv_mvar | float64
83 | res_trafo | pl_mw | float64
84 | res_trafo | ql_mvar | float64
85 | res_trafo | i_hv_ka | float64
86 | res_trafo | i_lv_ka | float64
87 | res_trafo | vm_hv_pu | float64
88 | res_trafo | va_hv_degree | float64
89 | res_trafo | vm_lv_pu | float64
90 | res_trafo | va_lv_degree | float64
91 | res_trafo | loading_percent | float64
92 | res_ext_grid | p_mw | float64
93 | res_ext_grid | q_mvar | float64
94 | res_load | p_mw | float64
95 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1